## Schedule B1
Schedule B1: Plant & Equipment supplied from abroad
Section-I | Extension of Two (02) 400kV AIS Bays at Existing 400kV Kaliakoir Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Code | Foreign Currency (in USD)
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR, CSD as phase switching mechanism with support structure |  | Set | 4
1A1.2 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 2
1A1.3 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 8
1A1.4 | Single-phase, 6-core, 400kV, 63kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 18
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 6
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 6
1A1.7 | Wave Trap,single phase, 420kV, 4000A, 1mH, 63kA/1s |  | No | 2
1A1.8 | Post type support insulators for 400kV busbar and switchgear |  | lot | 1
1A1.9 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectos with Nut-Bolts |  | lot | 1
1A1.10 | Steel Structures for gantry and equipment supports
a) | _Gantry Column including nut & bolts
i) | For Main Bus |  | Deleted
ii) | For Jack-Bus |  | No. | 8
b) | Gantry beam at Jack-Bus height including nut & bolts |  | No. | 8
c) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 2
ii) | DS without ES |  | set | 8
iii) | Bus ES |  | Deleted
iv) | CT |  | No | 18
v) | CVT/IVT |  | No | 6
vi) | LA |  | No | 6
vii) | Wave Trap |  | No | 2
viii) | PI |  | lot | 1
d) | Cable tray including fitting, fixing accessories |  | lot | 1
e) | All other necessary material and equipment required for completing 400 kV switchgear. |  | lot | 1
1A2 | 420kV Gas Insulated Switchgear |  | Not Applicable
1B | 245 kV AIS &GIS |  | Not Applicable
IC | 132 kV AIS &GIS |  | Not Applicable
1D | 33kV AIS &GIS |  | Not Applicable
1E | Power Transformer & Earthing/Auxiliary Transformer |  | Not Applicable
1F | Control, Protection, SAS and Metering
420kV Circuits
1F.1 | Control, Monitoring, Protection & Substation Automation Facility including event recording function for 400KV overhead line circuits bays
| Each Comprising |  | set | 2
| a) | One (01) set Control Mimic panel with all accessories including monitoring
| b) | Two (02) sets of Protection main relays, Main-1 & Main-2 with TTB
| c) | One (01) set of Auxiliary relays (TCS, Lockout etc)
| d) | One (01) set Complete Protection Panel including Auxuliary Relay Switches, wiring, lighting,heater, humidity sensor and other accessories
1F.2 | Modification / Extension of Busbar Protection
Each Comprising
| a | One (01) set of Complete Protection Panel including wiring, lighting, heater, humidity controller & other accessories (if required) | set | 2
| b | Two (02) sets of Protection main relay (BB-1 & BB-2 for each bus) (if required)
| i | One (01) lot of Bay unit with HMI
| ii | One (01) lot of Central unit with HMI including software modification
| c | One (01) lot of Selector Switch for Enabling/Disabling BBP,BFP, all function (if required)
1F.3 | Tarif metering
| a | Energy Meters (Main & Check) | set | 4
| b | Metering Panel including wiring, lighting, heater, humidity controller & other accessories (if required) | lot | 1
1F.4 | Substation Automation System
Each Comprising
| i. | BCU | Lot | 1
| a) | for 400kV Circuits as per protection SLD
| ii. | One (01) of Industrial Server PC -Deleted.
| iii. | 1 lot of Ethernet Switch for SAS
| iv. | 1 set of GPS system (if required)
| v. | One (01) lot of Renovation/Modification/Extension of Alarm Unit (if required)
| vi. | One (01) set of LCD Monitor, 55" or Large (Deleted)
| vii. | Two (02) sets of Printer, A4 Laser (One black & White, Other Color) (if required)
| viii. | One (01) set of Engineering PC for SAS & SCADA (if required)
| ix. | One (01) lot of Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | One (01) of complete Panel including wiring, lighting,heater,humidity controller & other accessories
| xi. | One (01) lot of other Accessories (if any)
1G | Digital Fault & Disturbance Recorder (Modification/Extension)
1G.1 | Each Comprising
| i. | One (01) set of DFDR processor-Deleted | Lot | 1
| ii. | Digital & Analog data acquisition channel
| a) | for 400kV Circuits as per protection SLD
| iii. | One (01) set of Ethernet Switch
| iv | One (01) set of GPS system (if required)
| v. | One (01) lot of Complete Panel including wiring, lighting, heater, humidity sensor & other accessories (if required)
| vi. | One (01) set of Engineering PC (if required)
| vii. | One (01) lot of Other Accessories (if any)
1H | SCADA system for Telecontrol and Telemetering
1H.1 | Modification/Extension of SCADA hardware & software
Each Comprising
| a) | Equipment at Substation for modification / extension of SCADA system | Lot | 1
| i. | One (01) set of Gateway (server, engineering software) (if required)
| ii. | One set of Ethernet Switch
| iii. | One set of Hardware Firewall
| iv. | Additional 33kV Feeder BCU - N/A
| v. | Complete Panel including wiring, lighting,heater, humidity controller & other accessories (if required)
| vi. | one lot Cables
| vii. | one lot Other Accessories
| b | Integration work with Master & Backup NLDC including Engineering & Commissioning | Refer to Schedule B4
1I | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1I.1 | One (01) complete lot of equipment for extension of existing fibre optic multiplexer equipment at local and remote end Substation for protection & communication, for required part of substation, shall be designed, supplied, delivered, installed, tested and commissioned and integrated into the existing system, under this contract. Fibre optic multiplexer equipment is to be provided for - |  | Lot | 1
21 (or 87 with built-in 21) relay for each transmission line protection (through fibre cores or backup PLC)
Distance relay carrier signal (main and back-up)
SCADA data from switchgear and control system through SAS
Hot-line telephone system
1I.2 | A lot of underground optical fibre (48 cores) cables from terminal box at gantry structure to MDF (Main distribution Frame) shall be designed, supplied, delivered, installed, tested and commissioned, including supply and installation of MDF and digital cables |  | Lot | 1
I1.3 | A complete lot of PLC equipment for extension of existing PLCC system at Kaliakoir Substation including line matching unit and necessary cables & other accessories for completing PLC communication. |  | Lot | 1
1I.4 | Installation,testing & commissioning |  | refer to schedule B4
1J | Power Cable |  | Deleted
1K | Multicore Cables
1K.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1L | Earthing and Lightning Protection
1L.1 | _Extension of Earthing system for 400kV Switchyard |  | lot | 1
1L.2 | _Extension of Lightning Protection System for 400kV Switchyard |  | lot | 1
1M | Batteries, chargers & DC distribution
1M.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel, MCC type and board/New DCDB panel (if required) |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers | lot | 1
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
a) | iii. | Insulation Monitoring system for complete DC system(if required) | lot | 1
1M.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
1N | LVAC Distribution
1N.1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
1N.2 | _Tariff metering at LV side(Main & Check) |  | Deleted
1O | Civil Works, Building and Foundation
1O.1 | Complete civil items required for outdoor works including boundary wall, gantry foundation, necessary land development. |  | Refer to Schedule B4
1O.2 | Complete civil works for new Switchyard Panel Room (SPR) & repair, modification works of other control houses for the extension work. |  | Refer to Schedule B4
1O.3 | Testing of Foundation |  | Refer to Schedule B4
1P | Lighting, small power, air conditioning and Ventilation
1P.1 | Extension of Lighting, small power and emergency DC lighting for new SPR and Local control houses. |  | lot | 1
1P.2 | Complete design, supply, installation and commissioning of equipment to provide Air Conditioning system (cassette type), Ventilation system for new SPR. |  | lot | 1
1P.3 | Extension of Lighting for ouside building for security, roadway, switchyard and emergency DC lighting. |  | lot | 1
1P.4 | Fire Fighting system for SPR |  | lot | 1
| Sub-Total Price of section-I (carried to Schedule-5: Grand Summary) | [6 empty] | Total of Section-2
Section-II | Mandatory Spares, Erection & Test Equipment | [6 empty] | (Carried to Schedule-5:Grand summary)
Mandatory Spares
2.1 | 420kV Switchgear
2.1.2 | 420kV Air Insulated Switchgear
2.1.2.1 | Complete SF6 gas, livetank type 420kV Circuit Breaker (single-pole operation type) suitable for Reactor switching |  | set | 1
2.1.2.2 | Complete SF6 gas, livetank type 420kV Circuit Breaker (gang operation type) |  | Deleted
2.1.2.3 | Complete 420kV disconnector switch (with & without ES) |  | set | 1
2.1.2.4 | Complete 420kV Current Transformer |  | Nos. | 1
2.1.2.5 | Complete 420kV capacitive VoltageTransformer |  | Nos. | 1
2.1.2.6 | 390kV Surge arrester |  | Nos. | 1
2.1.2.7 | Closing coils for CB (Offered Type) |  | Nos. | 1
2.1.2.8 | Tripping coils for CB (Offered Type) |  | Nos. | 2
2.1.2.9 | Motor for 420kV circuit breaker operating mechanism |  | Nos. | 1
2.1.2.10 | Motor for disconnector drive |  | Nos. | 1
2.1.2.11 | SF6 gas (45 kg) cylinder |  | Nos. | 1
2.1.2.12 | Contactors, relays, selector switches, push buttons, counters, heaters, humidity sensors etc., in motor drive mechanism and control cubicle, one of each type |  | set | 1
2.2 | 245kV Switchgear
2.2.1 | 245kV Gas Insulated Switchgear |  | Deleted
2.2.2 | 245kV Air Insulated Switchgear |  | Deleted
2.3 | Protection and Control
2.3.1 | Each type of protection relay for 400KV Extension of Kaiakoir Substation (Bidder to list) |  | set | 1
2.3.2 | Deleted
2.3.3 | Deleted
2.3.4 | Deleted
2.3.5 | Deleted |  | set | 1
2.3.6 | Tripping relays |  | sets | 1
2.3.7 | Each type of Auxiliary relays (Bidder to list) |  | sets | 1
2.3.8 | Each type of Trip circuit supervision relays (Bidder to list) |  | sets | 1
2.3.9 | Bay Control Unit |  | set | 1
2.3.10 | Each type of Switch (if applicable) |  | set | 1
2.3.11 | Each type of MCB |  | lot | 1
2.3.12 | Each type of Lamps |  | sets | 1
2.3.13 | Gateway Terminal |  | NA
2.3.14 | Ethernet Switches |  | nos. | 1
2.3.15 | Optical connectors (one for each) |  | lot | 1
2.3.16 | Relay Test Block & socket |  | No. | 1
2.3.17 | Heater |  | No. | 1
2.3.18 | Humidity Sensors |  | No. | 1
2.3.19 | Humidity stat and thermostat |  | No. | 1
2.3.20 | Ammeter |  | No. | Deleted
2.3.21 | Voltmeter |  | No. | Deleted
2.3.22 | Annunciator bulbs |  | No. | 1
2.3.23 | Bulbs for discrepancy switches |  | No. | 1
2.3.24 | Multifunction Meter | nos. | No. | 1
2.4 | DC & Charger Equipment
2.4.1 | Each type of Printed Circuit Board for Charger |  | Deleted
2.4.2 | Contactors, relays,selector switches, push buttons, counters, heaters, etc., one of each type |  | Deleted
2.4.3 | Miniature circuit breaker of each type and rating (Bidder to list all types) |  | lot | 1
2.5 | LVAC Equipment
2.5.1 | Miniature circuit breaker of each type and rating (Bidder to list all types) |  | lot | 1
2.5.2 | 3-phase LVAC board incoming MCCB |  | No. | Deleted
2.5.3 | 3-phase outgoing MCCBs |  | No. | 1
2.5.4 | 1-phase sets outgoing MCBs |  | No. | 1
2.5.5 | Contactors, relays,selector switches, push buttons, counters, heaters, etc., one of each type |  | lot | 1
2.6 | Power, Control and Auxiliary Cables |  | Deleted
2.6.1 | Power Cables (230kV) (for Dhamrai Substation) |  | meter
2.6.2 | Power Cables (36kV) |  | Deleted
2.6.3 | Control Cables, each type, 100m ( for Kaliakoir & Baghabari Substtaion) |  | lot
2.6.4 | LV Power cables, 100m of each type ( for Kaliakoir & Baghabari Substtaion) |  | lot
2.7 | Transformers and Shunt Reactor |  | Deleted
2.8 | Miscellaneous
2.8.1 | SF6 evacuation and filling plant |  | Deleted
2.8.2 | XLPE termination kits
2.8.3 | All types of control valves for SF6 gas |  | Deleted
2.8.4 | Rubber gaskets “O” rings and seals for SF6 gas |  | Deleted
2.8.5 | Post Type Insulator
i) | For 420kV |  | No. | 2
ii) | For 245kV |  | No. | Deleted
iii) | For 145kV |  | No. | Deleted
2.8.6 | Disc Insulator
i) | Each type of set of Disc Insulator |  | set | 2
2.8.7 | Conductor
i) | Each type of Bus Conductor |  | m | Delete
ii) | Each size of Rigid Tubular Conductor |  | m | Delete
2.8.8 | Clamp and Fitting
i) | Each type of Clamps and Fittings |  | set | 2
2.9 | Test O&M EQUIPMENT |  | Deleted
Sub-Total Price of section-II (carried to Schedule-5: Grand Summary)
|  |  | Name of Bidder |  | _________________________________________
|  |  | Signature of Bidder |  | _________________________________________
1 Specify currencies in accordance with ITB 19.1 of the BDS.
2 Bidders shall enter a code representing the country of origin of all imported plant and equipment.
3 Definition of route km: Route km is the transmission line distance between two terminal points in plan view. Route km is exclusive sag and other electrical
clearances, elevation differences etc. The Contractor shall incorporate all such extra costs in his unit rate.
4. Due to decrease or increase of any quantity mentioned above in unit "sets, nos., m, m², m³, liter, kg " during execution stage, the payment shall be at actual basis.
5. Detail design of GIS, Control building & SPR shall be finalized during execution stage, payment shall be at actual area size (sqmm) of the approved building
Country of Origin Declaration Form
Item | Description |  | Code | Country

## Schedule B2
Schedule B2: Plant & Equipment supplied from within Employer's Country
Section-I | Extension of Two (02) 400kV AIS Bays at Existing 400kV Kaliakoir Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in USD)
[5 empty] | Unit Price | Total Price
|  |  |  | (1) | (2) | (3) = (1) x (2)
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR, CSD as phase switching mechanism with support structure |  | Set | 4
1A1.2 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 2
1A1.3 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 8
1A1.4 | Single-phase, 6-core, 400kV, 63kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 18
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 6
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 6
1A1.7 | Wave Trap,single phase, 420kV, 4000A, 1mH, 63kA/1s |  | No | 2
1A1.8 | Post type support insulators for 400kV busbar and switchgear |  | lot | 1
1A1.9 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectos with Nut-Bolts |  | lot | 1
1A1.10 | Steel Structures for gantry and equipment supports
a) | _Gantry Column including nut & bolts
i) | For Main Bus |  | Deleted
ii) | For Jack-Bus |  | No. | 8
b) | Gantry beam at Jack-Bus height including nut & bolts |  | No. | 8
c) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 2
ii) | DS without ES |  | set | 8
iii) | Bus ES |  | Deleted
iv) | CT |  | No | 18
v) | CVT/IVT |  | No | 6
vi) | LA |  | No | 6
vii) | Wave Trap |  | No | 2
viii) | PI |  | lot | 1
d) | Cable tray including fitting, fixing accessories |  | lot | 1
e) | All other necessary material and equipment required for completing 400 kV switchgear. |  | lot | 1
1A2 | 420kV Gas Insulated Switchgear |  | Not Applicable
1B | 245 kV AIS &GIS |  | Not Applicable
IC | 132 kV AIS &GIS |  | Not Applicable
1D | 33kV AIS &GIS |  | Not Applicable
1E | Power Transformer & Earthing/Auxiliary Transformer |  | Not Applicable
1F | Control, Protection, SAS and Metering
420kV Circuits
1F.1 | Control, Monitoring, Protection & Substation Automation Facility including event recording function for 400KV overhead line circuits bays
| Each Comprising |  | set | 2
| a) | One (01) set Control Mimic panel with all accessories including monitoring
| b) | Two (02) sets of Protection main relays, Main-1 & Main-2 with TTB
| c) | One (01) set of Auxiliary relays (TCS, Lockout etc)
| d) | One (01) set Complete Protection Panel including Auxuliary Relay Switches, wiring, lighting,heater, humidity sensor and other accessories
1F.2 | Modification / Extension of Busbar Protection
Each Comprising
| a | One (01) set of Complete Protection Panel including wiring, lighting, heater, humidity controller & other accessories (if required) | set | 2
| b | Two (02) sets of Protection main relay (BB-1 & BB-2 for each bus) (if required)
| i | One (01) lot of Bay unit with HMI
| ii | One (01) lot of Central unit with HMI including software modification
| c | One (01) lot of Selector Switch for Enabling/Disabling BBP,BFP, all function (if required)
1F.3 | Tarif metering
| a | Energy Meters (Main & Check) | set | 4
| b | Metering Panel including wiring, lighting, heater, humidity controller & other accessories (if required) | lot | 1
1F.4 | Substation Automation System
Each Comprising
| i. | BCU | Lot | 1
| a) | for 400kV Circuits as per protection SLD
| ii. | One (01) of Industrial Server PC -Deleted.
| iii. | 1 lot of Ethernet Switch for SAS
| iv. | 1 set of GPS system (if required)
| v. | One (01) lot of Renovation/Modification/Extension of Alarm Unit (if required)
| vi. | One (01) set of LCD Monitor, 55" or Large (Deleted)
| vii. | Two (02) sets of Printer, A4 Laser (One black & White, Other Color) (if required)
| viii. | One (01) set of Engineering PC for SAS & SCADA (if required)
| ix. | One (01) lot of Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | One (01) of complete Panel including wiring, lighting,heater,humidity controller & other accessories
| xi. | One (01) lot of other Accessories (if any)
1G | Digital Fault & Disturbance Recorder (Modification/Extension)
1G.1 | Each Comprising
| i. | One (01) set of DFDR processor-Deleted | Lot | 1
| ii. | Digital & Analog data acquisition channel
| a) | for 400kV Circuits as per protection SLD
| iii. | One (01) set of Ethernet Switch
| iv | One (01) set of GPS system (if required)
| v. | One (01) lot of Complete Panel including wiring, lighting, heater, humidity sensor & other accessories (if required)
| vi. | One (01) set of Engineering PC (if required)
| vii. | One (01) lot of Other Accessories (if any)
1H | SCADA system for Telecontrol and Telemetering
1H.1 | Modification/Extension of SCADA hardware & software
Each Comprising
| a) | Equipment at Substation for modification / extension of SCADA system | Lot | 1
| i. | One (01) set of Gateway (server, engineering software) (if required)
| ii. | One set of Ethernet Switch
| iii. | One set of Hardware Firewall
| iv. | Additional 33kV Feeder BCU - N/A
| v. | Complete Panel including wiring, lighting,heater, humidity controller & other accessories (if required)
| vi. | one lot Cables
| vii. | one lot Other Accessories
| b | Integration work with Master & Backup NLDC including Engineering & Commissioning | Refer to Schedule B4
1I | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1I.1 | One (01) complete lot of equipment for extension of existing fibre optic multiplexer equipment at local and remote end Substation for protection & communication, for required part of substation, shall be designed, supplied, delivered, installed, tested and commissioned and integrated into the existing system, under this contract. Fibre optic multiplexer equipment is to be provided for - |  | Lot | 1
21 (or 87 with built-in 21) relay for each transmission line protection (through fibre cores or backup PLC)
Distance relay carrier signal (main and back-up)
SCADA data from switchgear and control system through SAS
Hot-line telephone system
1I.2 | A lot of underground optical fibre (48 cores) cables from terminal box at gantry structure to MDF (Main distribution Frame) shall be designed, supplied, delivered, installed, tested and commissioned, including supply and installation of MDF and digital cables |  | Lot | 1
I1.3 | A complete lot of PLC equipment for extension of existing PLCC system at Kaliakoir Substation including line matching unit and necessary cables & other accessories for completing PLC communication. |  | Lot | 1
1I.4 | Installation,testing & commissioning |  | refer to schedule B4
1J | Power Cable |  | Deleted
1K | Multicore Cables
1K.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1L | Earthing and Lightning Protection
1L.1 | _Extension of Earthing system for 400kV Switchyard |  | lot | 1
1L.2 | _Extension of Lightning Protection System for 400kV Switchyard |  | lot | 1
1M | Batteries, chargers & DC distribution
1M.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel, MCC type and board/New DCDB panel (if required) |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers | lot | 1
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
a) | iii. | Insulation Monitoring system for complete DC system(if required) | lot | 1
1M.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
1N | LVAC Distribution
1N.1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
1N.2 | _Tariff metering at LV side(Main & Check) |  | Deleted
1O | Civil Works, Building and Foundation
1O.1 | Complete civil items required for outdoor works including boundary wall, gantry foundation, necessary land development. |  | Refer to Schedule B4
1O.2 | Complete civil works for new Switchyard Panel Room (SPR) & repair, modification works of other control houses for the extension work. |  | Refer to Schedule B4
1O.3 | Testing of Foundation |  | Refer to Schedule B4
1P | Lighting, small power, air conditioning and Ventilation
1P.1 | Extension of Lighting, small power and emergency DC lighting for new SPR and Local control houses. |  | lot | 1
1P.2 | Complete design, supply, installation and commissioning of equipment to provide Air Conditioning system (cassette type), Ventilation system for new SPR. |  | lot | 1
1P.3 | Extension of Lighting for ouside building for security, roadway, switchyard and emergency DC lighting. |  | lot | 1
1P.4 | Fire Fighting system for SPR |  | lot | 1
Sub-Total Price of section-I (carried to Schedule-5: Grand Summary)
Section-II | Mandatory Spares, Erection & Test Equipment
Mandatory Spares
2.1 | 420kV Switchgear
2.1.2 | 420kV Air Insulated Switchgear
2.1.2.1 | Complete SF6 gas, livetank type 420kV Circuit Breaker (single-pole operation type) suitable for Reactor switching |  | set | 1
2.1.2.2 | Complete SF6 gas, livetank type 420kV Circuit Breaker (gang operation type) |  | Deleted
2.1.2.3 | Complete 420kV disconnector switch (with & without ES) |  | set | 1
2.1.2.4 | Complete 420kV Current Transformer |  | Nos. | 1
2.1.2.5 | Complete 420kV capacitive VoltageTransformer |  | Nos. | 1
2.1.2.6 | 390kV Surge arrester |  | Nos. | 1
2.1.2.7 | Closing coils for CB (Offered Type) |  | Nos. | 1
2.1.2.8 | Tripping coils for CB (Offered Type) |  | Nos. | 2
2.1.2.9 | Motor for 420kV circuit breaker operating mechanism |  | Nos. | 1
2.1.2.10 | Motor for disconnector drive |  | Nos. | 1
2.1.2.11 | SF6 gas (45 kg) cylinder |  | Nos. | 1
2.1.2.12 | Contactors, relays, selector switches, push buttons, counters, heaters, humidity sensors etc., in motor drive mechanism and control cubicle, one of each type |  | set | 1
2.2 | 245kV Switchgear
2.2.1 | 245kV Gas Insulated Switchgear |  | Deleted
2.2.2 | 245kV Air Insulated Switchgear |  | Deleted
2.3 | Protection and Control
2.3.1 | Each type of protection relay for 400KV Extension of Kaiakoir Substation (Bidder to list) |  | set | 1
2.3.2 | Deleted
2.3.3 | Deleted
2.3.4 | Deleted
2.3.5 | Deleted |  | set | 1
2.3.6 | Tripping relays |  | sets | 1
2.3.7 | Each type of Auxiliary relays (Bidder to list) |  | sets | 1
2.3.8 | Each type of Trip circuit supervision relays (Bidder to list) |  | sets | 1
2.3.9 | Bay Control Unit |  | set | 1
2.3.10 | Each type of Switch (if applicable) |  | set | 1
2.3.11 | Each type of MCB |  | lot | 1
2.3.12 | Each type of Lamps |  | sets | 1
2.3.13 | Gateway Terminal |  | NA
2.3.14 | Ethernet Switches |  | nos. | 1
2.3.15 | Optical connectors (one for each) |  | lot | 1
2.3.16 | Relay Test Block & socket |  | No. | 1
2.3.17 | Heater |  | No. | 1
2.3.18 | Humidity Sensors |  | No. | 1
2.3.19 | Humidity stat and thermostat |  | No. | 1
2.3.20 | Ammeter |  | No. | Deleted
2.3.21 | Voltmeter |  | No. | Deleted
2.3.22 | Annunciator bulbs |  | No. | 1
2.3.23 | Bulbs for discrepancy switches |  | No. | 1
2.3.24 | Multifunction Meter | nos. | No. | 1
2.4 | DC & Charger Equipment
2.4.1 | Each type of Printed Circuit Board for Charger |  | Deleted
2.4.2 | Contactors, relays,selector switches, push buttons, counters, heaters, etc., one of each type |  | Deleted
2.4.3 | Miniature circuit breaker of each type and rating (Bidder to list all types) |  | lot | 1
2.5 | LVAC Equipment
2.5.1 | Miniature circuit breaker of each type and rating (Bidder to list all types) |  | lot | 1
2.5.2 | 3-phase LVAC board incoming MCCB |  | No. | Deleted
2.5.3 | 3-phase outgoing MCCBs |  | No. | 1
2.5.4 | 1-phase sets outgoing MCBs |  | No. | 1
2.5.5 | Contactors, relays,selector switches, push buttons, counters, heaters, etc., one of each type |  | lot | 1
2.6 | Power, Control and Auxiliary Cables |  | Deleted
2.6.1 | Power Cables (230kV) (for Dhamrai Substation) |  | meter
2.6.2 | Power Cables (36kV) |  | Deleted
2.6.3 | Control Cables, each type, 100m ( for Kaliakoir & Baghabari Substtaion) |  | lot
2.6.4 | LV Power cables, 100m of each type ( for Kaliakoir & Baghabari Substtaion) |  | lot
2.7 | Transformers and Shunt Reactor |  | Deleted
2.8 | Miscellaneous
2.8.1 | SF6 evacuation and filling plant |  | Deleted
2.8.2 | XLPE termination kits
2.8.3 | All types of control valves for SF6 gas |  | Deleted
2.8.4 | Rubber gaskets “O” rings and seals for SF6 gas |  | Deleted
2.8.5 | Post Type Insulator
i) | For 420kV |  | No. | 2
ii) | For 245kV |  | No. | Deleted
iii) | For 145kV |  | No. | Deleted
2.8.6 | Disc Insulator
i) | Each type of set of Disc Insulator |  | set | 2
2.8.7 | Conductor
i) | Each type of Bus Conductor |  | m | Delete
ii) | Each size of Rigid Tubular Conductor |  | m | Delete
2.8.8 | Clamp and Fitting
i) | Each type of Clamps and Fittings |  | set | 2
2.9 | Test O&M EQUIPMENT |  | Deleted
Sub-Total Price of section-II (carried to Schedule-5: Grand Summary)
Name of Bidder
Signature of Bidder
1 Specify currencies in accordance with ITB 19.1 of the BDS.
2 Bidders shall enter a code representing the country of origin of all imported plant and equipment.
3 Definition of route km: Route km is the transmission line distance between two terminal points in plan view. Route km is exclusive sag and other electrical
clearances, elevation differences etc. The Contractor shall incorporate all such extra costs in his unit rate.
4. Due to decrease or increase of any quantity mentioned above in unit "sets, nos., m, m², m³, liter, kg " during execution stage, the payment shall be at actual basis.
Country of Origin Declaration Form
Item | Description |  | Code | Country

## Schedule B3
Schedule B3: Design Services
Section-I | Extension of Two (02) 400kV AIS Bays at Existing 400kV Kaliakoir Substation
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in USD)
|  |  |  | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion
|  |  | (1) | (2) | (3) = (1) x (2)
1 | Design and engineering services of the substation, local and foreign part | Lump sum | 1
2 | LA rating, PIR rating, Breaker Selection analysis for bay extension in Kalikoir 400kV Substation | Lump sum | 1
3 | Relay Co-ordination study for bay extension in the Substation with software demonstration | Lump sum | 1
Sub-Total Price of section-I (carried to Schedule-5: Grand Summary)
|  | Name of Bidder |  | ______________________________________________________________
|  | Signature of Bidder |  | _______________________________________________________________
1. Specify currencies in accordance with ITB 19.1 of the BDS.
2. Bidder shall quote the amount considering clause 14.1 of section 8(Special Conditions of Contract), Volume 1 of 3 of the bidding document. The amount quoted by
bidder is subject to arithmatic correction by Employer as required.

## Schedule B4
Schedule B4: Installation and Other Services
01. Extension of Two (02) 400kV AIS Bays at Existing 400kV Kaliakoir Substation
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in USD)
[5 empty] | Unit Price | Total Price
|  |  |  | (1) | (2) | (3) = (1) x (2)
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR, CSD as phase switching mechanism with support structure |  | Set | 4
1A1.2 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 2
1A1.3 | 420kV, 4000A, 63kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 8
1A1.4 | Single-phase, 6-core, 400kV, 63kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 18
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 6
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 6
1A1.7 | Wave Trap,single phase, 420kV, 4000A, 1mH, 63kA/1s |  | No | 2
1A1.8 | Post type support insulators for 400kV busbar and switchgear |  | lot | 1
1A1.9 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectos with Nut-Bolts |  | lot | 1
1A1.10 | Steel Structures for gantry and equipment supports
a) | _Gantry Column including nut & bolts
i) | For Main Bus |  | Deleted
ii) | For Jack-Bus |  | No. | 8
b) | Gantry beam at Jack-Bus height including nut & bolts |  | No. | 8
c) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 2
ii) | DS without ES |  | set | 8
iii) | Bus ES |  | Deleted
iv) | CT |  | No | 18
v) | CVT/IVT |  | No | 6
vi) | LA |  | No | 6
vii) | Wave Trap |  | No | 2
viii) | PI |  | lot | 1
d) | Cable tray including fitting, fixing accessories |  | lot | 1
e) | All other necessary material and equipment required for completing 400 kV switchgear. |  | lot | 1
1A2 | 420kV Gas Insulated Switchgear |  | Not Applicable
1B | 245 kV AIS &GIS |  | Not Applicable
IC | 132 kV AIS &GIS |  | Not Applicable
1D | 33kV AIS &GIS |  | Not Applicable
1E | Power Transformer & Earthing/Auxiliary Transformer |  | Not Applicable
1F | Control, Protection, SAS and Metering
420kV Circuits
1F.1 | Control, Monitoring, Protection & Substation Automation Facility including event recording function for 400KV overhead line circuits bays
| Each Comprising |  | set | 2
| a) | One (01) set Control Mimic panel with all accessories including monitoring
| b) | Two (02) sets of Protection main relays, Main-1 & Main-2 with TTB
| c) | One (01) set of Auxiliary relays (TCS, Lockout etc)
| d) | One (01) set Complete Protection Panel including Auxuliary Relay Switches, wiring, lighting,heater, humidity sensor and other accessories
1F.2 | Modification / Extension of Busbar Protection
Each Comprising
| a | One (01) set of Complete Protection Panel including wiring, lighting, heater, humidity controller & other accessories (if required) | set | 2
| b | Two (02) sets of Protection main relay (BB-1 & BB-2 for each bus) (if required)
| i | One (01) lot of Bay unit with HMI
| ii | One (01) lot of Central unit with HMI including software modification
| c | One (01) lot of Selector Switch for Enabling/Disabling BBP,BFP, all function (if required)
1F.3 | Tarif metering
| a | Energy Meters (Main & Check) | set | 4
| b | Metering Panel including wiring, lighting, heater, humidity controller & other accessories (if required) | lot | 1
1F.4 | Substation Automation System
Each Comprising
| i. | BCU | Lot | 1
| a) | for 400kV Circuits as per protection SLD
| ii. | One (01) of Industrial Server PC -Deleted.
| iii. | 1 lot of Ethernet Switch for SAS
| iv. | 1 set of GPS system (if required)
| v. | One (01) lot of Renovation/Modification/Extension of Alarm Unit (if required)
| vi. | One (01) set of LCD Monitor, 55" or Large (Deleted)
| vii. | Two (02) sets of Printer, A4 Laser (One black & White, Other Color) (if required)
| viii. | One (01) set of Engineering PC for SAS & SCADA (if required)
| ix. | One (01) lot of Cable (Fiber Optic, Ethernet, Copper etc.)
| x. | One (01) of complete Panel including wiring, lighting,heater,humidity controller & other accessories
| xi. | One (01) lot of other Accessories (if any)
1G | Digital Fault & Disturbance Recorder (Modification/Extension)
1G.1 | Each Comprising
| i. | One (01) set of DFDR processor-Deleted | Lot | 1
| ii. | Digital & Analog data acquisition channel
| a) | for 400kV Circuits as per protection SLD
| iii. | One (01) set of Ethernet Switch
| iv | One (01) set of GPS system (if required)
| v. | One (01) lot of Complete Panel including wiring, lighting, heater, humidity sensor & other accessories (if required)
| vi. | One (01) set of Engineering PC (if required)
| vii. | One (01) lot of Other Accessories (if any)
1H | SCADA system for Telecontrol and Telemetering
1H.1 | Modification/Extension of SCADA hardware & software
Each Comprising
| a) | Equipment at Substation for modification / extension of SCADA system | Lot | 1
| i. | One (01) set of Gateway (server, engineering software) (if required)
| ii. | One set of Ethernet Switch
| iii. | One set of Hardware Firewall
| iv. | Additional 33kV Feeder BCU - N/A
| v. | Complete Panel including wiring, lighting,heater, humidity controller & other accessories (if required)
| vi. | one lot Cables
| vii. | one lot Other Accessories
| b | Integration work with Master & Backup NLDC including Engineering & Commissioning | Refer to Schedule B4
1I | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1I.1 | One (01) complete lot of equipment for extension of existing fibre optic multiplexer equipment at local and remote end Substation for protection & communication, for required part of substation, shall be designed, supplied, delivered, installed, tested and commissioned and integrated into the existing system, under this contract. Fibre optic multiplexer equipment is to be provided for - |  | Lot | 1
21 (or 87 with built-in 21) relay for each transmission line protection (through fibre cores or backup PLC)
Distance relay carrier signal (main and back-up)
SCADA data from switchgear and control system through SAS
Hot-line telephone system
1I.2 | A lot of underground optical fibre (48 cores) cables from terminal box at gantry structure to MDF (Main distribution Frame) shall be designed, supplied, delivered, installed, tested and commissioned, including supply and installation of MDF and digital cables |  | Lot | 1
I1.3 | A complete lot of PLC equipment for extension of existing PLCC system at Kaliakoir Substation including line matching unit and necessary cables & other accessories for completing PLC communication. |  | Lot | 1
1I.4 | Installation,testing & commissioning |  | refer to schedule B4
1J | Power Cable |  | Deleted
1K | Multicore Cables
1K.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1L | Earthing and Lightning Protection
1L.1 | _Extension of Earthing system for 400kV Switchyard |  | lot | 1
1L.2 | _Extension of Lightning Protection System for 400kV Switchyard |  | lot | 1
1M | Batteries, chargers & DC distribution
1M.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel, MCC type and board/New DCDB panel (if required) |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers | lot | 1
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
a) | iii. | Insulation Monitoring system for complete DC system(if required) | lot | 1
1M.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
1N | LVAC Distribution
1N.1 | _Extension of AC 415V or 240V distribution panels (MCC type) |  | lot | 1
1N.2 | _Tariff metering at LV side(Main & Check) |  | Deleted
1O | Civil Works, Building and Foundation
1O.1 | Complete civil items required for outdoor works including boundary wall, necessary land development and slope protection
| i | Outdoor gantry foundation 400kV switchyard | No. | 8
| ii | Outdoor equipment foundation 400kV switchyard
| a) | CB | set | 4
| b) | DS with ES | set | 2
| c) | DS without ES | set | 8
| d) | BUS ES | Deleted
| e) | CT | No. | 18
| f) | CVT | No. | 6
| g) | LA | No. | 6
| h) | WaveTrap | No. | 2
| i) | PI | lot | 1
| iii | Indoor equipment foundation 400kV switchyard | Deleted
| iv | Outdoor gantry foundation 230kV switchyard | Deleted
| v | Outdoor equipment foundation 230kV switchyard | Deleted
| vi | Indoor equipment foundation 132kV switchyard | Deleted
| vii | Outdoor gantry foundation 33kV switchyard including 33kV Bus | Deleted
| viii | Outdoor equipment foundation 33kV switchyard | Deleted
| ix | Transformer foundation including oilpit & carrage way | Deleted
| x | Blast wall with foundation | Deleted
| xi | Property Line Demarkation | Deleted
| xii | Security Boundary Wall for overall plan | Deleted
| xiii | Substation Main gate | Deleted
| xiv | _Chainlink Fencing including three (3) personal gates | Deleted
| xv | Approach road (6m width) | Deleted
| xvi | Box Culvert | Deleted
| xvii | Internal road
| a) | 8m wide road | m | 10
| b) | 6m wide road | m | 20
| c) | 4.5m wide road | m | 100
| d) | 2.5m wide road | m | 200
| xviii | Surface drain | Deleted
| xix | Cable Trench / Tunnel with soakpit for
| a) | LV power & control cable | m | 500
| b) | HV Power cable | m | 0
| xx | _Whole scope area with necessary land development, surface finishing with drainage system | lot | 1
| xxi | Gravelling in switchyard area | sqm | 15000
| xxii | Septic tank, sowak way | Deleted
| xxiii | Pump house including deep tubewell, motor, pump, water reservoir, water pipe line etc. | Deleted
| xxiv | Guard house | Deleted
| xxv | sentry post | no | 1
| xxvi | car port | Deleted
1O.2 | Complete civil works for Control Room, Operation & Panel Room
| a) | Modification works for Control Room | Lot | 1
| b) | Complete civil works for 1 No. 400kV Panel Room with battery
| i) | _Foundation works | lot | 1
| ii) | _Super structures | lot | 1
| iii) | _All finish works | lot | 1
1O.3 | Testing of Foundation
| i) | _Compression Test | No. | 1
| ii) | _ Uplift Test | No. | 1
1P | Lighting, small power, air conditioning and Ventilation
1P.1 | Extension of Lighting, small power and emergency DC lighting for new SPR and other control houses. |  | lot | 1
1P.2 | Complete design, supply, installation and commissioning of equipment to provide Air Conditioning system (cassette type), Ventilation system for new SPR. |  | lot | 1
1P.3 | Extension of Lighting for ouside building for security, roadway, switchyard and emergency DC lighting. |  | lot | 1
1P.4 | Fire Fighting system for SPR |  | lot | 1
Sub-Total Price of section-I (carried to Schedule-5: Grand Summary)
|  |  | Name of Bidder |  | ______________________________________
|  |  | Signature of Bidder |  | _____________________________________
1 The bidder shall not keep price for this item blank and shall not write included. The prices are fixed for the mentioned items, but the Payments will be made
from the quoted amount on the basis of percentage of test and inspection completed for an item upon submission of relevant documents. The Contractor may
need to submit justification and price breakup in support of the quoted price against these items during the contract execution.
2. Due to decrease or increase of any quantity mentioned above in unit "sets, nos., m, m², m³, liter, kg " during execution stage, the payment shall be at actual basis.
3. Detail design of GIS, Control building & SPR shall be finalized during execution stage, payment shall be at actual area size (sqmm) of the approved building

## Schedule B5
Schedules of Rates and Prices
Schedule 5: Grand Summary
Schedule No | Description | Total Price
|  | Foreign Currency (in……….) | Local Currency (in BDT)
Section-I:
Schedule No. 1: | Plant & Equipment Supplied from Abroad
Schedule No. 2: | Plant & Equipment Supplied from within the Employer’s Country
Schedule No. 3: | Design Services
Schedule No. 4: | Installation and Other Services
Total of Section-I
Section-2: Mandatory Spares, Erection & Test Equipment
Schedule No. 1: | Plant & Equipment Supplied from Abroad
Schedule No. 2: | Plant & Equipment Supplied from within the Employer’s Country
Total of Section-2
GRAND TOTAL (Schedule No.1 to Schedule No.4 (to Letter of Price Bid)
| Name of Bidder | ---------------------------------------------------
| Signature of Bidder | ---------------------------------------------------

## Schedule B6
Schedule B6: Recommended Spare Parts
No | Description | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | EXW | EXW | EXW | EXW
|  |  | (1) | (2) | (3)=(1)x(2) | (4) | (5)=(1)x(4)
|  |  |  | Name of Bidder |  | ______________________________
|  |  |  | Signature of Bidder |  | ______________________________
1. Specify currencies in accordance with ITB 19.1 of the BDS.