## Schedule B1
Schedule B1: Plant & Equipment Supplied from Abroad
[6 empty] | Foreign Currency (in .......) |  | Remarks
No. | Equipment |  | Quantity (1) | Unit | Code | Unit Price CIP (2) | Total Price CIP (3)=(1)x(2)
Section-1: 132/33kV transformer replacement at Joydebpur 132/33kV Substation
1A | Power Transformer (replaced)
1A1 | 132/33kV, 80/120 MVA (ONAN/ONAF), three phase outdoor type power transformers |  | 2 | set
1B | 132 Air Insulated Switchgear (AIS) (Replaced)
1B1 | Deleted
1B2 | Deleted
1B3 | Single-phase, 4-core, multi ratio, 132kV, 40kA/1sec, 50Hz, 650kVp BIL, outdoor, post type current transformer |  | 6 | nos.
1C | 132 Gas Insulated Switchgear (GIS) (Replaced)
1C1 | Single-phase, 6-core, multi ratio, 132kV, 40kA/1sec, 50Hz, 650kVp BIL, current transformer |  | 3 | nos.
1D | 33kV Air Insulated Switches (AIS)
1D1 | Deleted
1D2 | Deleted
1E | Flexible Conductor, clamps & connectors for busbar,jackbus, jumper & equipment connection(132kV & 33kV)
10 | i) | Flexible conductor for jackbus,jumper,equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
1F | Insulator & fittings
1F1 | i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
1G | Steel structures & Cable tray
1G1 | i) | Modification of existing Equipment support structures including nut & bolts (132kV & 33kV) | 1 | lot
| v) | Cable tray including fitting, fixing accessories | 1 | lot
1H | HV Power Cables, Cable Termination and GIS
1H1 | Deleted
1H2 | Deleted
1I | Control, Protection SAS & Metering
For 132kV control & Protection
1I1 | Modification of existing of control and protection panel to integrate the new replaced transformers for 132kV Side of Transformer Bay |  | 2 | set
1I2 | Tap changer panel for 132kV Side of Transformer Bay |  | 2 | set
1I3 | Deleted
For 33kV control & Protection
1I4 | Modification of existing control and protection panel to integrate the new replaced transformers for 33kV Side of Transformer Bay |  | 2 | set
1J | Multicore Cables
1J1 | Multicore, XLPE, LV Power & Control Cable for control, protection,metering & power circuits
| i) | LV Control Cable | 1 | lot
| ii) | LV Power Cable | 1 | lot
1K | Earthing & lightning protection
1K1 | Earthing system for renovation portion |  | 1 | lot
1L | Dismantle arrengement
1L1 | i) | Removal, Shifting & Handover 75 MVA three phase power transformer | Refer to Schedule B4
| ii) | Dismantle of Existing equipment & hand over to store (132 kV)
| a) | CT
| iii) | Dismantle of Existing equipment structure & hand over to store (132 kV)
| iv) | Dismantling of existing RTCC panels
| v) | Dismantle of Existing equipment structure & hand over to store (33kV)
1M | Civil Works
1M1 | i) | New 132kV power transformer foundation (shallow/pile foundation) including oil pit | Refer to Schedule B4
| ii) | Modification of 132kV power transformer foundation
| iii) | Modification of existing/new outdoor equipment foundation in 132kV switchyard
| iv) | Modification of existing/new outdoor equipment foundation in 33kV switchyard
| v) | Dismantiling & removal of existing structure & civil foundation as required
1M2 | i) | Dismantiling & removal of existing transformer pad & foundation as required.
Subtotal price for 132/33kV transformer replacement at Joydebpur 132/33kV Substation carried to Schedule 5
Section-2: 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation
2A | Capacitor Bank
2A1 | Capacitor Bank (33kV, 15 MVar, 50 Hz) |  | 2 | set
2A2 | Damping Reactor (0.2%, 36 kV, 410A) |  | 6 | nos.
2A3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 |  | 2 | nos.
2A4 | Key interlocking system |  | 2 | set
2B | 33kV Switchgear
2B1 | 33kV, 1250A, 31.5kA/1sec, 50Hz, 170kVp BIL, outdoor type, gang pole operated Vacuum Circuit Breakers with spring-stored energy operating mechanism |  | 2 | set
2B2 | 33kV, 1250A, 31.5kA/1sec, 50Hz, 170kVp BIL, post type, disconnectors without earth switch |  | 2 | set
2B3 | Single-phase, 3-core, 33kV, 31.5kA/1sec, 50Hz, 170kVp BIL, post type current transformer |  | 6 | nos.
2B4 | 30kV rated voltage, 10kA nominal discharge current, 50Hz, Heavy duty station class, single phase surge arresters |  | 12 | nos.
2C | Control, Protection and Metering
2C1 | 33kV Control, Metering and Protection Panel with associated meters and relays |  | 2 | set
2D | LV and HV cable including accessories
2D1 | 33kV 1Cx500mm2 XLPE Power cable with laying |  | 600 | m
2D2 | 33kV Cable termination kit with connection material for both ends (three phase per set) |  | 4 | set
2D3 | Multi-core cable for control, indication and protection |  | 1 | lot
2E | Conductor, Steel Structure, Insulator & Hardware & Fittings
2E1 | Flexible Conductor/Al Tube, clamps & connectors for main bus, Jackbus,Jumper & equipment Connection
| i) | Flexible Conductor/Al Tube for main bus, jackbus, jumper, equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
2E2 | Insulator & Fittings
| i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
2E3 | Steel structures & cable tray
| i) | Gantry structure with nut & bolts
| a) | Deleted
| b) | Deleted
| iii) | Equipment support structures including nut & bolts
| a) | Capacitor bank | 2 | set
| b) | Reactor | 6 | nos.
| c) | NCT | 2 | nos.
| d) | CB | 2 | set
| e) | DS | 2 | set
| f) | CT | 6 | nos.
| g) | LA | 12 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 4 | set
| iv) | Deleted
| v) | LV Cable tray including fitting, fixing accessories | 1 | lot
2F | Earthing and Lightning Protection System
2F1 | Earthing system for extended part |  | 1 | lot
2F2 | Lighting Protection System for extended part |  | 1 | lot
2G | DC Distribution
2G1 | Extension of DC Distribution System with necessary material for new bays/equipment |  | 1 | lot
2H | LVAC Distribution
2H1 | Extension of LVAC Distribution System with necessary material for new bays/equipment |  | 1 | lot
2I | Lighting, Small Power
2I1 | Outdoor switchyard Lighting, Small Power
| i) | Outdoor Small power (extended part) | 1 | lot
| ii) | Outdoor Lighting (extended part) | 1 | lot
2J | Civil Works
2J1 | Complete outdoor civil works |  | Refer to Schedule B4
| i) | Outdoor gantry foundation in 33kV switchyard
| a) | Deleted
| ii) | Outdoor equiment foundation in 33kV switchyard
| a) | Capacitor bank
| b) | Reactor
| c) | NCT
| d) | CB
| e) | DS
| f) | CT
| g) | LA
| h) | Outdoor type 33kV XLPE cable termination
| iii) | Cable trench with soakpit
| a) | Extension of LV cable trenches
| iv) | Internal road
| a) | Extension of 3m wide road
| v) | Switchyard surface finishing with drainage system
| vi) | Gravelling in switchyard area
| vii) | Chain linked fence with gate around capacitor bank
| viii) | Modification of existing control room to accommodate new panels
Subtotal price for 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation carried to Schedule 5
Section-3: 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation
3A | Capacitor Bank
3A1 | Capacitor Bank (33kV, 15 MVar, 50 Hz) |  | 3 | set
3A2 | Damping Reactor (6%, 36 kV, 410A) |  | 9 | nos.
3A3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 |  | 3 | nos.
3A4 | Key interlocking system |  | 3 | set
3A5 | 30kV rated voltage, 10kA nominal discharge current, 50Hz, Heavy duty station class, single phase surge arresters |  | 9 | nos.
3B | 33kV GIS Switchgear
3B1 | 36kV GIS Line Feeder Bay |  | 2 | set
3C | Control, Protection and Metering
3C1 | 33kV Control, Metering and Protection Panel with associated meters and relays |  | 3 | set
3D | LV and HV cable including accessories
3D1 | 33kV 1Cx500mm2 XLPE Power cable with laying |  | 600 | m
3D2 | 33kV Cable termination kit with connection material for at capacitor ends (three phase per set) |  | 3 | set
3D3 | Multi-core cable for control, indication and protection |  | 1 | lot
3E | Conductor, Steel Structure, Insulator & Hardware & Fittings
3E1 | Flexible Conductor/Al Tube, clamps & connectors for main bus, Jackbus,Jumper & equipment Connection
| i) | Flexible Conductor/Al Tube for main bus, jackbus, jumper, equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
3E2 | Insulator & Fittings
| i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
3E3 | Steel structures & cable tray
| i) | Gantry structure with nut & bolts
| a) | Deleted
| b) | Deleted
| iii) | Equipment support structures including nut & bolts
| a) | Capacitor bank | 3 | set
| b) | Reactor | 9 | nos.
| c) | NCT | 3 | nos.
| d) | LA | 9 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 3 | set
| iv) | Deleted
| v) | LV Cable tray including fitting, fixing accessories | 1 | lot
3F | Earthing and Lightning Protection System
3F1 | Earthing system for extended part |  | 1 | lot
3F2 | Lighting Protection System for extended part |  | 1 | lot
3G | DC Distribution
3G1 | Extension of DC Distribution System with necessary material for new bays/equipment |  | 1 | lot
3H | LVAC Distribution
3H1 | Extension of LVAC Distribution System with necessary material for new bays/equipment |  | 1 | lot
3I | Lighting, Small Power
3I1 | Outdoor switchyard Lighting, Small Power
| i) | Outdoor Small power (extended part) | 1 | lot
| ii) | Outdoor Lighting (extended part) | 1 | lot
3J | Civil Works
3J1 | Complete outdoor civil works |  | Refer to Schedule B4
| i) | Outdoor gantry foundation in 33kV switchyard
| a) | Deleted
| ii) | Outdoor equiment foundation in 33kV switchyard
| a) | Capacitor bank
| b) | Reactor
| c) | NCT
| d) | LA
| e) | Outdoor type 33kV XLPE cable termination
| iii) | Cable trench with soakpit
| a) | Extension of LV cable trenches
| iv) | Internal road
| a) | Extension of 3m wide road
| v) | Switchyard surface finishing with drainage system
| vi) | Gravelling in switchyard area
| vii) | Chain linked fence with gate around capacitor bank
| viii) | Modification of existing control room to accommodate new panels
Subtotal price for 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation carried to Schedule 5

## Schedule B1_Spare
Schedule B1: Mandatory Spare, Maintanence & Test Equipement Supplied from Outside the Employer's Country
Item No. | Description of Equipment Requirement | Unit | Quantity | Code | Foreign Currency (in……….) |  | Remark
[5 empty] | Unit Price | Total Price
[5 empty] | CIP | CIP
|  |  | (1) |  | (2) | (3) = (1) x (2)
CS | 36kV Capacitor bank
CS1 | Capacitor Units for offered type (5% of total supplied units) | lot | 1
CS2 | Damping Reactor (0.2%, 36 kV, 410A) | no | 3
CS3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 | no | 2
Total Price carried to Summary of Price Schedule (Spare, Maintanence & Test Equipement of S/S)

## Schedule B2
Schedule B2: Plant & Equipment Supplied from within the Employer's Country
[6 empty] | Local Currency (BDT) |  | Remarks
No. | Equipment |  | Quantity (1) | Unit | Code | Unit Price EXW (2) | Total Price EXW (3)=(1)x(2)
Section-1: 132/33kV transformer replacement at Joydebpur 132/33kV Substation
1A | Power Transformer (replaced)
1A1 | 132/33kV, 80/120 MVA (ONAN/ONAF), three phase outdoor type power transformers |  | 2 | set
1B | 132 Air Insulated Switchgear (AIS) (Replaced)
1B1 | Deleted
1B2 | Deleted
1B3 | Single-phase, 4-core, multi ratio, 132kV, 40kA/1sec, 50Hz, 650kVp BIL, outdoor, post type current transformer |  | 6 | nos.
1C | 132 Gas Insulated Switchgear (GIS) (Replaced)
1C1 | Single-phase, 6-core, multi ratio, 132kV, 40kA/1sec, 50Hz, 650kVp BIL, current transformer |  | 3 | nos.
1D | 33kV Air Insulated Switches (AIS)
1D1 | Deleted
1D2 | Deleted
1E | Flexible Conductor, clamps & connectors for busbar,jackbus, jumper & equipment connection(132kV & 33kV)
10 | i) | Flexible conductor for jackbus,jumper,equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
1F | Insulator & fittings
1F1 | i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
1G | Steel structures & Cable tray
1G1 | i) | Modification of existing Equipment support structures including nut & bolts (132kV & 33kV) | 1 | lot
| v) | Cable tray including fitting, fixing accessories | 1 | lot
1H | HV Power Cables, Cable Termination and GIS
1H1 | Deleted
1H2 | Deleted
1I | Control, Protection SAS & Metering
For 132kV control & Protection
1I1 | Modification of existing of control and protection panel to integrate the new replaced transformers for 132kV Side of Transformer Bay |  | 2 | set
1I2 | Tap changer panel for 132kV Side of Transformer Bay |  | 2 | set
1I3 | Deleted
For 33kV control & Protection
1I4 | Modification of existing control and protection panel to integrate the new replaced transformers for 33kV Side of Transformer Bay |  | 2 | set
1J | Multicore Cables
1J1 | Multicore, XLPE, LV Power & Control Cable for control, protection,metering & power circuits
| i) | LV Control Cable | 1 | lot
| ii) | LV Power Cable | 1 | lot
1K | Earthing & lightning protection
1K1 | Earthing system for renovation portion |  | 1 | lot
1L | Dismantle arrengement
1L1 | i) | Removal, Shifting & Handover 75 MVA three phase power transformer | Refer to Schedule B4
| ii) | Dismantle of Existing equipment & hand over to store (132 kV)
| a) | CT
| iii) | Dismantle of Existing equipment structure & hand over to store (132 kV)
| iv) | Dismantling of existing RTCC panels
| v) | Dismantle of Existing equipment structure & hand over to store (33kV)
1M | Civil Works
1M1 | i) | New 132kV power transformer foundation (shallow/pile foundation) including oil pit | Refer to Schedule B4
| ii) | Modification of 132kV power transformer foundation
| iii) | Modification of existing/new outdoor equipment foundation in 132kV switchyard
| iv) | Modification of existing/new outdoor equipment foundation in 33kV switchyard
| v) | Dismantiling & removal of existing structure & civil foundation as required
1M2 | i) | Dismantiling & removal of existing transformer pad & foundation as required.
Subtotal price for 132/33kV transformer replacement at Joydebpur 132/33kV Substation carried to Schedule 5
Section-2: 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation
2A | Capacitor Bank
2A1 | Capacitor Bank (33kV, 15 MVar, 50 Hz) |  | 2 | set
2A2 | Damping Reactor (0.2%, 36 kV, 410A) |  | 6 | nos.
2A3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 |  | 2 | nos.
2A4 | Key interlocking system |  | 2 | set
2B | 33kV Switchgear
2B1 | 33kV, 1250A, 31.5kA/1sec, 50Hz, 170kVp BIL, outdoor type, gang pole operated Vacuum Circuit Breakers with spring-stored energy operating mechanism |  | 2 | set
2B2 | 33kV, 1250A, 31.5kA/1sec, 50Hz, 170kVp BIL, post type, disconnectors without earth switch |  | 2 | set
2B3 | Single-phase, 3-core, 33kV, 31.5kA/1sec, 50Hz, 170kVp BIL, post type current transformer |  | 6 | nos.
2B4 | 30kV rated voltage, 10kA nominal discharge current, 50Hz, Heavy duty station class, single phase surge arresters |  | 12 | nos.
2C | Control, Protection and Metering
2C1 | 33kV Control, Metering and Protection Panel with associated meters and relays |  | 2 | set
2D | LV and HV cable including accessories
2D1 | 33kV 1Cx500mm2 XLPE Power cable with laying |  | 600 | m
2D2 | 33kV Cable termination kit with connection material for both ends (three phase per set) |  | 4 | set
2D3 | Multi-core cable for control, indication and protection |  | 1 | lot
2E | Conductor, Steel Structure, Insulator & Hardware & Fittings
2E1 | Flexible Conductor/Al Tube, clamps & connectors for main bus, Jackbus,Jumper & equipment Connection
| i) | Flexible Conductor/Al Tube for main bus, jackbus, jumper, equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
2E2 | Insulator & Fittings
| i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
2E3 | Steel structures & cable tray
| i) | Gantry structure with nut & bolts
| a) | Deleted
| b) | Deleted
| iii) | Equipment support structures including nut & bolts
| a) | Capacitor bank | 2 | set
| b) | Reactor | 6 | nos.
| c) | NCT | 2 | nos.
| d) | CB | 2 | set
| e) | DS | 2 | set
| f) | CT | 6 | nos.
| g) | LA | 12 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 4 | set
| iv) | Deleted
| v) | LV Cable tray including fitting, fixing accessories | 1 | lot
2F | Earthing and Lightning Protection System
2F1 | Earthing system for extended part |  | 1 | lot
2F2 | Lighting Protection System for extended part |  | 1 | lot
2G | DC Distribution
2G1 | Extension of DC Distribution System with necessary material for new bays/equipment |  | 1 | lot
2H | LVAC Distribution
2H1 | Extension of LVAC Distribution System with necessary material for new bays/equipment |  | 1 | lot
2I | Lighting, Small Power
2I1 | Outdoor switchyard Lighting, Small Power
| i) | Outdoor Small power (extended part) | 1 | lot
| ii) | Outdoor Lighting (extended part) | 1 | lot
2J | Civil Works
2J1 | Complete outdoor civil works |  | Refer to Schedule B4
| i) | Outdoor gantry foundation in 33kV switchyard
| a) | Deleted
| ii) | Outdoor equiment foundation in 33kV switchyard
| a) | Capacitor bank
| b) | Reactor
| c) | NCT
| d) | CB
| e) | DS
| f) | CT
| g) | LA
| h) | Outdoor type 33kV XLPE cable termination
| iii) | Cable trench with soakpit
| a) | Extension of LV cable trenches
| iv) | Internal road
| a) | Extension of 3m wide road
| v) | Switchyard surface finishing with drainage system
| vi) | Gravelling in switchyard area
| vii) | Chain linked fence with gate around capacitor bank
| viii) | Modification of existing control room to accommodate new panels
Subtotal price for 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation carried to Schedule 5
Section-3: 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation
3A | Capacitor Bank
3A1 | Capacitor Bank (33kV, 15 MVar, 50 Hz) |  | 3 | set
3A2 | Damping Reactor (6%, 36 kV, 410A) |  | 9 | nos.
3A3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 |  | 3 | nos.
3A4 | Key interlocking system |  | 3 | set
3A5 | 30kV rated voltage, 10kA nominal discharge current, 50Hz, Heavy duty station class, single phase surge arresters |  | 9 | nos.
3B | 33kV GIS Switchgear
3B1 | 36kV GIS Line Feeder Bay |  | 2 | set
3C | Control, Protection and Metering
3C1 | 33kV Control, Metering and Protection Panel with associated meters and relays |  | 3 | set
3D | LV and HV cable including accessories
3D1 | 33kV 1Cx500mm2 XLPE Power cable with laying |  | 600 | m
3D2 | 33kV Cable termination kit with connection material for at capacitor ends (three phase per set) |  | 3 | set
3D3 | Multi-core cable for control, indication and protection |  | 1 | lot
3E | Conductor, Steel Structure, Insulator & Hardware & Fittings
3E1 | Flexible Conductor/Al Tube, clamps & connectors for main bus, Jackbus,Jumper & equipment Connection
| i) | Flexible Conductor/Al Tube for main bus, jackbus, jumper, equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
3E2 | Insulator & Fittings
| i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
3E3 | Steel structures & cable tray
| i) | Gantry structure with nut & bolts
| a) | Deleted
| b) | Deleted
| iii) | Equipment support structures including nut & bolts
| a) | Capacitor bank | 3 | set
| b) | Reactor | 9 | nos.
| c) | NCT | 3 | nos.
| d) | LA | 9 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 3 | set
| iv) | Deleted
| v) | LV Cable tray including fitting, fixing accessories | 1 | lot
3F | Earthing and Lightning Protection System
3F1 | Earthing system for extended part |  | 1 | lot
3F2 | Lighting Protection System for extended part |  | 1 | lot
3G | DC Distribution
3G1 | Extension of DC Distribution System with necessary material for new bays/equipment |  | 1 | lot
3H | LVAC Distribution
3H1 | Extension of LVAC Distribution System with necessary material for new bays/equipment |  | 1 | lot
3I | Lighting, Small Power
3I1 | Outdoor switchyard Lighting, Small Power
| i) | Outdoor Small power (extended part) | 1 | lot
| ii) | Outdoor Lighting (extended part) | 1 | lot
3J | Civil Works
3J1 | Complete outdoor civil works |  | Refer to Schedule B4
| i) | Outdoor gantry foundation in 33kV switchyard
| a) | Deleted
| ii) | Outdoor equiment foundation in 33kV switchyard
| a) | Capacitor bank
| b) | Reactor
| c) | NCT
| d) | LA
| e) | Outdoor type 33kV XLPE cable termination
| iii) | Cable trench with soakpit
| a) | Extension of LV cable trenches
| iv) | Internal road
| a) | Extension of 3m wide road
| v) | Switchyard surface finishing with drainage system
| vi) | Gravelling in switchyard area
| vii) | Chain linked fence with gate around capacitor bank
| viii) | Modification of existing control room to accommodate new panels
Subtotal price for 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation carried to Schedule 5

## Schedule B3
Design, Supply, Installation and Commissioning of Power Transformers and Capacitor Banks with associated switchgears on turnkey basis under Capacity Enhancement of Existing Grid Substations and Transmission Lines. (Package-2, Lot-2)
(Contract No.: PGCB/
Schedule B3: Design Services
|  |  |  | Foreign Currency (in .......) |  | Local Currency (BDT)
No. | Description | Unit | Quantity (1) | Unit Price Foreign Portion (2) | Total Price Foreign Portion (3)=(1)x(2) | Unit Price Local Portion (4) | Total Price Local Portion (5)=(1)x(4)
1 | 132/33kV transformer replacement at Joydebpur 132/33kV AIS Substation
| Design and engineering services, local and foreign part | Lump sum | 1 | All Design Cost for this Contract is deemed to be included in Schedule 1, 2 & 4
Subtotal to Schedule 5 - Grand Total
2 | 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation
| Design and engineering services, local and foreign part | Lump sum | 1 | All Design Cost for this Contract is deemed to be included in Schedule 1, 2 & 4
Subtotal to Schedule 5 - Grand Total
3 | 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation
| Design and engineering services, local and foreign part | Lump sum | 1 | All Design Cost for this Contract is deemed to be included in Schedule 1, 2 & 4
Subtotal to Schedule 5 - Grand Total

## Schedule B4
Schedule B4: Installation and Other Services
[5 empty] | Foreign Currency (in .......) |  | Local Currency (BDT)
No. | Equipment |  | Quantity (1) | Unit | Unit Price Foreign Portion (2) | Total Price Foreign Portion (3)=(1)x(2) | Unit Price Local Portion (4) | Total Price Local Portion (5)=(1)x(4)
Section-1: 132/33kV transformer replacement at Joydebpur 132/33kV Substation
1A | Power Transformer (replaced)
1A1 | 132/33kV, 80/120 MVA (ONAN/ONAF), three phase outdoor type power transformers |  | 2 | set
1B | 132 Air Insulated Switchgear (AIS) (Replaced)
1B1 | Deleted
1B2 | Deleted
1B3 | Single-phase, 4-core, multi ratio, 132kV, 40kA/1sec, 50Hz, 650kVp BIL, outdoor, post type current transformer |  | 6 | nos.
1C | 132 Gas Insulated Switchgear (GIS) (Replaced)
1C1 | Single-phase, 6-core, multi ratio, 132kV, 40kA/1sec, 50Hz, 650kVp BIL, current transformer |  | 3 | nos.
1D | 33kV Air Insulated Switches (AIS)
1D1 | Deleted
1D2 | Deleted
1E | Flexible Conductor, clamps & connectors for busbar,jackbus, jumper & equipment connection(132kV & 33kV)
10 | i) | Flexible conductor for jackbus,jumper,equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
1F | Insulator & fittings
1F1 | i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
1G | Steel structures & Cable tray
1G1 | i) | Modification of existing Equipment support structures including nut & bolts (132kV & 33kV) | 1 | lot
| v) | Cable tray including fitting, fixing accessories | 1 | lot
1H | HV Power Cables, Cable Termination and GIS
1H1 | Deleted
1H2 | Deleted
1I | Control, Protection SAS & Metering
For 132kV control & Protection
1I1 | Modification of existing of control and protection panel to integrate the new replaced transformers for 132kV Side of Transformer Bay |  | 2 | set
1I2 | Tap changer panel for 132kV Side of Transformer Bay |  | 2 | set
1I3 | Deleted
For 33kV control & Protection
1I4 | Modification of existing control and protection panel to integrate the new replaced transformers for 33kV Side of Transformer Bay |  | 2 | set
1J | Multicore Cables
1J1 | Multicore, XLPE, LV Power & Control Cable for control, protection,metering & power circuits
| i) | LV Control Cable | 1 | lot
| ii) | LV Power Cable | 1 | lot
1K | Earthing & lightning protection
1K1 | Earthing system for renovation portion |  | 1 | lot
1L | Dismantle arrengement
1L1 | i) | Removal, Shifting & Handover 75 MVA three phase power transformer | 2 | set
| ii) | Dismantle of Existing equipment & hand over to store (132 kV)
| a) | CT | 3 | nos.
| iii) | Dismantle of Existing equipment structure & hand over to store (132 kV) | 1 | lot
| iv) | Dismantling of existing RTCC panels | 2 | set
| v) | Dismantle of Existing equipment structure & hand over to store (33kV) | 1 | lot
1M | Civil Works
1M1 | i) | New 132kV power transformer foundation (shallow/pile foundation) including oil pit | 1 | nos.
| ii) | Modification of 132kV power transformer foundation | 1 | nos.
| iii) | Modification of existing/new outdoor equipment foundation in 132kV switchyard | 1 | lot
| iv) | Modification of existing/new outdoor equipment foundation in 33kV switchyard | 1 | lot
| v) | Dismantiling & removal of existing structure & civil foundation as required | 1 | lot
1M2 | i) | Dismantiling & removal of existing transformer pad & foundation as required. | 1 | nos.
Subtotal price for 132/33kV transformer replacement at Joydebpur 132/33kV Substation carried to Schedule 5
Section-2: 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation
2A | Capacitor Bank
2A1 | Capacitor Bank (33kV, 15 MVar, 50 Hz) |  | 2 | set
2A2 | Damping Reactor (0.2%, 36 kV, 410A) |  | 6 | nos.
2A3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 |  | 2 | nos.
2A4 | Key interlocking system |  | 2 | set
2B | 33kV Switchgear
2B1 | 33kV, 1250A, 31.5kA/1sec, 50Hz, 170kVp BIL, outdoor type, gang pole operated Vacuum Circuit Breakers with spring-stored energy operating mechanism |  | 2 | set
2B2 | 33kV, 1250A, 31.5kA/1sec, 50Hz, 170kVp BIL, post type, disconnectors without earth switch |  | 2 | set
2B3 | Single-phase, 3-core, 33kV, 31.5kA/1sec, 50Hz, 170kVp BIL, post type current transformer |  | 6 | nos.
2B4 | 30kV rated voltage, 10kA nominal discharge current, 50Hz, Heavy duty station class, single phase surge arresters |  | 12 | nos.
2C | Control, Protection and Metering
2C1 | 33kV Control, Metering and Protection Panel with associated meters and relays |  | 2 | set
2D | LV and HV cable including accessories
2D1 | 33kV 1Cx500mm2 XLPE Power cable with laying |  | 600 | m
2D2 | 33kV Cable termination kit with connection material for both ends (three phase per set) |  | 4 | set
2D3 | Multi-core cable for control, indication and protection |  | 1 | lot
2E | Conductor, Steel Structure, Insulator & Hardware & Fittings
2E1 | Flexible Conductor/Al Tube, clamps & connectors for main bus, Jackbus,Jumper & equipment Connection
| i) | Flexible Conductor/Al Tube for main bus, jackbus, jumper, equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
2E2 | Insulator & Fittings
| i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
2E3 | Steel structures & cable tray
| i) | Gantry structure with nut & bolts
| a) | Deleted
| b) | Deleted
| iii) | Equipment support structures including nut & bolts
| a) | Capacitor bank | 2 | set
| b) | Reactor | 6 | nos.
| c) | NCT | 2 | nos.
| d) | CB | 2 | set
| e) | DS | 2 | set
| f) | CT | 6 | nos.
| g) | LA | 12 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 4 | set
| iv) | Deleted
| v) | LV Cable tray including fitting, fixing accessories | 1 | lot
2F | Earthing and Lightning Protection System
2F1 | Earthing system for extended part |  | 1 | lot
2F2 | Lighting Protection System for extended part |  | 1 | lot
2G | DC Distribution
2G1 | Extension of DC Distribution System with necessary material for new bays/equipment |  | 1 | lot
2H | LVAC Distribution
2H1 | Extension of LVAC Distribution System with necessary material for new bays/equipment |  | 1 | lot
2I | Lighting, Small Power
2I1 | Outdoor switchyard Lighting, Small Power
| i) | Outdoor Small power (extended part) | 1 | lot
| ii) | Outdoor Lighting (extended part) | 1 | lot
2J | Civil Works
2J1 | Complete outdoor civil works
| i) | Outdoor gantry foundation in 33kV switchyard
| a) | Deleted
| ii) | Outdoor equiment foundation in 33kV switchyard
| a) | Capacitor bank | 2 | set
| b) | Reactor | 6 | nos.
| c) | NCT | 2 | nos.
| d) | CB | 2 | set
| e) | DS | 2 | set
| f) | CT | 6 | nos.
| g) | LA | 12 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 4 | set
| iii) | Cable trench with soakpit
| a) | Extension of LV cable trenches | 1 | lot
| iv) | Internal road
| a) | Extension of 3m wide road | 30 | meter
| v) | Switchyard surface finishing with drainage system | 1 | lot
| vi) | Gravelling in switchyard area | 1 | lot
| vii) | Chain linked fence with gate around capacitor bank | 1 | lot
| viii) | Modification of existing control room to accommodate new panels | 1 | lot
Subtotal price for 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation carried to Schedule 5
Section-3: 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation
3A | Capacitor Bank
3A1 | Capacitor Bank (33kV, 15 MVar, 50 Hz) |  | 3 | set
3A2 | Damping Reactor (6%, 36 kV, 410A) |  | 9 | nos.
3A3 | Neutral Current Transformers for unbalanced protection, 15VA, 5P10 |  | 3 | nos.
3A4 | Key interlocking system |  | 3 | set
3A5 | 30kV rated voltage, 10kA nominal discharge current, 50Hz, Heavy duty station class, single phase surge arresters |  | 9 | nos.
3B | 33kV GIS Switchgear
3B1 | 36kV GIS Line Feeder Bay |  | 2 | set
3C | Control, Protection and Metering
3C1 | 33kV Control, Metering and Protection Panel with associated meters and relays |  | 3 | set
3D | LV and HV cable including accessories
3D1 | 33kV 1Cx500mm2 XLPE Power cable with laying |  | 600 | m
3D2 | 33kV Cable termination kit with connection material for at capacitor ends (three phase per set) |  | 3 | set
3D3 | Multi-core cable for control, indication and protection |  | 1 | lot
3E | Conductor, Steel Structure, Insulator & Hardware & Fittings
3E1 | Flexible Conductor/Al Tube, clamps & connectors for main bus, Jackbus,Jumper & equipment Connection
| i) | Flexible Conductor/Al Tube for main bus, jackbus, jumper, equipment connections | 1 | lot
| ii) | Clamps & Connectors | 1 | lot
3E2 | Insulator & Fittings
| i) | Insulator | 1 | lot
| ii) | Fittings | 1 | lot
3E3 | Steel structures & cable tray
| i) | Gantry structure with nut & bolts
| a) | Deleted
| b) | Deleted
| iii) | Equipment support structures including nut & bolts
| a) | Capacitor bank | 3 | set
| b) | Reactor | 9 | nos.
| c) | NCT | 3 | nos.
| d) | LA | 9 | nos.
| h) | Outdoor type 33kV XLPE cable termination | 3 | set
| iv) | Deleted
| v) | LV Cable tray including fitting, fixing accessories | 1 | lot
3F | Earthing and Lightning Protection System
3F1 | Earthing system for extended part |  | 1 | lot
3F2 | Lighting Protection System for extended part |  | 1 | lot
3G | DC Distribution
3G1 | Extension of DC Distribution System with necessary material for new bays/equipment |  | 1 | lot
3H | LVAC Distribution
3H1 | Extension of LVAC Distribution System with necessary material for new bays/equipment |  | 1 | lot
3I | Lighting, Small Power
3I1 | Outdoor switchyard Lighting, Small Power
| i) | Outdoor Small power (extended part) | 1 | lot
| ii) | Outdoor Lighting (extended part) | 1 | lot
3J | Civil Works
3J1 | Complete outdoor civil works
| i) | Outdoor gantry foundation in 33kV switchyard
| a) | Deleted
| ii) | Outdoor equiment foundation in 33kV switchyard
| a) | Capacitor bank | 3 | set
| b) | Reactor | 9 | nos.
| c) | NCT | 3 | nos.
| d) | LA | 9 | nos.
| e) | Outdoor type 33kV XLPE cable termination | 3 | set
| iii) | Cable trench with soakpit
| a) | Extension of LV cable trenches | 1 | lot
| iv) | Internal road
| a) | Extension of 3m wide road | 50 | meter
| v) | Switchyard surface finishing with drainage system | 1 | lot
| vi) | Gravelling in switchyard area | 1 | lot
| vii) | Chain linked fence with gate around capacitor bank | 1 | lot
| viii) | Modification of existing control room to accommodate new panels | 1 | lot
Subtotal price for 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation carried to Schedule 5

## Schedule B5
Schedule B5: Grand Summary (Schedules 1 to 4)
Total Price
|  | Foreign Currency (in……….) | Local Currency (in BDT)
Section-1: 132/33kV transformer replacement at Joydebpur 132/33kV AIS Substation
Schedule No. 1: | Plant & Equipment Supplied from Abroad
Schedule No. 2: | Plant & Equipment Supplied from within the Employer’s Country
Schedule No. 3: | Design Services
Schedule No. 4: | Installation and Other Services
132/33kV transformer replacement at Joydebpur 132/33kV AIS Substation
Grand Total
Section-2: 36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation
Schedule No. 1: | Plant & Equipment Supplied from Abroad
Schedule No. 2: | Plant & Equipment Supplied from within the Employer’s Country
Schedule No. 3: | Design Services
Schedule No. 4: | Installation and Other Services
36kV Capacitor banks at Lalmonirhat 132/33kV AIS Substation
Subtotal - to Schedule 5 - Grand Total
Section-3: 36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation
Schedule No. 1: | Plant & Equipment Supplied from Abroad
Schedule No. 2: | Plant & Equipment Supplied from within the Employer’s Country
Schedule No. 3: | Design Services
Schedule No. 4: | Installation and Other Services
36kV Capacitor banks at Rajendrapur 132/33kV GIS Substation
Subtotal - to Schedule 5 - Grand Total
Mandatory Spare, Maintanence & Test Equipement
Schedule No. 1: | Mandatory Spare, Maintanence & Test Equipement Supplied from Outside the Employer's Country
Mandatory Spare, Maintanence & Test Equipement
Subtotal - to Schedule 5 - Grand Total
GRAND Total

## Code
Country of Origin
Item | Country | Code

## Schedule B6
Schedule B6: Recommended Spare Parts
No | Description | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | EXW | EXW | EXW | EXW
|  |  | (1) | (2) | (3)=(1)x(2) | (4) | (5)=(1)x(4)