## Schedule-B1
Design, Supply, Installation, Testing and Commissioning of 400kV Transformer Bay and 230kV Transmission Line Diameter Extension at Kaliakoir Substation on Turnkey Basis
Schedule 1: Plant & Equipment supplied from abroad
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency
[5 empty] | Unit Price | Total Price
[5 empty] | CIP | CIP
|  |  |  | (1) | (2) | (3) = (1) x (2)
For Kaliakoir substation
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR or CSD as phase switching mechanism with support structure |  | Set | 0
1A1.2 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 1
1A1.3 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 2
1A1.4 | Single-phase, 6-core, 400kV, 50kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 3
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 0
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 0
1A1.7 | Post type support insulators for 400kV busbar and switchgear |  | No | 15
1A1.8 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | _Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectors with Nut-Bolts |  | lot | 1
1A1.9 | Steel Structures for gantry and equipment supports
a) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 1
ii) | DS without ES |  | set | 2
iii) | CT |  | No | 3
iv) | CVT/IVT |  | No | 0
v) | LA |  | No | 0
vi) | PI |  | No | 15
b)* | Cable tray including fitting, fixing accessories |  | lot | 1
1B |  | 230kV Switchyard, structures & connections
230kV Air Insulated Switchgear, Equipment Connection and Steel Structure
1B1 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single-pole operation, SF6 gas circuit breakers with spring-stored energy operating mechanism | Sets | 0
1B2 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors with motor-operated earthing switch. | Sets | 3
1B3 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors without earthing switch | Sets | 6
1B4 |  | Single-phase, 5-core, 230kV, 50kA/1sec, 3000-1500/1A, 50Hz, 1425kVp BIL post type current transformer | Nos | 12
1B5 |  | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformers. | Nos | 0
1B6 |  | 198kV rated voltage, 158kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. | Nos | 0
1B7 |  | 230kV post type support insulators required for completing 230kV busbar and switchgear as specified in the technical specifications and bid drawings. | Nos | 36
1B8 |  | rigid tubular bus [Aluminium of grade 63401 WP], flexible conductors, insulators, fittings including all necessary clamps and connectors required for completing 230kV busbar and switchgear connection as specified in the technical specifications and bid drawings. Bus capacity shall be minimum 4000A/50kA/1s. Existing Bus is Aluminium Tube with outer dia. 160mm. | lot | 1
1B9 |  | Steel structures for gantry and equipment supports required for completing 230kV busbar and switchgear as specified in the technical specifications and bid drawings. | lot | 1
| a) | _Gantry Column including nut & bolts | nos | 12
| b) | _Gantry beam including nut & bolts | nos | 6
| c) | _Equipment support structures including nut & bolts
| i) | Circuit Breaker | nos | 3
| ii) | Disconnector without Earth Switch | nos | 6
| iii) | Disconnector with Earth Switch | nos | 3
| iv) | Current Transformer | nos | 12
| v) | Voltage Transformer | nos | 9
| vi) | Surge Arrester | nos | 12
| vii) | Post type support insulators | nos | 36
| viii) | Cable Sealing End(CSE) | nos | 8
| d) | _Cable tray including fitting, fixing accessories | lot | 1
1C | Power Transformer & Earthing/Auxiliary Transformer
1C1 | Auxiliary transformer 33/0.415kV, 300kVA: to be supplied by power grid. But its installation, 33kV & 415V connection to it, including 33kV CT, PT, LA, CB, DS/DES & other 33kV & 415V equipment as required; necessary 33kV and 415V cables/conductors, LVAC panels as required, including incoming & outgoing feeder breakers (Nos. to be fixed at design stage), busbars and full LVAC panel arrangements shall be under this project scope. |  | lot | 1
1C2 | Necessary grounding arrangements for the tertiary 33kV side of the 400/230/33kV, 520MVA Transformer (project scope), including 33kV LA, PT, and other necessary conductor/clamp-connectors. |  | lot | 1
1D | Control, Protection, SAS and Metering
420kV Circuits
1D.1 | Confiiguration/modification of existing Control Panel for for 400/230kV, 520MVA Power Transformer bay with required accessories and materials. (PGCB will supply only CSD and BCU ) |  | lot | 1
1D.1.1 | Confiiguration/modification of Power Grid supplied Relay Panel for 400/230kV, 520MVA Power Transformer bay . Required accessories and materials shall be supply to complete the Protection functionality as per PGCB Standard. (PGCB will supply Bay Unit for busbar protection) |  | lot | 1
1D.2 | Modification / Extension of Busbar Protection including all necessary requirements. |  | set | 1
1D.3 | Tarif metering : Energy Meters (Main & Check) total 2 Nos with Panel |  | lot | 1
230kV Circuits
1D.4 |  | Control, Monitoring, Protection (Main-1 & Main-2 relay) & Substation Automation Facility including event recording function for 230KV circuits line bays. | sets | 2
1D.5 |  | Upgradation/modification of existing CRP Panel of line feeder to use as a 230kV incomer bays of 400/230kV Transformer and to integrate SAS system | sets | 1
1D.6 |  | Renovation/Extension of existing Busbar protection for 230kV system. | lot | 1
1D.7 | Tarif metering : Energy Meters (Main & Check) total 6 Nos with Panel |  | Lot | 1
1D.8 | Extension of the existing Substation Automation System, including all necessary requirements. |  | Lot | 1
1E | Digital Fault & Disturbance Recorder (Modification/Extension of existing system), including all necessary requirements. |  | Lot | 1
1F | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection |  | Lot | 1
1G | Power Cable
1G.1 | 2000 mm2 (least), 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, single phase XLPE cable. Four phases cable shall be laid of which one phase as spare. Length: 330x4=1320 meter. |  | m | 1320
1G.2 | 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, cable terminal end & associated support structures for single phase XLPE cable. |  | Nos. | 8
1H | Multicore Cables
1H.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1I | Earthing and Lightning Protection
1I.1 | _Extension of Earthing system |  | lot | 1
1I.2 | _Extension of Lightning Protection System |  | lot | 1
1J | Batteries, chargers & DC distribution
1J.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel and board/New DCDB panel |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
1J.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel |  | Lot | 1
1K | LVAC Distribution
1K.1 | _Extension of AC 415V or 240V distribution panels |  | lot | 1
1L | Civil Works, Building and Foundation
1L.1 | Complete civil items required for outdoor works including boundary wall, gantry foundation, necessary land development. |  | Refer to Schedule B4
1L.2 | Complete civil works for new Switchyard Panel Room (SPR) & repair, modification works of other control houses for the extension work. |  | Refer to Schedule B4
1L.3 | Testing of Foundation |  | Refer to Schedule B4
1M | Lighting, small power, air conditioning and Ventilation
1M.1 | Extension of Lighting, Air Conditioning system, small power and emergency DC lighting for new SPR and Local control houses. |  | lot | 1
1M.2 | Extension of Lighting for ouside building for security, roadway, switchyard and emergency DC lighting. |  | lot | 1
TOTAL (To be indicated in Schedule No.6 Grand Summary)

## Schedule-B2
Schedule B2: Plant & Equipment Supplied from within the Procuring Entity’s Country
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Unit Price |  | Total Price
[5 empty] | Foreign Currency | Local Currency | Foreign Currency | Local Currency
[5 empty] | EXW | EXW | EXW | EXW
|  |  |  | (1) | (2) | (3) | (4) = (1) x (2) | (5) = (1) x (3)
For Kaliakoir substation
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR or CSD as phase switching mechanism with support structure |  | Set | 0
1A1.2 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 1
1A1.3 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 2
1A1.4 | Single-phase, 6-core, 400kV, 50kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 3
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 0
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 0
1A1.7 | Post type support insulators for 400kV busbar and switchgear |  | No | 15
1A1.8 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectos with Nut-Bolts |  | lot | 1
1A1.9 | Steel Structures for gantry and equipment supports
a) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 1
ii) | DS without ES |  | set | 2
iii) | CT |  | No | 3
iv) | CVT/IVT |  | No | 0
v) | LA |  | No | 0
vi) | PI |  | No | 15
b)* | Cable tray including fitting, fixing accessories |  | lot | 1
1B |  | 230kV Switchyard, structures & connections
230kV Air Insulated Switchgear, Equipment Connection and Steel Structure
1B1 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single-pole operation, SF6 gas circuit breakers with spring-stored energy operating mechanism | Sets | 0
1B2 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors with motor-operated earthing switch. | Sets | 3
1B3 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors without earthing switch | Sets | 6
1B4 |  | Single-phase, 5-core, 230kV, 50kA/1sec, 3000-1500/1A, 50Hz, 1425kVp BIL post type current transformer | Nos | 12
1B5 |  | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformers. | Nos | 0
1B6 |  | 198kV rated voltage, 158kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. | Nos | 0
1B7 |  | 230kV post type support insulators required for completing 230kV busbar and switchgear as specified in the technical specifications and bid drawings. | Nos | 36
1B8 |  | rigid tubular bus [Aluminium of grade 63401 WP], flexible conductors, insulators, fittings including all necessary clamps and connectors required for completing 230kV busbar and switchgear connection as specified in the technical specifications and bid drawings. Bus capacity shall be minimum 4000A/50kA/1s. Existing Bus is Aluminium Tube with outer dia. 160mm. | lot | 1
1B9 |  | Steel structures for gantry and equipment supports required for completing 230kV busbar and switchgear as specified in the technical specifications and bid drawings. | lot | 1
| a) | _Gantry Column including nut & bolts | nos | 12
| b) | _Gantry beam including nut & bolts | nos | 6
| c) | _Equipment support structures including nut & bolts
| i) | Circuit Breaker | nos | 3
| ii) | Disconnector without Earth Switch | nos | 6
| iii) | Disconnector with Earth Switch | nos | 3
| iv) | Current Transformer | nos | 12
| v) | Voltage Transformer | nos | 9
| vi) | Surge Arrester | nos | 12
| vii) | Post type support insulators | nos | 36
| viii) | Cable Sealing End(CSE) | nos | 8
| d) | _Cable tray including fitting, fixing accessories | lot | 1
1C | Power Transformer & Earthing/Auxiliary Transformer
1C1 | Auxiliary transformer 33/0.415kV, 300kVA: to be supplied by power grid. But its installation, 33kV & 415V connection to it, including 33kV CT, PT, LA, CB, DS/DES & other 33kV & 415V equipment as required; necessary 33kV and 415V cables/conductors, LVAC panels as required, including incoming & outgoing feeder breakers (Nos. to be fixed at design stage), busbars and full LVAC panel arrangements shall be under this project scope. |  | lot | 1
1C2 | Necessary grounding arrangements for the tertiary 33kV side of the 400/230/33kV, 520MVA Transformer (project scope), including 33kV LA, PT, and other necessary conductor/clamp-connectors. |  | lot | 1
1D | Control, Protection, SAS and Metering
420kV Circuits
1D.1 | Confiiguration/modification of existing Control Panel for for 400/230kV, 520MVA Power Transformer bay with required accessories and materials. (PGCB will supply only CSD and BCU ) |  | lot | 1
1D.1.1 | Confiiguration/modification of Power Grid supplied Relay Panel for 400/230kV, 520MVA Power Transformer bay . Required accessories and materials shall be supply to complete the Protection functionality as per PGCB Standard. (PGCB will supply Bay Unit for busbar protection) |  | lot | 1
1D.2 | Modification / Extension of Busbar Protection including all necessary requirements. |  | set | 1
1D.3 | Tarif metering : Energy Meters (Main & Check) total 2 Nos with Panel |  | lot | 1
230kV Circuits
1D.4 |  | Control, Monitoring, Protection (Main-1 & Main-2 relay) & Substation Automation Facility including event recording function for 230KV circuits line bays. | sets | 2
1D.5 |  | Upgradation/modification of existing CRP Panel of line feeder to use as a 230kV incomer bays of 400/230kV Transformer and to integrate SAS system | sets | 1
1D.6 |  | Renovation/Extension of existing Busbar protection for 230kV system. | lot | 1
1D.7 | Tarif metering : Energy Meters (Main & Check) total 6 Nos with Panel |  | Lot | 1
1D.8 | Extension of the existing Substation Automation System, including all necessary requirements. |  | Lot | 1
1E | Digital Fault & Disturbance Recorder (Modification/Extension of existing system), including all necessary requirements. |  | Lot | 1
1F | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection |  | Lot | 1
1G | Power Cable
1G.1 | 2000 mm2 (least), 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, single phase XLPE cable. Four phases cable shall be laid of which one phase as spare. Length: 330x4=1320 meter. |  | m | 1320
1G.2 | 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, cable terminal end & associated support structures for single phase XLPE cable. |  | Nos. | 8
1H | Multicore Cables
1H.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1I | Earthing and Lightning Protection
1I.1 | _Extension of Earthing system |  | lot | 1
1I.2 | _Extension of Lightning Protection System |  | lot | 1
1J | Batteries, chargers & DC distribution
1J.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel and board/New DCDB panel |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
1J.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel |  | Lot | 1
1K | LVAC Distribution
1K.1 | _Extension of AC 415V or 240V distribution panels |  | lot | 1
1L | Civil Works, Building and Foundation
1L.1 | Complete civil items required for outdoor works including boundary wall, gantry foundation, necessary land development. |  | Refer to Schedule B4
1L.2 | Complete civil works for new Switchyard Panel Room (SPR) & repair, modification works of other control houses for the extension work. |  | Refer to Schedule B4
1L.3 | Testing of Foundation |  | Refer to Schedule B4
1M | Lighting, small power, air conditioning and Ventilation
1M.1 | Extension of Lighting, Air Conditioning system, small power and emergency DC lighting for new SPR and Local control houses. |  | lot | 1
1M.2 | Extension of Lighting for ouside building for security, roadway, switchyard and emergency DC lighting. |  | lot | 1
TOTAL (To be indicated in Schedule No.6 Grand Summary)

## Schedule-B3
Schedule 3: Design Services
|  |  | Qty | Unit Price 1 |  | Total Price 1
No. | Description | Unit |  | Foreign currency | Local currency | Foreign currency | Local currency
|  |  | (1) | (2) | (3) | (1) X (2) | (1) X (3)
Kaliakoir SS 400kV and 230kV Bay Extension Works
a) | Design and engineering services, local and foreign part | Lump sum | 1
TOTAL OF SCHEDULE NO.3 (To be indicated in Schedule No.6 Grand Summary)
Name of Bidder
Signature of Bidder
Notes:
1 Specify currency in accordance with Tender Data Sheet

## Schedule-B4
Schedule 4: Civil Works
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price
|  |  |  | (1) | (2) | (3) = (1) x (2)
For Kaliakoir substation
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR or CSD as phase switching mechanism with support structure |  | Set | 1
1A1.2 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 1
1A1.3 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 2
1A1.4 | Single-phase, 6-core, 400kV, 50kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 3
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 3
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 3
1A1.7 | Post type support insulators for 400kV busbar and switchgear |  | Nos | 15
1A1.8 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectos with Nut-Bolts |  | lot | 1
1A1.9 | Steel Structures for gantry and equipment supports
a) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 1
ii) | DS without ES |  | set | 2
iii) | CT |  | No | 3
iv) | CVT/IVT |  | No | 3
v) | LA |  | No | 3
vi) | PI |  | No | 15
b)* | Cable tray including fitting, fixing accessories |  | lot | 1
1B |  | 230kV Switchyard, structures & connections
230kV Air Insulated Switchgear, Equipment Connection and Steel Structure
1B1 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single-pole operation, SF6 gas circuit breakers with spring-stored energy operating mechanism | Sets | 3
1B2 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors with motor-operated earthing switch. | Sets | 3
1B3 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors without earthing switch | Sets | 6
1B4 |  | Single-phase, 5-core, 230kV, 50kA/1sec, 3000-1500/1A, 50Hz, 1425kVp BIL post type current transformer | Nos | 12
1B5 |  | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformers. | Nos | 9
1B6 |  | 198kV rated voltage, 158kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. | Nos | 12
1B7 |  | 400kV post type support insulators required for completing 400kV busbar and switchgear as specified in the technical specifications and bid drawings. | Nos | 36
1B8 |  | rigid tubular bus [Aluminium of grade 63401 WP], flexible conductors, insulators, fittings including all necessary clamps and connectors required for completing 230kV busbar and switchgear connection as specified in the technical specifications and bid drawings. Bus capacity shall be minimum 4000A/50kA/1s. Existing Bus is Aluminium Tube with outer dia. 160mm. | lot | 1
1B9 |  | Steel structures for gantry and equipment supports required for completing 230kV busbar and switchgear as specified in the technical specifications and bid drawings. | lot | 1
| a) | _Gantry Column including nut & bolts | nos | 12
| b) | _Gantry beam including nut & bolts | nos | 6
| c) | _Equipment support structures including nut & bolts | nos
| i) | Circuit Breaker | nos | 3
| ii) | Disconnector without Earth Switch | nos | 6
| iii) | Disconnector with Earth Switch | nos | 3
| iv) | Current Transformer | nos | 12
| v) | Voltage Transformer | nos | 9
| vi) | Surge Arrester | nos | 12
| vii) | Post type support insulators | nos | 36
| viii) | Cable Sealing End(CSE) | nos | 8
| d) | _Cable tray including fitting, fixing accessories | lot | 1
1C | Power Transformer & Earthing/Auxiliary Transformer
1C1 | Auxiliary transformer 33/0.415kV, 300kVA: to be supplied by power grid. But its installation, 33kV & 415V connection to it, including 33kV CT, PT, LA, CB, DS/DES & other 33kV & 415V equipment as required; necessary 33kV and 415V cables/conductors, LVAC panels as required, including incoming & outgoing feeder breakers (Nos. to be fixed at design stage), busbars and full LVAC panel arrangements shall be under this project scope. |  | lot | 1
1C2 | Necessary grounding arrangements for the tertiary 33kV side of the 400/230/33kV, 520MVA Transformer (project scope), including 33kV LA, PT, and other necessary conductor/clamp-connectors. |  | lot | 1
1D | Control, Protection, SAS and Metering
420kV Circuits
1D.1 | Confiiguration/modification of existing Control Panel for for 400/230kV, 520MVA Power Transformer bay with required accessories and materials. (PGCB will supply only CSD and BCU ) |  | lot | 1
1D.1.1 | Confiiguration/modification of Power Grid supplied Relay Panel for 400/230kV, 520MVA Power Transformer bay . Required accessories and materials shall be supply to complete the Protection functionality as per PGCB Standard. (PGCB will supply Bay Unit for busbar protection) |  | lot | 1
1D.2 | Modification / Extension of Busbar Protection including all necessary requirements. |  | set | 1
1D.3 | Tarif metering : Energy Meters (Main & Check) total 2 Nos with Panel |  | lot | 1
230kV Circuits
1D.4 |  | Control, Monitoring, Protection (Main-1 & Main-2 relay) & Substation Automation Facility including event recording function for 230KV circuits line bays. | sets | 2
1D.5 |  | Upgradation/modification of existing CRP Panel of line feeder to use as a 230kV incomer bays of 400/230kV Transformer and to integrate SAS system | sets | 1
1D.6 |  | Renovation/Extension of existing Busbar protection for 230kV system. | lot | 1
1D.7 |  | Tarif metering : Energy Meters (Main & Check) total 6 Nos with Panel | lot | 2
1D.8 | Extension of the existing Substation Automation System integration, including all necessary requirements. |  | Lot | 1
1E | Digital Fault & Disturbance Recorder (Modification/Extension of existing system), including all necessary requirements. |  | Lot | 1
1F | SCADA system for Telecontrol and Telemetering including as follows:
1F.1 | Modification/Extension of SCADA hardware & software
| a) | Modification/Extension of SCADA hardware & software including all necessary requirements. | Lot | 1
| b | Integration work with Master & Backup NLDC including Engineering & Commissioning | Lot | 1
1G | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1H | Power Cable
1H.1 | 2000 mm2 (least), 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, single phase XLPE cable. Four phases cable shall be laid of which one phase as spare. Length: 330x4=1320 meter. |  | m | 1320
1H.2 | 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, cable terminal end & associated support structures for single phase XLPE cable. |  | Nos. | 8
1I | Multicore Cables
1I.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1J | Earthing and Lightning Protection
1J.1 | _Extension of Earthing system |  | lot | 1
1J.2 | _Extension of Lightning Protection System |  | lot | 1
1K | Batteries, chargers & DC distribution
1K.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
1K.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
1L | LVAC Distribution
1L.1 | _Extension of AC 415V or 240V distribution panel |  | lot | 1
1M | Civil Works, Building and Foundation
1M.1 | Complete civil items required for outdoor works including boundary wall, necessary land development and slope protection
| i | Outdoor equipment foundation 400kV switchyard
| a) | CB | set | 1
| b) | DS with ES | set | 1
| c) | DS without ES | set | 2
| d) | CT | No. | 3
| e) | CVT | No. | 3
| f) | LA | No. | 3
| g) | PI | No. | 15
| ii | Outdoor gantry foundation 230kV switchyard | Nos. | 12
| iii | Outdoor equipment foundation 230kV switchyard
| a) | CB | set | 3
| b) | DS with ES | set | 3
| c) | DS without ES | set | 6
| d) | CT | Nos. | 12
| e) | CVT | Nos. | 9
| f) | LA | Nos. | 12
| g) | PI | Nos. | 36
| iv | Internal road
| a) | 8m wide road | m | 30
| b) | 4.5m wide road | m | 85
| v | Cable Trench / Tunnel with soakpit for
| a) | LV power & control cable for 230kV system | m | 300
| b) | HV Power cable for 230kV system | m | 330
| vi | _Whole scope area with necessary land development, surface finishing with drainage system | lot | 1
| vii | Gravelling in switchyard area | sqm | 3500
1M.2 | Complete civil works for Control Room, Operation & Panel Room
| a) | Modification works for Control Room and SPR room as necessary for 400kV & 230kV system | Lot | 1
| b) | Complete civil works for 1 No. 230kV Switchyard Panel Room with battery
| i) | _Foundation works | lot | 1
| ii) | _Super structures | lot | 1
| iii) | _All finish works | lot | 1
1M.3 | Testing of Foundation
| i) | _Compression Test | No. | 1
| ii) | _ Uplift Test | No. | 1
1N | Lighting, small power, air conditioning and Ventilation
1N.1 | Extension of Lighting, Air Conditioning system, small power and emergency DC lighting for new SPR and Local control houses. |  | lot | 1
1N.2 | Extension of AC Lighting for ouside building for security, roadway, switchyard and incorporation of emergency DC lighting for all. |  | lot | 1
1O | Transportation of equipments
1O.1 | Transportation of Item no: 1A1.1, 1A1.5, 1A1.6, 1B1, 1B5, 1B6 |  | lot | 1
TOTAL (To be indicated in Schedule No.6 Grand Summary)

## Schedule-B5
Schedule 5: Installation and Other Services
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price
|  |  |  | (1) | (2) | (3) = (1) x (2)
For Kaliakoir substation
1A1 | 400 kV Air Insulated Switchgear, equipment connection and steel structures
1A1.1 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single pole operated, SF6 gas circuit breakers with spring-stored energy operating mechanism with PIR or CSD as phase switching mechanism with support structure |  | Set | 1
1A1.2 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors with motor/manual operated earthing switch. |  | Set | 1
1A1.3 | 420kV, 4000A, 50kA/1sec, 50Hz, 1425kVp BIL,horizontal double break, post type, motor operated disconnectors without earthing switch. |  | Set | 2
1A1.4 | Single-phase, 6-core, 400kV, 50kA/1sec,4000-2000/1A, 50Hz, 1425kVp BIL, post type current transformer. |  | No | 3
1A1.5 | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformer. |  | No | 3
1A1.6 | 390kV rated voltage, 312kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. |  | No | 3
1A1.7 | Post type support insulators for 400kV busbar and switchgear |  | Nos | 15
1A1.8 | Rigid tubular bus and/ or flexible conductors, insulators, fittings including all necessary clamps and connectors as required for completing extension of 400kV AIS Switchyard
i) | Rigid Tubular Bus |  | lot | 1
ii) | _Flexible Conductor for jumper, equipment connections |  | lot | 1
iii) | _Insulator |  | lot | 1
iv) | _Fittings, Clamp & Connectos with Nut-Bolts |  | lot | 1
1A1.9 | Steel Structures for gantry and equipment supports
a) | Equipment support structures including nut & bolts
i) | DS with ES |  | set | 1
ii) | DS without ES |  | set | 2
iii) | CT |  | No | 3
iv) | CVT/IVT |  | No | 3
v) | LA |  | No | 3
vi) | PI |  | No | 15
b)* | Cable tray including fitting, fixing accessories |  | lot | 1
1B |  | 230kV Switchyard, structures & connections
230kV Air Insulated Switchgear, Equipment Connection and Steel Structure
1B1 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, live tank type, single-pole operation, SF6 gas circuit breakers with spring-stored energy operating mechanism | Sets | 3
1B2 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors with motor-operated earthing switch. | Sets | 3
1B3 |  | 230kV, 3150A, 50kA/1sec, 50Hz, 1425kVp BIL, horizontal double break, post type, motor operated disconnectors without earthing switch | Sets | 6
1B4 |  | Single-phase, 5-core, 230kV, 50kA/1sec, 3000-1500/1A, 50Hz, 1425kVp BIL post type current transformer | Nos | 12
1B5 |  | Single-phase, 3-core, 400kV, 50Hz, 1425kVp BIL, capacitor type voltage transformers. | Nos | 9
1B6 |  | 198kV rated voltage, 158kV(rms) continuous operating voltage at 50˚c 10kA nominal discharge current, 50Hz, Heavy duty station class, gapless metal oxide type, single phase surge arresters. | Nos | 12
1B7 |  | 400kV post type support insulators required for completing 400kV busbar and switchgear as specified in the technical specifications and bid drawings. | Nos | 36
1B8 |  | rigid tubular bus [Aluminium of grade 63401 WP], flexible conductors, insulators, fittings including all necessary clamps and connectors required for completing 230kV busbar and switchgear connection as specified in the technical specifications and bid drawings. Bus capacity shall be minimum 4000A/50kA/1s. Existing Bus is Aluminium Tube with outer dia. 160mm. | lot | 1
1B9 |  | Steel structures for gantry and equipment supports required for completing 230kV busbar and switchgear as specified in the technical specifications and bid drawings. | lot | 1
| a) | _Gantry Column including nut & bolts | nos | 12
| b) | _Gantry beam including nut & bolts | nos | 6
| c) | _Equipment support structures including nut & bolts | nos
| i) | Circuit Breaker | nos | 3
| ii) | Disconnector without Earth Switch | nos | 6
| iii) | Disconnector with Earth Switch | nos | 3
| iv) | Current Transformer | nos | 12
| v) | Voltage Transformer | nos | 9
| vi) | Surge Arrester | nos | 12
| vii) | Post type support insulators | nos | 36
| viii) | Cable Sealing End(CSE) | nos | 8
| d) | _Cable tray including fitting, fixing accessories | lot | 1
1C | Power Transformer & Earthing/Auxiliary Transformer
1C1 | Auxiliary transformer 33/0.415kV, 300kVA: to be supplied by power grid. But its installation, 33kV & 415V connection to it, including 33kV CT, PT, LA, CB, DS/DES & other 33kV & 415V equipment as required; necessary 33kV and 415V cables/conductors, LVAC panels as required, including incoming & outgoing feeder breakers (Nos. to be fixed at design stage), busbars and full LVAC panel arrangements shall be under this project scope. |  | lot | 1
1C2 | Necessary grounding arrangements for the tertiary 33kV side of the 400/230/33kV, 520MVA Transformer (project scope), including 33kV LA, PT, and other necessary conductor/clamp-connectors. |  | lot | 1
1D | Control, Protection, SAS and Metering
420kV Circuits
1D.1 | Confiiguration/modification of existing Control Panel for for 400/230kV, 520MVA Power Transformer bay with required accessories and materials. (PGCB will supply only CSD and BCU ) |  | lot | 1
1D.1.1 | Confiiguration/modification of Power Grid supplied Relay Panel for 400/230kV, 520MVA Power Transformer bay . Required accessories and materials shall be supply to complete the Protection functionality as per PGCB Standard. (PGCB will supply Bay Unit for busbar protection) |  | lot | 1
1D.2 | Modification / Extension of Busbar Protection including all necessary requirements. |  | set | 1
1D.3 | Tarif metering : Energy Meters (Main & Check) total 2 Nos with Panel |  | lot | 1
230kV Circuits
1D.4 |  | Control, Monitoring, Protection (Main-1 & Main-2 relay) & Substation Automation Facility including event recording function for 230KV circuits line bays. | sets | 2
1D.5 |  | Upgradation/modification of existing CRP Panel of line feeder to use as a 230kV incomer bays of 400/230kV Transformer and to integrate SAS system | sets | 1
1D.6 |  | Renovation/Extension of existing Busbar protection for 230kV system. | lot | 1
1D.7 |  | Tarif metering : Energy Meters (Main & Check) total 6 Nos with Panel | lot | 2
1D.8 | Extension of the existing Substation Automation System integration, including all necessary requirements. |  | Lot | 1
1E | Digital Fault & Disturbance Recorder (Modification/Extension of existing system), including all necessary requirements. |  | Lot | 1
1F | SCADA system for Telecontrol and Telemetering including as follows:
1F.1 | Modification/Extension of SCADA hardware & software
| a) | Modification/Extension of SCADA hardware & software including all necessary requirements. | Lot | 1
| b | Integration work with Master & Backup NLDC including Engineering & Commissioning | Lot | 1
1G | Extension of Fibre Optic Multiplexer Equipment and PLC Equipment for Communication and Protection
1H | Power Cable
1H.1 | 2000 mm2 (least), 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, single phase XLPE cable. Four phases cable shall be laid of which one phase as spare. Length: 330x4=1320 meter. |  | m | 1320
1H.2 | 245 kV, 2,000A, 50kA/ 1 sec, 50Hz, 1,050/460 kV BIL, cable terminal end & associated support structures for single phase XLPE cable. |  | Nos. | 8
1I | Multicore Cables
1I.1 | Multicore Cables for control, protection, metering & power circuits
| i) LV Control Cable |  | lot | 1
| ii) LV Power Cable |  | lot | 1
1J | Earthing and Lightning Protection
1J.1 | _Extension of Earthing system |  | lot | 1
1J.2 | _Extension of Lightning Protection System |  | lot | 1
1K | Batteries, chargers & DC distribution
1K.1 | 110V Ni-cad Batteries with chargers & distribution board
| a) Extension of 110V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
| b) | 110V Ni-cad Batteries with chargers
| i. | _110V Battery Banks, not less than 400Ah | set | 1
| ii. | _Charger, not less than 150A | set | 1
1K.2 | 48V Ni-cad Batteries with chargers & distribution board
| i) Extension of 48V DC Distribution panel and board/New DCDB panel (if required) |  | Lot | 1
1L | LVAC Distribution
1L.1 | _Extension of AC 415V or 240V distribution panel |  | lot | 1
1M | Civil Works, Building and Foundation
1M.1 | Complete civil items required for outdoor works including boundary wall, necessary land development and slope protection
| i | Outdoor equipment foundation 400kV switchyard
| a) | CB | set | 1
| b) | DS with ES | set | 1
| c) | DS without ES | set | 2
| d) | CT | No. | 3
| e) | CVT | No. | 3
| f) | LA | No. | 3
| g) | PI | No. | 15
| ii | Outdoor gantry foundation 230kV switchyard | Nos. | 12
| iii | Outdoor equipment foundation 230kV switchyard
| a) | CB | set | 3
| b) | DS with ES | set | 3
| c) | DS without ES | set | 6
| d) | CT | Nos. | 12
| e) | CVT | Nos. | 9
| f) | LA | Nos. | 12
| g) | PI | Nos. | 36
| iv | Internal road
| a) | 8m wide road | m | 30
| b) | 4.5m wide road | m | 85
| v | Cable Trench / Tunnel with soakpit for
| a) | LV power & control cable for 230kV system | m | 300
| b) | HV Power cable for 230kV system | m | 330
| vi | _Whole scope area with necessary land development, surface finishing with drainage system | lot | 1
| vii | Gravelling in switchyard area | sqm | 3500
1M.2 | Complete civil works for Control Room, Operation & Panel Room
| a) | Modification works for Control Room and SPR room as necessary for 400kV & 230kV system | Lot | 1
| b) | Complete civil works for 1 No. 230kV Switchyard Panel Room with battery
| i) | _Foundation works | lot | 1
| ii) | _Super structures | lot | 1
| iii) | _All finish works | lot | 1
1M.3 | Testing of Foundation
| i) | _Compression Test | No. | 1
| ii) | _ Uplift Test | No. | 1
1N | Lighting, small power, air conditioning and Ventilation
1N.1 | Extension of Lighting, Air Conditioning system, small power and emergency DC lighting for new SPR and Local control houses. |  | lot | 1
1N.2 | Extension of AC Lighting for ouside building for security, roadway, switchyard and incorporation of emergency DC lighting for all. |  | lot | 1
1O | Transportation of equipments
1O.1 | Transportation of Item no: 1A1.1, 1A1.5, 1A1.6, 1B1, 1B5, 1B6 |  | lot | 1
TOTAL (To be indicated in Schedule No.6 Grand Summary)

## Schedule-B6
Schedule 6: Grand Summary
Schedule No | Description | Total Price
|  | Foreign Currency (in……….) | Local Currency (in BDT)
Schedule No. 1: | Plant & Equipment (including Mandatory Spare Parts) Supplied from Abroad
Schedule No. 2: | Plant & Equipment (including Mandatory Spare Parts) Supplied from within the Procuring Entity’s Country
Schedule No. 3: | Design Services
Schedule No. 4: | Civil works
Schedule No. 5: | Installation and Other Services
GRAND TOTAL (Schedule No.1 to Schedule No.5) (to Letter of Price Bid)
Name of Bidder
Signature of Bidder