## Schedule B1(Purbachal)
Schedule B1 : Plant and Equipment Supplied from Outside the Employer's Country
New 400/230/132 kV Substation at Purbachal
(For deatailed description of the technical requirements please refer to clause 1.2.1: Technical Requirements for 400/230/132KV GIS Substation at Purbachal, Schedule A: Scope of Works, volume 3 of 3 of the bidding document)
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Code | Foreign Currency (in……….) |  | Remark
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
1A | 420 kV switchgear, equipment connection and steel structures
1A1 | 420kV GIS Line Feeder Bays |  | Set | 4
1A2 | 420kV GIS Auto Transformer Feeder Bays |  | Set | 3
1A3 | 420kV Bus Coupler Bays |  | Set | 2
1A4 | 420kV GIS Bus Section Bays |  | Set | 2
1A5 | 420 kV GIS type three phase LA |  | Set | 4
1A6 | 420kV GIS type Bus FES and Bus VT |  | Set | 4
1A7 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
1A8 | Standalone Partial Discharge measurement and analyzer system for Complete GIS |  | Lot | 1
AIS Switchgear, Equipment & Structure
1A9 | 390kV rated voltage at 50°C, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 21
1A10 | 420kV CVT, Single-phase, 50Hz, 1425kVp BIL, 3 windings |  | No. | 12
1A11 | 420kV, 4000A, single phase Wavetrap |  | No. | 4
1A12 | 400kV Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 400kV Switchyard including LA, CVT and WT conncetion
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1A13 | Insulator and fittings including all necessary clamps and connectors as required for completing 400kV GIS Switchyard
| i. | Insulator | Lot | 1
| ii. | Fittings & Clamps, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1A14 | Steel gantry each circuit of 400kV Transmission Line, Transformer & Equipment support structure including all necessary accessories required for completing 400kV GIS Switchyard
| i. | Steel Structure for T/L with Nut & Bolts
| a) | Gantry Column | No. | 5
| b) | Beam | No. | 4
| ii | Equipment Structure
| a) | LA | No. | 21
| b) | 420kV CVT | No. | 12
| iii. | Nut-Bolt | Lot | 1
| iv. | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1B | 245 kV switchgear, equipment connection and steel structures
1B1 | 245kV GIS Line Feeder Bays |  | Set | 2
1B2 | 245kV GIS Auto Transformer Feeder Bays |  | Set | 6
1B3 | 245kV Bus Coupler Bays |  | Set | 2
1B4 | 245kV Bus Section Bays |  | Set | 2
1B5 | 245kV GIS type Bus FES and Bus VT |  | Set | 4
1B6 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
AIS Switchgear, Equipment & Structure
1B7 | 198kV rated voltage, 158 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 24
1B8 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 230kV Switchyard
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1B9 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV Switchyard
| i. | Insulator | Lot | 1
| ii. | Fittings & Clamps, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1B10 | Steel gantry for each circuit of 245kV Transmission Line, Transformer & Equipment support Structure including all necessary accessories required for completing 230kV Switchyard
| i. | Steel Structure for T/L with Nut & Bolts
| a) | Gantry Column | No. | 3
| b) | Beam | No. | 2
| ii. | Steel Structure for 400/230kV & 230/132kV Transformers with Nut & Bolts
| a) | Gantry Column | No. | 14
| b) | Beam | No. | 12
| iii. | Equipment structure
| a) | LA | No. | 24
| iv. | Nut & Bolts | Lot | 1
| v. | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1C | 145 kV switchgear, equipment connection and steel structures
1C1 | 145kV GIS Line Feeder Bays |  | Set | 6
1C2 | 145kV GIS Auto Transformer Feeder Bays |  | Set | 2
1C3 | 145kV Bus Coupler Bays |  | Set | 2
1C4 | 145kV Bus Section Bays |  | Set | 2
1C5 | 145kV GIS type Bus FES and Bus VT |  | Set | 4
1C6 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
AIS Switchgear, Equipment & Structure
1C7 | 120kV rated voltage, 102 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 24
1C8 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 132kV Switchyard
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1C9 | Insulator and fittings including all necessary clamps and connectors as required for completing 132kV Switchyard
| i | Insulator, Post & Disk | Lot | 1
| ii | Fittings & Clamp, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1C10 | Steel gantry for each circuit of 145kV Transmission Line, Transformer & Equipment support Structure including all necessary accessories required for completing 132kV Switchyard
| i. | Steel Structure for T/Lwith Nut & Bolts
| a) | Gantry Column | No. | 8
| b) | Beam | No. | 6
| ii. | Equipment Structure
| a) | LA | No. | 24
| iii. | Nut & Bolts | Lot | 1
| iv. | LV power & control Cable tray including fitting, fixing accessories | Lot | 1
| v. | HV power Cable tray including fitting, fixing accessories | Lot | 1
1D | 36kV Switchgears, equipment connection and steel structures
1D1 | 36kV AIS Switchgears for Aux. Power Bays, comprises with:
| i) | 36kV, 630A, 31.5kA/3sec, 50Hz, 170kVp BIL, VCB with spring operating mechanism | Set | 2
| ii) | 36kV, 630A, 31.5kA/3sec, 50Hz, 170kVp BIL, single vertical/horizontal break, post type, motor operated Disconnector with Earth Switch | Set | 4
| iii) | 36kV, single-phase, 31.5kA/3sec, 50Hz, 170kVp BIL, Current Transformers | No. | 6
| iv) | 36kV, 31.5kA/3sec, single-phase 50Hz, 170kVp BIL, inductive Voltage Transformers | No. | 6
| v) | 30kV rated voltage, 24 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type | No. | 6
1D1.x | 36kV AIS Switchgears for Unloaded tertiary Auto-Transformer Bays, comprises with:
| i) | 36kV, 31.5kA/3sec, single-phase 50Hz, 170kVp BIL, inductive Voltage Transformers | No. | 9
| ii) | 30kV rated voltage, 24 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type | No. | 9
1D2 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 36kV Switchyard
| i) | Tubular Conductor and/or Flexible Conductor | Lot | 1
1D3 | Insulator and fittings including all necessary clamps and connectors as required for completing 36kV Switchyard
| i) | Insulator, Post & Disk | Lot | 1
| ii) | Fittings & Clamps, Connector | Lot | 1
| iii) | Nut-bolt | Lot | 1
1D4 | Steel structure for each circuit of Aux. power TR and Auto.TR tertiary side connection including all necessary accessories required for completing 36kV Switchyard
| i) | Equipment Structure with Nut & Bolts | Lot | 1
| ii) | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1D5 | 33kV Power Cable with associated material
| i) | 33kV, single phase, 300 sqmm XLPE cable | meter | 50
| ii) | 33kV, single phase, outdoor cable termination with accessories | No. | 12
1E | Power Transformers and Auxuliary Transformer
1E1 | 400/235/34.5 kV, 520/750 MVA (ONAN/ONAF), threephase outdoor type auto transformer equipped with delta connected 33 kV tertiary winding (brought out to terminal bushings) and Remote Tap Changer Control (RTCC) Panel. Direct Hot Spot Temperature measurement facility using fiber optic shall be available. |  | Set | 3
1E2 | On-line Dissolved Gas (multi-gas) & Moisture Analyzer system for 400/235/34.5 kV auto transformers. |  | Set | 3
1E3 | 230/135/34.5 kV, 350/450 MVA (ONAN/ONAF), three phase outdoor type auto transformer equipped with delta connected 33 kV tertiary winding (brought out to terminal bushings) and RTCC Panel. Direct Hot Spot Temperature measurement facility using fiber optic shall be available. |  | Set | 2
1E4 | Potable dissolved gas monitoring system for transformer |  | Set | 1
1E5 | 33/0.415 kV, 500kVA, three phase outdoor type earthing/auxiliary Zig-Zag transformer and BCT with off-load tap changer, associated outdoor neutral CTs and steel support structures including all necessary connections. |  | Set | 2
1E6 | CAFS of Fire Fighting system for transformer with water feeding equipment
| i) | 400/235/34.5 kV Auto-transformer | set | 3
| ii) | 230/135/34.5 kV Auto-transformer | set | 2
1F | Control, Protection, Substation Automation & Metering
400kV Circuit
1F1 | Control, protection and Monitoring including SAS Function for Overhead Line circuits, along with Control & Protection Cubicles |  | Set | 4
1F2 | Control, protection and Monitoring including SAS Function for Auto transformer circuits, along with Control & Protection Cubicles |  | Set | 3
1F3 | Control, Protection, Monitoring including SAS Function for Bus Coupler circuits, along with Control & Protection Cubicles |  | Set | 2
1F4 | Control, Protection, Monitoring including SAS Function for Bus section circuits, along with Control & Protection Cubicles |  | Set | 2
1F5 | Busbar Protection including SAS Function (400kV Circuit) [Main-1 & Mian-2, different make] |  | Set | 2
1F6 | Tariff metering comprises with : |  | Lot | 1
| i. | Meters (Main meter & Check meter in one set) | Set | 7
| ii. | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
230kV Circuits
1F7 | Control, Protection, Monitoring including SAS Function for overhead line circuits, along with Control & Protection Cubicles |  | Set | 2
1F8 | Control, Protection, Monitoring including SAS Function for Auto transformer (750MVA) circuits, along with Control & Protection Cubicles |  | Set | 3
1F9 | Control, protection and Monitoring including SAS Function for Auto transformer (450MVA) circuits, along with Control & Protection Cubicles |  | Set | 3
1F10 | Control, Protection, Monitoring including SAS Function for Bus Coupler circuits, along with Control & Protection Cubicles |  | Set | 2
1F11 | Control, Protection, Monitoring including SAS Function for Bus section circuits, along with Control & Protection Cubicles |  | Set | 2
1F12 | Busbar Protection including SAS Function (230kV Circuit) |  | Set | 1
1F13 | Tariff metering comprises with : |  | Lot | 1
| i. | Meters (Main & Check) | set | 8
| ii. | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
132kV Circuits
1F14 | Control, Protection, Monitoring including SAS Function for overhead line circuits, along with Control & Protection Cubicles |  | set | 6
1F15 | Control, Protection, Monitoring including SAS Function for Auto transformer circuits, along with Control & Protection Cubicles |  | set | 2
1F16 | Control, Protection, Monitoring & SAS for Bus Coupler circuits, including Control & Protection Cubicles |  | set | 2
1F17 | Control, Protection, Monitoring & SAS Function for Bus section circuits, including Control & Protection Cubicles |  | set | 2
1F18 | Busbar Protection including SAS Function (132kV Circuit) |  | set | 1
1F19 | Tariff metering comprises with : |  | Lot | 1
| i) | Meters (Main & Check) | Set | 8
| ii) | Complete Panel including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
36kV Circuit
1F20 | Control, Monitoring, Protection & SAS function for 33kV station power system, including Control & Protection Cubicles |  | Set | 2
1F21 | Control, Monitoring, Protection & SAS function for Unloaded tertiary side of Auto-tranformer, including Control & Protection Cubicles (can be merged with TR main/backup protection) |  | Set | 3
1F22 | Tariff metering comprises with : |  | Lot | 1
| i) | Meters (Main & Check) | set | 2
| ii) | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
1F23 | Substation Automation system |  | Lot | 1
1G | Digital Fault & Disturbance Recorder |  | Lot | 1
1H | Power Cable & GIL
1H1 | 420kV Gas Insulated Line (GIL) for seven (7) feeders, single phase encloser, which consist of four (4) T/L & three (3) T/R, terminating chambers complete with support structure, etc. The Length of GIL maybe different from each bay as per actual design (25 - 140 meter). Actual payment shall be as per final design. The Length given here is as single phase length. |  | m | 1800
1H2 | 245kV Gas Insulated Line (GIL) for eight (8) feeders, single phase encloser, which consist of two (2) T/L &six (6) T/R, terminating chambers complete with support structure, etc. The Length of GIL maybe different from each bay as per actual design (30 - 135 meter). Actual payment shall be as per final design. The Length given here is as single phase length |  | m | 1800
1H3 | 132kV, 2000sqmm (minimum), XLPE Power cable & termination
| i. | XLPE HV Power cable (Cable shall be laid in cable trench with flat formation arrangement) | m | 1900
| ii. | Outdoor type Cable Sealing End per phase with required necessary accessories for line & transformer bays | Nos. | 24
1H4 | Steel structure for each circuit of 132kV cable connection
| i. | Equipment Structure with Nut & Bolts
| a) | Outdoor type Cable Sealing End | Nos. | 24
1I | Multicore Cables for control, protection, metering & power circuits
| i. | LV Control Cable | Lot | 1
| ii. | LV Power Cable | Lot | 1
1J | Earthing and Lightning Protection system Design, supply and installation of earthing system and lightning protection screen including connections, connectors and clamps, to suit the substation overall arrangement and provide supporting design calculations.
1J1 | Earthing system for complete substation (grounding mesh, grounding rod/ needle type grounding rod) including GIS Building |  | Lot | 1
1J2 | Lightning Protection System for complete substation (overhead, mast type) |  | Lot | 1
1J3 | 3-phase Portable earthing devices (for maintenance) with connectors and telescopic glass fibre operating pole suitable for plant shall be supplied (for each voltage level, respectively) |  | Set | 2
1K | Batteries, Chargers & DC distribution board
1K1 | 110V Ni-cad Batteries with chargers & distribution board
| i. | for 400kV system
| a) | _110V Battery Banks, minimum 400Ah at the 5-hours rate of discharge | Set | 2
| b) | _Charger (IGBT Type), each float charge shall not be less than 150A rating | Set | 2
| c) | _110V DC Distribution panel, MCC type (LV S.W room, SPR, control Room) with Digital Display & Controller | Lot | 1
| d) | Inverter, Input- AC & DC, output -AC 230V 5kVA 60min | set | 2
| ii. | for 230kV & 132kV system
| a) | _110V Battery Banks, minimum 400Ah at the 5-hours rate of discharge | Set | 2
| b) | _Charger (IGBT Type), each float charge shall not be less than 150A rating | Set | 2
| c) | _110V DC Distribution panel, MCC type (Panel Room) with Digital Display & Controller | Lot | 1
1K2 | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks, minimum 200Ah at the 5-hours rate of discharge | Set | 2
| ii. | _Charger (IGBT Type) each float charge shall not be less than 120A rating | Set | 2
| iii. | _48V DC Distribution Panel with Digital Display & Controller | Lot | 1
1L | LVAC Distribution
1L1 | AC 415V / 230V Distribution panels (MCC type, LV S.W room, Each Panel & Control room, Generator room etc) with Digital Display & Controller |  | Lot | 1
1L2 | Tariff metering at LV side |  | Lot | 1
1M | Civil Works, Building and Foundation (Details in Schedule B4)
1M1 | Complete land development |  | Refer to Schedule B4
1M2 | Complete civil items required for outdoor works |  | Refer to Schedule B4
1M3 | i. | Complete civil works for 420kV Indoor GIS Building including Protection & Metering Room, Control Room, 110V Battery Room, 48 Battery Room, Warehouse etc.
| a) | _Foundation works | Refer to Schedule B4
| b) | _Super structures | Refer to Schedule B4
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture etc. | Refer to Schedule B4
| d) | _10 ton EOT crane (price for supply of EOT crane) | No. | 1
| e) | _Warehouse_separate spare materials by installing shelves and labels. | Refer to Schedule B4
| ii. | Complete civil works for 245kV cum 132kV Indoor GIS Building including Protection & Metering Room, 110V Battery Room etc. | Refer to Schedule B4
| a) | _Foundation works | Refer to Schedule B4
| b) | _Super structures | Refer to Schedule B4
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture, etc. | Refer to Schedule B4
| d) | _10 ton EOT crane (price for supply of EOT crane) | No. | 1
| iii. | Emergency auxulary power room & water feeding room | Refer to Schedule B4
| a) | _Foundation works | Refer to Schedule B4
| b) | _Super structures | Refer to Schedule B4
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture, etc. | Refer to Schedule B4
| d) | _Complete civil work for CAF system including pipe network | Refer to Schedule B4
1M4 | Testing of Foundation |  | Refer to Schedule B4
1N | Lighting, small power, air conditioning and Ventilation, Fire Fighting System & CCTV
1N1 | Indoor Lighting (LED type), small power, air conditioning (except GIS Hall) and Ventilation (GIS hall, Batterys Rooms, other rooms, etc.) and emergency DC lighting for Indoor. |  | Lot | 1
1N2 | Lighting (LED type) for outside building for security, roadway, switchyard |  | Lot | 1
1N3 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For 230kV cum 132kV GIS Hall & Panel Room | Lot | 1
| ii) | Fire Fighting system For 400kV GIS Hall & Panel Room | Lot | 1
| iii) | Fire Fighting system For Control Room | Lot | 1
1N4 | Complete CCTV with motion sensor |  | Lot | 1
1O | Fibre Optic Multiplexer Equipment & PLC Equipment and System for Communication and Protection at Local & Remote end substations - 87 or 21 relay for each transmission line protection (through fibre cores) - 21 relay carrier signal (main and back-up) - SCADA data from switchgear and control system - IP and Analog telephone system - Hot-line telephone system All PLC terminal equipment at remote end substations are ABB make
1O1 | Indoor Fibre Optic Multiplexer, at Local end SS, Equipment each comprising
| i. | ADM with TP unit without booster with Panels (Front opening, Swing Frame type) & accessories | Set | 1
| ii. | IDF/SDF | Set | 1
| iii. | Cables | Lot | 1
| iv. | EOW telephone with board | Set | 1
| v. | Panel including wiring, lighting, filtering fan, humidity controller, heater, power socket & other accessories | Lot | 1
| vi. | All other Accessories not included above | Lot | 1
1O2 | Other Indoor equipment, at Local end SS
| i. | PABX Card (FXO) | Set | 1
| ii. | Primary phone (IP phone) | No. | 2
| iii. | Secondary phone (2W phone) | No. | 10
| iv. | Indoor MDF | Set | 1
1O3 | Outdoor equipment, at Local end SS
| i. | Underground optical fiber cable, armoured, 48 core | Lot | 1
| ii. | Pigtail cables | Lot | 1
| iii. | Outdoor termination box | Set | 1
1O4 | Extension/Adaptation of Indoor Fibre Optic Multiplexer Equipment & system at remote end substations each comprising
| i. | Optical STM-16 Card for each 400 kV line at remote end | Lot | 1
| ii. | Optical STM-4 Card for each 230 kV line at remote end | Lot | 1
| iii. | Optical STM-4 Card for each 132 kV line at remote end | Lot | 1
| iv. | Required no. of cards with 4 commands for distance protection after detail design | Lot | 1
| v. | Optical Booster, if required | Lot | 1
| vi. | Outdoor termination box | Set | 1
| vii. | Cables, ODF, MDF, panels as required | Lot | 1
1O5 | PLC equipment at Local end SS
| i. | Indoor PLC Equipment with all acessories & Panels (Front opening, Swing Frame type) | Set | 4
| ii. | Line matching unit | No. | 8
| iii. | Cables & other accessories for complete PLCC system | Lot | 1
| iv. | Indoor PLC Equipment & accessories as complete system for Remote end station | Lot | 1
1O6 | Installation, testing & commissioning |  | Lot | 1
1P | SCADA system for Telecontrol and Telemetering
1P1 | i. | Equipment at Substation
| a) | Gateway (server, engineering software) | Set | 2
| b) | Ethernet Switch | Set | 2
| c) | Hardware Firewall | Set | 1
| d) | Complete Panel ( Swing Frame type) including wiring, lighting, heater, humidity controller & other accessories | Lot | 1
| e) | Cables | Lot | 1
| f) | All Other Accessories | Lot | 1
| ii. | Integration work with Master & Backup NLDC including Engineering & Commissioning | Lot | 1
1R | Generator for Emergency Aux. Power (with smoke reduction device)
1R1 | 250kW 0.415kV, 50Hz Diesel generator • Expected Operation Time 24h • Noise level Less than 55dB at a distance of 10m • Fuel Tank Capacity: Adequate capacity for three days’continuous operation • With Smoke reduction device |  | Set | 1
1S | Other equipment
1S1 | Scissor Lift : Battery type for one person / Minimum working height greater than 10m |  | Set | 1
1S2 | Emergency Interphone (each room) |  | Lot | 1
Total Price( for New Purbachal 400/230/132kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Purbachal 400/230/132kV SS)……………………………………………………………

## Schedule B1_Spare(Purbachal)
Schedule B1 : Mandatory Spare, Maintanence & Test Equipement Supplied from Outside the Employer's Country
New 400/230/132 kV Substation at Purbachal
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Code | Foreign Currency (in……….) |  | Remark
[6 empty] | Unit Price | Total Price
[6 empty] | CIP | CIP
|  |  |  | (1) |  | (2) | (3) = (1) x (2)
AS | 420kV Switchgear, equipment and connection
AS1 | Complete CB module for GIS |  | phase | 2
AS2 | Complete Operation Mechanism with accessories of CB for GIS |  | set | 1
AS3 | Tripping coil for GIS |  | no | 6
AS4 | Closing coil for GIS |  | no | 3
AS5 | Complete DS/ES module for GIS | set | phase | 2
AS6 | Complete Operation Mechanism with accessories of DS/ES for GIS |  | set | 1
AS7 | Complete HSES module for GIS | sets | phase | 2
AS8 | Complete Operation Mechanism with accessories of HSES for GIS |  | set | 1
AS9 | Complete CT module for GIS | sets | phase | 2
AS10 | Complete VT module for GIS | sets | phase | 2
AS11 | Complete LA module for GIS |  | phase | 2
AS12 | Gas pressure gauge |  | no | 6
AS13 | Pressure Relief Device |  | no | 6
AS14 | Rubber gaskets “O” rings and seals for SF6 gas |  | lot | 1
AS15 | All types of control valves for SF6 gas |  | lot | 1
AS16 | GIS-to-Air Bushing |  | phase | 2
AS17 | Each type of Supporting insulator for GIS |  | set | 3
AS18 | Each type of Spacer for GIS | No | set | 4
AS19 | Set of special tools, gauges and instruments for operation and maintenance of GIS (To be listed up by Bidder) |  | set | 2
AS20 | SF6 gas cylinders - 45 kg |  | no | 10
AS21 | 420kV CVT, Single-phase, 50Hz, 1425kVp BIL, 3 windings | sets | No. | 9
AS22 | 390kV rated voltage at 50°C, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 9
AS23 | Each type of Clamps and Fittings (Minimum 2 nos. or 10% of supplied quantity, whichever is the highest) |  | lot | 1
BS | 245kV Switchgear, equipment and connection
BS1 | Complete CB module for GIS |  | phase | 2
BS2 | Complete Operation Mechanism with accessories of CB for GIS |  | set | 1
BS3 | Tripping coil for GIS |  | no | 6
BS4 | Closing coil for GIS |  | no | 3
BS5 | Complete DS/ES module for GIS | set | phase | 2
BS6 | Complete Operation Mechanism with accessories of DS/ES for GIS |  | set | 1
BS7 | Complete HSES module for GIS | sets | phase | 2
BS8 | Complete Operation Mechanism with accessories of HSES for GIS |  | set | 1
BS9 | Complete CT module for GIS | sets | phase | 2
BS10 | Complete VT module for GIS | sets | phase | 2
BS11 | Gas pressure gauge |  | no | 6
BS12 | Pressure Relief Device |  | no | 6
BS13 | Rubber gaskets “O” rings and seals for SF6 gas |  | lot | 1
BS14 | All types of control valves for SF6 gas |  | lot | 1
BS15 | GIS-to-Air Bushing |  | phase | 2
BS16 | Each type of Supporting insulator for GIS |  | set | 3
BS17 | Each type of Spacer for GIS | No | set | 4
BS18 | Set of special tools, gauges and instruments for operation and maintenance of GIS (To be listed up by Bidder) |  | set | 2
BS19 | SF6 gas cylinders - 45 kg |  | no | 10
BS20 | 198kV rated voltage, 158 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | no | 4
BS21 | Each type of Clamps and Fittings (Minimum 2 nos. or 10% of supplied quantity, whichever is the highest) |  | lot | 1
CS | 145kV Switchgear, equipment and connection
CS1 | Complete CB module for GIS |  | phase | 3
CS2 | Complete Operation Mechanism with accessories of CB for GIS |  | set | 1
CS3 | Tripping coil for GIS |  | no | 6
CS4 | Closing coil for GIS |  | no | 3
CS5 | Complete DS/ES module for GIS | set | phase | 3
CS6 | Complete Operation Mechanism with accessories of DS/ES for GIS |  | set | 1
CS7 | Complete HSES module for GIS | sets | phase | 3
CS8 | Complete Operation Mechanism with accessories of HSES for GIS |  | set | 1
CS9 | Complete CT module for GIS | sets | phase | 3
CS10 | Complete VT module for GIS | sets | phase | 3
CS11 | Gas pressure gauge |  | no | 6
CS12 | Pressure Relief Device |  | no | 6
CS13 | Rubber gaskets “O” rings and seals for SF6 gas |  | lot | 1
CS14 | All types of control valves for SF6 gas |  | lot | 1
CS15 | Each type of Supporting insulator for GIS |  | set | 3
CS16 | Each type of Spacer for GIS | No | set | 4
CS17 | Set of special tools, gauges and instruments for operation and maintenance of GIS (To be listed up by Bidder) |  | set | 2
CS18 | SF6 gas cylinders - 45 kg |  | no | 10
CS19 | 120kV rated voltage, 102 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | no | 4
CS20 | Each type of Clamps and Fittings (Minimum 2 nos. or 10% of supplied quantity, whichever is the highest) |  | lot | 1
CS21 | 132kV XLPE Power Cable |  | m | 500
CS22 | 132kV Outdoor type Cable Sealing End |  | no. | 3
ES | Power Transformers
400/235/34.5kV Auto Transformer
ES1 | Each type of Bushings
| a | 420kV | no | 3
| b | 245kV | no | 3
| c | 36kV | no | 3
| d | Neutral | no | 1
ES2 | Buchholz Relay |  | Set | 1
ES3 | Pressure Relief Device |  | Set | 1
ES4 | WTI |  | Set | 2
ES5 | OTI |  | Set | 1
ES6 | Oil level monitor |  | Set | 1
ES7 | Complete Cooling Fan module with Motor |  | Set | 2
ES8 | Each type of Breathers module with Silicagel |  | Set | 2
ES9 | Set of O-rings and Gaskets with cutting tools |  | Set | 2
ES10 | Transformer oil 200 litter barrel |  | nos. | 20
ES11 | Oil Insulation Tester |  | No | 1
ES12 | Each type of Clamps and Fittings (Minimum 2 nos. or 10% of supplied quantity, whichever is the highest) |  | lot | 1
ES13 | Set of special tools, gauges and instruments for operation and maintenance of Transformer and OLTC (To be listed up by Bidder) | set | Set | 2
230/135/34.5kV Auto Transformer
ES1 | Each type of Bushings
| a | 245kV | no | 3
| b | 145kV | no | 3
| c | 36kV | no | 3
| d | Neutral | no | 1
ES2 | Buchholz Relay |  | Set | 1
ES3 | Pressure Relief Device |  | Set | 1
ES4 | WTI |  | Set | 2
ES5 | OTI |  | Set | 1
ES6 | Oil level monitor |  | Set | 1
ES7 | Complete Cooling Fan module with Motor |  | Set | 2
ES8 | Each type of Breathers module with Silicagel |  | Set | 2
ES9 | Set of O-rings and Gaskets with cutting tools |  | Set | 2
ES10 | Transformer oil 200 litter barrel |  | nos. | 20
ES11 | Each type of Clamps and Fittings (Minimum 2 nos. or 10% of supplied quantity, whichever is the highest) |  | lot | 1
ES12 | Set of special tools, gauges and instruments for operation and maintenance of Transformer and OLTC (To be listed up by Bidder) | set | Set | 2
FS | Control, Protection, SAS and Metering
FS1 | Each type of Protection Relays
| a | Line Differential Protection Relay with backup Distance Protection & Directional Earth Fault Protection Functions | no. | 24
| b | Transformer Differential Relay | no. | 3
| c | Directional & Non-directional Overcurrent and Directional & Non-directional Earth Fault Protection Relay | no. | 4
| d | BCU | no. | 4
FS2 | Heater |  | set | 6
FS3 | Humidity Sensors |  | set | 6
FS4 | Thermostat |  | set | 6
FS5 | Tripping relays |  | set | 8
FS6 | Each type of Trip circuit supervision relays (Bidder to list) |  | set | 8
FS7 | Each type of MCB |  | set | 2
FS8 | Ethernet Switches |  | nos. | 2
FS9 | Relay Test Block & socket | sets | no. | 1
GS | DFDR
GS1 | Each type MCBs |  | set | 1
GS2 | Each type of Ethernet switches |  | set | 1
KS | Battery, Charger & DC distribution
KS1 | Each type of Fuses |  | set | 1
KS2 | Each type of MCB for battery |  | no. | 2
KS3 | Each type of MCB for charger |  | no. | 2
LS | LVAC distribution
LS1 | 3-phase set LVAC board incoming MCCB |  | set | 1
LS2 | 3-phase sets outgoing MCCBs |  | set | 2
LS3 | 1-phase sets outgoing MCBs |  | set | 6
SS | Test Equipment
SS1 | SF6 Multi-Analyser for measurement of % SF6, Moisture and SO2 concetration (DILO) |  | No. | 1
SS2 | SF6 Gas leakage detector (infared type) |  | No. | 1
MS | Maintenance Equipment
MS1 | SF6 Gas Treatment Plant for Gas Filling, Recovery,Evacuation, Filtering, Drying and Storage (DILO) |  | No. | 1
MS2 | Portable vacuum pump suitable for SF6 circuit breaker | set | No. | 1
MS3 | 3-phase Portable earthing devices (for maintenance) with connectors and telescopic glass fibre operating pole suitable for plant shall be supplied (for each voltage level, respectively) |  | Set | 2
Total Price carried to Summary of Price Schedule (Spare, Maintanence & Test Equipement of S/S)

## Schedule B2(Purbachal)
Schedule B2 : Plant and Equipment Supplied from within the Employer's Country
New 400/230/132 kV Substation at Purbachal
(For deatailed description of the technical requirements please refer to clause 1.2.1: Technical Requirements for 400/230/132KV GIS Substation at Purbachal, Schedule A: Scope of Works, volume 3 of 3 of the bidding document)
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Local Currency (in BDT) |  | Remark
[5 empty] | Unit Price | Total Price
[5 empty] | EXW | EXW
|  |  |  | (1) | (2) | (3) = (1) x (2)
1A | 420 kV switchgear, equipment connection and steel structures
1A1 | 420kV GIS Line Feeder Bays |  | Set | 4
1A2 | 420kV GIS Auto Transformer Feeder Bays |  | Set | 3
1A3 | 420kV Bus Coupler Bays |  | Set | 2
1A4 | 420kV GIS Bus Section Bays |  | Set | 2
1A5 | 420 kV GIS type three phase LA |  | Set | 4
1A6 | 420kV GIS type Bus FES and Bus VT |  | Set | 4
1A7 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
1A8 | Standalone Partial Discharge measurement and analyzer system for Complete GIS |  | Lot | 1
AIS Switchgear, Equipment & Structure
1A9 | 390kV rated voltage at 50°C, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 21
1A10 | 420kV CVT, Single-phase, 50Hz, 1425kVp BIL, 3 windings |  | No. | 12
1A11 | 420kV, 4000A, single phase Wavetrap |  | No. | 4
1A12 | 400kV Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 400kV Switchyard including LA, CVT and WT conncetion
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1A13 | Insulator and fittings including all necessary clamps and connectors as required for completing 400kV GIS Switchyard
| i. | Insulator | Lot | 1
| ii. | Fittings & Clamps, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1A14 | Steel gantry each circuit of 400kV Transmission Line, Transformer & Equipment support structure including all necessary accessories required for completing 400kV GIS Switchyard
| i. | Steel Structure for T/L with Nut & Bolts
| a) | Gantry Column | No. | 5
| b) | Beam | No. | 4
| ii | Equipment Structure
| a) | LA | No. | 21
| b) | 420kV CVT | No. | 12
| iii. | Nut-Bolt | Lot | 1
| iv. | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1B | 245 kV switchgear, equipment connection and steel structures
1B1 | 245kV GIS Line Feeder Bays |  | Set | 2
1B2 | 245kV GIS Auto Transformer Feeder Bays |  | Set | 6
1B3 | 245kV Bus Coupler Bays |  | Set | 2
1B4 | 245kV Bus Section Bays |  | Set | 2
1B5 | 245kV GIS type Bus FES and Bus VT |  | Set | 4
1B6 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
AIS Switchgear, Equipment & Structure
1B7 | 198kV rated voltage, 158 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 24
1B8 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 230kV Switchyard
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1B9 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV Switchyard
| i. | Insulator | Lot | 1
| ii. | Fittings & Clamps, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1B10 | Steel gantry for each circuit of 245kV Transmission Line, Transformer & Equipment support Structure including all necessary accessories required for completing 230kV Switchyard
| i. | Steel Structure for T/L with Nut & Bolts
| a) | Gantry Column | No. | 3
| b) | Beam | No. | 2
| ii. | Steel Structure for 400/230kV & 230/132kV Transformers with Nut & Bolts
| a) | Gantry Column | No. | 14
| b) | Beam | No. | 12
| iii. | Equipment structure
| a) | LA | No. | 24
| iv. | Nut & Bolts | Lot | 1
| v. | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1C | 145 kV switchgear, equipment connection and steel structures
1C1 | 145kV GIS Line Feeder Bays |  | Set | 6
1C2 | 145kV GIS Auto Transformer Feeder Bays |  | Set | 2
1C3 | 145kV Bus Coupler Bays |  | Set | 2
1C4 | 145kV Bus Section Bays |  | Set | 2
1C5 | 145kV GIS type Bus FES and Bus VT |  | Set | 4
1C6 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
AIS Switchgear, Equipment & Structure
1C7 | 120kV rated voltage, 102 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 24
1C8 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 132kV Switchyard
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1C9 | Insulator and fittings including all necessary clamps and connectors as required for completing 132kV Switchyard
| i | Insulator, Post & Disk | Lot | 1
| ii | Fittings & Clamp, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1C10 | Steel gantry for each circuit of 145kV Transmission Line, Transformer & Equipment support Structure including all necessary accessories required for completing 132kV Switchyard
| i. | Steel Structure for T/Lwith Nut & Bolts
| a) | Gantry Column | No. | 8
| b) | Beam | No. | 6
| ii. | Equipment Structure
| a) | LA | No. | 24
| iii. | Nut & Bolts | Lot | 1
| iv. | LV power & control Cable tray including fitting, fixing accessories | Lot | 1
| v. | HV power Cable tray including fitting, fixing accessories | Lot | 1
1D | 36kV Switchgears, equipment connection and steel structures
1D1 | 36kV AIS Switchgears for Aux. Power Bays, comprises with:
| i) | 36kV, 630A, 31.5kA/3sec, 50Hz, 170kVp BIL, VCB with spring operating mechanism | Set | 2
| ii) | 36kV, 630A, 31.5kA/3sec, 50Hz, 170kVp BIL, single vertical/horizontal break, post type, motor operated Disconnector with Earth Switch | Set | 4
| iii) | 36kV, single-phase, 31.5kA/3sec, 50Hz, 170kVp BIL, Current Transformers | No. | 6
| iv) | 36kV, 31.5kA/3sec, single-phase 50Hz, 170kVp BIL, inductive Voltage Transformers | No. | 6
| v) | 30kV rated voltage, 24 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type | No. | 6
1D1.x | 36kV AIS Switchgears for Unloaded tertiary Auto-Transformer Bays, comprises with:
| i) | 36kV, 31.5kA/3sec, single-phase 50Hz, 170kVp BIL, inductive Voltage Transformers | No. | 9
| ii) | 30kV rated voltage, 24 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type | No. | 9
1D2 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 36kV Switchyard
| i) | Tubular Conductor and/or Flexible Conductor | Lot | 1
1D3 | Insulator and fittings including all necessary clamps and connectors as required for completing 36kV Switchyard
| i) | Insulator, Post & Disk | Lot | 1
| ii) | Fittings & Clamps, Connector | Lot | 1
| iii) | Nut-bolt | Lot | 1
1D4 | Steel structure for each circuit of Aux. power TR and Auto.TR tertiary side connection including all necessary accessories required for completing 36kV Switchyard
| i) | Equipment Structure with Nut & Bolts | Lot | 1
| ii) | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1D5 | 33kV Power Cable with associated material
| i) | 33kV, single phase, 300 sqmm XLPE cable | meter | 50
| ii) | 33kV, single phase, outdoor cable termination with accessories | No. | 12
1E | Power Transformers and Auxuliary Transformer
1E1 | 400/235/34.5 kV, 520/750 MVA (ONAN/ONAF), threephase outdoor type auto transformer equipped with delta connected 33 kV tertiary winding (brought out to terminal bushings) and Remote Tap Changer Control (RTCC) Panel. Direct Hot Spot Temperature measurement facility using fiber optic shall be available. |  | Set | 3
1E2 | On-line Dissolved Gas (multi-gas) & Moisture Analyzer system for 400/235/34.5 kV auto transformers. |  | Set | 3
1E3 | 230/135/34.5 kV, 350/450 MVA (ONAN/ONAF), three phase outdoor type auto transformer equipped with delta connected 33 kV tertiary winding (brought out to terminal bushings) and RTCC Panel. Direct Hot Spot Temperature measurement facility using fiber optic shall be available. |  | Set | 2
1E4 | Potable dissolved gas monitoring system for transformer |  | Set | 1
1E5 | 33/0.415 kV, 500kVA, three phase outdoor type earthing/auxiliary Zig-Zag transformer and BCT with off-load tap changer, associated outdoor neutral CTs and steel support structures including all necessary connections. |  | Set | 2
1E6 | CAFS of Fire Fighting system for transformer with water feeding equipment
| i) | 400/235/34.5 kV Auto-transformer | set | 3
| ii) | 230/135/34.5 kV Auto-transformer | set | 2
1F | Control, Protection, Substation Automation & Metering
400kV Circuit
1F1 | Control, protection and Monitoring including SAS Function for Overhead Line circuits, along with Control & Protection Cubicles |  | Set | 4
1F2 | Control, protection and Monitoring including SAS Function for Auto transformer circuits, along with Control & Protection Cubicles |  | Set | 3
1F3 | Control, Protection, Monitoring including SAS Function for Bus Coupler circuits, along with Control & Protection Cubicles |  | Set | 2
1F4 | Control, Protection, Monitoring including SAS Function for Bus section circuits, along with Control & Protection Cubicles |  | Set | 2
1F5 | Busbar Protection including SAS Function (400kV Circuit) [Main-1 & Mian-2, different make] |  | Set | 2
1F6 | Tariff metering comprises with : |  | Lot | 1
| i. | Meters (Main meter & Check meter in one set) | Set | 7
| ii. | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
230kV Circuits
1F7 | Control, Protection, Monitoring including SAS Function for overhead line circuits, along with Control & Protection Cubicles |  | Set | 2
1F8 | Control, Protection, Monitoring including SAS Function for Auto transformer (750MVA) circuits, along with Control & Protection Cubicles |  | Set | 3
1F9 | Control, protection and Monitoring including SAS Function for Auto transformer (450MVA) circuits, along with Control & Protection Cubicles |  | Set | 3
1F10 | Control, Protection, Monitoring including SAS Function for Bus Coupler circuits, along with Control & Protection Cubicles |  | Set | 2
1F11 | Control, Protection, Monitoring including SAS Function for Bus section circuits, along with Control & Protection Cubicles |  | Set | 2
1F12 | Busbar Protection including SAS Function (230kV Circuit) |  | Set | 1
1F13 | Tariff metering comprises with : |  | Lot | 1
| i. | Meters (Main & Check) | set | 8
| ii. | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
132kV Circuits
1F14 | Control, Protection, Monitoring including SAS Function for overhead line circuits, along with Control & Protection Cubicles |  | set | 6
1F15 | Control, Protection, Monitoring including SAS Function for Auto transformer circuits, along with Control & Protection Cubicles |  | set | 2
1F16 | Control, Protection, Monitoring & SAS for Bus Coupler circuits, including Control & Protection Cubicles |  | set | 2
1F17 | Control, Protection, Monitoring & SAS Function for Bus section circuits, including Control & Protection Cubicles |  | set | 2
1F18 | Busbar Protection including SAS Function (132kV Circuit) |  | set | 1
1F19 | Tariff metering comprises with : |  | Lot | 1
| i) | Meters (Main & Check) | Set | 8
| ii) | Complete Panel including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
36kV Circuit
1F20 | Control, Monitoring, Protection & SAS function for 33kV station power system, including Control & Protection Cubicles |  | Set | 2
1F21 | Control, Monitoring, Protection & SAS function for Unloaded tertiary side of Auto-tranformer, including Control & Protection Cubicles (can be merged with TR main/backup protection) |  | Set | 3
1F22 | Tariff metering comprises with : |  | Lot | 1
| i) | Meters (Main & Check) | set | 2
| ii) | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
1F23 | Substation Automation system |  | Lot | 1
1G | Digital Fault & Disturbance Recorder |  | Lot | 1
1H | Power Cable & GIL
1H1 | 420kV Gas Insulated Line (GIL) for seven (7) feeders, single phase encloser, which consist of four (4) T/L & three (3) T/R, terminating chambers complete with support structure, etc. The Length of GIL maybe different from each bay as per actual design (25 - 140 meter). Actual payment shall be as per final design. The Length given here is as single phase length. |  | m | 1800
1H2 | 245kV Gas Insulated Line (GIL) for eight (8) feeders, single phase encloser, which consist of two (2) T/L &six (6) T/R, terminating chambers complete with support structure, etc. The Length of GIL maybe different from each bay as per actual design (30 - 135 meter). Actual payment shall be as per final design. The Length given here is as single phase length |  | m | 1800
1H3 | 132kV, 2000sqmm (minimum), XLPE Power cable & termination
| i. | XLPE HV Power cable (Cable shall be laid in cable trench with flat formation arrangement) | m | 1900
| ii. | Outdoor type Cable Sealing End per phase with required necessary accessories for line & transformer bays | Nos. | 24
1H4 | Steel structure for each circuit of 132kV cable connection
| i. | Equipment Structure with Nut & Bolts
| a) | Outdoor type Cable Sealing End | Nos. | 24
1I | Multicore Cables for control, protection, metering & power circuits
| i. | LV Control Cable | Lot | 1
| ii. | LV Power Cable | Lot | 1
1J | Earthing and Lightning Protection system Design, supply and installation of earthing system and lightning protection screen including connections, connectors and clamps, to suit the substation overall arrangement and provide supporting design calculations.
1J1 | Earthing system for complete substation (grounding mesh, grounding rod/ needle type grounding rod) including GIS Building |  | Lot | 1
1J2 | Lightning Protection System for complete substation (overhead, mast type) |  | Lot | 1
1J3 | 3-phase Portable earthing devices (for maintenance) with connectors and telescopic glass fibre operating pole suitable for plant shall be supplied (for each voltage level, respectively) |  | Set | 2
1K | Batteries, Chargers & DC distribution board
1K1 | 110V Ni-cad Batteries with chargers & distribution board
| i. | for 400kV system
| a) | _110V Battery Banks, minimum 400Ah at the 5-hours rate of discharge | Set | 2
| b) | _Charger (IGBT Type), each float charge shall not be less than 150A rating | Set | 2
| c) | _110V DC Distribution panel, MCC type (LV S.W room, SPR, control Room) with Digital Display & Controller | Lot | 1
| d) | Inverter, Input- AC & DC, output -AC 230V 5kVA 60min | set | 2
| ii. | for 230kV & 132kV system
| a) | _110V Battery Banks, minimum 400Ah at the 5-hours rate of discharge | Set | 2
| b) | _Charger (IGBT Type), each float charge shall not be less than 150A rating | Set | 2
| c) | _110V DC Distribution panel, MCC type (Panel Room) with Digital Display & Controller | Lot | 1
1K2 | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks, minimum 200Ah at the 5-hours rate of discharge | Set | 2
| ii. | _Charger (IGBT Type) each float charge shall not be less than 120A rating | Set | 2
| iii. | _48V DC Distribution Panel with Digital Display & Controller | Lot | 1
1L | LVAC Distribution
1L1 | AC 415V / 230V Distribution panels (MCC type, LV S.W room, Each Panel & Control room, Generator room etc) with Digital Display & Controller |  | Lot | 1
1L2 | Tariff metering at LV side |  | Lot | 1
1M | Civil Works, Building and Foundation (Details in Schedule B4)
1M1 | Complete land development |  | Refer to Schedule B4
1M2 | Complete civil items required for outdoor works |  | Refer to Schedule B4
1M3 | i. | Complete civil works for 420kV Indoor GIS Building including Protection & Metering Room, Control Room, 110V Battery Room, 48 Battery Room, Warehouse etc.
| a) | _Foundation works | Refer to Schedule B4
| b) | _Super structures | Refer to Schedule B4
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture etc. | Refer to Schedule B4
| d) | _10 ton EOT crane (price for supply of EOT crane) | No. | 1
| e) | _Warehouse_separate spare materials by installing shelves and labels. | Refer to Schedule B4
| ii. | Complete civil works for 245kV cum 132kV Indoor GIS Building including Protection & Metering Room, 110V Battery Room etc. | Refer to Schedule B4
| a) | _Foundation works | Refer to Schedule B4
| b) | _Super structures | Refer to Schedule B4
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture, etc. | Refer to Schedule B4
| d) | _10 ton EOT crane (price for supply of EOT crane) | No. | 1
| iii. | Emergency auxulary power room & water feeding room | Refer to Schedule B4
| a) | _Foundation works | Refer to Schedule B4
| b) | _Super structures | Refer to Schedule B4
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture, etc. | Refer to Schedule B4
| d) | _Complete civil work for CAF system including pipe network | Refer to Schedule B4
1M4 | Testing of Foundation |  | Refer to Schedule B4
1N | Lighting, small power, air conditioning and Ventilation, Fire Fighting System & CCTV
1N1 | Indoor Lighting (LED type), small power, air conditioning (except GIS Hall) and Ventilation (GIS hall, Batterys Rooms, other rooms, etc.) and emergency DC lighting for Indoor. |  | Lot | 1
1N2 | Lighting (LED type) for outside building for security, roadway, switchyard |  | Lot | 1
1N3 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For 230kV cum 132kV GIS Hall & Panel Room | Lot | 1
| ii) | Fire Fighting system For 400kV GIS Hall & Panel Room | Lot | 1
| iii) | Fire Fighting system For Control Room | Lot | 1
1N4 | Complete CCTV with motion sensor |  | Lot | 1
1O | Fibre Optic Multiplexer Equipment & PLC Equipment and System for Communication and Protection at Local & Remote end substations - 87 or 21 relay for each transmission line protection (through fibre cores) - 21 relay carrier signal (main and back-up) - SCADA data from switchgear and control system - IP and Analog telephone system - Hot-line telephone system All PLC terminal equipment at remote end substations are ABB make
1O1 | Indoor Fibre Optic Multiplexer, at Local end SS, Equipment each comprising
| i. | ADM with TP unit without booster with Panels (Front opening, Swing Frame type) & accessories | Set | 1
| ii. | IDF/SDF | Set | 1
| iii. | Cables | Lot | 1
| iv. | EOW telephone with board | Set | 1
| v. | Panel including wiring, lighting, filtering fan, humidity controller, heater, power socket & other accessories | Lot | 1
| vi. | All other Accessories not included above | Lot | 1
1O2 | Other Indoor equipment, at Local end SS
| i. | PABX Card (FXO) | Set | 1
| ii. | Primary phone (IP phone) | No. | 2
| iii. | Secondary phone (2W phone) | No. | 10
| iv. | Indoor MDF | Set | 1
1O3 | Outdoor equipment, at Local end SS
| i. | Underground optical fiber cable, armoured, 48 core | Lot | 1
| ii. | Pigtail cables | Lot | 1
| iii. | Outdoor termination box | Set | 1
1O4 | Extension/Adaptation of Indoor Fibre Optic Multiplexer Equipment & system at remote end substations each comprising
| i. | Optical STM-16 Card for each 400 kV line at remote end | Lot | 1
| ii. | Optical STM-4 Card for each 230 kV line at remote end | Lot | 1
| iii. | Optical STM-4 Card for each 132 kV line at remote end | Lot | 1
| iv. | Required no. of cards with 4 commands for distance protection after detail design | Lot | 1
| v. | Optical Booster, if required | Lot | 1
| vi. | Outdoor termination box | Set | 1
| vii. | Cables, ODF, MDF, panels as required | Lot | 1
1O5 | PLC equipment at Local end SS
| i. | Indoor PLC Equipment with all acessories & Panels (Front opening, Swing Frame type) | Set | 4
| ii. | Line matching unit | No. | 8
| iii. | Cables & other accessories for complete PLCC system | Lot | 1
| iv. | Indoor PLC Equipment & accessories as complete system for Remote end station | Lot | 1
1O6 | Installation, testing & commissioning |  | Lot | 1
1P | SCADA system for Telecontrol and Telemetering
1P1 | i. | Equipment at Substation
| a) | Gateway (server, engineering software) | Set | 2
| b) | Ethernet Switch | Set | 2
| c) | Hardware Firewall | Set | 1
| d) | Complete Panel ( Swing Frame type) including wiring, lighting, heater, humidity controller & other accessories | Lot | 1
| e) | Cables | Lot | 1
| f) | All Other Accessories | Lot | 1
| ii. | Integration work with Master & Backup NLDC including Engineering & Commissioning | Lot | 1
1R | Generator for Emergency Aux. Power (with smoke reduction device)
1R1 | 250kW 0.415kV, 50Hz Diesel generator • Expected Operation Time 24h • Noise level Less than 55dB at a distance of 10m • Fuel Tank Capacity: Adequate capacity for three days’continuous operation • With Smoke reduction device |  | Set | 1
1S | Other equipment
1S1 | Scissor Lift : Battery type for one person / Minimum working height greater than 10m |  | Set | 1
1S2 | Emergency Interphone (each room) |  | Lot | 1
Total Price( for New Purbachal 400/230/132kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Purbachal 400/230/132kV SS)……………………………………………………………

## Schedule B3 (Purbachal)
Schedule B3: Design Services
New 400/230/132 kV Substation at PURBACHAL
Item No | Description of Required Services | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | foreign portion | foreign portion | local portion | local portion
|  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5)=(1) x (4)
1 | Design and engineering services of the whole substation, local and foreign part | Lump sum | 1
2 | Overvoltage and Insulation Co-ordination study for 400kV Substaion | Lump sum | 1
3 | Relay Co-ordination study for the Substation with software | Lump sum | 1
New 400/230/132 kV Substation at Purbachal
Subtotal - to Schedule B5 - Grand Total

## Schedule B4.1(Purbachal)
Schedule B4.1 : Installation and Other Services
New 400/230/132 kV Substation at Purbachal
(For deatailed description of the technical requirements please refer to clause 1.2.1: Technical Requirements for 400/230/132KV GIS Substation at Purbachal, Schedule A: Scope of Works, volume 3 of 3 of the bidding document)
Item No. | Description of Equipment Requirement |  | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
[5 empty] | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | (1) | (2) | (3) = (1) x (2) | (4) | (5) = (1) x (4)
1A | 420 kV switchgear, equipment connection and steel structures
1A1 | 420kV GIS Line Feeder Bays |  | Set | 4
1A2 | 420kV GIS Auto Transformer Feeder Bays |  | Set | 3
1A3 | 420kV Bus Coupler Bays |  | Set | 2
1A4 | 420kV GIS Bus Section Bays |  | Set | 2
1A5 | 420 kV GIS type three phase LA |  | Set | 4
1A6 | 420kV GIS type Bus FES and Bus VT |  | Set | 4
1A7 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
1A8 | Standalone Partial Discharge measurement and analyzer system for Complete GIS |  | Lot | 1
AIS Switchgear, Equipment & Structure
1A9 | 390kV rated voltage at 50°C, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 21
1A10 | 420kV CVT, Single-phase, 50Hz, 1425kVp BIL, 3 windings |  | No. | 12
1A11 | 420kV, 4000A, single phase Wavetrap |  | No. | 4
1A12 | 400kV Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 400kV Switchyard including LA, CVT and WT conncetion
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1A13 | Insulator and fittings including all necessary clamps and connectors as required for completing 400kV GIS Switchyard
| i. | Insulator | Lot | 1
| ii. | Fittings & Clamps, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1A14 | Steel gantry each circuit of 400kV Transmission Line, Transformer & Equipment support structure including all necessary accessories required for completing 400kV GIS Switchyard
| i. | Steel Structure for T/L with Nut & Bolts
| a) | Gantry Column | No. | 5
| b) | Beam | No. | 4
| ii | Equipment Structure
| a) | LA | No. | 21
| b) | 420kV CVT | No. | 12
| iii. | Nut-Bolt | Lot | 1
| iv. | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1B | 245 kV switchgear, equipment connection and steel structures
1B1 | 245kV GIS Line Feeder Bays |  | Set | 2
1B2 | 245kV GIS Auto Transformer Feeder Bays |  | Set | 6
1B3 | 245kV Bus Coupler Bays |  | Set | 2
1B4 | 245kV Bus Section Bays |  | Set | 2
1B5 | 245kV GIS type Bus FES and Bus VT |  | Set | 4
1B6 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
AIS Switchgear, Equipment & Structure
1B7 | 198kV rated voltage, 158 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 24
1B8 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 230kV Switchyard
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1B9 | Insulator and fittings including all necessary clamps and connectors as required for completing 230kV Switchyard
| i. | Insulator | Lot | 1
| ii. | Fittings & Clamps, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1B10 | Steel gantry for each circuit of 245kV Transmission Line, Transformer & Equipment support Structure including all necessary accessories required for completing 230kV Switchyard
| i. | Steel Structure for T/L with Nut & Bolts
| a) | Gantry Column | No. | 3
| b) | Beam | No. | 2
| ii. | Steel Structure for 400/230kV & 230/132kV Transformers with Nut & Bolts
| a) | Gantry Column | No. | 14
| b) | Beam | No. | 12
| iii. | Equipment structure
| a) | LA | No. | 24
| iv. | Nut & Bolts | Lot | 1
| v. | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1C | 145 kV switchgear, equipment connection and steel structures
1C1 | 145kV GIS Line Feeder Bays |  | Set | 6
1C2 | 145kV GIS Auto Transformer Feeder Bays |  | Set | 2
1C3 | 145kV Bus Coupler Bays |  | Set | 2
1C4 | 145kV Bus Section Bays |  | Set | 2
1C5 | 145kV GIS type Bus FES and Bus VT |  | Set | 4
1C6 | Busbar extension module, each set comprises with sufficient buffer gas compartments and appropriate disconnect facilities |  | Set | 2
AIS Switchgear, Equipment & Structure
1C7 | 120kV rated voltage, 102 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type |  | No. | 24
1C8 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 132kV Switchyard
| i. | Tubular Conductor and/or Flexible Conductor | Lot | 1
1C9 | Insulator and fittings including all necessary clamps and connectors as required for completing 132kV Switchyard
| i | Insulator, Post & Disk | Lot | 1
| ii | Fittings & Clamp, Connector | Lot | 1
| iii. | Nut-bolt | Lot | 1
1C10 | Steel gantry for each circuit of 145kV Transmission Line, Transformer & Equipment support Structure including all necessary accessories required for completing 132kV Switchyard
| i. | Steel Structure for T/Lwith Nut & Bolts
| a) | Gantry Column | No. | 8
| b) | Beam | No. | 6
| ii. | Equipment Structure
| a) | LA | No. | 24
| iii. | Nut & Bolts | Lot | 1
| iv. | LV power & control Cable tray including fitting, fixing accessories | Lot | 1
| v. | HV power Cable tray including fitting, fixing accessories | Lot | 1
1D | 36kV Switchgears, equipment connection and steel structures
1D1 | 36kV AIS Switchgears for Aux. Power Bays, comprises with:
| i) | 36kV, 630A, 31.5kA/3sec, 50Hz, 170kVp BIL, VCB with spring operating mechanism | Set | 2
| ii) | 36kV, 630A, 31.5kA/3sec, 50Hz, 170kVp BIL, single vertical/horizontal break, post type, motor operated Disconnector with Earth Switch | Set | 4
| iii) | 36kV, single-phase, 31.5kA/3sec, 50Hz, 170kVp BIL, Current Transformers | No. | 6
| iv) | 36kV, 31.5kA/3sec, single-phase 50Hz, 170kVp BIL, inductive Voltage Transformers | No. | 6
| v) | 30kV rated voltage, 24 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type | No. | 6
1D1.x | 36kV AIS Switchgears for Unloaded tertiary Auto-Transformer Bays, comprises with:
| i) | 36kV, 31.5kA/3sec, single-phase 50Hz, 170kVp BIL, inductive Voltage Transformers | No. | 9
| ii) | 30kV rated voltage, 24 kV(rms) continuous operating voltage at 50oC, 10kA nominal discharge current, 50Hz, gapless metal oxide type, single phase Surge Arresters, outdoor type | No. | 9
1D2 | Rigid tubular conductor and/or stranded conductors including accessories for each connection as required for completing 36kV Switchyard
| i) | Tubular Conductor and/or Flexible Conductor | Lot | 1
1D3 | Insulator and fittings including all necessary clamps and connectors as required for completing 36kV Switchyard
| i) | Insulator, Post & Disk | Lot | 1
| ii) | Fittings & Clamps, Connector | Lot | 1
| iii) | Nut-bolt | Lot | 1
1D4 | Steel structure for each circuit of Aux. power TR and Auto.TR tertiary side connection including all necessary accessories required for completing 36kV Switchyard
| i) | Equipment Structure with Nut & Bolts | Lot | 1
| ii) | LV power & control cable tray including fitting, fixing accessories | Lot | 1
1D5 | 33kV Power Cable with associated material
| i) | 33kV, single phase, 300 sqmm XLPE cable | meter | 50
| ii) | 33kV, single phase, outdoor cable termination with accessories | No. | 12
1E | Power Transformers and Auxuliary Transformer
1E1 | 400/235/34.5 kV, 520/750 MVA (ONAN/ONAF), threephase outdoor type auto transformer equipped with delta connected 33 kV tertiary winding (brought out to terminal bushings) and Remote Tap Changer Control (RTCC) Panel. Direct Hot Spot Temperature measurement facility using fiber optic shall be available. |  | Set | 3
1E2 | On-line Dissolved Gas (multi-gas) & Moisture Analyzer system for 400/235/34.5 kV auto transformers. |  | Set | 3
1E3 | 230/135/34.5 kV, 350/450 MVA (ONAN/ONAF), three phase outdoor type auto transformer equipped with delta connected 33 kV tertiary winding (brought out to terminal bushings) and RTCC Panel. Direct Hot Spot Temperature measurement facility using fiber optic shall be available. |  | Set | 2
1E4 | Potable dissolved gas monitoring system for transformer |  | Set | 1
1E5 | 33/0.415 kV, 500kVA, three phase outdoor type earthing/auxiliary Zig-Zag transformer and BCT with off-load tap changer, associated outdoor neutral CTs and steel support structures including all necessary connections. |  | Set | 2
1E6 | CAFS of Fire Fighting system for transformer with water feeding equipment
| i) | 400/235/34.5 kV Auto-transformer | set | 3
| ii) | 230/135/34.5 kV Auto-transformer | set | 2
1F | Control, Protection, Substation Automation & Metering
400kV Circuit
1F1 | Control, protection and Monitoring including SAS Function for Overhead Line circuits, along with Control & Protection Cubicles |  | Set | 4
1F2 | Control, protection and Monitoring including SAS Function for Auto transformer circuits, along with Control & Protection Cubicles |  | Set | 3
1F3 | Control, Protection, Monitoring including SAS Function for Bus Coupler circuits, along with Control & Protection Cubicles |  | Set | 2
1F4 | Control, Protection, Monitoring including SAS Function for Bus section circuits, along with Control & Protection Cubicles |  | Set | 2
1F5 | Busbar Protection including SAS Function (400kV Circuit) [Main-1 & Mian-2, different make] |  | Set | 2
1F6 | Tariff metering comprises with : |  | Lot | 1
| i. | Meters (Main meter & Check meter in one set) | Set | 7
| ii. | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
230kV Circuits
1F7 | Control, Protection, Monitoring including SAS Function for overhead line circuits, along with Control & Protection Cubicles |  | Set | 2
1F8 | Control, Protection, Monitoring including SAS Function for Auto transformer (750MVA) circuits, along with Control & Protection Cubicles |  | Set | 3
1F9 | Control, protection and Monitoring including SAS Function for Auto transformer (450MVA) circuits, along with Control & Protection Cubicles |  | Set | 3
1F10 | Control, Protection, Monitoring including SAS Function for Bus Coupler circuits, along with Control & Protection Cubicles |  | Set | 2
1F11 | Control, Protection, Monitoring including SAS Function for Bus section circuits, along with Control & Protection Cubicles |  | Set | 2
1F12 | Busbar Protection including SAS Function (230kV Circuit) |  | Set | 1
1F13 | Tariff metering comprises with : |  | Lot | 1
| i. | Meters (Main & Check) | set | 8
| ii. | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
132kV Circuits
1F14 | Control, Protection, Monitoring including SAS Function for overhead line circuits, along with Control & Protection Cubicles |  | set | 6
1F15 | Control, Protection, Monitoring including SAS Function for Auto transformer circuits, along with Control & Protection Cubicles |  | set | 2
1F16 | Control, Protection, Monitoring & SAS for Bus Coupler circuits, including Control & Protection Cubicles |  | set | 2
1F17 | Control, Protection, Monitoring & SAS Function for Bus section circuits, including Control & Protection Cubicles |  | set | 2
1F18 | Busbar Protection including SAS Function (132kV Circuit) |  | set | 1
1F19 | Tariff metering comprises with : |  | Lot | 1
| i) | Meters (Main & Check) | Set | 8
| ii) | Complete Panel including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
36kV Circuit
1F20 | Control, Monitoring, Protection & SAS function for 33kV station power system, including Control & Protection Cubicles |  | Set | 2
1F21 | Control, Monitoring, Protection & SAS function for Unloaded tertiary side of Auto-tranformer, including Control & Protection Cubicles (can be merged with TR main/backup protection) |  | Set | 3
1F22 | Tariff metering comprises with : |  | Lot | 1
| i) | Meters (Main & Check) | set | 2
| ii) | Complete Panel (Front opening, Swing frame type) including wiring, lighting, heater, humidity controller, TTB, MCBs & other accessories | Lot | 1
1F23 | Substation Automation system |  | Lot | 1
1G | Digital Fault & Disturbance Recorder |  | Lot | 1
1H | Power Cable & GIL
1H1 | 420kV Gas Insulated Line (GIL) for seven (7) feeders, single phase encloser, which consist of four (4) T/L & three (3) T/R, terminating chambers complete with support structure, etc. The Length of GIL maybe different from each bay as per actual design (25 - 140 meter). Actual payment shall be as per final design. The Length given here is as single phase length. |  | m | 1800
1H2 | 245kV Gas Insulated Line (GIL) for eight (8) feeders, single phase encloser, which consist of two (2) T/L &six (6) T/R, terminating chambers complete with support structure, etc. The Length of GIL maybe different from each bay as per actual design (30 - 135 meter). Actual payment shall be as per final design. The Length given here is as single phase length |  | m | 1800
1H3 | 132kV, 2000sqmm (minimum), XLPE Power cable & termination
| i. | XLPE HV Power cable (Cable shall be laid in cable trench with flat formation arrangement) | m | 1900
| ii. | Outdoor type Cable Sealing End per phase with required necessary accessories for line & transformer bays | Nos. | 24
1H4 | Steel structure for each circuit of 132kV cable connection
| i. | Equipment Structure with Nut & Bolts
| a) | Outdoor type Cable Sealing End | Nos. | 24
1I | Multicore Cables for control, protection, metering & power circuits
| i. | LV Control Cable | Lot | 1
| ii. | LV Power Cable | Lot | 1
1J | Earthing and Lightning Protection system Design, supply and installation of earthing system and lightning protection screen including connections, connectors and clamps, to suit the substation overall arrangement and provide supporting design calculations.
1J1 | Earthing system for complete substation (grounding mesh, grounding rod/ needle type grounding rod) including GIS Building |  | Lot | 1
1J2 | Lightning Protection System for complete substation (overhead, mast type) |  | Lot | 1
1J3 | 3-phase Portable earthing devices (for maintenance) with connectors and telescopic glass fibre operating pole suitable for plant shall be supplied (for each voltage level, respectively) |  | Set | 2
1K | Batteries, Chargers & DC distribution board
1K1 | 110V Ni-cad Batteries with chargers & distribution board
| i. | for 400kV system
| a) | _110V Battery Banks, minimum 400Ah at the 5-hours rate of discharge | Set | 2
| b) | _Charger (IGBT Type), each float charge shall not be less than 150A rating | Set | 2
| c) | _110V DC Distribution panel, MCC type (LV S.W room, SPR, control Room) with Digital Display & Controller | Lot | 1
| d) | Inverter, Input- AC & DC, output -AC 230V 5kVA 60min | set | 2
| ii. | for 230kV & 132kV system
| a) | _110V Battery Banks, minimum 400Ah at the 5-hours rate of discharge | Set | 2
| b) | _Charger (IGBT Type), each float charge shall not be less than 150A rating | Set | 2
| c) | _110V DC Distribution panel, MCC type (Panel Room) with Digital Display & Controller | Lot | 1
1K2 | 48V Ni-cad Batteries with chargers & distribution board
| i. | _48V battery Banks, minimum 200Ah at the 5-hours rate of discharge | Set | 2
| ii. | _Charger (IGBT Type) each float charge shall not be less than 120A rating | Set | 2
| iii. | _48V DC Distribution Panel with Digital Display & Controller | Lot | 1
1L | LVAC Distribution
1L1 | AC 415V / 230V Distribution panels (MCC type, LV S.W room, Each Panel & Control room, Generator room etc) with Digital Display & Controller |  | Lot | 1
1L2 | Tariff metering at LV side |  | Lot | 1
1M | Civil Works, Building and Foundation
1M1* | Complete land development
| i. | Complete compacted land development with carried/dredged earthfilling including approach road | CuM | 378312
| ii. | Slpoe protection
| a) | _Slpoe (1V:2H) protection with turfing | sqm | 6675
| b) | _Slpoe (1V:2H) protection with CC block | sqm | 6675
1M2* | Complete civil items required for outdoor works
| i | Outdoor gantry foundation in 400kV switchyard
| a) | _Gantry column | Nos | 5
| ii | Outdoor equipment foundation in 400kV switchyard
| a) | _SA/LA | Nos | 21
| b) | _CVT | Nos | 12
| c) | _Busduct support | Lot | 1
| iii. | Outdoor gantry foundation in 230kV switchyard
| a) | _Gantry column | Nos | 17
| iv. | Outdoor equipment foundation in 230kV switchyard
| a) | _SA/LA | Nos | 24
| v. | Outdoor gantry foundation in 132kV switchyard
| a) | _Gantry column | Nos | 8
| vi. | Outdoor equipment foundation in 132kV switchyard
| a) | _SA/LA | Nos | 24
| vii. | Outdoor equipment foundation 33kV switchyard
| a) | _CB | Set** | 2
| b) | _DS | Set** | 4
| c) | _CT | Nos | 6
| d) | _IVT | Nos | 15
| e) | _SA/LA | Nos | 15
| f) | _Zigzag/auxilary transformer | Nos | 2
| g) | _Tertiary bus connection | Nos | 2
| viii. | Transformer foundation | Nos | 5
| ix. | Blast wall with foundation | Nos | 4
| x. | Property line demarkation | Meter | 950
| xi. | Security boundary wall for overall plan | Meter | 857
| xii. | Substation main gate | Nos | 2
| xiii. | Approach road (pavement width 6m) | Meter | 60
| xiv. | Internal road
| a) | _6m wide road | Meter | 400
| b) | _4.5m wide road | Meter | 850
| c) | _3m wide road | Meter | 50
| xv. | Surface drain | Meter | 858
| xvi. | Cable trench/tunnel with soakpit
| a) | _For LV control, communication, relay etc. cables | Lot | 1
| b) | _For HV power cables | Meter | 280
| xvii. | Whole substation surface finishing with drainage system including outlet (excluding surface drain) | Lot | 1
| xviii. | Gravelling in switchyard area | Lot | 1
| xix. | Septic tank (capacity: 25users for 5 years) and soakpit | Nos | 4
| xx. | Pump shed including deep tubewell, motor, pump, water reservoir, water pipe line, electrical connetion etc. | Nos | 4
| xxi. | Guard house | Nos | 1
| xxii. | Sentry post | Nos | 4
| xxiii. | Car port | Nos | 1
| xxiv. | RCC box culvert | Nos | 1
1M3 | i. | Complete civil works for 420kV Indoor GIS Building including Protection & Metering Room, Control Room, 110V Battery Room, 48 Battery Room, Warehouse etc.
| a) | _Foundation works | Lot | 1
| b) | _Super structures | Lot | 1
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture etc. | Lot | 1
| d) | _10 ton EOT crane installation arrangement (excluding price for supply of EOT crane) | Lot | 1
| e) | _Warehouse_separate spare materials by installing shelves and labels. | Lot | 1
| ii. | Complete civil works for 245kV cum 132kV Indoor GIS Building including Protection & Metering Room, 110V Battery Room etc.
| a) | _Foundation works | Lot | 1
| b) | _Super structures | Lot | 1
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture, etc. | Lot | 1
| d) | _10 ton EOT crane installation arrangement (excluding price for supply of EOT crane) | Lot | 1
| iii. | Emergency auxulary power room & water feeding room
| a) | _Foundation works | Lot | 1
| b) | _Super structures | Lot | 1
| c) | _All finish works like rendering, painting, water supply, sanitary, floor finish, furniture, etc. | Lot | 1
| d) | _Complete civil work for CAF system including pipe network | Lot | 1
1M4 | Testing of foundation
| i | Compression test of pile | No | 5
| ii | Uplift test of pile | No | 3
* actual payment shall be as per actual work at site
** set means three phase
1N | Lighting, small power, air conditioning and Ventilation, Fire Fighting System & CCTV
1N1 | Indoor Lighting (LED type), small power, air conditioning (except GIS Hall) and Ventilation (GIS hall, Batterys Rooms, other rooms, etc.) and emergency DC lighting for Indoor. |  | Lot | 1
1N2 | Lighting (LED type) for outside building for security, roadway, switchyard |  | Lot | 1
1N3 | Fire Fighting system for GIS Hall & Control Room
| i) | Fire Fighting system For 230kV cum 132kV GIS Hall & Panel Room | Lot | 1
| ii) | Fire Fighting system For 400kV GIS Hall & Panel Room | Lot | 1
| iii) | Fire Fighting system For Control Room | Lot | 1
1N4 | Complete CCTV with motion sensor |  | Lot | 1
1O | Fibre Optic Multiplexer Equipment & PLC Equipment and System for Communication and Protection at Local & Remote end substations - 87 or 21 relay for each transmission line protection (through fibre cores) - 21 relay carrier signal (main and back-up) - SCADA data from switchgear and control system - IP and Analog telephone system - Hot-line telephone system All PLC terminal equipment at remote end substations are ABB make
1O1 | Indoor Fibre Optic Multiplexer, at Local end SS, Equipment each comprising
| i. | ADM with TP unit without booster with Panels (Front opening, Swing Frame type) & accessories | Set | 1
| ii. | IDF/SDF | Set | 1
| iii. | Cables | Lot | 1
| iv. | EOW telephone with board | Set | 1
| v. | Panel including wiring, lighting, filtering fan, humidity controller, heater, power socket & other accessories | Lot | 1
| vi. | All other Accessories not included above | Lot | 1
1O2 | Other Indoor equipment, at Local end SS
| i. | PABX Card (FXO) | Set | 1
| ii. | Primary phone (IP phone) | No. | 2
| iii. | Secondary phone (2W phone) | No. | 10
| iv. | Indoor MDF | Set | 1
1O3 | Outdoor equipment, at Local end SS
| i. | Underground optical fiber cable, armoured, 48 core | Lot | 1
| ii. | Pigtail cables | Lot | 1
| iii. | Outdoor termination box | Set | 1
1O4 | Extension/Adaptation of Indoor Fibre Optic Multiplexer Equipment & system at remote end substations each comprising
| i. | Optical STM-16 Card for each 400 kV line at remote end | Lot | 1
| ii. | Optical STM-4 Card for each 230 kV line at remote end | Lot | 1
| iii. | Optical STM-4 Card for each 132 kV line at remote end | Lot | 1
| iv. | Required no. of cards with 4 commands for distance protection after detail design | Lot | 1
| v. | Optical Booster, if required | Lot | 1
| vi. | Outdoor termination box | Set | 1
| vii. | Cables, ODF, MDF, panels as required | Lot | 1
1O5 | PLC equipment at Local end SS
| i. | Indoor PLC Equipment with all acessories & Panels (Front opening, Swing Frame type) | Set | 4
| ii. | Line matching unit | No. | 8
| iii. | Cables & other accessories for complete PLCC system | Lot | 1
| iv. | Indoor PLC Equipment & accessories as complete system for Remote end station | Lot | 1
1O6 | Installation, testing & commissioning |  | Lot | 1
1P | SCADA system for Telecontrol and Telemetering
1P1 | i. | Equipment at Substation
| a) | Gateway (server, engineering software) | Set | 2
| b) | Ethernet Switch | Set | 2
| c) | Hardware Firewall | Set | 1
| d) | Complete Panel ( Swing Frame type) including wiring, lighting, heater, humidity controller & other accessories | Lot | 1
| e) | Cables | Lot | 1
| f) | All Other Accessories | Lot | 1
| ii. | Integration work with Master & Backup NLDC including Engineering & Commissioning | Lot | 1
1R | Generator for Emergency Aux. Power (with smoke reduction device)
1R1 | 250kW 0.415kV, 50Hz Diesel generator • Expected Operation Time 24h • Noise level Less than 55dB at a distance of 10m • Fuel Tank Capacity: Adequate capacity for three days’continuous operation • With Smoke reduction device |  | Set | 1
1S | Other equipment
1S1 | Scissor Lift : Battery type for one person / Minimum working height greater than 10m |  | Set | 1
1S2 | Emergency Interphone (each room) |  | Lot | 1
Total Price (for New Purbachal 400/230/132kV SS) carried to Summary of Price Schedule
Total Price in words ( for New Purbachal 400/230/132kV SS)……………………………………………………………

## Schedule B4.2 (Cost of FAT)
Schedule B4.2: Installation and Other Services
Item No. | Description of Required Services | Unit | Quantity | Foreign Currency (in USD) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  | (1) | (2) | (3) = (1) x (2)
2 | Additional Services (Provisional Sum)*
2.1 | Employer's Factory Acceptance Tests Witness (refer to clause 1.3 (b), Scope of Works, Volume 2 of the bdding document) | Lot | 1 | 115500 | 115500 | - | -
2.2 | International Training (refer to clause 1.3 (a), Scope of Works, Volume 2 of the bdding document) | Lot | 1 | 66000 | 66000 | - | -
2.3 | Local O&M Training (refer to clause 1.3 (c), Scope of Works, Volume 2 of the bdding document) | Lot | 1 | 33000 | 33000 | - | -
Total Price for Additional Services |  |  |  |  | 214500
(carried to Schedule-5 : Grand Summary)
*These costs are fixed ceiling and will be included in total price. But the payment shall be at actual.

## Schedule B5
Schedule B5: Grand Summary
Total price
|  | Foreign Currency (in……….) | Local Currency (in BDT)
New 400/230/132 kV Substation at PURBACHAL
Schedule No. B1: | Plant and Equipment Supplied from Outside the Employer's Country
Schedule No.B2: | Plant & Equipment Supplied from within the Employer’s Country
Schedule No. B3: | Design Services
Schedule No. B4.1: | Installation and Other Services
New 400/230/132 kV Substation at PURBACHAL
Grand Total
Mandatory Spare, Maintanence & Test Equipement
Schedule No. B1: | Mandatory Spare, Maintanence & Test Equipement Supplied from Outside the Employer's Country
Mandatory Spare, Maintanence & Test Equipement
Grand Total
Additional Services
Schedule No. B4.2: | Installation and Other Services : Additional Services (Provisional Sum) | USD 214,500.00
Additional Services |  | USD 214,500.00
Grand Total
Grand Grand Total

## Schedule B6
Schedule B6: Recommended Spare Parts
No | Description | Unit | Quantity | Foreign Currency (in……….) |  | Local Currency (in BDT)
|  |  |  | Unit Price | Total Price | Unit Price | Total Price
|  |  |  | CIP | CIP | EXW | EXW
|  |  | (1) | (2) | (3)=(1)x(2) | (4) | (5)=(1)x(4)

## Code
Country of Origin
Item | Country | Code