## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | September 2019 |  | August 2019 |  | September 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12717 | 01/09/19 | 12738 | 05/08/19 | 11623 | 19/09/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 6957 | 27/09/19 | 6449 | 14/08/19 | 6739.4 | 21/09/18 | - | -
|  |  | 8:00 |  | 8:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12717 | 01/09/19 | 12738 | 05/08/19 | 11623 | 19/09/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10636.2 | 01/09/19 | 10539.2 | 22/08/19 | 9788 | 19/09/18 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 21:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12717 | 01/09/19 | 12738 | 05/08/19 | 11623 | 19/09/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11679.0667 |  | 11505.9 |  | 10919.57 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 9378.1933 |  | 891.59 |  | 8779.26 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 930 | 22/09/19 | 934 | 18/08/19 | 788 | 21/09/18 | 956 | 27/3/2019
|  |  | 17:00 |  | 17:00 |  | 22:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 194 | 19/09/19 | 192 | 31/08/19 | 186 | 18/09/18 | 194 | 12/06/19
|  |  | 20:00 |  | 20:00 |  | 22:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3805.7195 |  | 3752.29 |  | 3397.09 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 124.6645 |  | 135.33 |  | 104.37
22 | Net Generation of BPDB (MKWH) | 3681.055 |  | 3616.96 |  | 3292.72
23 | Net Generation of IPP & RPCL (MKWH) | 2209.5029 |  | 2201.91 |  | 1811.95
24 | Net Generation of REB (MKWH) | 154.8794 |  | 171.49 |  | 147.49
24 | Net Generation of Rental Power Plant (MKWH) | 508.2955 |  | 460.44 |  | 784.35
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6553.7328 |  | 6450.81 |  | 6036.51 |  | 6553.7328 | Sept-19
26 | Energy Generation by Gas (MKWH) | 4756.9561 |  | 4666.77 |  | 4212.3 |  | 4756.96 | Sept-19
27 | Energy Generation by Diesel (MKWH) | 171.5174 |  | 256.55 |  | 428.9 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1362.4513 |  | 1284.23 |  | 1333.26 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 139.7935 |  | 151.4 |  | 100.16 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 22.5649 |  | 5.04 |  | 1.8 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 243.718 |  | 223.04 |  | 64.46 |  | 243.72 | Sept-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 762.6167 |  | 739.47 |  | 583.75 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 81.4703 |  | 77.31 |  | 80.36 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12717 | 01/09/19 | 21:00
Generation Period
| Dhaka | MW | 4402
| Chattogram | MW | 1076
| Cumilla | MW | 1133
| Mymensingh | MW | 1012
| Sylhet | MW | 491
a) | Total supply in East zone | MW | 8114
| Khulna | MW | 1506
| Barisal | MW | 353
| Rajshahi | MW | 1358
| Rangpur | MW | 776
b) | Total supply in West zone | MW | 3993
c) | Total supply in both zone ( a+b) | MW | 12107
Ref: | 27.21.0000.603.16.086.18.195 | Date: 14/10/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 680 | 29/09/19 | 10:00
| b) Ishurdi end | MW | 180 | 24/09/19 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 500 | 24/09/19 | 15:00
| b) Ishurdi end | MW | 280 | 29/09/19 | 10:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 7.3541
| b) Ishurdi end | MKWH | 50.866
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 49.34
| b) Ishurdi end | MKWH | 7.0412
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 270 | 23/09/19 | 21:00
| b)Serajganj end | MW | 400 | 04/09/19 | 17:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 390 | 04/09/19 | 17:00
| b)Sirajganj end | MW | 240 | 23/09/19 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.912 | 18/09/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 1.876 | 18/09/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 18.96
| b)Sirajganj end | MKWH | 74.132
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 72.614
| b)Sirajganj end | MKWH | 18.898
30 | Transmission loss of EWI /NO-2 | % | 1.56
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV Transformer-T2 | 2019-09-02 08:40 | 2019-09-02 10:16 | 1:36 | E/O | Due to red hot maintenance | 30 | 48 | Power interruption
Mymensingh | 132/33 kV Transformer-T1 | 2019-09-03 23:40 | 2019-09-04 03:33 | 3:53 | E/O | Due to red hot maintenance | 40 | 155.3333 | Power interruption
Jamalpur | 132/33 kV Transformer-T2 | 2019-09-05 07:47 | 2019-09-05 11:48 | 4:01 | E/O | Due to red hot maintenance 33 kV side | 5 | 20.0833 | No interruption
Tongi | 230/132 kV all Transformer | 2019-09-07 12:32 | 2019-09-07 12:57 | 0:25 | T |  | 462 | 192.5 | Power interruption
Kishoreganj | 132/33 kV Transformers-T1 | 2019-09-10 18:55 | 2019-09-10 19:04 | 0:09 | T | Tripped showing E/F relay | 92 | 13.8 | Power interruption 18:55 to 19:04
| 132/33 kV Transformers-T2 | 2019-09-10 18:55 | 2019-09-10 19:10 | 0:15 | T
Tangail | 132/33 kV Transformers-T1 | 2019-09-15 19:18 | 2019-09-15 19:35 | 0:17 | T | Tripped showing O/C relay | 190 | 53.8333 | Power interruption
| 132/33 kV Transformers-T2 | 2019-09-15 19:18 | 2019-09-15 19:36 | 0:18 | T
| 132/33 kV Transformers-T3 | 2019-09-15 19:18 | 2019-09-15 19:37 | 0:19 | T
| 132/33 kV Transformers-T4 | 2019-09-15 19:18 | 2019-09-15 19:38 | 0:20 | T
Jamalpur | 132/33 kV Transformers-T4 | 2019-09-17 09:45 | 2019-09-17 13:32 | 3:47 | E/O | Due to red hot maintenance | 20 | 75.6667 | Power interruption
Valuka | 132/33 kV Transformer-T2 | 2019-09-19 15:13 | 2019-09-19 15:29 | 0:16 | E/O | Due to Breaker maintenance | 20 | 5.3333 | Power interruption
Tangail | 132/33 kV Transformers-T1 | 2019-09-21 20:02 | 2019-09-21 20:41 | 0:39 | T | Tripped showing Diff,& O/C relay
| 132/33 kV Transformers-T2 | 2019-09-21 20:02 | 2019-09-21 21:01 | 0:59 | T
| 132/33 kV Transformers-T3 | 2019-09-21 20:02 | 2019-09-21 20:37 | 0:35 | T |  | 164 | 95.6667 | Power interruption 20:02 to 20:37
| 132/33 kV Transformers-T2 | 2019-09-21 21:22 | 2019-09-21 21:47 | 0:25 | T | Tripped showing O/C relay at 33 kV side | 65 | 27.0833 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-09-27 22:05 | 2019-09-27 22:07 | 0:02 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 18:16 |  | Unserved Energy: |  | 687.3
Dhaka (South) Grid Circle :
Hasnabad | 33 kV main Bus | 2019-09-01 09:56 | 2019-09-01 12:28 | 2:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-09-08 08:05 | 2019-09-08 09:43 | 1:38 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformers-T1 | 2019-09-09 00:20 | 2019-09-09 03:35 | 3:15 | T | Tripped showing PRD relay | 15 | 48.75 | Power interruption
| 132/33 kV Transformers-T2 | 2019-09-09 00:20 | 2019-09-09 04:47 | 4:27 | T
Munshiganj | 33 kV Bus | 2019-09-15 07:22 | 2019-09-15 08:50 | 1:28 | E/O | Due to red hot maintenance | 50 | 73.3333 | Power interruption
Hasnabad | 132/33 kV Transformers-T1,T2, & T3 | 2019-09-23 09:22 | 2019-09-23 09:50 | 0:28 | T | Tripped showing O/C relay at 33 kV side | 110 | 51.3333 | Power interruption
| 132/33 kV Transformer-T5 | 2019-09-28 11:06 | 2019-09-28 13:26 | 2:20 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 16:08 |  | Unserved Energy: |  | 173.4167
Chattogram Grid Circle :
Hathazari | 132/33 kV Transformer-T1 | 2019-09-02 21:17 | 2019-09-02 22:16 | 0:59 | T | Tripped showing 33 kV feeder fault | 22 | 21.6333 | Power interruption
Dohazari | 132/33 kV Transformer-T2 | 2019-09-07 14:19 | 2019-09-07 15:24 | 1:05 | E/O | Due to red hot maintenance at 33 kV side | 22 | 23.8333 | Power interruption
Madunaghat | 132/33 kV Transformer-T1 | 2019-09-12 21:24 | 2019-09-12 22:10 | 0:46 | E/O | Due to red hot maintenance at 33 kV side | 35 | 26.8333 | Power interruption
Chandraghona | 132/33 kV Transformer-T2 | 2019-09-16 07:04 | 2019-09-16 08:12 | 1:08 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T2 | 2019-09-22 06:12 | 2019-09-22 08:57 | 2:45 | T | Tripped showing buchhloz & Lockout relay | 20 | 55 | Power interruption
| 132/33 kV Transformer-T2 | 2019-09-24 02:32 | 2019-09-24 02:55 | 0:23 |  |  | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2019-09-24 20:50 | 2019-09-24 22:15 | 1:25 | E/O | Due to red hot maintenance at 33 kV side | 40 | 56.6667 | Power interruption
Halishahar | 132/33 kV Transformer-T1 | 2019-09-24 21:07 | 2019-09-24 22:20 | 1:13 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T2 | 2019-09-25 09:26 | 2019-09-25 10:35 | 1:09 | E/O | Due to red hot maintenance at 33 kV side | 35 | 40.25 | Power interruption
Halishahar | 132/33 kV Transformer-T1 | 2019-09-26 00:10 | 2019-09-26 01:31 | 1:21 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2019-09-26 07:12 | 2019-09-26 13:40 | 6:28 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 18:42 |  | Unserved Energy: |  | 224.2167
Cumilla Grid Circle :
Feni | 132/33 kV Transformer-T1 | 2019-09-01 03:19 | 2019-09-01 07:03 | 3:44 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-09-02 09:21 | 2019-09-02 09:53 | 0:32 | E/O | Due to red hot maintenance at 33 kV side | 15 | 8 | Power interruption
Cumilla(S) | 132/33 kV Transformer-T2 | 2019-09-08 21:30 | 2019-09-08 23:02 | 1:32 | E/O | Due to red hot maintenance at 33 kV side | 38 | 58.2667 | Power interruption
| 132/33 kV Transformer-T2 & 33 kV Bus | 2019-09-09 01:28 | 2019-09-09 01:48 | 0:20 | E/O | Due to red hot maintenance at 33 kV side | 25 | 8.3333 | Power interruption
Chatak | 132/33 kV Transformer-T2 | 2019-09-12 14:59 | 2019-09-12 15:10 | 0:11 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-09-14 19:50 | 2019-09-14 21:01 | 1:11 | E/O | Due to red hot maintenance at 132 kV side | 7 | 8.2833 | Power interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2019-09-15 06:13 | 2019-09-15 06:47 | 0:34 | T | Tripped showing E/F &/C relay | 14 | 7.9333 | Power interruption
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chowmuhani | 132/33 kV Transformer-T2 | 2019-09-16 16:32 | 2019-09-16 17:20 | 0:48 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 & 33 kV Bus | 2019-09-23 07:05 | 2019-09-23 08:25 | 1:20 | E/O | Due to red hot maintenance | 14 | 18.6667 | Power interruption
Sreemongal | 132/33 kV Transformer-T1 | 2019-09-27 08:05 | 2019-09-27 11:45 | 3:40 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T2 | 2019-09-27 21:03 | 2019-09-27 21:38 | 0:35 | E/O | Due to red hot maintenance at 132 kV side | 30 | 17.5 | Power interruption
|  |  | Total : | 14:27 |  | Unserved Energy: |  | 126.9833
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformers-T1 | 2019-09-04 12:48 | 2019-09-04 13:02 | 2:48 | T | Tripped showing O/C relay | 45 | 126 | Power interruption
| 132/33 kV Transformers-T2 | 2019-09-04 12:48 | 2019-09-04 13:05 | 0:17 | T |  | 0 | 0 | No interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-09-04 12:57 | 2019-09-04 14:17 | 1:20 | T | Tripped showing O/C at 33 kV side | 0 | 0 | No interruption
Norail | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-09-07 08:01 | 2019-09-07 09:15 | 1:14 | E/O | Due to red hot maintenance at 33 kV side | 6 | 7.4 | Power interruption
Barisal | 132/33 kV Transformer-T1 | 2019-09-17 16:12 | 2019-09-17 17:28 | 1:16 | E/O | Due to emergency maintenance of 33 kV Bakerganj feeder | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2019-09-22 17:10 | 2019-09-22 17:54 | 0:44 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Khulna(S) | 132 kV capacitor bank | 2019-09-22 07:10 | 2019-10-03 12:36 | 269:26 | T | Tripped showing unbalance current | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-09-23 05:02 | 2019-09-23 05:12 | 0:10 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T1 | 2019-09-25 17:32 | 2019-09-25 17:55 | 0:23 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 & T2 | 2019-09-26 01:58 | 2019-09-26 03:22 | 1:24 | T | Tripped showing 33 kV feeder fault | 40 | 56 | Power interruption
| 132/33 kV Transformer-T1 | 2019-09-26 04:24 | 2019-09-26 05:00 | 0:36 | T | Tripped showing 33 kV feeder fault | 10 | 6 | Power interruption
Barishal(S) | 132/33 kV Transformer-T2 | 2019-09-27 15:53 | 2019-09-27 17:30 | 1:37 | T | Tripped showing 33 kV feeder fault | 29 | 46.8833 | Power interruption
|  |  | Total : | 281:15 |  | Unserved Energy: |  | 242.2833
HVDC Grid Circle :
Shahjadpur | 132/ kV Transformer-T2 | 2019-09-04 10:10 | 2019-09-04 17:20 | 7:10 | E/O | Due to breaker maintenance | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T1 | 2019-09-08 15:12 | 2019-09-08 15:22 | 0:10 | T | Tripped showing O/C at 33 kV side | 37 | 6.1667 | Power interruption
| 132/33 kV Transformer-T2 | 2019-09-08 21:33 | 2019-09-08 22:11 | 0:38 | E/O | Due to red hot maintenance at 33 kV side | 7 | 4.4333 | No interruption
Chuadanga | 132/33 kV Transformer-T1 | 2019-09-13 09:08 | 2019-09-13 10:08 | 1:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2019-09-19 01:03 | 2019-09-19 03:12 | 4:22 | T | Tripped showing inst.E/F relay | 80 | 349.3333 | Power interruption
Shahjadpur | 132/ kV Transformer-T3 | 2019-09-23 10:04 | 2019-09-23 12:13 | 2:09 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T2 | 2019-09-26 10:48 | 2019-09-26 11:24 | 0:36 | E/O | Due to red hot maintenance at 33 kV side | 21 | 12.6 | Power interruption
|  |  | Total : | 16:05 |  |  |  | 372.5333
Bogura Grid Circle:
Thakurgaon | 132/33 kV Transformer-T2 | 2019-09-05 10:30 | 2019-09-05 10:47 | 0:17 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T2 | 2019-09-08 21:18 | 2019-09-08 21:45 | 0:27 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Naogaon | 132 kV main Bus | 2019-09-09 07:05 | 2019-09-09 09:10 | 2:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformers-T1 | 2019-09-10 18:40 | 2019-09-10 20:58 | 2:18 | E/O | Due to bursting of PT | 30 | 69 | Power interruption 18:40 to 20:58
| 132/33 kV Transformers-T3 | 2019-09-10 18:40 | 2019-09-10 21:49 | 3:09 | E/O
| 132/33 kV Transformers-T3 | 2019-09-11 22:08 | 2019-09-12 00:41 | 2:33 | T | Tripped showing 33 kV R-phase snapped | 25 | 63.75 | Power interruption
Naogaon | 132/33 kV Transformer-T1 | 2019-09-12 10:41 | 2019-09-12 11:32 | 0:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2019-09-12 20:18 | 2019-09-12 21:45 | 1:27 | E/O | Due to red hot maintenance | 20 | 29 | Power interruption
Joldhaka | 132/33 kV Transformer-T1 | 2019-09-15 12:50 | 2019-09-15 14:10 | 1:20 | E/O | Due to Oil leakage | 20 | 26.6667 | Power interruption
Pabna | 132/33 kV Transformers-T1 | 2019-09-16 19:00 | 2019-09-16 19:17 | 0:17 | T | Tripped showing 33 kV feeder fault | 104 | 29.4667 | Power interruption 19:00 to 19:28
| 132/33 kV Transformers-T2 | 2019-09-16 19:00 | 2019-09-16 19:28 | 0:28 | T
Rajshahi | 132/33 kV Transformers-T1 & T3 | 2019-09-20 05:36 | 2019-09-20 06:02 | 0:26 | T | Tripped showing O/C & E/F relay | 110 | 47.6667 | Power interruption
Bogura(O) | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-09-20 08:20 | 2019-09-20 10:05 | 1:45 | E/O | Due to red hot maintenance | 60 | 105 | Power interruption
Purbasadipur | 132/33 kV Transformer-T2 | 2019-09-22 15:25 | 2019-09-22 16:36 | 1:11 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T5 | 2019-09-26 10:50 | 2019-09-26 13:08 | 2:18 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 20:52 |  | Unserved Energy: |  | 370.55
Others :
Basundhara | 132/33 kV Transformers-T1 | 2019-09-08 16:25 | 2019-09-08 16:30 | 0:05 | T | Tripped showing O/L relay | 78 | 6.5 | Power interruption
| 132/33 kV Transformers-T2 | 2019-09-08 16:25 | 2019-09-08 17:25 | 1:00 | T | Tripped showing PRD relay
|  |  | Total : | 1:05 |  | Unserved Energy: |  | 6.5
Total outage period of Sub-station Equipment : |  |  |  | 386:50 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-09-11 10:09 | 2019-09-11 10:25 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
United Jamalpur | United Jamalpur-Sherpur 132 kV line-2 | 2019-09-18 18:46 | 2019-09-18 19:12 | 0:26 | T | Tripped showing dist. & E/F relay | 567 | 245.7 | Power interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-09-18 21:59 | 2019-09-18 22:13 | 0:14 | T | Tripped showing dist.& O/C relay | 140 | 32.6667 | Power interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 & 2 | 2019-09-19 11:53 | 2019-09-19 12:04 | 0:11 | T
Kalyanpur | Kalyanpur-Aminbazar 132 kV line-1 | 2019-09-20 12:45 | 2019-09-20 18:11 | 5:26 | E/O | Due to bursting of lightning arrester | 0 | 0 | No interruption
|  |  | Total : | 6:33 |  | Unserved Energy: |  | 278.3667
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-09-06 06:18 | 2019-09-06 09:43 | 3:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madanganj | Madanganj-Bashundhara 132 kV line | 2019-09-06 06:10 | 2019-09-06 21:02 | 14:52 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2019-09-14 16:28 | 2019-09-14 17:07 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV line-2 | 2019-09-15 09:14 | 2019-09-15 20:40 | 11:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2019-09-15 23:21 | 2019-09-16 00:34 | 1:13 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi 132 kV line-2 | 2019-09-16 19:30 | 2019-09-16 19:35 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2019-09-18 09:39 | 2019-09-18 09:51 | 0:12 | T | Tripped showing dist. relay | 100 | 20 | Power interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-2 | 2019-09-18 11:02 | 2019-09-18 11:22 | 0:20 | T | Tripped showing remote protection relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-2 | 2019-09-18 12:40 | 2019-09-18 21:34 | 8:54 | T |  | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2019-09-18 21:08 | 2019-09-19 13:35 | 16:27 | E/O | Due to SF6 gas pressure low | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2019-09-18 22:59 | 2019-09-19 00:58 | 1:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-09-21 14:04 | 2019-09-21 14:22 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-09-23 06:08 | 2019-09-23 11:40 | 5:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2019-09-24 13:23 | 2019-09-24 13:34 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ullon | Ullon-Dhanmondi 132 kV line-3 | 2019-09-28 10:33 | 2019-09-28 10:46 | 0:13 | T | Tripped showing dist. relay | 80 | 17.3333 | Power interruption
| Ullon-Dhanmondi 132 kV line-2 | 2019-09-28 10:33 | 2019-09-28 11:05 | 0:32 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 66:18 |  | Unserved Energy: |  | 37.3333
Chittagong Grid Circle :
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2019-09-02 10:41 | 2019-09-02 13:59 | 3:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Madunaghat-Sikalbaha 132 kV line | 2019-09-06 05:44 | 2019-09-06 07:57 | 2:13 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2019-09-11 03:24 | 2019-09-11 03:57 | 0:33 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Sikalbaha-T.k.chemical 132 kV line | 2019-09-11 03:24 | 2019-09-11 03:45 | 0:21 | T | Tripped showing dist.(B-phase) relay | 0.5 | 0.175 | Power interruption
Kaptai | Kaptai-Chandraghona 132 kV line-2 | 2019-09-14 07:34 | 2019-09-14 11:10 | 3:36 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2019-09-15 19:14 | 2019-09-16 17:20 | 22:06 | T | Tripped showing VT fail | 0 | 0 | No interruption
BSRM | BSRM-Abul Khair 230 kV line | 2019-09-18 10:43 | 2019-09-18 10:50 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan230 kV line-2 | 2019-09-22 09:54 | 2019-09-22 11:32 | 1:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-2 | 2019-09-23 17:41 | 2019-09-23 18:36 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV line | 2019-09-25 12:08 | 2019-09-25 12:24 | 0:16 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2019-09-28 05:31 | 2019-09-28 06:58 | 1:27 | T |  | 0 | 0 | No interruption
|  |  | Total : | 36:30 |  | Unserved Energy: |  | 0.175
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-1 | 2019-09-01 13:08 | 2019-09-01 13:25 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2019-09-02 22:25 | 2019-09-02 22:33 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Bhulta 400 kV line-2 | 2019-09-02 21:58 | 2019-09-02 23:36 | 1:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bibiyana | Bibiyana-Dia(3) line(South) 230 kV line | 2019-09-12 09:10 | 2019-09-12 13:01 | 3:51 | T | Tripped showing general trip | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur Desh 132 kV line-1 | 2019-09-15 07:42 | 2019-09-15 07:57 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur Desh 132 kV line | 2019-09-15 07:42 | 2019-09-16 15:34 | 31:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-2 | 2019-09-15 08:52 | 2019-09-15 09:45 | 0:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 132 kV line-2 | 2019-09-19 10:34 | 2019-09-19 10:48 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Chandpur desh | Chandpur desh-Ramganj 132 kV line-1 & 2 | 2019-09-23 22:42 | 2019-09-23 23:19 | 0:37 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line | 2019-09-27 12:07 | 2019-09-27 12:46 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 40:24 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(C) | Khulna©-Goalpara 132 kV line-1 | 2019-09-01 21:34 | 2019-09-02 09:06 | 11:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-09-04 12:35 | 2019-09-04 12:56 | 0:21 | T | Tripped showing O/C. relay | 30 | 10.5 | Power interruption
Noapara | Noapara-Bangla track 132 kV line | 2019-09-13 17:05 | 2019-09-13 17:14 | 0:09 | T | Tripped showing 86A & OPTD signal | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line | 2019-09-15 05:59 | 2019-09-15 06:15 | 0:16 | T | Tripped showing dist. relay | 64 | 17.0667 | Power interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2019-09-22 16:46 | 2019-09-22 17:46 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 13:18 |  | Unserved Energy: |  | 27.5667
HVDC Grid Circle :
| Ishurdi-Natore 132 kV line-1 | 2019-09-19 01:03 | 2019-09-19 03:12 | 2:09 | T | Tripped showing dist.CAR,CDE,STA signal | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV line-1 &2 | 2019-09-19 01:03 | 2019-09-19 05:35 | 4:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV line | 2019-09-19 01:04 | 2019-09-19 01:36 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV line | 2019-09-22 11:34 | 2019-09-22 12:45 | 1:11 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-1 | 2019-09-22 11:36 | 2019-09-22 11:41 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-2 | 2019-09-22 11:36 | 2019-09-22 11:38 | 0:02 | T |  | 0 | 0 | No interruption
|  |  | Total : | 8:31 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Purbasadipur | Purbasadipur -Saidpur 132 kV line-1 | 2019-09-01 06:12 | 2019-09-01 08:03 | 1:51 | E/O | Due to breaker problem | 155 | 286.75 | Power interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2019-09-04 12:48 | 2019-09-04 12:58 | 0:10 | T | Tripped showing dist. relay | 190 | 31.6667 | Power interruption 12:48 to 12:58
| Rajshahi-Natore 132 kV line-2 | 2019-09-04 12:48 | 2019-09-04 13:08 | 0:20
| Rajshahi-Amnura 132 kV line | 2019-09-04 12:48 | 2019-09-04 13:10 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Panchughar 132 kV line | 2019-09-04 18:16 | 2019-09-04 18:21 | 0:05 | T | Tripped showing E/F relay | 40 | 3.3333 | Power interruption
| Thakurgaon-Panchughar 132 kV line | 2019-09-04 18:28 | 2019-09-04 19:09 | 0:41 | T |  | 40 | 27.3333 | Power interruption
| Thakurgaon-Panchughar 132 kV line | 2019-09-04 19:21 | 2019-09-04 21:21 | 2:00 | T |  | 40 | 80 | Power interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line | 2019-09-15 05:59 | 2019-09-15 06:15 | 0:16 | T | Tripped showing dist. relay | 64 | 17.0667 | Power interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2019-09-20 15:38 | 2019-09-20 15:46 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2019-09-23 19:40 | 2019-09-23 21:30 | 1:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Rangpur-Rangpur P/S 132 kV line-1 | 2019-09-27 08:05 | 2019-09-27 08:25 | 0:20 | T | Tripped showing PT MCB trip | 0 | 0 | No interruption
|  |  | Total : | 8:03 |  | Unserved Energy: |  | 446.15
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Unserved Energy:
Total outage period of Sub-station Equipment : |  |  |  | 147:44 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV Transformer-T1 | 2019-09-03 11:05 | 2019-09-03 11:47 | 0:42 | S/O | Due to testing Oil of OLTC | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-09-03 11:50 | 2019-09-03 12:17 | 0:27 | S/O |  | 0 | 0 | No interruption
Mirpur | 132 kV main Bus | 2019-09-04 07:55 | 2019-09-04 17:44 | 9:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2019-09-08 10:55 | 2019-09-08 11:40 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-09-10 11:30 | 2019-09-10 12:28 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-09-10 08:01 | 2019-09-10 16:58 | 8:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T2 | 2019-09-11 07:30 | 2019-09-11 07:56 | 0:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2019-09-12 11:06 | 2019-09-12 11:15 | 0:09 | S/O | Due to over loading of Tongi-Ghorashal 230 kV line | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-09-15 10:40 | 2019-09-15 13:56 | 3:16 | S/O | Due to tan delta test | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2019-09-16 12:37 | 2019-09-16 16:17 | 3:40 | S/O | Due to protection test | 0 | 0 | No interruption
Bhulta | 230/132 kV Transformer-ART2 | 2019-09-17 11:04 | 2019-09-17 16:23 | 5:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| 400/230 kV Transformer-ART-1 | 2019-09-17 16:51 | 2019-09-17 17:49 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 | 2019-09-17 15:12 | 2019-09-17 16:56 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1 & T2 | 2019-09-19 07:05 | 2019-09-19 10:30 | 3:25 | S/O | Due to DESCO work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2019-09-19 22:00 | 2019-09-19 23:47 | 1:47 | S/O | Due to D/W work | 40 | 71.3333 | Power interruption
| 132/33 kV Transformer-T4 | 2019-09-20 10:08 | 2019-09-20 23:25 | 13:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV main Bus-2 | 2019-09-21 12:49 | 2019-09-24 16:52 | 76:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2(New) |  | 2019-09-21 17:54 |  |  | New connection | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-09-22 16:37 | 2019-09-22 17:36 | 0:59 | S/O | Due to protection test | 0 | 0 | No interruption
Kadda | 33 kV full Bus | 2019-09-23 07:35 | 2019-09-23 10:16 | 2:41 | S/O | Due to PBS work | 140 | 375.6667 | Power interruption
Tangail | 132/33 kV Transformer-T2 | 2019-09-24 07:07 | 2019-09-24 18:59 | 11:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer ICT-11 | 2019-09-25 09:33 | 2019-09-25 16:08 | 6:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T1 | 2019-09-26 10:43 | 2019-09-26 11:45 | 1:02 | S/O | Due to maintenance work | 50 | 51.6667 | Power interruption
Dhamrai | 132/33 kV Transformer-T1 | 2019-09-26 10:54 | 2019-09-26 15:30 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2019-09-26 22:05 | 2019-09-28 17:50 | 43:45 | S/O | Due to D/W work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T1 | 2019-09-27 07:16 | 2019-09-27 08:45 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132 kV Bus-A | 2019-09-27 07:40 | 2019-09-27 16:46 | 9:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-09-27 07:40 | 2019-09-27 07:52 | 0:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-09-27 09:51 | 2019-09-27 12:22 | 2:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus | 2019-09-27 14:12 | 2019-09-27 16:33 | 2:21 | S/O | Due to isolator problem | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T03 | 2019-09-28 06:08 | 2019-09-28 11:54 | 5:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2019-09-29 07:03 | 2019-09-29 13:05 | 6:02 | S/O | Due to work on 33 kV PBS feeder | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2019-09-30 08:48 | 2019-09-30 09:43 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 231:34 |  | Unserved Energy: |  | 498.6667
Dhaka (South) Grid Circle :
Maniknagar | 132 kV main Bus-1 | 2019-09-06 10:25 | 2019-09-06 12:04 | 1:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T3 | 2019-09-07 06:30 | 2019-09-07 08:30 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-ART2 | 2019-09-16 11:59 | 2019-09-16 18:03 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2019-09-27 06:24 | 2019-09-27 10:06 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2019-09-28 15:12 | 2019-09-28 17:20 | 2:08 | S/O | Due to work on 33 kV PBS feeder | 30 | 64 | Power interruption
|  |  | Total : | 15:33 |  | Unserved Energy: |  | 64
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Feni | 132/33 kV Transformer-T1 | 2019-09-03 07:17 | 2019-09-03 09:32 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T1 | 2019-09-06 07:29 | 2019-09-06 16:26 | 8:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2019-09-10 21:52 | 2019-09-10 22:40 | 0:48 | S/O | Due to C/M work | 20 | 16 | Power interruption
Sikalbaha | 230/132 kV Transformer-T02 | 2019-09-14 09:55 | 2019-09-14 11:34 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 33 kV full Bus | 2019-09-20 07:23 | 2019-09-20 11:55 | 4:32 | S/O | Due to loop changing | 80 | 362.6667 | Power interruption
Sikalbaha | 230 kV Bus-2 | 2019-09-24 10:21 | 2019-09-24 12:34 | 2:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 | 2019-09-25 21:28 | 2019-09-25 23:36 | 2:08 | S/O | Due to C/M work | 1 | 2.1333 | No interruption
Baraulia | 132/33 kV Transformer-T2 | 2019-09-27 09:44 | 2019-09-27 12:11 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 24:59 |  | Unserved Energy : |  | 380.8
Cumilla Grid Circle :
Shahjibazar | 132/33 kV Transformer-T2 | 2019-09-02 07:24 | 2019-09-02 10:06 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2019-09-04 09:16 | 2019-09-04 10:52 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2019-09-06 09:13 | 2019-09-06 17:11 | 7:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformer-T3 | 2019-09-06 19:11 | 2019-09-06 20:23 | 1:12 | S/O | Due to PBS work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T2 | 2019-09-07 08:51 | 2019-09-07 17:00 | 8:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | 230 kV bus-1 | 2019-09-10 13:46 | 2019-09-11 14:28 | 24:42 | S/O | Due to project work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T3 | 2019-09-10 17:45 | 2019-09-10 18:25 | 0:40 | S/O | Due to project work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-09-11 10:34 | 2019-09-11 16:38 | 6:04 | S/O | Due to replacement work | 0 | 0 | No interruption
Ashuganj | 132/33 kV Transformer-T3 | 2019-09-13 08:26 | 2019-09-13 15:30 | 7:04 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-09-18 09:54 | 2019-09-18 11:05 | 1:11 | S/O | Due to temperature high | 0 | 0 | No interruption
Bibiyana | 400 kV main Bus-1 | 2019-09-21 08:40 | 2019-09-24 23:07 | 86:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2019-09-22 06:12 | 2019-09-22 08:48 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T2 & T3 | 2019-09-26 07:15 | 2019-09-26 09:15 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2019-09-30 07:28 | 2019-10-04 15:30 | 104:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2019-09-30 11:48 | 2019-09-30 13:56 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-09-30 08:57 | 2019-09-30 11:47 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 261:21 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Sariatpur | 132/33 kV Transformer-T1 | 2019-09-01 08:45 | 2019-09-01 11:33 | 2:48 | S/O | Due to PBS work | 0 | 0 | No interruption
Faridpur | 33 kV Bus section-2 | 2019-09-02 21:05 | 2019-09-02 21:30 | 0:25 | S/O | Due to maintenance work | 100 | 41.6667 | Power interruption
Barisal(N) | 132/33 kV Transformer-T4 & T5 | 2019-09-12 16:18 | 2019-09-12 19:24 | 3:06 | S/O | Due to protection work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2019-09-13 07:31 | 2019-09-13 16:55 | 9:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T1 | 2019-09-14 09:13 | 2019-09-14 14:18 | 5:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2019-09-15 06:22 | 2019-09-15 20:27 | 14:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-09-16 07:27 | 2019-09-16 09:39 | 2:12 | S/O | Due to replacement work | 35 | 77 | Power interruption
| 132/33 kV Transformer-T1 | 2019-09-17 14:01 | 2019-09-17 15:27 | 1:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-09-23 07:15 | 2019-09-23 08:09 | 0:54 | S/O | Due to fire at 33 kV under ground cable | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-09-26 03:33 | 2019-09-26 12:43 | 9:10 | S/O | Due to DC supply problem | 0 | 0 | No interruption
| 132 kV Bus-B | 2019-09-30 09:58 | 2019-09-30 16:58 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 55:35 |  | Unserved Energy : |  | 118.6667
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:September 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T1 & 33 kV Bus-1 | 2019-09-08 07:03 | 2019-09-08 08:13 | 1:10 | S/O | Due to C/M work | 30 | 35 | No interruption
Chuadanga | 33 kV Bus section-4 | 2019-09-25 06:30 | 2019-09-25 09:16 | 2:46 | S/O | Due to replacement work at 33 kV side | 18 | 49.8 | Power interruption
HVDC Bheramara | HVDC Bheramara-Bahrampur 400 kV line-1 & 2 | 2019-09-27 10:43 | 2019-09-27 18:15 | 7:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Chuadanga | 33 kV full Bus | 2019-09-30 06:11 | 2019-09-30 10:24 | 4:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-2 | 2019-09-30 06:46 | 2019-09-30 12:30 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 21:25 |  | Unserved Energy : |  | 84.8
Bogura Grid Circle:
Joldhaka | 132/ kV Transformer-T1 | 2019-09-01 11:30 | 2019-09-01 15:15 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/ kV Transformer-T2 | 2019-09-02 10:30 | 2019-09-02 13:37 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Mahastanghor | 132/ kV Transformer-T2 | 2019-09-03 10:37 | 2019-09-03 13:53 | 3:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | 132 kV Bus-1 | 2019-09-06 06:50 | 2019-09-06 13:35 | 6:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/ kV Transformer-T3 | 2019-09-06 12:01 | 2019-09-06 12:47 | 0:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2019-09-09 07:25 | 2019-09-09 09:45 | 2:20 | S/O | Due to C/M work | 40 | 93.3333 | Power interruption
Bogura (O) | 132/ kV Transformer-T1 | 2019-09-13 08:06 | 2019-09-13 11:36 | 3:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mahasthanagar | 132/33 kV Transformer-T1 | 2019-09-13 10:23 | 2019-09-13 17:09 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | 132 kV Bus-A | 2019-09-14 06:30 | 2019-09-14 07:35 | 1:05 | S/O | Due to D/W work | 30 | 32.5 | Power interruption
Mahastanghor | 33 kV incomer--1 | 2019-09-14 09:33 | 2019-09-14 17:05 | 7:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-09-15 09:43 | 2019-09-15 16:54 | 7:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T3 | 2019-09-18 09:12 | 2019-09-18 11:20 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2019-09-19 22:00 | 2019-09-19 22:58 | 0:58 | S/O | Due to D/W work | 40 | 38.6667 | Power interruption
Rajshahi | 132/33 kV Transformers-T1 | 2019-09-20 06:40 | 2019-09-20 09:14 | 2:34 | S/O | Due to C/M work | 50 | 128.3333 | Power interruption 06:40 to 09:14
| 132/33 kV Transformers-T2 | 2019-09-20 06:40 | 2019-09-20 10:15 | 3:35 | S/O
Ruppur | 132/ kV Transformer-T1 | 2019-09-20 10:15 | 2019-09-20 12:20 | 2:05 | S/O | Due to SAS work | 0 | 0 | No interruption
Amnura | 132 main Bus-1 & 2 | 2019-09-21 09:15 | 2019-09-21 17:55 | 8:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Ruppur | 132/ kV Transformer-T2 | 2019-09-21 11:35 | 2019-09-21 20:20 | 8:45 | S/O | Due to SAS work | 0 | 0 | No interruption
Pabna | 132/ kV Transformer-T3 | 2019-09-24 13:52 | 2019-09-24 15:11 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Mahasthanagar | 132 kV Bus | 2019-09-27 08:31 | 2019-09-27 17:13 | 8:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-1 & 2 | 2019-09-28 09:15 | 2019-09-28 16:33 | 7:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 33 kV Bus | 2019-09-29 12:58 | 2019-09-29 13:37 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 92:46 |  | Unserved Energy : |  | 292.8333
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 703:13 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Uttara 132 kV line | 2019-09-01 09:42 | 2019-09-14 15:44 | 318:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Gazipur summit-Kaliakoir 230 kV line | 2019-09-11 06:32 | 2019-09-11 16:55 | 10:23 | S/O | Due to maintenance at Power plant | 0 | 0 | No interruption
| Tongi-Gazipur summit-Kaliakoir 230 kV line | 2019-09-12 06:19 | 2019-09-12 22:45 | 16:26 | S/O |  | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakor 132 kV line-1 | 2019-09-17 10:34 | 2019-09-17 17:36 | 7:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2019-09-17 10:10 | 2019-09-17 11:41 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-2 | 2019-09-17 11:43 | 2019-09-17 13:11 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Siddhirganj 230 kV line-2 | 2019-09-18 07:40 | 2019-09-18 09:31 | 1:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakor 132 kV line-1 | 2019-09-18 10:03 | 2019-09-19 09:27 | 23:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Sherpur 132 kV line-2 | 2019-09-19 07:20 | 2019-09-19 14:53 | 7:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2019-09-20 09:39 | 2019-09-20 11:31 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kadda 132 kV line-2 | 2019-09-20 11:33 | 2019-09-20 12:41 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Gazipur summit-Kaliakoir 230 kV line | 2019-09-21 06:06 | 2019-09-21 23:44 | 17:38 | S/O | Due to testing busbar protection at power plant | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-09-24 08:18 | 2019-09-24 14:12 | 5:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Kailakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2019-09-24 10:28 | 2019-09-24 12:04 | 1:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-2 | 2019-09-25 10:24 | 2019-10-02 08:57 | 166:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-09-30 08:05 | 2019-09-30 11:18 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 585:34 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Shyampur | Shyampur-Haripur-Brahongaon 132 kV line | 2019-09-02 10:22 | 2019-09-02 11:13 | 0:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Lalbagh 132 kV line | 2019-09-05 12:03 | 2019-09-05 13:40 | 1:37 | S/O | Due to DPDC work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2019-09-06 10:38 | 2019-09-06 16:43 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV line-1 | 2019-09-06 10:52 | 2019-09-06 12:04 | 1:12 | S/O | Due to protection work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2019-09-07 07:58 | 2019-09-07 17:46 | 9:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 |  | 2019-09-10 20:27 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2019-09-11 13:21 | 2019-09-11 14:41 | 1:20 | S/O | Due to removing polythin hanging near tower no-84 | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2019-09-13 07:15 | 2019-09-13 16:24 | 9:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-09-13 06:34 | 2019-09-13 14:27 | 7:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV line | 2019-09-14 06:47 | 2019-09-14 11:22 | 4:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-B.gaon-Shyampur new-Haripur 132 kV line | 2019-09-16 07:30 | 2019-09-16 17:30 | 10:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2019-09-18 11:08 | 2019-09-18 15:52 | 4:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi-Rampura 132 kV line-2 | 2019-09-19 08:44 | 2019-09-19 09:20 | 0:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsingdi 132 kV line-2 | 2019-09-20 10:03 | 2019-09-20 16:35 | 6:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-09-20 06:12 | 2019-09-20 09:15 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2019-09-20 09:52 | 2019-09-20 11:02 | 1:10 | S/O | Due to mad man climbing on the tower | 30 | 35 | Power interruption
| Lalbagh-Kallyanpur 132 kV line-1 | 2019-09-20 09:53 | 2019-09-20 11:38 | 1:45 | S/O |  | 0 | 0 | No interruption
| Lalbagh-Kallyanpur 132 kV line-2 | 2019-09-20 09:52 | 2019-09-20 11:37 | 1:45 | S/O |  | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2019-09-21 10:16 | 2019-09-21 20:08 | 9:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi 132 kV line-1 | 2019-09-21 15:25 | 2019-09-23 10:00 | 42:35 | S/O | Due to GIS work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-2 |  | 2019-09-21 15:21 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-09-23 10:33 | 2019-10-05 13:00 | 290:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsingdi 132 kV line-1 | 2019-09-24 16:56 | 2019-09-28 11:50 | 90:54 | S/O | Due to reconductoring work | 0 | 0 | No interruption
Bhulta | Bhulta-Narsinghdi 132 kV line | 2019-09-26 11:25 | 2019-09-26 12:25 | 1:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ullon-Haripur 132 kV line-2 | 2019-09-28 07:05 | 2019-09-28 17:11 | 10:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-09-28 08:58 | 2019-09-28 16:21 | 7:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV line-1 | 2019-09-29 08:32 | 2019-09-29 16:45 | 8:13 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 532:35 |  | Unserved Energy: |  | 35
Chattogram Grid Circle :
Baraulia | Baraulia-BSRM 132 kV line | 2019-09-03 09:22 | 2019-09-03 12:56 | 3:34 | S/O | Due to testing Oil of OLTC | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Amnura 230 kV line-1 | 2019-09-13 10:47 | 2019-09-13 15:25 | 4:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Aminbazar 230 kV line-2 | 2019-09-14 08:24 | 2019-09-14 16:15 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Modern steel 132 kV line | 2019-09-17 08:07 | 2019-09-17 12:30 | 4:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2019-09-17 10:32 | 2019-09-17 14:17 | 3:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern Steel 132 kV line | 2019-09-18 08:20 | 2019-09-18 11:34 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chanraghona 132 kV line-1 | 2019-09-18 09:10 | 2019-09-18 10:35 | 1:25 | S/O | Due to tree trimming | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2019-09-19 10:25 | 2019-09-19 11:29 | 1:04 | S/O | Due to maintenance work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-09-20 10:21 | 2019-09-20 11:44 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 |  | 2019-09-23 14:53 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-1 | 2019-09-24 08:18 | 2019-09-24 14:12 | 5:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-BSRM 230 kV line | 2019-09-28 08:20 | 2019-09-28 20:06 | 11:46 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 48:57 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj (N) | Ashuganj(N) -Bhulta 400 kV line-1 | 2019-09-04 10:03 | 2019-09-04 16:10 | 6:07 | S/O | Due to teleprotection testing | 0 | 0 | No interruption
| Ashuganj(N) -Bhulta 400 kV line-2 | 2019-09-04 16:11 | 2019-09-04 17:45 | 1:34 | S/O |  | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-2 | 2019-09-07 08:11 | 2019-09-07 11:52 | 3:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2019-09-10 16:37 | 2019-09-10 21:06 | 4:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-2 | 2019-09-11 10:42 | 2019-09-11 14:39 | 3:57 | S/O | Due to project work | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur Desh 132 kV line-2 | 2019-09-15 07:22 | 2019-09-15 12:20 | 4:58 | S/O |  | 0 | 0 | No interruption
Amnura S/S | Amnura S/S-Amnura 50 MW P/S 132 kV line | 2019-09-26 09:54 | 2019-09-26 10:24 | 0:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Amnura S/S-Rajshahi (N) 132 kV line-1 | 2019-09-26 10:29 | 2019-09-26 14:20 | 3:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| Amnura S/S-C.nawabganj 100 MW P/S 132 kV line | 2019-09-26 14:40 | 2019-09-26 17:00 | 2:20 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 31:27 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2019-09-03 10:10 | 2019-09-03 16:41 | 6:31 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Faridpur-Madaripur 132 kV line-2 | 2019-09-04 09:30 | 2019-09-04 17:20 | 7:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madaripur 132 kV line | 2019-09-07 06:31 | 2019-09-07 10:22 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV line-2 | 2019-09-07 08:06 | 2019-09-07 17:06 | 9:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Patuakhali-Payra 132 kV line-1 | 2019-09-07 08:10 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-09-08 13:38 | 2019-09-08 14:48 | 1:10 | S/O | Due to protection test | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2019-09-12 11:54 | 2019-09-12 12:35 | 0:41 | S/O | Due to tree trimming | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line |  | 2019-09-15 18:15 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV line-1 | 2019-09-17 07:29 | 2019-09-17 18:08 | 10:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barishal-Madaripur 132 kV line-2 | 2019-09-18 09:02 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 & 2 | 2019-09-28 06:55 | 2019-09-28 06:58 | 0:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Magura | Magura-Norail 132 kV line-2 | 2019-09-28 09:23 | 2019-09-28 16:53 | 7:30 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 47:15 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2019-09-03 06:08 | 2019-09-03 09:08 | 3:00 | S/O | Due to high temperature | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Sirajganj132 kV line | 2019-09-05 06:04 | 2019-09-05 13:58 | 7:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-2 | 2019-09-11 09:34 | 2019-09-12 11:51 | 26:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 |  | 2019-09-14 16:26 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 | 2019-09-14 16:38 | 2019-09-16 16:43 | 48:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV line-1 | 2019-09-27 06:45 | 2019-09-27 22:33 | 15:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV line-2 | 2019-09-27 06:45 | 2019-09-27 22:44 | 15:59 | S/O |  | 0 | 0 | No interruption
| Ishurdi-Rppur 132 kV line-1 | 2019-09-30 09:45 | 2019-09-30 18:01 | 8:16 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 125:19 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Sirajganj | Sirajganj-Baghabari 132 kV line | 2019-09-04 05:58 | 2019-09-04 15:45 | 9:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Saidpur 132 kV line-1 | 2019-09-04 18:02 | 2019-09-04 18:07 | 0:05 | S/O | Due to replacement work | 20 | 1.6667 | Power interruption
Bogura | Bogura-Sirajganj 132 kV line-2 | 2019-09-06 06:55 | 2019-09-06 13:42 | 6:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2019-09-10 11:35 | 2019-09-10 13:27 | 1:52 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV line | 2019-09-11 06:08 | 2019-09-11 16:17 | 10:09 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari express 132 kV line | 2019-09-12 06:25 | 2019-09-12 17:05 | 10:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari express 132 kV line | 2019-09-13 06:52 | 2019-09-13 17:01 | 10:09 | S/O | Due to C/M work | 0 | 0 | No interruption
| Siddhirganj-Shahjadpur 132 kV line | 2019-09-14 06:10 | 2019-09-14 16:58 | 10:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV bay |  | 2019-09-14 17:10 |  |  | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2019-09-15 06:01 | 2019-09-15 14:45 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sirajganj-Shahjadpur 132 kV line | 2019-09-16 06:51 | 2019-09-16 16:30 | 9:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-1 | 2019-09-16 08:23 | 2019-09-22 17:35 | 153:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur-Sirajganj 132 kV line-1 |  | 2019-09-16 17:12 |  | S/O |  | 0 | 0 | No interruption
| Bogura-Sherpur-Bogura(O) 132 kV line-1 |  | 2019-09-16 17:33 |  | S/O |  | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Bogura | Bogura-Naogaon 132 kV line-1 | 2019-09-18 06:43 | 2019-09-18 14:18 | 7:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-2 | 2019-09-18 08:40 | 2019-09-22 14:01 | 101:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Mohastangarh | Mohastangarh-Palashbari 132 kV line-1 | 2019-09-18 09:35 | 2019-09-18 17:07 | 7:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mohastangarh-Palashbari 132 kV line-2 | 2019-09-19 09:59 | 2019-09-19 17:18 | 7:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2019-09-20 07:00 | 2019-09-20 14:42 | 7:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajshahi-C.nawabganj 132 kV line | 2019-09-20 06:57 | 2019-09-20 07:53 | 0:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Mohastangarh | Mohastangarh-Bogura(O) 132 kV line-1 | 2019-09-20 10:12 | 2019-09-20 19:47 | 9:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line-1 | 2019-09-20 09:09 | 2019-09-20 17:45 | 8:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-2 | 2019-09-20 09:38 | 2019-09-20 17:50 | 8:12 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line | 2019-09-21 08:53 | 2019-09-21 18:00 | 9:07 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2019-09-21 10:29 | 2019-09-21 14:42 | 4:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat -Kurigram 132 kV line | 2019-09-21 08:20 | 2019-09-21 11:45 | 3:25 | S/O | Due to project work | 0 | 0 | No interruption
Bogura | Bogura-Mohastangarh 132 kV line-2 | 2019-09-21 10:13 | 2019-09-21 15:48 | 5:35 | S/O | Due to project work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2019-09-21 15:10 | 2019-09-21 18:20 | 3:10 | S/O | Due to Kurigram Ckt. hook up work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line-1 | 2019-09-21 19:59 | 2019-09-22 12:22 | 16:23 | S/O | Due to reduce Natore-Ishurdi line load | 0 | 0 | No interruption
Amnura | Amnura-Rajshahi 132 kV line-2 | 2019-09-27 09:00 | 2019-09-27 15:30 | 6:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Amnura-C.nawabganj 132 kV line | 2019-09-28 09:38 | 2019-09-28 18:18 | 8:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Amnura-C.nawabganj P/S 132 kV line | 2019-09-29 09:36 | 2019-09-29 11:03 | 1:27 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 449:10 |  | Unserved Energy: |  | 1.6667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 1820:17 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September' 2019
| Area | Previous Month (August 2019) |  |  |  | Current Month (September 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 10 | 12 | 31 | 53 | 15 | 7 | 48 | 70
2 | Dhaka (South) Grid Circle. | 8 | 12 | 28 | 48 | 16 | 9 | 32 | 57
3 | Chattogram Grid Circle. | 14 | 7 | 9 | 30 | 11 | 10 | 20 | 41
4 | Cumilla Grid Circle. | 18 | 13 | 19 | 50 | 13 | 8 | 25 | 46
5 | Khulna Grid Circle. | 14 | 11 | 51 | 76 | 13 | 3 | 23 | 39
6 | Bheramara HVDC Grid Circle | 2 | 5 | 16 | 23 | 8 | 6 | 13 | 27
7 | Bogura Grid Circle. | 21 | 16 | 27 | 64 | 12 | 13 | 53 | 78
8 | Others | Total number of S/O: 1; Total number of Total: 1; Total number of T: 2; Total number of Total: 2
9 | Total | 87 | 76 | 182 | 345 | 90 | 56 | 214 | 360
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September' 2019
| Area | Previous Month (August 2019) |  |  |  | Current Month (September 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 70.27 | 244.53 | 73.5 | 388.3 | 661.25 | 304.41 | 498.67 | 1464.33
2 | Dhaka (South) Grid Circle. | 12.1 | 216.58 |  | 228.68 | 137.41 | 73.33 | 99 | 309.74
3 | Chattogram Grid Circle. | 1145.41 | 92.25 | 81 | 1318.66 | 76.8 | 147.58 | 380.8 | 605.18
4 | Cumilla Grid Circle. | 209.42 | 498.75 | 21.63 | 729.8 | 7.9333 | 119.05 | - | 126.9833
5 | Khulna Grid Circle. | 48.87 | 147.85 | 1074.3 | 1271.02 | 245.38 | 7.4 | 118.67 | 371.45
6 | Bheramara HVDC Grid Circle | 10.83 | 58.85 | 175.7 | 245.38 | 355.5 | 17.03 | 84.8 | 457.33
7 | Bogura Grid Circle. | 268.77 | 227.78 | 1710.67 | 2207.22 | 300.29 | 516.42 | 294.5 | 1111.21
8 | Others | - | - | - | 0 | 6.5 | - | - | 6.5
9 | Total | 1765.67 | 1486.59 | 3136.8 | 6389.06 | 1791.0633 | 1185.22 | 1476.44 | 4452.7233
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 10 | 3 | 13 | 6 |  | 7 | 1185.9667
2 | Dhaka (South) | 5031.6 | 3 | 1 | 4 | 1 |  | 3 | 237.42
3 | Chattogram | 2042 | 6 | 3 | 9 |  | 3 | 6 | 605.02
4 | Khulna | 2434 | 5 | 2 | 7 | 1 | 1 | 5 | 360.95
5 | Bheramara (HVDC) | 2423.3 | 4 | 2 | 6 | 1 | 2 | 3 | 457.33
6 | Bogura | 3145.6 | 7 | 4 | 11 | 2 | 1 | 8 | 663.38
7 | Cumilla | 2981 | 7 |  | 7 | 1 | 3 | 3 | 126.98
8 | Others | - | [6 empty] | 6.5
| Total | 23365.5 | [6 empty] | 3643.5467
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.91%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 | - | 2 | 2 |  |  | 278.37
2 | Dhaka (South) | 990.29 |  | 2 | 1 | 3 | 2 | - | 1 | 72.33
3 | Chattogram | 917 | 20+9(Partial) | 1 | - | 1 | 1 | - |  | 0.17
4 | Khulna | 1238.4 | 21 | 1 |  | 1 | 1 | - |  | 10.5
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 6 | 1 | 7 | 4 | 1 | 2 | 447.82
7 | Cumilla | 1648.16 | 17 | - | - | - | - | - | - | -
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 809.19
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.79%
3 | Chattogram | 99.94%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.95% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.9% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-09-18 | 8 |  | 6 | 09hr17min | 1 | 1hr51min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:September' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 1:36 | 30 | 48 | Due to red-hot maintenance of 132/33 kV Transformer T2
Mymensingh | 1 | 3:53 | 40 | 155.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Jamalpur | 1 | 4:01 | 5 | 20.0833 | Due to red-hot maintenance of 132/33 kV Transformer T2
Tongi | 1 | 0:25 | 462 | 192.5 | Due to tripping of 132/33 kV Transformer T1
Keraniganj | 1 | 0:09 | 92 | 13.8 | Due to tripping of 132/33 kV Transformers T1 & T2
Tangail | 1 | 0:17 | 190 | 53.8333 | Due to tripping of 132/33 kV Transformers T1 & T2
Jamalpur | 1 | 3:47 | 20 | 75.6667 | Due to red-hot maintenance of 132/33 kV Transformer T4
Valuka |  | 0:16 | 20 | 5.3333 | Due to Breaker maintenance of 132/33 kV Transformer T2
Tangail | 2 | 0:35 | 164 | 95.6667 | Due to tripping of 132/33 kV Transformer T3
|  | 0:25 | 65 | 27.0833 | Due to tripping of 132/33 kV Transformer T2
United Jamalpur | 1 | 0:26 | 567 | 245.7 | Due to tripping of Jamalpur-Sherpur 132 kV line
Tongi | 1 | 0:14 | 140 | 32.6667 | Due to tripping of Tongi-Kabirpur 132 kV line-2
Tangail | 1 | 1:47 | 40 | 71.3333 | Due to S/D of 132/33 kV Transformer T2
Kadda | 1 | 2:41 | 140 | 375.6667 | Due to S/D of 33 kV full Bus
Manikganj | 1 | 1:02 | 50 | 51.6667 | Due to S/D of 132/33 kV Transformer T1
Kamrangirchar | 1 | 3:15 | 15 | 48.75 | Due to tripping of 132/33 kV Transformer T1
Munshiganj | 1 | 1:28 | 50 | 73.3333 | Due to red-hot maintenance of 33 kV Bus
Hasnabad | 1 | 0:28 | 110 | 51.3333 | Due to tripping of 132/33 kV Transformers T1,T2 & T3
Siddhirganj | 1 | 0:12 | 100 | 20 | Due to tripping of Siddhirganj-Matuail 132 kV line
Ullon | 1 | 0:13 | 80 | 17.3333 | Due to tripping of Ullon-Dhanmondi 132 kV line-3
Sonargaon | 1 | 2:08 | 30 | 64 | Due to S/D of 132/33 kV Transformer T2
Lalbagh | 1 | 1:10 | 30 | 35 | Due to S/D of Lalbagh-Hasnabad 132 kV line
Basundhara | 1 | 0:05 | 78 | 6.5 | Due to tripping of 132/33 kV Transformers T1 ,&,T2
Hathazari | 1 | 0:59 | 22 | 21.6333 | Due to tripping of 132/33 kV Transformer T1
Dohazari | 1 | 1:05 | 22 | 23.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Madunaghat | 1 | 0:46 | 35 | 26.8333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Halishahar | 1 | 2:45 | 20 | 55 | Due to tripping of 132/33 kV Transformers T2
Hathazari | 1 | 1:25 | 40 | 56.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Dohazari | 1 | 1:09 | 35 | 40.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
Sikalbaha | 1 | 0:21 | 0.5 | 0.175 | Due to tripping of Sikalbaha-T.k. chemical 132 kV line
Madunaghat | 1 | 0:48 | 20 | 16 | Due to S/D of 132/33 kV Transformer T1
Halishahar | 2 | 4:32 | 80 | 362.6667 | Due to S/D of 33 kV full Bus
|  | 2:08 | 1 | 2.1333 | Due to S/D of 132/33 kV Transformer T3
Feni | 1 | 0:32 | 15 | 8 | Due to red-hot maintenance of 132/33 kV Transformer T1
Cumilla(S) | 2 | 1:32 | 38 | 58.2667 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 0:20 | 25 | 8.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Cumilla(N) | 1 | 1:11 | 7 | 8.2833 | Due to tripping of 132/33 kV Transformer T3
Fenchuganj | 1 | 0:34 | 14 | 7.9333 | Due to tripping of 132/33 kV Transformer T2
Chowmuhani | 1 | 1:20 | 14 | 18.6667 | Due to red-hot maintenance of 132/33 kV Transformer T2 & 33 kV Bus
Chandpur | 1 | 0:35 | 30 | 17.5 | Due to red-hot maintenance of 132/33 kV Transformer T2
Gopalganj | 1 | 2:48 | 45 | 126 | Due to red-hot maintenance of 132/33 kV Transformer T1
Norail | 1 | 1:14 | 6 | 7.4 | Due to red-hot maintenance of 132/33 kV Transformer T1
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:September' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Madaripur | 2 | 1:24 | 40 | 56 | Due to tripping of 132/33 kV Transformers T1 &T2
|  | 0:36 | 10 | 6 | Due to tripping of 132/33 kV Transformer T1
Barisal(S) | 1 | 1:37 | 29 | 46.8833 | Due to tripping of 132/33 kV Transformer T2
Bagerhat | 1 | 0:21 | 30 | 10.5 | Due to tripping of Bagerhat-Mongla 132 kV line
Thakurgaon | 1 | 0:16 | 64 | 17.0667 | Due to tripping of Thakurgaon -Purbasadipur 132 kV line
Faridpur | 1 | 0:25 | 100 | 41.6667 | Due to S/D of 33 kV Bus-2
Satkhira | 1 | 2:12 | 35 | 77 | Due to S/D of 132/33 kV Transformer T1
Gallamari | 2 | 0:10 | 37 | 6.1667 | Due to tripping of 132/33 kV Transformer T1
|  | 0:38 | 7 | 4.4333 | Due to red-hot maintenance of 13233 kV Transformer T2
Ishurdi | 1 | 4:22 | 80 | 349.3333 | Due to tripping of 132/33 kV Transformer T1
Jhenidah | 1 | 0:36 | 21 | 12.6 | Due to red-hot maintenance of 13233 kV Transformer T2
Bottail | 2 | 1:10 | 30 | 35 | Due to S/D of 132/33 kV Transformer T1
|  | 2:46 | 18 | 49.8 | Due to S/D of 33 kV Bus-4
Purbasadipur | 2 | 2:18 | 30 | 69 | Due to bursting of PT
| 1 | 2:33 | 25 | 63.75 | Due to tripping of 132/33 kV Transformer T3
Rajshahi | 1 | 1:27 | 20 | 29 | Due to red-hot maintenance of 132/33 kV Transformer T3
Joldhaka | 1 | 1:20 | 20 | 26.6667 | Due to Oil leakage of 132/33 kV Transformer T1
Pabna | 1 | 0:17 | 104 | 29.4667 | Due to tripping of 132/33 kV Transformer T1
Rajshahi | 1 | 0:26 | 110 | 47.6667 | Due to tripping of 132/33 kV Transformers T1 & T3
Bogura(O) | 1 | 1:45 | 60 | 105 | Due to red-hot maintenance of 132/33 kV Transformer T1
Purbasadipur | 1 | 1:51 | 155 | 286.75 | Due to Breaker problem at Purbasadipur- Saidpur 132 kV line-1
Rajshahi | 1 | 0:10 | 190 | 31.6667 | Due to tripping of Rajshahi-Natore 132 kV line-1 & 2
Thakurgaon | 3 | 0:05 | 40 | 3.3333 | Due to tripping of Thaurgaon-Panchugar 132 kV line
|  | 0:41 | 40 | 27.3333
|  | 2:00 | 40 | 80
Rajshahi | 1 | 2:20 | 40 | 93.3333 | Due to S/D of 132/33 kV Transformer T2
Rangpur | 1 | 1:05 | 30 | 32.5 | Due to S/D of 132 kV Bus-A
Rangpur | 1 | 0:58 | 40 | 38.6667 | Due to S/D of 132/33 kV Transformer T2
Rajshahi | 1 | 2:34 | 50 | 128.3333 | Due to S/D of 132/33 kV Transformer T1
Purbasadipur | 1 | 0:05 | 20 | 1.6667 | Due to S/D of Saidpur-Purbasadipur 132 kV line-1
| Total unserved energy : |  |  | 4452.7417 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 140 | 18 | 2019-09-03 | 1500
2 | Munsiganj | 126 | 1 | 2019-09-03 | 2100
3 | Sonargaon | 90 | 1 | 2019-09-03 | 2100
4 | Shyampur | 210 | 11 | 2019-09-03 | 2400
5 | Bhulta | 192 | 2 | 2019-09-03 | 1100
6 | Madanganj | 60 | 4 | 2019-09-03 | 100
7 | Shitalakhya | 120 | 16 | 2019-09-03 | 1600
8 | Rahim steel | 28 | 22 | 2019-09-03 | 1300
9 | Matuail | 100 | 1 | 2019-09-03 | 1000
10 | Ghorasal | 94 | 15 | 2019-09-03 | 1900
11 | Narsingdi | 160 | 20 | 2019-09-03 | 2100
12 | Haripur (SBU) | 110 | 16 | 2019-09-03 | 2300
13 | Ullon | 101 | 15 | 2019-09-03 | 1800
14 | Hasnabad | 229 | 17 | 2019-09-03 | 2000
15 | Magbazar | 155 | 1 | 2019-09-03 | 1600
16 | Maniknagar | 124 | 2 | 2019-09-03 | 1830
17 | Bangabhaban | 40 | 1 | 2019-09-03 | 1600
18 | Narinda | 100 | 2 | 2019-09-03 | 1600
19 | Dhanmondi | 190 | 1 | 2019-09-03 | 1300
20 | Lalbag | 99 | 23 | 2019-09-03 | 1300
21 | Madartek | 79 | 6 | 2019-09-03 | 100
22 | Mirpur | 119 | 18 | 2019-09-03 | 1800
23 | Kalyanpur | 126 | 1 | 2019-09-03 | 1900
24 | Gulshan | 182 | 1 | 2019-09-03 | 1500
25 | Uttara | 95 | 1 | 2019-09-03 | 2000
26 | Uttara(new) | 20 | 16 | 2019-09-03 | 1500
27 | Kamrangirchar | 83 | 9 | 2019-09-03 | 1500
28 | Savar | 154 | 1 | 2019-09-03 | 1600
29 | Bhasantec | 184 | 18 | 2019-09-03 | 1600
30 | Agargaon | 68 | 1 | 2019-09-03 | 1300
31 | Satmosjid | 123 | 3 | 2019-09-03 | 2000
32 | Tongi | 164 | 2 | 2019-09-03 | 1500
33 | Kabirpur | 243 | 17 | 2019-09-03 | 1500
34 | Basundhara | 144 | 1 | 2019-09-03 | 1830
35 | Manikganj | 100 | 19 | 2019-09-03 | 1930
36 | Joydevpur | 235 | 16 | 2019-09-03 | 1830
37 | New Tongi | 118 | 19 | 2019-09-03 | 1830
38 | Kodda | 266 | 18 | 2019-09-03 | 1830
39 | Dhamrai | 88 | 29 | 2019-09-03 | 2300
40 | Valuka | 120 | 18 | 2019-09-03 | 1830
41 | Tangail | 208 | 2 | 2019-09-03 | 2100
42 | Mymensing | 259 | 21 | 2019-09-03 | 2100
43 | Kishorganj | 140 | 4 | 2019-09-03 | 2100
44 | Netrokona | 113 | 3 | 2019-09-03 | 2000
45 | Jamalpur | 147 | 3 | 2019-09-03 | 100
46 | Sherpur | 116 | 1 | 2019-09-03 | 2300
47 | Srimongal | 45 | 1 | 2019-09-03 | 1900
48 | Shahjibazar | 129 | 15 | 2019-09-03 | 1900
49 | Fenchuganj | 53 | 1 | 2019-09-03 | 1900
50 | Kulawara | 50 | 2 | 2019-09-03 | 2000
51 | Sylhet | 164 | 3 | 2019-09-03 | 1830
52 | Chatak | 37 | 19 | 2019-09-03 | 1830
53 | Sunamganj | 47 | 1 | 2019-09-03 | 2300
54 | Bianibazar | 63 | 3 | 2019-09-03 | 2000
55 | Cumilla (S) | 194 | 19 | 2019-09-03 | 2000
56 | Cumilla(N) | 157 | 1 | 2019-09-03 | 1900
57 | Chandpur | 123 | 7 | 2019-09-03 | 1900
58 | Feni | 139 | 17 | 2019-09-03 | 2000
59 | Chowmuhani | 188 | 16 | 2019-09-03 | 1900
60 | Ashuganj | 61 | 4 | 2019-09-03 | 2100
61 | Daudkandi | 148 | 17 | 2019-09-03 | 2300
62 | B.Baria | 154 | 15 | 2019-09-03 | 2100
63 | Ramganj | 102 | 2 | 2019-09-03 | 2300
64 | Madanhat | 71 | 24 | 2019-09-03 | 1900
65 | Hathazari | 108 | 19 | 2019-09-03 | 1830
66 | Khulshi | 193 | 5 | 2019-09-03 | 1600
67 | Halishahar | 153 | 18 | 2019-09-03 | 1200
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 170 | 22 | 2019-09-03 | 100
69 | Sikalbaha | 37 | 7 | 2019-09-03 | 100
70 | Dohazari | 106 | 16 | 2019-09-03 | 1900
71 | Cox'sbazar | 100 | 15 | 2019-09-03 | 2000
72 | Chandraghona | 40 | 21 | 2019-09-03 | 1830
73 | Kaptai | 28 | 24 | 2019-09-03 | 2000
74 | A. Khaer Stl. | 16 | 14 | 2019-09-03 | 1700
75 | Bakulia | 111 | 18 | 2019-09-03 | 1830
76 | Julda | 23 | 5 | 2019-09-03 | 900
77 | TK chemical | 19 | 18 | 2019-09-03 | 1900
78 | Modern Steel | 16 | 14 | 2019-09-03 | 1200
79 | Shahmirpur | 33 | 4 | 2019-09-03 | 1900
80 | Khagrachhari | 33 | 24 | 2019-09-03 | 1830
81 | Matarbari | 30 | 17 | 2019-09-03 | 2100
82 | Baroiar Hat | 46 | 17 | 2019-09-03 | 1830
83 | Rangamati | 36 | 24 | 2019-09-03 | 1830
84 | Abul Khair 230 | 190.9 | 18 | 2019-09-03 | 1200
85 | BSRM | 154 | 8 | 2019-09-03 | 700
86 | Goalpara | 41 | 19 | 2019-09-03 | 2000
87 | Central s/s | 105 | 8 | 2019-09-03 | 2100
88 | Noapara | 80 | 9 | 2019-09-03 | 1900
89 | Jashore | 124 | 17 | 2019-09-03 | 1900
90 | Benapol | 50 | 18 | 2019-09-03 | 2100
91 | Jhenidah | 118 | 16 | 2019-09-03 | 2000
92 | Bottail | 132 | 1 | 2019-09-03 | 1930
93 | G.K Project | 72 | 5 | 2019-09-03 | 2000
94 | Faridpur | 186 | 2 | 2019-09-03 | 2000
95 | Madaripur | 119 | 1 | 2019-09-03 | 2100
96 | Sariatpur | 64 | 17 | 2019-09-03 | 2100
97 | Gopalganj | 97 | 16 | 2019-09-03 | 2000
98 | Bagerhat | 88 | 17 | 2019-09-03 | 2200
99 | Mongla | 40 | 16 | 2019-09-03 | 1200
100 | Satkhira | 105 | 18 | 2019-09-03 | 2000
101 | Gallamari | 54 | 18 | 2019-09-03 | 1200
102 | Magura | 57 | 20 | 2019-09-03 | 1900
103 | Norail | 30 | 23 | 2019-09-03 | 1930
104 | Chuadanga | 95 | 1 | 2019-09-03 | 2200
105 | Barsal(N) | 46 | 2 | 2019-09-03 | 2200
106 | Barsal(S) | 108 | 1 | 2019-09-03 | 1930
107 | Patuakhali | 115 | 19 | 2019-09-03 | 2200
108 | Bhandaria | 58 | 15 | 2019-09-03 | 2000
109 | Borhan Uddin | 44 | 23 | 2019-09-03 | 1930
110 | Ishurdi | 71 | 1 | 2019-09-03 | 2100
111 | Ruppur Paromanobik | 2 | 1 | 2019-09-03 | 2100
112 | Natore | 135 | 1 | 2019-09-03 | 2100
113 | Bogura | 260 | 2 | 2019-09-03 | 1930
114 | Naogaon | 129 | 2 | 2019-09-03 | 2100
115 | Rajshahi | 172 | 16 | 2019-09-03 | 2100
116 | Rajshahi New | 114 | 30 | 2019-09-03 | 1930
117 | C.Nawabganj | 84 | 1 | 2019-09-03 | 1930
118 | Amnura | 49 | 29 | 2019-09-03 | 2000
119 | Pabna | 129 | 19 | 2019-09-03 | 1930
120 | Shahjadpur | 114 | 18 | 2019-09-03 | 2000
121 | Serajganj | 117 | 1 | 2019-09-03 | 2000
122 | Niyamatpur | 80 | 29 | 2019-09-03 | 2000
123 | Joypurhat | 57 | 1 | 2019-09-03 | 2000
124 | Sherpur(Bogura) | 41 | 26 | 2019-09-03 | 1830
125 | Mohastangar | 18 | 21 | 2019-09-03 | 2000
126 | Rangpur | 158 | 4 | 2019-09-03 | 2000
127 | Lalmonirhat | 76 | 1 | 2019-09-03 | 2000
128 | Saidpur | 114 | 1 | 2019-09-03 | 2000
129 | Purbasadipur | 106 | 4 | 2019-09-03 | 2000
130 | Thakurgaon | 82 | 1 | 2019-09-03 | 2100
131 | Palshbari | 127 | 1 | 2019-09-03 | 1900
132 | Barapukuria | 59 | 5 | 2019-09-03 | 2100
133 | Panchugar | 47 | 8 | 2019-09-03 | 2100
134 | Joldhaka | 31 | 2 | 2019-09-03 | 2000
135 | Kurigram | 42 | 1 | 2019-09-03 | 2000
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4467 | 18.09.19 | 15:00
Chattogram | 1306 | 05.09.19 | 02:00
Khulna | 1508 | 17.09.19 | 22:00
Rajshahi | 1358 | 01.09.19 | 21:00
Cumilla | 1196 | 17.09.19 | 21:00
Mymensingh | 1024 | 02.09.19 | 21:00
Sylhet | 555 | 02.09.19 | 19:30
Barisal | 357 | 01.09.19 | 22:00
Rangpur | 788 | 01.09.19 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 383 | 387 | 3 | 2019-09-03 | 18:00 | 365 | 15 | 2019-06-03 | 10:00
2 | Bheramara | 388 | 410 | 14 | 2019-09-03 | 20:00 | 386 | 16 | 2019-06-03 | 19:00
3 | Ashuganj(N) | 376 | 387 | 2 | 2019-09-03 | 10:00 | 361 | 24 | 2019-06-03 | 12:00
4 | Kaliakoir | 400 | 369 | 13 | 2019-09-03 | 18:30 | 340 | 23 | 2019-06-03 | 15:00
5 | Bhulta | 400 | 382 | 3 | 2019-09-03 | 20:00 | 353 | 23 | 2019-06-03 | 12:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 25 | 2019-09-03 | 13:00 | 220 | 1 | 2019-09-03 | 9:00
2 | Ishurdi | 230 | 237 | 1 | 2019-09-03 | 6:00 | 224 | 2 | 2019-09-03 | 20:00
3 | Ashuganj | 230 | 236 | 4 | 2019-09-03 | 6:00 | 220 | 23 | 2019-09-03 | 12:00
4 | Serajganj | 230 | 232 | 4 | 2019-09-03 | 1:00 | 220 | 18 | 2019-09-03 | 19:00
5 | Baghabari | 230 | 237 | 15 | 2019-09-03 | 10:00 | 225 | 18 | 2019-09-03 | 19:30
6 | Barapukuria | 230 | 238 | 17 | 2019-09-03 | 15:00 | 221 | 3 | 2019-09-03 | 21:00
7 | Bogra | 230 | 227 | 3 | 2019-09-03 | 18:00 | 208 | 1 | 2019-09-03 | 20:00
8 | Khulna South | 230 | 230 | 7 | 2019-09-03 | 18:30 | 206 | 22 | 2019-09-03 | 11:00
9 | Rampura | 230 | 220 | 1 | 2019-09-03 | 4:00 | 208 | 21 | 2019-09-03 | 11:00
10 | Haripur | 230 | 220 | 3 | 2019-09-03 | 20:00 | 206 | 23 | 2019-09-03 | 12:00
11 | Hasnabad | 230 | 221 | 3 | 2019-09-03 | 21:00 | 206 | 24 | 2019-09-03 | 10:00
12 | Aminbazar | 230 | 222 | 2 | 2019-09-03 | 2:00 | 205 | 24 | 2019-09-03 | 11:00
13 | Tongi | 230 | 225 | 7 | 2019-09-03 | 24:00 | 203 | 24 | 2019-09-03 | 11:00
14 | Comilla (N) | 230 | 229 | 3 | 2019-09-03 | 18:00 | 211 | 29 | 2019-09-03 | 23:00
15 | Hathazari | 230 | 221 | 4 | 2019-09-03 | 6:00 | 208 | 16 | 2019-09-03 | 15:00
16 | Megnaghat | 230 | 222 | 1 | 2019-09-03 | 21:00 | 208 | 30 | 2019-09-03 | 12:00
17 | Fenchuganj | 230 | 235 | 4 | 2019-09-03 | 6:00 | 225 | 16 | 2019-09-03 | 18:00
18 | Siddhirganj | 230 | 221 | 4 | 2019-09-03 | 6:00 | 207 | 23 | 2019-09-03 | 12:00
19 | Maniknagar | 230 | 219 | 4 | 2019-09-03 | 6:00 | 205 | 23 | 2019-09-03 | 12:00
20 | Old Airport | 230 | 221 | 19 | 2019-09-03 | 7:00 | 203 | 24 | 2019-09-03 | 11:00
21 | Barisal | 230 | 234 | 8 | 2019-09-03 | 3:00 | 217 | 14 | 2019-09-03 | 15:00
22 | AKSML | 230 | 231 | 11 | 2019-09-03 | 13:00 | 204 | 18 | 2019-09-03 | 15:00
23 | BSRM | 230 | 220 | 4 | 2019-09-03 | 6:00 | 205 | 16 | 2019-09-03 | 10:00
24 | Bibiyana | 230 | 233 | 9 | 2019-09-03 | 3:00 | 202 | 4 | 2019-09-03 | 13:00
25 | Bhulta | 230 | 222 | 2 | 2019-09-03 | 6:00 | 208 | 11 | 2019-09-03 | 11:00
26 | Ashuganj (S) | 230 | 288 | 25 | 2019-09-03 | 19:00 | 220 | 23 | 2019-09-03 | 11:00
27 | Kaliakoir | 230 | 224 | 7 | 2019-09-03 | 19:00 | 204 | 1 | 2019-09-03 | 11:00
132 kV Substation
1 | Siddhirganj | 132 | 133 | 17 | 2019-09-03 | 2100 | 123 | 11 | 2019-09-03 | 1200
2 | Munsiganj | 132 | 135 | 4 | 2019-09-03 | 100 | 120 | 23 | 2019-09-03 | 1200
3 | Megnaghat | 132 | 132 | 8 | 2019-09-03 | 100 | 122 | 25 | 2019-09-03 | 1700
4 | Shyampur | 132 | 134 | 3 | 2019-09-03 | 6:00 | 123 | 24 | 2019-09-03 | 1000
5 | Bhulta | 132 | 128 | 2 | 2019-09-03 | 700 | 112 | 21 | 2019-09-03 | 1500
6 | Madanganj | 132 | 140 | 16 | 2019-09-03 | 1:00 | 121 | 2 | 2019-09-03 | 1000
7 | Shitalakhya | 132 | 141 | 3 | 2019-09-03 | 2000 | 121 | 24 | 2019-09-03 | 1000
8 | Rahim Steal | 132 | 133 | 17 | 2019-09-03 | 2100 | 123 | 23 | 2019-09-03 | 1200
9 | Matuail | 132 | 132 | 6 | 2019-09-03 | 1900 | 121 | 11 | 2019-09-03 | 12:00
10 | Ghorasal | 132 | 138 | 2 | 2019-09-03 | 200 | 121 | 26 | 2019-09-03 | 1600
11 | Narsinghdi | 132 | 135 | 13 | 2019-09-03 | 800 | 113 | 21 | 2019-09-03 | 1900
12 | Haripur (SBU) | 132 | 134 | 25 | 2019-09-03 | 1400 | 123 | 23 | 2019-09-03 | 1200
13 | Ullon | 132 | 136 | 2 | 2019-09-03 | 200 | 121 | 1 | 2019-09-03 | 1000
14 | Hasnabad | 132 | 137 | 3 | 2019-09-03 | 1900 | 124 | 24 | 2019-09-03 | 12:00
15 | Magbazar | 132 | 135 | 2 | 2019-09-03 | 200 | 120 | 1 | 2019-09-03 | 1100
16 | Maniknagar | 132 | 134 | 4 | 2019-09-03 | 600 | 123 | 11 | 2019-09-03 | 1200
17 | Bangabhaban | 132 | 134 | 4 | 2019-09-03 | 600 | 123 | 11 | 2019-09-03 | 1200
18 | Narinda | 132 | 134 | 4 | 2019-09-03 | 600 | 123 | 11 | 2019-09-03 | 1200
19 | Dhanmondi | 132 | 135 | 4 | 2019-09-03 | 600 | 121 | 1 | 2019-09-03 | 1000
20 | Lalbag | 132 | 137 | 15 | 2019-09-03 | 2100 | 119 | 24 | 2019-09-03 | 1200
21 | Madartek | 132 | 135 | 2 | 2019-09-03 | 700 | 120 | 1 | 2019-09-03 | 1100
22 | Mirpur | 132 | 137 | 13 | 2019-09-03 | 1800 | 122 | 1 | 2019-09-03 | 1000
23 | Kalyanpur | 132 | 137 | 4 | 2019-09-03 | 500 | 125 | 24 | 2019-09-03 | 1200
24 | Gulshan | 132 | 135 | 8 | 2019-09-03 | 500 | 121 | 11 | 2019-09-03 | 1200
25 | Uttara | 132 | 134 | 2 | 2019-09-03 | 200 | 120 | 1 | 2019-09-03 | 1100
26 | Uttara(New) | 132 | 133 | 1 | 2019-09-03 | 100 | 122 | 11 | 2019-09-03 | 1200
27 | Kamrangirchar | 132 | 136 | 23 | 2019-09-03 | 2000 | 119 | 24 | 2019-09-03 | 1000
28 | Savar | 132 | 134 | 4 | 2019-09-03 | 600 | 121 | 1 | 2019-09-03 | 1000
29 | Bhasantec | 132 | 134 | 13 | 2019-09-03 | 1800 | 120 | 1 | 2019-09-03 | 1000
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 136 | 13 | 2019-09-03 | 1800 | 122 | 1 | 2019-09-03 | 1000
31 | Satmosjid | 132 | 135 | 13 | 2019-09-03 | 1800 | 121 | 1 | 2019-09-03 | 1000
32 | Tongi | 132 | 137 | 7 | 2019-09-03 | 2400 | 123 | 24 | 2019-09-03 | 1100
33 | Kabirpur | 132 | 134 | 4 | 2019-09-03 | 500 | 115 | 15 | 2019-09-03 | 1300
34 | Basundhara | 132 | 133 | 2 | 2019-09-03 | 100 | 114 | 19 | 2019-09-03 | 1500
35 | Manikganj | 132 | 139 | 9 | 2019-09-03 | 1900 | 123 | 29 | 2019-09-03 | 900
36 | Joydevpur | 132 | 142 | 2 | 2019-09-03 | 100 | 126 | 19 | 2019-09-03 | 1500
37 | New Tongi | 132 | 135 | 7 | 2019-09-03 | 2400 | 121 | 24 | 2019-09-03 | 1600
38 | Kodda | 132 | 138 | 9 | 2019-09-03 | 1830 | 118 | 28 | 2019-09-03 | 800
39 | Dhamrai | 132 | 134 | 4 | 2019-09-03 | 600 | 119 | 18 | 2019-09-03 | 1900
40 | Valuka | 133 | 131 | 9 | 2019-09-03 | 1600 | 98 | 18 | 2019-09-03 | 1900
41 | Tangail | 132 | 134 | 13 | 2019-09-03 | 1600 | 115 | 21 | 2019-09-03 | 1900
42 | Mymensing | 132 | 132 | 9 | 2019-09-03 | 1600 | 110 | 2 | 2019-09-03 | 1100
43 | Kishorganj | 132 | 133 | 13 | 2019-09-03 | 1500 | 114 | 21 | 2019-09-03 | 2000
44 | Netrokona | 132 | 134 | 15 | 2019-09-03 | 1600 | 107 | 2 | 2019-09-03 | 2000
45 | Jamalpur | 132 | 140 | 18 | 2019-09-03 | 200 | 112 | 19 | 2019-09-03 | 1200
46 | Sherpur | 132 | 141 | 24 | 2019-09-03 | 1800 | 104 | 2 | 2019-09-03 | 1100
47 | Srimongal | 132 | 138 | 16 | 2019-09-03 | 100 | 127 | 5 | 2019-09-03 | 1800
48 | Shahjibazar | 132 | 137 | 13 | 2019-09-03 | 1400 | 127 | 3 | 2019-09-03 | 1830
49 | Fenchuganj | 132 | 135 | 4 | 2019-09-03 | 600 | 126 | 5 | 2019-09-03 | 1830
50 | Khulawara | 132 | 136 | 26 | 2019-09-03 | 100 | 125 | 5 | 2019-09-03 | 1830
51 | Sylhet | 132 | 135 | 14 | 2019-09-03 | 800 | 121 | 5 | 2019-09-03 | 1830
52 | Chattak | 132 | 134 | 10 | 2019-09-03 | 700 | 119 | 5 | 2019-09-03 | 1830
53 | Sunamganj | 132 | 134 | 14 | 2019-09-03 | 800 | 116 | 5 | 2019-09-03 | 1830
54 | Biani Bazar | 132 | 133 | 13 | 2019-09-03 | 1300 | 118 | 5 | 2019-09-03 | 1830
55 | Comilla(South) | 132 | 127 | 2 | 2019-09-03 | 600 | 116 | 22 | 2019-09-03 | 1400
56 | Comilla (North) | 132 | 136 | 19 | 2019-09-03 | 1800 | 126 | 23 | 2019-09-03 | 1200
57 | Chandpur | 132 | 138 | 8 | 2019-09-03 | 1100 | 118 | 15 | 2019-09-03 | 2100
58 | Feni | 132 | 128 | 3 | 2019-09-03 | 1800 | 111 | 17 | 2019-09-03 | 2100
59 | Chowmuhani | 132 | 134 | 16 | 2019-09-03 | 700 | 110 | 23 | 2019-09-03 | 2300
60 | Ashuganj | 132 | 140 | 13 | 2019-09-03 | 1500 | 127 | 27 | 2019-09-03 | 2100
61 | Daudkandi | 132 | 136 | 17 | 2019-09-03 | 2200 | 120 | 23 | 2019-09-03 | 1200
62 | Brahminbaria | 132 | 134 | 12 | 2019-09-03 | 1700 | 121 | 21 | 2019-09-03 | 1930
63 | Ramganj | 132 | 128 | 18 | 2019-09-03 | 700 | 109 | 15 | 2019-09-03 | 2200
64 | Madanhat | 132 | 134 | 12 | 2019-09-03 | 2100 | 113 | 5 | 2019-09-03 | 1100
65 | Hathazari | 132 | 131 | 1 | 2019-09-03 | 500 | 125 | 22 | 2019-09-03 | 1000
66 | Khulshi | 132 | 130 | 6 | 2019-09-03 | 1800 | 122 | 25 | 2019-09-03 | 300
67 | Halishahar | 132 | 133 | 6 | 2019-09-03 | 1900 | 125 | 24 | 2019-09-03 | 1600
68 | Baraulia | 132 | 131 | 1 | 2019-09-03 | 600 | 122 | 26 | 2019-09-03 | 1000
69 | Sikalbaha | 132 | 133 | 5 | 2019-09-03 | 400 | 126 | 19 | 2019-09-03 | 1500
70 | Dohazari | 132 | 133 | 23 | 2019-09-03 | 1700 | 123 | 19 | 2019-09-03 | 1400
71 | Cox'sbazar | 132 | 130 | 5 | 2019-09-03 | 700 | 114 | 5 | 2019-09-03 | 1830
72 | Chandraghona | 132 | 133 | 1 | 2019-09-03 | 700 | 127 | 14 | 2019-09-03 | 900
73 | Kaptai | 132 | 133 | 16 | 2019-09-03 | 700 | 127 | 18 | 2019-09-03 | 1200
74 | A. Khaer Stl. | 132 | 130 | 1 | 2019-09-03 | 500 | 124 | 19 | 2019-09-03 | 1500
75 | Bakulia | 132 | 132 | 8 | 2019-09-03 | 1400 | 124 | 24 | 2019-09-03 | 1600
76 | Julda | 132 | 132 | 7 | 2019-09-03 | 1000 | 125 | 25 | 2019-09-03 | 1600
77 | TK Chemical | 132 | 133 | 12 | 2019-09-03 | 2100 | 118 | 5 | 2019-09-03 | 1000
78 | Modern Steel | 132 | 132 | 1 | 2019-09-03 | 500 | 125 | 14 | 2019-09-03 | 1000
79 | Shahmirpur | 132 | 133 | 8 | 2019-09-03 | 1930 | 113 | 4 | 2019-09-03 | 2000
80 | Khagrachhari | 132 | 132 | 4 | 2019-09-03 | 600 | 123 | 22 | 2019-09-03 | 200
81 | Matarbari | 132 | 130 | 12 | 2019-09-03 | 1300 | 115 | 25 | 2019-09-03 | 400
82 | Baroiar Hat | 132 | 129 | 8 | 2019-09-03 | 1100 | 116 | 15 | 2019-09-03 | 2100
83 | Rangamati | 133 | 132 | 1 | 2019-09-03 | 600 | 123 | 25 | 2019-09-03 | 1930
84 | Goalpara | 132 | 139 | 9 | 2019-09-03 | 1100 | 124 | 10 | 2019-09-03 | 500
85 | Khulna Central | 132 | 139 | 7 | 2019-09-03 | 1830 | 124 | 23 | 2019-09-03 | 1100
86 | Noapara | 132 | 137 | 7 | 2019-09-03 | 1830 | 120 | 10 | 2019-09-03 | 500
87 | Jessore | 132 | 134 | 27 | 2019-09-03 | 700 | 113 | 15 | 2019-09-03 | 500
88 | Benapol | 132 | 134 | 4 | 2019-09-03 | 1700 | 116 | 15 | 2019-09-03 | 1300
89 | Jhenida | 132 | 134 | 27 | 2019-09-03 | 600 | 111 | 2 | 2019-09-03 | 1900
90 | Bottail | 132 | 137 | 27 | 2019-09-03 | 600 | 122 | 15 | 2019-09-03 | 1830
91 | G.K Project | 132 | 143 | 23 | 2019-09-03 | 1700 | 134 | 2 | 2019-09-03 | 2000
92 | Faridpur | 132 | 135 | 22 | 2019-09-03 | 1900 | 118 | 1 | 2019-09-03 | 2000
93 | Madaripur | 132 | 136 | 11 | 2019-09-03 | 1800 | 119 | 19 | 2019-09-03 | 2100
94 | Sariatpur | 132 | 136 | 14 | 2019-09-03 | 600 | 116 | 19 | 2019-09-03 | 2100
95 | Gopalganj | 132 | 144 | 10 | 2019-09-03 | 600 | 124 | 11 | 2019-09-03 | 1300
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Bagerhat | 132 | 138 | 12 | 2019-09-03 | 1200 | 122 | 14 | 2019-09-03 | 2000
97 | Mongla | 132 | 135 | 2 | 2019-09-03 | 1800 | 120 | 22 | 2019-09-03 | 1100
98 | Satkhira | 132 | 138 | 4 | 2019-09-03 | 600 | 123 | 14 | 2019-09-03 | 2000
99 | Gallamari | 132 | 139 | 5 | 2019-09-03 | 500 | 123 | 7 | 2019-09-03 | 500
100 | Magura | 132 | 133 | 27 | 2019-09-03 | 900 | 108 | 17 | 2019-09-03 | 1900
101 | Norail | 132 | 131 | 30 | 2019-09-03 | 600 | 106 | 2 | 2019-09-03 | 2000
102 | Chuadanga | 132 | 134 | 30 | 2019-09-03 | 900 | 100 | 15 | 2019-09-03 | 2000
103 | Barisal(N) | 132 | 141 | 21 | 2019-09-03 | 900 | 127 | 14 | 2019-09-03 | 1500
104 | Barisal(S) | 132 | 140 | 14 | 2019-09-03 | 600 | 125 | 3 | 2019-09-03 | 1500
105 | Patuakhali | 132 | 137 | 14 | 2019-09-03 | 600 | 120 | 18 | 2019-09-03 | 2100
106 | Bhandaria | 132 | 136 | 2 | 2019-09-03 | 900 | 125 | 1 | 2019-09-03 | 1300
107 | Ishurdi | 132 | 140 | 6 | 2019-09-03 | 1800 | 130 | 2 | 2019-09-03 | 2000
108 | Ruppur paromanobik | 132 | 140 | 17 | 2019-09-03 | 1800 | 132 | 1 | 2019-09-03 | 1900
109 | Natore | 132 | 139 | 24 | 2019-09-03 | 1800 | 125 | 1 | 2019-09-03 | 2100
110 | Bogra | 132 | 139 | 24 | 2019-09-03 | 1800 | 122 | 1 | 2019-09-03 | 2100
111 | Noagaon | 132 | 136 | 29 | 2019-09-03 | 1800 | 115 | 1 | 2019-09-03 | 2100
112 | Rajshahi | 132 | 137 | 24 | 2019-09-03 | 1800 | 121 | 1 | 2019-09-03 | 1300
113 | Rajshahi New | 132 | 136 | 28 | 2019-09-03 | 1800 | 124 | 28 | 2019-09-03 | 100
114 | C.Nawabganj | 132 | 133 | 17 | 2019-09-03 | 1800 | 115 | 1 | 2019-09-03 | 1400
115 | Amnura | 132 | 141 | 28 | 2019-09-03 | 1800 | 117 | 1 | 2019-09-03 | 1300
116 | Pabna | 132 | 139 | 27 | 2019-09-03 | 900 | 122 | 24 | 2019-09-03 | 100
117 | Shahjadpur | 132 | 142 | 13 | 2019-09-03 | 1800 | 125 | 17 | 2019-09-03 | 2000
118 | Serajganj | 132 | 141 | 29 | 2019-09-03 | 1800 | 124 | 17 | 2019-09-03 | 1800
119 | Niyamatpur | 132 | 136 | 29 | 2019-09-03 | 1830 | 108 | 1 | 2019-09-03 | 2100
120 | Joypurhat | 132 | 136 | 30 | 2019-09-03 | 1800 | 110 | 1 | 2019-09-03 | 1900
121 | Sherpur(Bogura) | 132 | 138 | 27 | 2019-09-03 | 1700 | 130 | 29 | 2019-09-03 | 1900
122 | Mohastangor | 132 | 137 | 24 | 2019-09-03 | 700 | 118 | 15 | 2019-09-03 | 2000
123 | Rangpur | 132 | 135 | 16 | 2019-09-03 | 1000 | 112 | 1 | 2019-09-03 | 1900
124 | Lalmonirhat | 132 | 130 | 3 | 2019-09-03 | 700 | 107 | 7 | 2019-09-03 | 2100
125 | Saidpur | 132 | 134 | 17 | 2019-09-03 | 1400 | 110 | 6 | 2019-09-03 | 2300
126 | Purbasadipur | 132 | 138 | 29 | 2019-09-03 | 400 | 110 | 3 | 2019-09-03 | 2100
127 | Thakurgaon | 132 | 130 | 17 | 2019-09-03 | 600 | 100 | 1 | 2019-09-03 | 2100
128 | Palashbari | 132 | 135 | 18 | 2019-09-03 | 500 | 115 | 3 | 2019-09-03 | 2000
129 | Barapukuria | 132 | 138 | 17 | 2019-09-03 | 1500 | 121 | 3 | 2019-09-03 | 2100
130 | Panchagar | 132 | 129 | 10 | 2019-09-03 | 900 | 90 | 7 | 2019-09-03 | 2100
131 | Joldhaka | 132 | 134 | 17 | 2019-09-03 | 1500 | 107 | 3 | 2019-09-03 | 2100
132 | Kurigram | 133 | 134 | 24 | 2019-09-03 | 1300 | 104 | 5 | 2019-09-03 | 2000
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:September' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 145 | 400
IP-299421 | Hasnabad | TR2 | 225 | 118 | 400 | 09.09.19 | 23:00
|  | TR3 | 225 | 110 | 360
|  | TR1 | 225 | 160 | 490
IP-299866 | Tongi | TR2 | 225 | 160 | 490 | 17.09.19 | 16:00
|  | TR3 | 225 | 160 | 490
|  | TR1 | 225 | 153 | 500
IP-299427 | Haripur | TR2 | 225 |  |  | 02.09.19 | 06:00 | S/D
|  | TR3 | 225 | 153 | 500
|  | TR1 | 225 | 187 | 575
IP-299728 | Rampura | TR2 | 225 | 187 | 575 | 07.09.19 | 15:00
|  | TR3 | 225 | 187 | 575
|  | TR1 | 225 | 140 | 410
IP-299264 | Aminbazar | TR2 | 225 | 140 | 410 | 16.09.19 | 15:00
|  | TR3 | 225 | 146 | 435
| Maniknagar | TR1 | 300 | 126 | 410 | 17.09.19 | 16:00
|  | TR2 | 300 | 126 | 410
IP-399266 | Cumilla (N) | TR1 | 225 | 170 | 500 | 25.09.19 | 1:00
|  | TR2 | 225 | 170 | 480
| Fenchuganj | TR1 | 300 | 157 | 402 | 21.09.19 | 18:00
|  | MT1 | 150 | 80 | 230
IP-399428 | Hathazari | MT2 | 150 | 80 | 205 | 23.09.19 | 23:00
|  | MT3 | 150 | 80 | 205
|  | MT4 | 150 | 80 | 205
|  | TR1 | 225 | 140 | 380
| Ishurdi | TR2 | 225 | 140 | 380 | 19.09.19 | 2:00
IP-499474 |  | TR3 | 225 | 140 | 380
| Khulna(S) | TR1 | 225 | 122 | 334
IP-58001/58002 |  | TR2 | 225 | 122 | 334 | 15.09.19 | 06:00
|  | TR3 | 300 | 158 | 432
| Bogra | TR1 | 225 | 136 | 247 | 02.09.19 | 18:00
|  | TR2 | 225 | 136 | 247
IP-43002/499264 |  | TR3 | 225 | 143 | 326
IP-499224 | Baghabari | TR1 | 225 | 170 | 520 | 14.09.19 | 20:00
| Barapukuria | TR1 | 225 | 196 | 950 | 20.09.19 | 19:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 225 | 167 | 860 |  |  | 132 kV current is being provided
|  | TR6 | 300 | 212 | 1090
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 196 | 345 | 27.09.19 | 11:45
|  | TR2(400/230 kV) | 520 | 198 | 351
|  | TR1(400/132 kV) | 325 | 245 | 461 | 18.09.19 | 18:45
|  | TR2(400/132 kV) | 325 | 245 | 461
| Bibiyana | ICT1(400/230 kV) | 520 | 154 | 276 | 14.09.19 | 12:00
|  | ICT2(400/230kV) | 520 | 153 | 279
| Bhulta | ATR1(400/230 kV) | 520 | 220 | 403 | 15.09.19 | 19:30
|  | ATR2(400/230kV) | 520 | 220 | 403
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:September' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:September' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-09-19 | 12717 | 12717 | - | - | - | - | - | - | - | - | - | - | - | - | 01-09-19 | 10636.2 | 10636.2 | - | - | - | - | - | - | - | - | - | - | - | -
02-09-19 | 12560 | 12560 | - | - | - | - | - | - | - | - | - | - | - | - | 02-09-19 | 10069.5 | 10069.5 | - | - | - | - | - | - | - | - | - | - | - | -
03-09-19 | 12472 | 12472 | - | - | - | - | - | - | - | - | - | - | - | - | 03-09-19 | 10162 | 10162 | - | - | - | - | - | - | - | - | - | - | - | -
04-09-19 | 12426 | 12426 | - | - | - | - | - | - | - | - | - | - | - | - | 04-09-19 | 9782.1 | 9782.1 | - | - | - | - | - | - | - | - | - | - | - | -
05-09-19 | 12344 | 12344 | - | - | - | - | - | - | - | - | - | - | - | - | 05-09-19 | 10216.4 | 10216.4 | - | - | - | - | - | - | - | - | - | - | - | -
06-09-19 | 11674 | 11674 | - | - | - | - | - | - | - | - | - | - | - | - | 06-09-19 | 8638.5 | 8638.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-09-19 | 12103 | 12103 | - | - | - | - | - | - | - | - | - | - | - | - | 07-09-19 | 9431 | 9431 | - | - | - | - | - | - | - | - | - | - | - | -
08-09-19 | 11979 | 11979 | - | - | - | - | - | - | - | - | - | - | - | - | 08-09-19 | 9889.1 | 9889.1 | - | - | - | - | - | - | - | - | - | - | - | -
09-09-19 | 11852 | 11852 | - | - | - | - | - | - | - | - | - | - | - | - | 09-09-19 | 9928 | 9928 | - | - | - | - | - | - | - | - | - | - | - | -
10-09-19 | 11854 | 11854 | - | - | - | - | - | - | - | - | - | - | - | - | 10-09-19 | 9256.8 | 9256.8 | - | - | - | - | - | - | - | - | - | - | - | -
11-09-19 | 12321 | 12321 | - | - | - | - | - | - | - | - | - | - | - | - | 11-09-19 | 10061 | 10061 | - | - | - | - | - | - | - | - | - | - | - | -
12-09-19 | 11432 | 11432 | - | - | - | - | - | - | - | - | - | - | - | - | 12-09-19 | 9386.9 | 9386.9 | - | - | - | - | - | - | - | - | - | - | - | -
13-09-19 | 10597 | 10597 | - | - | - | - | - | - | - | - | - | - | - | - | 13-09-19 | 7746.8 | 7746.8 | - | - | - | - | - | - | - | - | - | - | - | -
14-09-19 | 12038 | 12038 | - | - | - | - | - | - | - | - | - | - | - | - | 14-09-19 | 9210.3 | 9210.3 | - | - | - | - | - | - | - | - | - | - | - | -
15-09-19 | 12324 | 12324 | - | - | - | - | - | - | - | - | - | - | - | - | 15-09-19 | 9894.9 | 9894.9 | - | - | - | - | - | - | - | - | - | - | - | -
16-09-19 | 12119 | 12119 | - | - | - | - | - | - | - | - | - | - | - | - | 16-09-19 | 9837.9 | 9837.9 | - | - | - | - | - | - | - | - | - | - | - | -
17-09-19 | 12442 | 12442 | - | - | - | - | - | - | - | - | - | - | - | - | 17-09-19 | 9943.9 | 9943.9 | - | - | - | - | - | - | - | - | - | - | - | -
18-09-19 | 12329 | 12329 | - | - | - | - | - | - | - | - | - | - | - | - | 18-09-19 | 10140.3 | 10140.3 | - | - | - | - | - | - | - | - | - | - | - | -
19-09-19 | 12473 | 12473 | - | - | - | - | - | - | - | - | - | - | - | - | 19-09-19 | 10212.7 | 10212.7 | - | - | - | - | - | - | - | - | - | - | - | -
20-09-19 | 11717 | 11717 | - | - | - | - | - | - | - | - | - | - | - | - | 20-09-19 | 8836.2 | 8836.2 | - | - | - | - | - | - | - | - | - | - | - | -
21-09-19 | 11991 | 11991 | - | - | - | - | - | - | - | - | - | - | - | - | 21-09-19 | 9363 | 9363 | - | - | - | - | - | - | - | - | - | - | - | -
22-09-19 | 11378 | 11378 | - | - | - | - | - | - | - | - | - | - | - | - | 22-09-19 | 9866.3 | 9866.3 | - | - | - | - | - | - | - | - | - | - | - | -
23-09-19 | 11620 | 11620 | - | - | - | - | - | - | - | - | - | - | - | - | 23-09-19 | 9367.7 | 9367.7 | - | - | - | - | - | - | - | - | - | - | - | -
24-09-19 | 10641 | 10641 | - | - | - | - | - | - | - | - | - | - | - | - | 24-09-19 | 9059 | 9059 | - | - | - | - | - | - | - | - | - | - | - | -
25-09-19 | 10279 | 10279 | - | - | - | - | - | - | - | - | - | - | - | - | 25-09-19 | 8717.5 | 8717.5 | - | - | - | - | - | - | - | - | - | - | - | -
26-09-19 | 11219 | 11219 | - | - | - | - | - | - | - | - | - | - | - | - | 26-09-19 | 8904.7 | 8904.7 | - | - | - | - | - | - | - | - | - | - | - | -
27-09-19 | 10379 | 10379 | - | - | - | - | - | - | - | - | - | - | - | - | 27-09-19 | 7687.7 | 7687.7 | - | - | - | - | - | - | - | - | - | - | - | -
28-09-19 | 10687 | 10687 | - | - | - | - | - | - | - | - | - | - | - | - | 28-09-19 | 8004.6 | 8004.6 | - | - | - | - | - | - | - | - | - | - | - | -
29-09-20 | 9979 | 9979 | - | - | - | - | - | - | - | - | - | - | - | - | 29-09-20 | 8624.1 | 8624.1 | - | - | - | - | - | - | - | - | - | - | - | -
30-09-19 | 10426 | 10426 | - | - | - | - | - | - | - | - | - | - | - | - | 30-09-19 | 8470.7 | 8470.7 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:September' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12717 | 01/09/19 | 21:00
2 | Maximum day peak Genaration | MW | 10636.2 | 01/09/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 12717 | 01/09/19 | 21:00
4 | Minimum Generation | MW | 6957 | 27/09/19 | 8:00
5 | Average of the daily evening peak Genaration | MW | 11679.0667
6 | Average of the daily day peak Genaration | MW | 9378.1933
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 7441.014
12 | Total Generation by IPP | MKWH | 2065.5385 | % of total Gen. | 27.76%
13 | Total Generation by BPDB | MKWH | 3805.7195 | " | 51.15%
14 | A) Total Generation by RPCL | MKWH | 143.9645 | '' | 1.935%
| B) Total Generation by REB | MKWH | 154.8794 | " | 2.081%
| C) Total Generation by RENTAL | MKWH | 508.2955 | " | 6.831%
| D) Total Imported from India (HVDC) | MKWH | 655.5738 | " | 8.81%
| E) Total Imported from Tripura, India (A.C) | MKWH | 107.0429 | " | 1.439%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4756.9561 | % of total Gen. | 63.93%
| B) Oil | MKWH | 1533.9687 | '' | 20.62%
| C) Hydro | MKWH | 139.7935 | '' | 1.879%
| D) Solar | MKWH | 3.961 | '' | 0.05323%
| E) Coal | MKWH | 243.718 | '' | 3.275%
| F) HVDC (Import from India) | MKWH | 655.5738 | '' | 8.81%
| G) A.C (Import from Tripura, India) | MKWH | 107.0429 | '' | 1.439%
16 | Maximun of the daily total Generation . | MKWH | 285.4943 | 22/09/19
17 | Monthly Load factor | % | 81.4703
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 18927.6936
| A) Gas | M.Taka | 4374.3642
| B) Liquid fuel | M.Taka | 13498.1459
| C) Coal | M.Taka | 1055.1834
| D) HVDC (Import from India) | M.Taka | 3343.4264
| E) Tripura(Import from India) | M.Taka | 732.1733
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 859.9448 | 18/09/19
| A) Gas | M.Taka | 187.9229 | 22/09/19
| B) Liquid fuel | M.Taka | 684.1397 | 18/09/19
| C) Coal | M.Taka | 38.2842 | 27/09/19
| D) HVDC (Import from India) | M.Taka | 112.3372 | 22-09-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.1877
| B) Excluding Hydro & Solar | Taka/KWHR | 3.2504
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 105.76 | 30/09/19 | 06:00
b) | Actual | FT (MSL) | 104.53 | 30/09/19 | 06:00
22 | Peak Genaration of September 2018 | MW | 11623 | 19/09/18 | 19:30
23 | Peak Demand of September 2018 | MW | 11623 | 19/09/18 | 19:30
24 | Maximum peak Generation recorded upto 30/09/19 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 30/09/19 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 30/09/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.