## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:August' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | August 2019 |  | July 2019 |  | August 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12738 | 05/08/19 | 12436 | 21/07/19 | 11217 | 13/08/18 | 12893 | 29/05/19
|  |  | 19:30 |  | 21:00 |  | 22:00 |  | 21:00
2 | Minimum Generation (MW) | 6449 | 14/08/19 | 6202 | 14/07/19 | 5450.6 | 22/08/18 | - | -
|  |  | 8:00 |  | 6:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12738 | 05/08/19 | 12436 | 21/07/19 | 11174 | 13/08/18 | 12893 | 29/05/19
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10539.2 | 22/08/19 | 10285.4 | 22/07/19 | 9621.4 | 19/08/18 | 10539.2 | 22/08/19
|  |  | 21:00 |  | 12:00 |  | 12:00 |  | 21:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12738 | 05/08/19 | 12436 | 21/07/19 | 11174 | 13/08/18 | 12893 | 29/05/19
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11505.9032 |  | 11518.32 |  | 10324.52 |  | 11505.9 | 2019-08-19
7 | Average Generation (MW) at Day Peak | 8911.5948 |  | 9293.47 |  | 8305.85 |  | 8911.59 | 2019-08-19
8 | Maximum Power Import from India, HVDC (MW) | 934 | 18/08/19 | 936 | 26/07/19 | 494 | 10/08/18 | 956 | 27/3/2019
|  |  | 17:00 |  | 5:30 |  | 8:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 192 | 31/08/19 | 194 | 21/07/19 | 188 | 21/08/18 | 194 | 12/06/19
|  |  | 20:00 |  | 22:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3752.2923 |  | 3406.33 |  | 3413.62 |  | 3752.2923 | 2019-08-19
21 | Station Use of BPDB (MKWH) | 135.3315 |  | 125.09 |  | 109.14
22 | Net Generation of BPDB (MKWH) | 3616.9608 |  | 3281.24 |  | 3304.48
23 | Net Generation of IPP & RPCL (MKWH) | 2201.9123 |  | 2468.12 |  | 1876.55
24 | Net Generation of REB (MKWH) | 171.4948 |  | 143.68 |  | 142.89
24 | Net Generation of Rental Power Plant (MKWH) | 460.4374 |  | 572.35 |  | 731.21
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6450.8053 |  | 6465.39 |  | 6055.13 |  | 6465.39 | July-19
26 | Energy Generation by Gas (MKWH) | 4666.7708 |  | 4492.67 |  | 4226.29 |  | 4666.77 | August-19
27 | Energy Generation by Diesel (MKWH) | 256.5472 |  | 279.08 |  | 549.03 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1284.2266 |  | 1524.02 |  | 1252.68 |  | 1524.02.49 | July-19
29 | Energy Generation by Hydro (MKWH) | 151.3983 |  | 102.89 |  | 125.53 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 5.0388 |  | 3.18 |  | 0.32 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 223.0374 |  | 189.31 |  | 10.42 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 739.468 |  | 736.99 |  | 458.02 |  | 739.47 | August-19
33 | Monthly Load Factor (%) | 77.3075 |  | 79.2 |  | 79.35 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:August' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12738 | 05/08/19 | 19:30
Generation Period
| Dhaka | MW | 4487
| Chattogram | MW | 1148
| Cumilla | MW | 1085
| Mymensingh | MW | 947
| Sylhet | MW | 547
a) | Total supply in East zone | MW | 8214
| Khulna | MW | 1499
| Barisal | MW | 334
| Rajshahi | MW | 1315
| Rangpur | MW | 702
b) | Total supply in West zone | MW | 3850
c) | Total supply in both zone ( a+b) | MW | 12064
Ref: | 27.21.0000.603.16.086.18.188 | Date: 15/09/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 770 | 11/08/19 | 7:00
| b) Ishurdi end | MW | 275 | 7/08/19 | 9:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 600 | 7/08/19 | 9:00
| b) Ishurdi end | MW | 290 | 11/08/19 | 7:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.8138 | 11/08/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 3.3825 | 11/08/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 28.6282
| b) Ishurdi end | MKWH | 31.8487
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 30.8933
| b) Ishurdi end | MKWH | 27.4385
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 440 | 04/08/19 | 23:00
| b)Serajganj end | MW | 400 | 08/08/19 | 8:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 330 | 08/08/19 | 8:00
| b)Sirajganj end | MW | 420 | 04/08/19 | 23:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.84 | 11/08/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 4.692 | 11/08/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 50.058
| b)Sirajganj end | MKWH | 43.316
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 42.726
| b)Sirajganj end | MKWH | 49.666
30 | Transmission loss of EWI /NO-2 | % | 1.052
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-08-02 09:32 | 2019-08-02 11:07 | 1:35 | E/O | Due to red hot maintenance | 60 | 95 | Power interruption
Joydevpur | 132/33 kV Transformers-T3 & T4 | 2019-08-05 14:28 | 2019-08-05 14:35 | 0:07 | T | Tripped showing E/F relay at 33 kV side | 78 | 9.1 | Power interruption
Dhamrai | 132/33 kV Transformer-T1 | 2019-08-06 08:05 | 2019-08-06 12:19 | 4:14 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2019-08-06 08:16 | 2019-08-06 09:50 | 1:34 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-08-10 23:04 | 2019-08-10 23:36 | 0:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T2 | 2019-08-16 11:38 | 2019-08-16 11:48 | 0:10 | T | Tripped showing 33 kV feeder fault | 76 | 12.6667 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-08-16 14:37 | 2019-08-16 15:27 | 0:50 | T |  | 40 | 33.3333 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-08-17 06:14 | 2019-08-17 06:27 | 0:13 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2019-08-22 15:16 | 2019-08-22 15:44 | 0:28 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T4 | 2019-08-22 07:27 | 2019-08-22 08:18 | 0:51 | E/O | Due to red hot maintenance 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-08-22 17:32 | 2019-08-22 18:10 | 0:38 | E/O | Due to red hot maintenance 33 kV side | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2019-08-26 06:22 | 2019-08-26 07:12 | 0:50 | E/O | Due to red hot maintenance at 33 kV side | 40 | 33.3333 | Power interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2019-08-31 07:17 | 2019-08-31 08:53 | 1:36 | E/O | Due to red hot maintenance | 40 | 64 | Power interruption
Tongi(O) | 132/33 kV Transformers-T1 & T2 | 2019-08-31 09:44 | 2019-08-31 09:57 | 0:13 | T | Tripped showing O/C relay at 33 kV side | 70 | 15.1667 | Power interruption
Sonargaon | 132/33 kV Transformer-T1 | 2019-08-31 08:55 | 2019-08-31 12:20 | 3:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 17:16 |  | Unserved Energy: |  | 262.6
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-T01 | 2019-08-01 12:06 | 2019-08-01 13:15 | 1:09 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2019-08-06 09:17 | 2019-08-06 10:26 | 1:09 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T5 | 2019-08-12 08:35 | 2019-08-12 09:44 | 1:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2019-08-15 11:32 | 2019-08-15 11:51 | 0:19 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-GT2 | 2019-08-17 21:13 | 2019-08-17 21:57 | 0:44 | E/O | Due to red hot maintenance 33 kV side | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2019-08-17 14:30 | 2019-08-17 15:03 | 0:33 | T | Tripped showing inter trip relay | 22 | 12.1 | Power interruption
Rampura | 230/132 kV Transformer-T3 | 2019-08-20 19:36 | 2019-08-20 23:03 | 3:27 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 with 33 kV Bus | 2019-08-30 07:07 | 2019-08-30 10:20 | 3:13 | E/O | Due to red hot maintenance | 35 | 112.5833 | Power interruption
Rampura | 230/132 kV Transformer-T1 | 2019-08-30 06:04 | 2019-08-30 09:54 | 3:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2019-08-31 07:15 | 2019-08-31 08:32 | 1:17 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 16:50 |  | Unserved Energy: |  | 124.6833
Chattogram Grid Circle :
Sikalbaha | 230/132 kV Transformers-T1 & T2 | 2019-08-01 15:29 | 2019-08-01 15:57 | 0:28 | T | Tripped showing general trip | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-03 09:20 | 2019-08-03 12:15 | 2:55 | E/O | Due to red hot maintenance | 17 | 49.5833 | Power interruption
Hathazari | 230/132 kV Transformer-T3 | 2019-08-05 18:28 | 2019-08-05 22:06 | 3:38 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2019-08-19 15:58 | 2019-08-19 16:03 | 0:05 | T | Due to 33 kV feeder fault | 40 | 3.3333 | Power interruption
| 132/33 kV Transformer-T1 | 2019-08-25 09:10 | 2019-08-25 11:08 | 1:58 | E/O | Due to red hot maintenance at 33 kV side | 20 | 39.3333 | Power interruption
Khulshi | 132/33 kV Transformers-T1 & T2 | 2019-08-26 06:02 | 2019-08-26 07:12 | 1:10 | T | Tripped showing O/C relay | 20 | 23.3333 | Power interruption
| 132/33 kV Transformer-T1 | 2019-08-28 06:01 | 2019-08-28 08:58 | 2:57 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2019-08-30 06:11 | 2019-08-30 08:24 | 2:13 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-31 06:42 | 2019-08-31 08:20 | 1:38 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 17:02 |  | Unserved Energy: |  | 115.5833
Cumilla Grid Circle :
Cumilla(N) | 132/33 kV Transformer-T1 | 2019-08-02 16:05 | 2019-08-02 17:08 | 1:03 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Chowmuhani | 132 kV main Bus | 2019-08-03 10:50 | 2019-08-03 12:05 | 1:15 | E/O | Due to red hot maintenance at 132 kV side | 74 | 92.5 | Power interruption
Chatak | 132/33 kV Transformer-T2 | 2019-08-04 02:48 | 2019-08-04 05:17 | 2:29 | T | Tripped showing O/C relay (B-phase) relay | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformers-T3 & T4 | 2019-08-05 17:23 | 2019-08-05 18:47 | 1:24 | T | Tripped showing E/F relay at 33 kV side | 70 | 98 | Power interruption
| 132/33 kV Transformers-T3 & T4 | 2019-08-05 21:04 | 2019-08-05 21:41 | 0:37 | T | Tripped showing O/C relay | 100 | 61.6667 | Power interruption
Ramganj | 132/33 kV Transformer-T1 | 2019-08-11 10:12 | 2019-08-11 11:29 | 1:17 | E/O | Due to red hot maintenance at 33 kV side | 20 | 25.6667 | Power interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2019-08-11 21:25 | 2019-08-11 23:35 | 2:10 | T | Tripped showing PRDE/F relay at 132 kV side | 60 | 130 | Power interruption
Chandpur | 132/33 kV Transformer-T1 | 2019-08-12 06:42 | 2019-08-12 07:04 | 0:22 | E/O | Due to red hot maintenance at 132 kV side | 10 | 3.6667 | Power interruption
B.Baria | 33 kV Bus | 2019-08-13 20:44 | 2019-08-13 21:15 | 0:31 | E/O | Due to red hot maintenance at 132 kV side | 80 | 41.3333 | Power interruption
Ramganj | 132/33 kV Transformer-T2 | 2019-08-13 22:55 | 2019-08-13 23:50 | 0:55 | E/O | Due to red hot maintenance at 33 kV side | 26 | 23.8333 | Power interruption
Chandpur | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-08-19 00:44 | 2019-08-19 01:54 | 1:10 | E/O | Due to red hot maintenance at 33 kV side | 25 | 29.1667 | Power interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2019-08-20 06:05 | 2019-08-20 07:10 | 1:05 | E/O | Due to red hot maintenance at 33 kV side | 35 | 37.9167 | Power interruption
Sunamganj | 132/33 kV Transformer-T1 | 2019-08-23 10:27 | 2019-08-23 11:27 | 1:00 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T1 | 2019-08-23 21:05 | 2019-08-23 21:24 | 0:19 | T | Due to 33 kV feeder fault | 15 | 4.75 | Power interruption 21:05 to 21:24
| 132/33 kV Transformers-T2 | 2019-08-23 21:05 | 2019-08-23 21:10 | 0:05 | T
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ramganj | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-08-23 22:11 | 2019-08-23 23:01 | 0:50 | E/O | Due to red hot maintenance at 33 kV side | 35 | 29.1667 | Power interruption
Kulaura | 132/33 kV Transformer-T1 | 2019-08-27 18:44 | 2019-08-27 18:56 | 0:12 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformers-T4 & T6 | 2019-08-31 07:23 | 2019-08-31 10:14 | 2:51 | E/O | Due to red hot maintenance | 30 | 85.5 | Power interruption
|  |  | Total : | 19:35 |  | Unserved Energy: |  | 663.1667
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T2 | 2019-08-06 06:05 | 2019-08-06 06:11 | 0:06 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T-1 | 2019-08-06 07:51 | 2019-08-06 09:04 | 1:13 | E/O | Due to red hot maintenance | 12 | 14.6 | Power interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-08-07 12:20 | 2019-08-07 12:31 | 0:11 | T | Tripped showing E/F relay at 33 kV side | 8 | 1.4667 | Power interruption
| 132/33 kV Transformer-T2 | 2019-08-07 13:32 | 2019-08-07 16:44 | 3:12 | E/O | Due to CB pole Y-phase sparking | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 & 33 kV Bus section-2 | 2019-08-09 06:38 | 2019-08-09 09:15 | 2:37 | E/O | Due to red hot maintenance | 10 | 26.1667 | Power interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-08-10 13:22 | 2019-08-10 14:02 | 0:40 | E/O | Due to red hot maintenance | 30 | 20 | Power interruption
Khulna© | 132/33 kV Transformer-T1 | 2019-08-10 21:38 | 2019-08-10 21:47 | 0:09 | T | Tripped showing O/C & E/F relay | 36 | 5.4 | Power interruption
| 132/33 kV Transformer-T1 | 2019-08-10 21:38 | 2019-08-10 21:47 | 0:09 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Norail | 132/33 kV Transformer-T2 | 2019-08-11 12:01 | 2019-08-11 13:28 | 1:27 | E/O | Due to red hot maintenance ae 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-11 23:28 | 2019-08-11 23:50 | 0:22 | E/O | Due to red hot maintenance ae 33 kV side | 60 | 22 | Power interruption
Sariatpur | 132/33 kV Transformer-T2 | 2019-08-13 05:01 | 2019-08-13 06:35 | 1:34 | T | Tripped showing O/C at 33 kV side | 27 | 42.3 | Power interruption
Barisal(N) | 132/33 kV Transformer-T4 | 2019-08-13 10:27 | 2019-08-13 11:28 | 1:01 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformers-T1 & T2 & 33 kV Bus | 2019-08-17 09:36 | 2019-08-17 10:24 | 0:48 | E/O | Due to red hot maintenance | 20 | 16 | Power interruption
Khulna© | 132/33 kV Transformer-T2 | 2019-08-18 10:56 | 2019-08-18 11:25 | 0:29 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-08-25 16:36 | 2019-08-25 16:46 | 4:22 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2019-08-26 07:12 | 2019-08-26 08:07 | 0:55 | E/O | Tripped showing E/F relay at 33 kV side | 5 | 4.5833 | Power interruption
Bagerhat | 33 kV Bus-1 | 2019-08-27 16:08 | 2019-08-27 17:37 | 1:29 | E/O | Due to red hot maintenance | 30 | 44.5 | Power interruption
|  |  | Total : | 20:44 |  | Unserved Energy: |  | 197.0167
HVDC Grid Circle :
Jhenidah | 132 kV Bus-B | 2019-08-06 06:14 | 2019-08-06 07:19 | 1:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Jessore | 132 kV capacitor bank | 2019-08-15 06:00 | 2019-08-29 17:04 | 347:04 | E/O | Due to bursting of post insulator | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 with 33 kV Bus-1 | 2019-08-24 07:14 | 2019-08-24 09:01 | 1:47 | E/O | Due to red hot maintenance at 33 kV side | 33 | 58.85 | Power interruption
Bheramara | 230 kV main Bus-1 | 2019-08-28 09:34 | 2019-08-28 14:51 | 5:17 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 355:13 |  |  |  | 58.85
Bogura Grid Circle:
Barapukuria | 132/33 kV Transformer-T3 | 2019-08-03 09:50 | 2019-08-03 10:57 | 1:07 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2019-08-03 11:16 | 2019-08-04 03:40 | 16:24 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2019-08-03 20:35 | 2019-08-03 20:42 | 0:07 | T | Tripped showing O/C relay | 5 | 0.58333 | Power interruption
| 230/132 kV Transformer-T6 | 2019-08-03 20:35 | 2019-08-03 20:46 | 0:11 | T |  | 0 | 0 | No interruption
Rajshahi | 132/ kV Transformer-T1 | 2019-08-03 22:40 | 2019-08-04 00:15 | 1:35 | T | Tripped showing O/C relay at 33 kV side | 135 | 213.75 | Power interruption
| 132/ kV Transformer-T3 | 2019-08-03 22:40 | 2019-08-04 00:27 | 1:47 | T |  | 0 | 0 | No interruption
Natore | 33 kV Bus-1 | 2019-08-08 20:35 | 2019-08-08 21:13 | 0:38 | E/O | Due to red hot maintenance at 33 kV side | 55 | 34.8333 | Power interruption
Baghabari | 230/132 kV Transformer-T2 | 2019-08-09 20:47 | 2019-08-09 22:23 | 1:36 | T | Tripped showing O/C & E/F relay | 5 | 8 | Power interruption
Rangpur | 132/33 kV Transformers-T1 & T2 | 2019-08-12 11:45 | 2019-08-13 01:21 | 13:36 | T | Due to 33 kV feeder fault |  | 0
Rajshahi | 132/ kV Transformer-T2 | 2019-08-13 22:22 | 2019-08-13 23:17 | 0:55 | E/O | Due to red hot maintenance at 33 kV side | 14 | 12.8333 | Power interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2019-08-14 08:44 | 2019-08-14 09:17 | 0:33 | E/O | Due to Oil temperature high | 5 | 2.75 | Power interruption
Saidpur | 132/33 kV Transformer-T4 | 2019-08-14 10:56 | 2019-08-14 11:50 | 0:54 | E/O | Due to red hot maintenance at 33 kV side | 10 | 9 | Power interruption
Naogaon | 132/33 kV Transformer-T2 | 2019-08-14 21:41 | 2019-08-14 22:20 | 0:39 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-08-15 23:10 | 2019-08-16 00:05 | 0:55 | E/O | Due to red hot maintenance at 33 kV side | 32 | 29.3333 | Power interruption
Natore | 132/33 kV Transformer-T1 | 2019-08-16 10:18 | 2019-08-16 11:30 | 1:12 | E/O | Due to red hot maintenance |  | 0
C.nawabganj | 132/33 kV Transformer-T4 | 2019-08-16 12:53 | 2019-08-16 13:09 | 0:16 | T | Tripped showing Oil temperature high | 5 | 1.3333 | Power interruption
Bogura | 132/33 kV Transformer-T3 | 2019-08-16 11:12 | 2019-08-16 12:35 | 1:23 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Rajshahi | 33 kV Bus | 2019-08-18 21:22 | 2019-08-18 22:35 | 1:13 | E/O | Due to red hot maintenance at 33 kV side | 14 | 17.0333 | Power interruption
Naogaon | 132/33 kV Transformers-T1 & T2 & 33 kV Bus-1 & 2 | 2019-08-19 07:42 | 2019-08-19 09:28 | 1:46 | E/O | Due to red hot maintenance at 33 kV side | 45 | 79.5 | Power interruption
Barapukuria | 132/33 kV Transformer-T3 | 2019-08-19 16:17 | 2019-08-19 18:07 | 1:50 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2019-08-23 16:57 | 2019-08-23 17:05 | 0:08 | T | Tripped showing O/C relay | 6 | 0.8 | Power interruption
Naogaon | 132/ kV Transformer-T2 & 33 kV Bus | 2019-08-27 07:08 | 2019-08-27 08:50 | 1:42 | E/O | Due to red hot maintenance | 25 | 42.5 | Power interruption
| 132/33 kV Transformer-T2 | 2019-08-27 23:40 | 2019-08-28 00:48 | 1:08 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 51:35 |  | Unserved Energy: |  | 452.25
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 498:15 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2019-08-02 06:33 | 2019-08-02 08:33 | 2:04 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 | 2019-08-02 16:28 | 2019-08-02 18:18 | 1:50 | T | Tripped showing dist. (B-phase) relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2019-08-06 00:54 | 2019-08-06 01:16 | 0:22 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Sherpur | Sherpur-Jamapur United 132 kV line-1 & 2 | 2019-08-06 16:48 | 2019-08-06 17:46 | 0:58 | E/O | Due to bursting of PT | 54 | 52.2 | Power interruption
Tangail | Tangail-Myemsingh RPCL 132 kV line-1 | 2019-08-16 12:07 | 2019-08-16 12:14 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-1 | 2019-08-23 13:40 | 2019-08-23 14:11 | 0:31 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 5:52 |  | Unserved Energy: |  | 52.2
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-08-02 09:13 | 2019-08-02 11:40 | 2:27 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-2 | 2019-08-05 22:57 | 2019-08-05 23:19 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-2 | 2019-08-09 08:47 | 2019-08-09 11:52 | 3:05 | T | Tripped showing General trip & DTT signal | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV line-2 | 2019-08-12 04:05 | 2019-08-12 04:18 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur -APR Hasnabad 230 kV line | 2019-08-21 07:34 | 2019-08-21 12:09 | 4:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line-1 | 2019-08-23 06:25 | 2019-08-23 06:56 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line-2 | 2019-08-23 08:13 | 2019-08-23 08:30 | 0:17 | T | Tripped showing dist.R-phase relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2019-08-23 20:55 | 2019-08-24 00:20 | 3:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV line | 2019-08-26 06:04 | 2019-08-26 09:45 | 3:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2019-08-30 11:29 | 2019-08-30 11:51 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2019-08-31 10:30 | 2019-08-31 13:58 | 3:28 | E/O | Due to red hot maintenance | 30 | 104 | Power interruption
|  |  | Total : | 18:58 |  | Unserved Energy: |  | 104
Chittagong Grid Circle :
Madunaghat | Madunaghat-Khulshi 132 kV line-1 | 2019-08-03 06:46 | 2019-08-03 06:54 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 & 2 | 2019-08-05 15:12 | 2019-08-05 21:41 | 6:29 | T | Tripped showing dist. relay | 160 | 1037.3333 | Power interruption
| Dohazari-Cox'xbazar 132 kV line-1 | 2019-08-05 15:12 | 2019-08-05 15:45 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 132 kV line-1 & 2 | 2019-08-05 18:28 | 2019-08-05 18:58 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV line-2 | 2019-08-06 11:57 | 2019-08-06 12:49 | 0:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-1 & 2 | 2019-08-11 22:46 | 2019-08-11 22:57 | 0:11 | T | Tripped showing dist. relay | 25 | 4.5833 | Power interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2019-08-21 17:31 | 2019-08-21 18:04 | 0:33 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 & 2 | 2019-08-22 22:29 | 2019-08-22 22:38 | 0:09 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2019-08-25 14:29 | 2019-08-25 14:57 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line | 2019-08-28 09:52 | 2019-08-28 11:06 | 1:14 | T | Tripped showing dist.& E/F relay | 65 | 80.1667 | Power interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2019-08-31 11:33 | 2019-08-31 11:58 | 0:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 11:32 |  | Unserved Energy: |  | 1122.0833
Cumilla Grid Circle :
B.Baria | B.Baria-Ashuganj 132 kV line-1 | 2019-08-01 11:03 | 2019-08-01 12:06 | 1:03 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| B.Baria-Ashuganj 132 kV line-2 | 2019-08-01 12:39 | 2019-08-01 15:05 | 2:26 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-2 | 2019-08-04 10:51 | 2019-08-04 11:05 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-08-04 11:22 | 2019-08-04 11:48 | 0:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 132 kV line-1 | 2019-08-05 21:42 | 2019-08-05 22:04 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-2 | 2019-08-11 10:23 | 2019-08-11 16:43 | 6:20 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Cumilla(N)-Feni 132 kV line-1 | 2019-08-12 00:53 | 2019-08-12 01:16 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-1 | 2019-08-12 01:56 | 2019-08-12 02:05 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2019-08-12 01:56 | 2019-08-12 02:10 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 132 kV line-2 | 2019-08-20 13:56 | 2019-08-20 14:06 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2019-08-23 01:21 | 2019-08-23 01:25 | 0:04 | T | Tripped showing dist. (A-phase)relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV line-1 | 2019-08-27 05:48 | 2019-08-27 06:06 | 0:18 | T | Tripped showing dist. relay | 150 | 45 | Power interruption
| Cumilla(S)-Surjamoninagar 132 kV line-2 | 2019-08-27 05:48 | 2019-08-27 06:24 | 0:36 | T |  |  | 0
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2019-08-28 00:38 | 2019-08-29 22:26 | 45:48 | E/O | Due to CT burn at P/S | 0 | 0 | No interruption
|  |  | Total : | 58:33 |  | Unserved Energy: |  | 45
Khulna Grid Circle :
Patuakhali | Patuakhali-Payra 132 kV line | 2019-08-07 17:27 | 2019-08-07 19:10 | 1:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Patuakhali-Payra 132 kV line | 2019-08-07 19:13 | 2019-08-07 20:46 | 1:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-2 | 2019-08-10 10:08 | 2019-08-10 10:50 | 0:42 | T |  | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2019-08-13 11:20 | 2019-08-13 16:50 | 5:30 | E/O | Due to oil leakage at CT | 0 | 0 | No interruption
Bagerhat | Bagerhat-Rupsha P/P 132 kV line | 2019-08-17 03:53 | 2019-08-17 04:14 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line | 2019-08-17 05:11 | 2019-08-17 05:42 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2019-08-19 12:19 | 2019-08-19 12:33 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna | Khulna-Fenchuganj 132 kV line-2 | 2019-08-25 14:34 | 2019-08-25 15:25 | 0:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 13 kV line | 2019-08-30 05:55 | 2019-08-31 03:38 | 21:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Barishal 132 kV line-2 | 2019-08-30 11:04 | 2019-08-30 11:26 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 33:30 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenidah | Jhenidah-Magura 132 kV line | 2019-08-05 19:58 | 2019-08-05 20:08 | 0:10 | T | Tripped showing dist. relay | 65 | 10.8333 | Power interruption
Bheramara | Bheramara-Ishurdi 132 kV line-4 | 2019-08-16 14:15 | 2019-08-16 16:18 | 2:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kustia | Kustia-Bheramara 132 kV line-2 | 2019-08-23 15:31 | 2019-08-23 17:11 | 1:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 3:53 |  | Unserved Energy: |  | 10.8333
Bogura Grid Circle :
Saidpur | Saidpur-Purbasadipur 132 kV line | 2019-08-02 20:12 | 2019-08-02 20:15 | 0:03 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Mohastanghor 132 kV line-1 & 2 | 2019-08-03 20:34 | 2019-08-03 20:45 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bogura(O)-Mohastanghor 132 kV line-1 & 2 | 2019-08-03 20:34 | 2019-08-03 20:45 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2019-08-06 16:45 | 2019-08-06 16:55 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 & 2 | 2019-08-06 19:34 | 2019-08-06 19:41 | 0:07 | T | Tripped showing dist. relay | 260 | 30.3333 | Power interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2019-08-13 00:15 | 2019-08-13 00:21 | 0:06 | T | Tripped showing dist. relay | 65 | 6.5 | Power interruption
Rajshahi | Rajshahi-Natore 132 kV line | 2019-08-10 22:37 | 2019-08-11 10:28 | 11:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Rajshahi-C.nawabganj 132 kV line | 2019-08-15 02:07 | 2019-08-15 04:01 | 1:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rajshahi-Amnura 132 kV line | 2019-08-15 02:07 | 2019-08-15 02:23 | 0:16 | T | Tripped showing dist.& E/F relay | 28 | 7.4667 | Power interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2019-08-15 02:07 | 2019-08-15 02:26 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV line-1 | 2019-08-16 20:19 | 2019-08-17 12:56 | 16:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2019-08-16 16:32 | 2019-08-16 16:48 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2019-08-16 16:32 | 2019-08-16 16:51 | 0:19 | T | Tripped showing Dir.& E/F relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-2 | 2019-08-22 16:02 | 2019-08-22 16:50 | 0:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 33:08 |  | Unserved Energy: |  | 44.3
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Unserved Energy:
Total outage period of Sub-station Equipment : |  |  |  | 165:26 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | 132/33 kV Transformer-T2 | 2019-08-02 05:04 | 2019-08-02 06:25 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformers-T1 & T2 | 2019-08-02 08:45 | 2019-08-02 12:14 | 3:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-08-05 14:25 | 2019-08-05 16:54 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-08-05 16:52 | 2019-08-05 21:10 | 4:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132 kV main Bus | 2019-08-07 06:18 | 2019-08-07 07:33 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2019-08-07 09:20 | 2019-08-07 15:50 | 6:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230 kV main Bus-1 | 2019-08-09 06:38 | 2019-08-09 11:17 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-08-09 07:18 | 2019-08-09 09:45 | 2:27 | S/O | Due to C/M work | 30 | 73.5 | Power interruption
Tangail | 33 kV Bus-1,2 & 3 | 2019-08-09 06:38 | 2019-08-09 08:25 | 1:47 | S/O | Due to C/M work by PDB | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 | 2019-08-10 09:40 | 2019-08-10 13:41 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132 kV main Bus | 2019-08-16 06:13 | 2019-08-16 07:43 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2019-08-22 06:26 | 2019-08-22 07:54 | 1:28 | S/O | Due to winding temperature high at 33 kV side | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-08-28 06:30 | 2019-08-28 16:27 | 9:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2019-08-28 10:28 | 2019-08-28 12:52 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2019-08-28 11:58 | 2019-08-28 15:15 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-08-28 15:50 | 2019-08-28 19:15 | 3:25 | S/O | Due to projection work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1 & T2 | 2019-08-31 11:25 | 2019-08-31 12:20 | 0:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 55:12 |  | Unserved Energy: |  | 73.5
Dhaka (South) Grid Circle :
Narsinghdi | 132 kV main Bus-1 | 2019-08-05 09:10 | 2019-08-05 13:20 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T1 | 2019-08-06 10:01 | 2019-08-06 12:19 | 2:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T5 | 2019-08-11 23:58 | 2019-08-12 05:34 | 5:36 | S/O | Due to replacement work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T3 | 2019-08-23 06:35 | 2019-08-23 06:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2019-08-25 07:19 | 2019-08-25 08:09 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T3 |  | 2019-08-25 17:37 | 0:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | 132 kV main Bus-1 | 2019-08-27 07:02 | 2019-08-27 17:20 | 10:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2019-08-27 10:54 | 2019-08-27 14:15 | 3:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T2 | 2019-08-29 09:07 | 2019-08-29 11:32 | 2:25 | S/O | Due to spark at isolator of B-phase. | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2019-08-31 17:07 | 2019-08-31 17:42 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 30:28 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baraulia | 132/33 kV Transformer-T1 | 2019-08-02 06:08 | 2019-08-02 10:04 | 3:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2019-08-07 21:10 | 2019-08-07 23:10 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-08-07 23:15 | 2019-08-07 23:55 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
T.K. chemical | 132 kv main Bus | 2019-08-09 07:30 | 2019-08-09 10:47 | 3:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2019-08-16 12:05 | 2019-08-16 16:16 | 4:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T2 | 2019-08-30 06:57 | 2019-08-30 09:39 | 2:42 | S/O | Due to C/M work | 30 | 81 | Power interruption
|  |  | Total : | 16:46 |  | Unserved Energy : |  | 81
Cumilla Grid Circle :
Daudkandi | 132/33 kV Transformer-T3 | 2019-08-01 14:44 | 2019-08-01 16:36 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2019-08-04 07:44 | 2019-08-04 08:43 | 0:59 | S/O | Due to C/M work | 22 | 21.6333 | Power interruption
Kulaura | 132/33 kV Transformer-T1 | 2019-08-20 10:59 | 2019-08-20 17:41 | 6:42 | S/O | Due to 33 kV feeder maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-22 09:00 | 2019-08-22 15:25 | 6:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T1 | 2019-08-22 12:25 | 2019-08-22 13:50 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2019-08-22 21:55 | 2019-08-22 23:05 | 1:10 | S/O | Due to CT problem | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-08-23 07:40 | 2019-08-23 10:40 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2019-08-23 07:31 | 2019-08-23 09:35 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 23:37 |  | Unserved Energy : |  | 21.6333
Khulna Grid Circle :
Barisal(O) | 132/33 kV Transformer-T1 | 2019-08-03 06:45 | 2019-08-03 07:39 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-08-03 08:31 | 2019-08-03 09:33 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-08-03 11:15 | 2019-08-03 15:11 | 3:56 | S/O | Due to replacement work | 0 | 0 | No interruption
Sariatpur | 33 kV Bus | 2019-08-04 08:17 | 2019-08-04 13:09 | 4:52 | S/O | Due to D/W work | 20 | 97.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-08-05 08:04 | 2019-08-05 10:46 | 2:42 | S/O | Due to C/M work | 20 | 54 | Power interruption
Gopalganj | 132/33 kV Transformer-T2 | 2019-08-06 09:14 | 2019-08-06 10:29 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T2 | 2019-08-07 08:02 | 2019-08-07 11:41 | 3:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-08-08 09:50 | 2019-08-08 12:36 | 2:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-08 12:36 | 2019-08-08 12:46 | 0:10 | S/O |  | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-08-09 07:10 | 2019-08-09 09:32 | 2:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2019-08-14 08:26 | 2019-08-14 10:15 | 1:49 | S/O | Due to changing work | 5 | 9.0833 | Power interruption
Barisal(N) | 132/33 kV Transformer-T5 | 2019-08-19 11:37 | 2019-08-19 13:01 | 1:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-08-19 13:10 | 2019-08-19 13:57 | 0:47 | S/O | Due to changing work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-08-23 09:35 | 2019-08-23 13:02 | 3:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Norail | 33 kV Bus of Transformers T1 & T2 | 2019-08-24 08:38 | 2019-08-24 12:31 | 3:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2019-08-24 14:23 | 2019-08-24 17:05 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Norail | 132/33 kV Transformer-T2 | 2019-08-25 15:41 | 2019-08-25 16:40 | 0:59 | S/O | Due to winding temperature high | 0 | 0 | No interruption
Faridpur | 132 kV Bus-A | 2019-08-25 16:21 | 2019-08-25 16:40 | 0:19 | S/O | Due to reconducting work | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T2 | 2019-08-26 09:15 | 2019-08-26 16:00 | 6:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-27 11:04 | 2019-08-27 11:52 | 0:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformer-T1 | 2019-08-27 11:20 | 2019-08-27 11:42 | 0:22 | S/O | Due to Oil sampling | 20 | 7.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-08-27 11:45 | 2019-08-27 11:56 | 0:11 | S/O |  | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T2 | 2019-08-28 13:07 | 2019-08-28 16:50 | 3:43 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-28 16:51 | 2019-08-28 17:49 | 0:58 | S/O | Due to testing fire fighting system | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-30 09:21 | 2019-08-30 18:06 | 8:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-08-30 08:27 | 2019-08-30 11:05 | 2:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-08-31 09:03 | 2019-08-31 11:37 | 2:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T2 | 2019-08-31 08:24 | 2019-08-31 11:05 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2019-08-31 07:33 | 2019-08-31 14:08 | 6:35 | S/O | Due to D/W work | 65 | 427.9167 | Power interruption
|  |  | Total : | 74:58 |  | Unserved Energy : |  | 595.6667
HVDC Grid Circle :
Bheramara | 132 kV Bus-A | 2019-08-05 07:48 | 2019-08-05 16:56 | 0:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-A | 2019-08-06 07:56 | 2019-08-06 16:13 | 8:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Kustia | 132 kV Bus-A | 2019-08-08 07:52 | 2019-08-08 17:25 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2019-08-10 06:33 | 2019-08-10 11:58 | 5:25 | S/O | Due to D/W work | 30 | 162.5 | Power interruption
Jessore | 132/33 kV Transformer-T3 | 2019-08-18 16:36 | 2019-08-18 17:09 | 0:33 | S/O | Due to 33 kV feeder maintenance | 24 | 13.2 | Power interruption
|  |  | Total : | 24:32 |  | Unserved Energy : |  | 175.7
Bogura Grid Circle:
Bogura new | 132 kV bus | 2019-08-03 05:39 | 2019-08-03 06:23 | 0:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main Bus | 2019-08-05 05:46 | 2019-08-05 06:55 | 1:09 | S/O | Due to C/M work | 250 | 287.5 | Power interruption
Bogura | 132/33 kV Transformer-T2 | 2019-08-06 06:08 | 2019-08-06 06:08 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Norail | 132/33 kV Transformer-T2 |  | 2019-08-06 17:32 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T2 | 2019-08-07 07:09 | 2019-08-07 07:09 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2019-08-07 15:21 | 2019-08-07 16:44 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Mahastanghor | 132/ kV Transformer-T1 |  | 2019-08-08 14:39 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Baghabari | 230/33 kV Transformer T1 |  | 2019-08-10 15:35 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Natore | 132/ kV Transformer-T1 | 2019-08-10 21:12 | 2019-08-10 22:14 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 & 33 Bus | 2019-08-16 11:45 | 2019-08-16 12:50 | 1:05 | S/O | Due to replacement work | 20 | 21.6667 | Power interruption
C.nawabganj | 132/33 kV Transformer-T4 |  | 2019-08-17 12:35 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Amnura | 132/ kV Transformer-T1 | 2019-08-19 08:21 | 2019-08-19 10:30 | 2:09 | S/O | Due to replacement work at 33 kV side | 0 | 0 | No interruption
Naogaon | 132/ kV Transformer-T2 | 2019-08-25 00:25 | 2019-08-25 01:04 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132 kV Bus | 2019-08-31 06:14 | 2019-08-31 09:12 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/ kV Transformer-T1 | 2019-08-31 09:47 | 2019-08-31 11:25 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 12:47 |  | Unserved Energy : |  | 309.1667
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 238:20 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: August 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line-2 & main Bus | 2019-08-01 06:20 | 2019-08-01 07:44 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2019-08-02 16:31 | 2019-08-02 17:44 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 & main Bus | 2019-08-04 06:21 | 2019-08-04 07:36 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 kV line-1 | 2019-08-05 15:34 | 2019-08-05 17:39 | 2:05 | S/O | Due to descending at mat from tower | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2019-08-06 11:46 | 2019-08-06 14:54 | 3:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-08-06 08:10 | 2019-08-06 13:30 | 5:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2019-08-07 06:07 | 2019-08-07 11:20 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2019-08-08 08:25 | 2019-08-08 13:55 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2019-08-08 08:25 | 2019-08-08 11:08 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-1 | 2019-08-16 06:03 | 2019-08-16 07:52 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2019-08-17 12:45 | 2019-08-17 15:43 | 2:58 | S/O | Due to replacement work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-08-24 05:52 | 2019-08-24 14:55 | 9:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2019-08-24 12:16 | 2019-08-24 14:05 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2019-08-30 09:55 | 2019-08-30 12:27 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 46:02 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Shyampur | Shyampur-Meghnaghat 230 kV line-2 | 2019-08-01 15:27 | 2019-08-01 17:08 | 1:41 | S/O | Due to abnormal sound of B-phase L/A | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2019-08-02 06:01 | 2019-08-02 21:43 | 15:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur GIS 230 kV line-2 | 2019-08-05 09:35 | 2019-08-05 16:02 | 6:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-2 | 2019-08-06 07:02 | 2019-08-06 08:52 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line-1 | 2019-08-08 10:49 | 2019-08-08 12:26 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 |  | 2019-08-08 17:48 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2019-08-09 07:43 | 2019-08-09 15:13 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur GIS 230 kV line-2 | 2019-08-09 09:18 | 2019-08-09 22:27 | 13:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2019-08-10 08:35 | 2019-08-10 10:18 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2019-08-10 08:35 | 2019-08-10 10:52 | 3:17 | S/O |  | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hathazari 132 kV line-2 | 2019-08-16 09:17 | 2019-08-16 12:03 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur(N) 132 kV line-1 | 2019-08-16 08:42 | 2019-08-16 09:40 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| Shyampur(O)-Shyampur(N) 132 kV line-2 | 2019-08-16 09:45 | 2019-08-16 12:49 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj S/S-Siddhirganj 230 MW P/S 132 kV line | 2019-08-27 08:30 | 2019-08-27 17:29 | 8:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2019-08-29 08:25 | 2019-08-29 15:30 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV (cable line-2 | 2019-08-29 11:40 | 2019-08-29 15:41 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2019-08-30 10:25 | 2019-08-30 11:20 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2019-08-30 09:53 | 2019-08-30 14:31 | 4:38 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 82:30 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Raozan 230 kV line-1 | 2019-08-08 09:54 | 2019-08-09 15:41 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2019-08-10 09:35 | 2019-08-10 11:05 | 1:13 | S/O | Due to winding temperature high | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2019-08-10 12:28 | 2019-08-10 16:42 | 4:14 | S/O | Due to joning OPGW | 0 | 0 | No interruption
|  |  | Total : | 7:44 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj -Sirajganj 230 kV line-1 | 2019-08-03 10:16 | 2019-08-03 18:44 | 8:28 | S/O | Due to new TF transportation. | 0 | 0 | No interruption
| Ashuganj -Sirajganj 230 kV line-1 | 2019-08-05 06:04 | 2019-08-05 06:45 | 0:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV line-2 | 2019-08-20 09:21 | 2019-08-20 11:47 | 2:26 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 230 kV line-2 | 2019-08-20 09:23 | 2019-08-20 10:31 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2019-08-20 16:45 | 2019-08-21 08:01 | 15:16 | S/O | Due to replacement work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-2 | 2019-08-25 16:01 | 2019-08-25 21:15 | 5:14 | S/O | Due tobus protection relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV line-2 | 2019-08-26 08:34 | 2019-08-26 21:49 | 13:15 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-08-27 05:56 | 2019-08-28 18:36 | 36:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2019-08-29 06:35 | 2019-08-29 16:46 | 10:11 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2019-08-30 06:30 | 2019-08-30 16:27 | 9:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Srimongal 132 kV line-1 & 2 | 2019-08-30 08:18 | 2019-08-30 10:24 | 2:06 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 105:22 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal(N) | Barisal(N)-Madaripur 132 kV line-1 | 2019-08-02 08:28 | 2019-08-02 17:38 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV line-1 | 2019-08-03 06:16 | 2019-08-03 09:59 | 3:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barishal-Bhola-Borhanuddin 230 kV line-1 | 2019-08-03 10:50 | 2019-08-03 15:33 | 4:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: August 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Sariatpur 132 kV line-1 |  | 2019-08-07 17:58 |  | S/O | Due to new connecton | 0 | 0 | No interruption
| Madaripur-Sariatpur 132 kV line-2 | 2019-08-08 10:30 | 2019-08-08 12:58 | 2:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Madaripur 132 kV line-1 |  | 2019-08-08 17:24 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-08-09 09:03 | 2019-08-09 10:40 | 1:37 | S/O | Due to C/M work | 24 | 38.8 | Power interruption
Khulna(S) | Khulna(S)-Khulna© 132 kV line-2 | 2019-08-09 10:08 | 2019-08-09 13:55 | 3:47 | S/O | Due to changing of ratio | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-1 | 2019-08-11 07:22 | 2019-08-11 13:26 | 6:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barishal-Bhola 230 kV line-1 | 2019-08-16 07:18 | 2019-08-16 09:14 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2019-08-18 08:31 | 2019-09-04 08:31 |  | S/O | Due to D/W work | 0 | 0 | No interruption
| Faridpur-Madaripur 132 kV line-2 | 2019-08-23 06:31 | 2019-08-23 09:24 | 2:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Faridpur S/S-Faridpur P/S 132 kV line | 2019-08-23 09:40 | 2019-08-23 12:45 | 3:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madaripur 132 kV line | 2019-08-23 07:01 | 2019-08-23 13:47 | 6:46 | S/O | Due to C/M work | 65 | 439.8333 | Power interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2019-08-24 14:29 | 2019-08-24 17:03 | 2:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| Faridpur-Bheramara 132 kV line-2 | 2019-08-25 07:11 | 2019-08-25 09:33 | 2:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV line | 2019-08-26 10:37 | 2019-08-26 21:02 | 10:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-Faridpur P/S 132 kV line | 2019-08-30 08:28 | 2019-08-30 10:28 | 2:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2019-08-31 06:32 | 2019-08-31 08:53 | 2:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| Faridpur-Bheramara 132 kV line-1 | 2019-08-31 09:10 | 2019-08-31 11:36 | 2:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV line | 2019-08-31 08:37 | 2019-08-31 15:25 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2019-08-31 11:44 | 2019-08-31 14:46 | 3:02 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 78:10 |  | Unserved Energy: |  | 478.6333
HVDC Grid Circle :
Bheramara | Bheramara-Bottail 132 kV line-1 | 2019-08-02 08:16 | 2019-08-02 17:27 | 9:11 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Bheramara(G.K) 132 kV line | 2019-08-03 06:47 | 2019-08-03 08:57 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara Kustia 132 kV line-2 | 2019-08-04 09:24 | 2019-08-04 18:45 | 9:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Bottail | Bottail-Bheramara 132 kV line-2 | 2019-08-05 07:33 | 2019-08-05 17:19 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Bottai 132 kV line-1 | 2019-08-06 06:36 | 2019-08-06 16:22 | 9:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-1 |  | 2019-08-07 15:43 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara Kustia 132 kV line-2 | 2019-08-08 07:27 | 2019-08-08 18:03 | 10:36 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara Kustia 132 kV line-2 | 2019-08-09 07:10 | 2019-08-09 17:14 | 10:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2019-08-26 14:25 | 2019-08-26 16:02 | 1:37 | S/O | Due to Rail work | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 |  | 2019-08-26 16:05 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ishurdi-Bheramara HVDC 230 kV line-2 | 2019-08-28 06:25 | 2019-08-28 08:54 | 2:29 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 65:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2019-08-02 06:02 | 2019-08-02 19:58 | 13:56 | S/O | Due to C/M work | 60 | 836 | Power interruption
| Saidpur-Barapukuria 132 kV line-2 | 2019-08-06 12:17 | 2019-08-06 15:39 | 3:22 | S/O | Due to C/M work | 65 | 218.8333 | Power interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2019-08-06 16:20 | 2019-08-06 17:33 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Rangpur 132 kV line-2 | 2019-08-07 10:55 | 2019-08-07 13:08 | 2:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 230 kV line-1 | 2019-08-09 08:02 | 2019-08-09 12:06 | 4:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 132 kV line-1 & 2 |  | 2019-08-18 23:30 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line | 2019-08-19 10:15 | 2019-08-19 17:09 | 6:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 132 kV line-1 | 2019-08-20 08:01 | 2019-08-20 08:22 | 0:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line | 2019-08-22 09:16 | 2019-08-22 16:31 | 7:15 | S/O | Due to relay changing | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line-2 | 2019-08-23 06:01 | 2019-08-23 12:35 | 6:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Lalmonirhat 132 kV line | 2019-08-24 06:10 | 2019-08-24 10:30 | 4:20 | S/O | Due to D/W work | 80 | 346.6667 | Power interruption
Bogura | Bogura-Bogura confidence 132 kV line | 2019-08-29 12:17 | 2019-08-29 15:01 | 2:44 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 52:56 |  | Unserved Energy: |  | 1401.5
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-2 | 2019-08-17 09:39 | 2019-08-17 16:30 | 6:51 | S/O | Due to DPDC work | 0 | 0 | No interruption
|  |  | Total : | 6:51 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 444:35 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August' 2019
| Area | Previous Month (July 2019) |  |  |  | Current Month (August 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 13 | 7 | 41 | 61 | 10 | 12 | 31 | 53
2 | Dhaka (South) Grid Circle. | 12 | 3 | 26 | 41 | 8 | 12 | 28 | 48
3 | Chattogram Grid Circle. | 29 | 12 | 36 | 77 | 14 | 7 | 9 | 30
4 | Cumilla Grid Circle. | 20 | 3 | 18 | 41 | 18 | 13 | 19 | 50
5 | Khulna Grid Circle. | 18 | 10 | 28 | 56 | 14 | 11 | 51 | 76
6 | Bheramara HVDC Grid Circle | 7 | 7 | 18 | 32 | 2 | 5 | 16 | 23
7 | Bogura Grid Circle. | 13 | 12 | 42 | 67 | 21 | 16 | 27 | 64
8 | Others | bar: Total number of T; Total number of Total; Total number of S/O to Total number of Total
9 | Total | 113 | 54 | 209 | 376 | 87 | 76 | 182 | 345
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August' 2019
| Area | Previous Month (July 2019) |  |  |  | Current Month (August 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 246.7 | 1021.66 | 622.72 | 1891.08 | 70.27 | 244.53 | 73.5 | 388.3
2 | Dhaka (South) Grid Circle. | 66.4 | 75.33 | 108 | 249.73 | 12.1 | 216.58 |  | 228.68
3 | Chattogram Grid Circle. | 394.35 | 145 | 6 | 545.35 | 1145.41 | 92.25 | 81 | 1318.66
4 | Cumilla Grid Circle. | 139.1 | 62 | 239.58 | 440.68 | 209.42 | 498.75 | 21.63 | 729.8
5 | Khulna Grid Circle. | 809.38 | 225.58 | 303.42 | 1338.38 | 48.87 | 147.85 | 1074.3 | 1271.02
6 | Bheramara HVDC Grid Circle | 36.66 | 61.58 | 25.08 | 123.32 | 10.83 | 58.85 | 175.7 | 245.38
7 | Bogura Grid Circle. | 74.12 | 266.22 | 698.07 | 1038.41 | 268.77 | 227.78 | 1710.67 | 2207.22
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 1766.71 | 1857.37 | 2002.87 | 5626.95 | 1765.67 | 1486.59 | 3136.8 | 6389.06
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 6 | 1 | 7 | 3 | 1 | 3 | 232.1
2 | Dhaka (South) | 5031.6 | 3 |  | 3 |  | 1 | 2 | 228.68
3 | Chattogram | 2042 | 4 | 1 | 5 | 1 |  | 4 | 196.58
4 | Khulna | 2434 | 10 | 5 | 15 | 4 | 2 | 8 | 792.69
5 | Bheramara (HVDC) | 2423.3 | 1 | 2 | 3 |  | 1 | 2 | 234.55
6 | Bogura | 3145.6 | 12 | 2 | 14 | 3 | 4 | 7 | 761.4167
7 | Cumilla | 2981 | 13 | 1 | 14 | 2 | 3 | 8 | 677.84
| Total | 23365.5 | [6 empty] | 3123.8567
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.89%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99% | [6 empty] | Executive Engineer
6 | Bogura | 99.71% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 | - | 2 | 1 |  | 1 | 156.2
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | -
3 | Chattogram | 917 | 20+9(Partial) | 3 | - | 3 | 1 | - | 2 | 1122.08
4 | Khulna | 1238.4 | 21 |  | 2 | 2 | - | - | 2 | 478.63
5 | Bheramara (HVDC) | 598.7 |  | 1 | - | 1 | 1 | - | - | 10.83
6 | Bogura | 1803.3 | 38 | 3 | 3 | 6 | 2 |  | 4 | 1445.8
7 | Cumilla | 1648.16 | 17 | 1 |  | 1 | 1 |  | - | 45
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 3258.54
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.94%
4 | Khulna | 99.83%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogura | 99.94% | [7 empty] | Information Management Division
7 | Cumilla | 99.82% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-08-18 | 9 |  | 6 | 6hr52min | 2 | 4hr26min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:August' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 1:35 | 60 | 95 | Due to red-hot maintenance of 132/33 kV Transformer T2
Jodevpur | 1 | 0:07 | 78 | 9.1 | Due to tripping of 132/33 kV Transformers T3,& T4
Jamalpur | 1 | 0:10 | 76 | 12.6667 | Due to tripping of 132/33 kV Transformers T1,& T2
| 1 | 0:50 | 40 | 33.3333
Mymensingh | 1 | 0:50 | 40 | 33.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Kaliakoir | 1 | 1:36 | 40 | 64 | Due to red-hot maintenance of 400/132 kV Transformer T1
Tongi(O) | 1 | 0:13 | 70 | 15.1667 | Due to tripping of 132/33 kV Transformers T1 & T2
Sherpur | 1 | 0:58 | 54 | 52.2 | Due to tripping of Sherpur-Jamalpur 132 kV line-1 & 2
Jamalpur |  | 2:27 | 30 | 73.5 | Due to S/D of 132/33 kV Transformer T3
Bhulta | 1 | 3:28 | 30 | 104 | Due to red-hot maintenance of Bhulta-Haripur 132 kV line
Narsingdi | 1 | 0:33 | 22 | 12.1 | Due to tripping of 132/33 kV Transformer T2
Sonargaon | 1 | 3:13 | 35 | 112.5833 | Due to red-hot maintenance of 132/33 kV Transformer T2
Sikalbaha | 1 | 2:55 | 17 | 49.5833 | Due to red-hot maintenance of 132/33 kV Transformer T1
Chandpur | 1 | 1:10 | 25 | 29.1667
Madunaghat | 2 | 0:05 | 40 | 3.3333 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 1:58 | 20 | 39.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Khulshi | 1 | 1:10 | 20 | 23.3333 | Due to tripping of 132/33 kV Transformers T1 & T2
Dohazari | 1 | 6:29 | 160 | 1037.3333 | Due to tripping of Dohazari-Sikalbaha 132 kV line-1 & 2
Chandraghona | 1 | 0:11 | 25 | 4.5833 | Due to tripping of Chandraghona-Rangamati 132 kV line-1 & 2
Dohazari | 1 | 1:14 | 65 | 80.1667 | Due to tripping of Dohazari-Cox'sbazar 132 kV line
Khulshi | 1 | 2:42 | 30 | 81 | Due to S/D of 132/33 kV Transformer T2
Chowmuhani |  | 1:15 | 74 | 92.5 | Due to red-hot maintenance of 132 kV main bus
Cumilla(S) | 2 | 1:24 | 70 | 98 | Due to tripping of 132/33 kV Transformers T3 & T4
|  | 0:37 | 100 | 61.6667
Ramganj | 1 | 1:17 | 20 | 25.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Chowmuhani | 1 | 2:10 | 60 | 130 | Due to tripping of 132/33 kV Transformer T1
Chandpur | 1 | 0:22 | 10 | 3.6667
B.Baria | 1 | 0:31 | 80 | 41.3333 | Due to red-hot maintenance of 33 kV Bus
Ramganj | 1 | 0:55 | 26 | 23.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Chowmuhani | 1 | 1:05 | 35 | 37.9167 | Due to red-hot maintenance of 132/33 kV Transformer T3
Sreemongal | 1 | 0:19 | 15 | 4.75 | Due to tripping of 132/33 kV Transformers T2
Ramganj | 1 | 0:50 | 35 | 29.1667 | Due to red-hot maintenance of 132/33 kV Transformer T1 & 33 kV Bus
Shahjibazar | 1 | 2:51 | 30 | 85.5 | Due to red-hot maintenance of 132/33 kV Transformer T4 & T6
Cumilla(S) | 1 | 0:18 | 150 | 45 | Due to tripping of Cumilla(S)-Surjamoninagar 132 kV line-1 & 2
Sylhet | 1 | 0:59 | 22 | 21.63 | Due to S/D of 132/33 kV Transformer T2
Gopalganj | 1 | 1:13 | 12 | 14.6 | Due to red-hot maintenance of 132/33 kV Transformer T1
Madaripur | 1 | 0:11 | 8 | 1.4667 | Due to tripping of 132/33 kV Transformer T3
Bagerhat |  | 2:37 | 10 | 26.1667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Faridpur | 1 | 0:40 | 30 | 20
Khulna© | 1 | 0:09 | 36 | 5.4 | Due to tripping of 132/33 kV Transformer T2
Norail | 1 | 0:22 | 60 | 22 | Due to red-hot maintenance of 132/33 kV Transformer T1
Sariatpur | 1 | 1:34 | 27 | 42.3 | Due to tripping of 132/33 kV Transformer T2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:August' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Patuakhali | 1 | 0:48 | 20 | 16 | Due to red-hot maintenance of 132/33 kV Transformer T1 & T2
Bottail | 1 | 1:47 | 33 | 58.85 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Khulna© | 1 | 0:55 | 5 | 4.5833 | Due to tripping of 132/33 kV Transformer T1
Bagerhat | 1 | 1:29 | 30 | 44.5 | Due to red-hot maintenance of 33 kV bus-1
Sariatpur | 2 | 4:52 | 20 | 97.3333 | Due to S/D of 33 kV Bus
|  | 2:42 | 20 | 54 | Due to S/D of 132/33 kV Transformer T2
Satkhira |  | 1:49 | 5 | 9.0833 | Due to S/D of 132/33 kV Transformer T1
Barisal(N) | 2 | 0:22 | 20 | 7.3333
|  | 6:35 | 65 | 427.9167 | Due to S/D of 132/33 kV Transformer T2
Bagerhat | 1 | 1:37 | 24 | 38.8 | Due to S/D of Bagerhat-Mongla 132 kV line
Goplaganj |  | 6:46 | 65 | 439.8333 | Due to S/D of Gapalganj-Madaripur 132 kV line
Jhenidah |  | 0:10 | 65 | 10.8333 | Due to tripping of Jhenidah-Magura 132 kV line
| 2 | 5:25 | 30 | 162.5 | Due to S/D of 132/33 kV Transformer T1
Jessore | 1 | 0:33 | 24 | 13.2 | Due to S/D of 132/33 kV Transformer T3
Barapukuria | 1 | 0:07 | 5 | 0.58333 | Due to tripping of 230/132 kV Transformer T2
Rajshahi | 1 | 1:35 | 135 | 213.75 | Due to tripping of 132/33 kV Transformer T1
Natore | 1 | 0:38 | 55 | 34.8333 | Due to red-hot maintenance of 33 kV Bus-1
Baghabari | 1 | 1:36 | 5 | 8 | Due to tripping of 230/132 kV Transformer T2
Rajshahi | 1 | 0:55 | 14 | 12.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
C.nawabganj | 1 | 0:33 | 5 | 2.75 | Due to tripping of 230/132 kV Transformer T4
Saidpur | 1 | 0:54 | 10 | 9 | Due to red-hot maintenance of 132/33 kV Transformer T4
Naogaon | 1 | 0:55 | 32 | 29.3333 | Due to red-hot maintenance of 132/33 kV Transformer T3
C.nawabganj | 1 | 0:16 | 5 | 1.3333 | Due to tripping of 132/33 kV Transformer T4
Rajshahi | 1 | 1:13 | 14 | 17.0333 | Due to red-hot maintenance of 33 kV Bus
Naogaon | 1 | 1:46 | 45 | 79.5 | Due to red-hot maintenance of 132/33 kV Transformer T1 & T2
C.nawabganj | 1 | 0:08 | 6 | 0.8 | Due to tripping of 132/33 kV Transformer T4
Naogaon | 1 | 1:42 | 25 | 42.5 | Due to red-hot maintenance of 132/33 kV Transformer T2
Rajshahi | 1 | 0:07 | 260 | 30.3333 | Due to tripping of Rajshahi-Natore 132 kV line-1 & 2
Naogaon | 1 | 0:06 | 65 | 6.5 | Due to tripping of Naogaon-Niyamatpur 132 kV line
Rajshahi | 1 | 0:16 | 28 | 7.4667 | Due to tripping of Rajshahi-Amnura 132 kV line
Bogura | 1 | 1:09 | 250 | 287.5 | Due to S/D of 132 kV Bus
Naogaon | 1 | 1:05 | 20 | 21.6667 | Due to S/D of 132/33 kV Transformer T3
Saidpur | 2 | 13:56 | 60 | 836 | Due to S/D of Saidpur-Purbasadipur 132 kV line-1 & 2
|  | 3:22 | 65 | 218.8333
Rangpur | 1 | 4:20 | 80 | 346.6667 | Due to S/D of Rangpur-Lalmonirhat 132 kV line
| Total unserved energy : |  |  | 6389.3633 | MWH | 6.9667
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 5 | 2019-08-03 | 100
2 | Munsiganj | 134 | 5 | 2019-08-03 | 2100
3 | Sonargaon | 96 | 31 | 2019-08-03 | 1930
4 | Shyampur | 200 | 1 | 2019-08-03 | 100
5 | Bhulta | 204 | 4 | 2019-08-03 | 2300
6 | Madanganj | 61 | 4 | 2019-08-03 | 2000
7 | Shitalakhya | 121 | 27 | 2019-08-03 | 1600
8 | Rahim steel | 15 | 1 | 2019-08-03 | 700
9 | Matuail | 100 | 5 | 2019-08-03 | 1000
10 | Ghorasal | 92 | 4 | 2019-08-03 | 2400
11 | Narsingdi | 153 | 28 | 2019-08-03 | 2000
12 | Haripur (SBU) | 112 | 6 | 2019-08-03 | 1900
13 | Ullon | 101 | 5 | 2019-08-03 | 1500
14 | Hasnabad | 239 | 5 | 2019-08-03 | 2100
15 | Magbazar | 161 | 27 | 2019-08-03 | 1600
16 | Maniknagar | 120 | 19 | 2019-08-03 | 1300
17 | Bangabhaban | 42 | 6 | 2019-08-03 | 1300
18 | Narinda | 102 | 4 | 2019-08-03 | 1500
19 | Dhanmondi | 192 | 22 | 2019-08-03 | 1300
20 | Lalbag | 93 | 5 | 2019-08-03 | 1600
21 | Madartek | 65 | 5 | 2019-08-03 | 2200
22 | Mirpur | 122 | 5 | 2019-08-03 | 2100
23 | Kalyanpur | 132 | 5 | 2019-08-03 | 2100
24 | Gulshan | 184 | 5 | 2019-08-03 | 1500
25 | Uttara | 99 | 27 | 2019-08-03 | 1700
26 | Uttara(new) | 20 | 5 | 2019-08-03 | 1930
27 | Kamrangirchar | 81 | 6 | 2019-08-03 | 900
28 | Savar | 150 | 22 | 2019-08-03 | 600
29 | Bhasantec | 183 | 5 | 2019-08-03 | 1500
30 | Agargaon | 68 | 22 | 2019-08-03 | 1300
31 | Satmosjid | 121 | 5 | 2019-08-03 | 1900
32 | Tongi | 169 | 29 | 2019-08-03 | 1500
33 | Kabirpur | 236 | 5 | 2019-08-03 | 1500
34 | Basundhara | 146 | 6 | 2019-08-03 | 1930
35 | Manikganj | 102 | 5 | 2019-08-03 | 2100
36 | Joydevpur | 240 | 6 | 2019-08-03 | 21:00
37 | New Tongi | 116 | 31 | 2019-08-03 | 1200
38 | Kodda | 271 | 4 | 2019-08-03 | 1930
39 | Dhamrai | 78 | 27 | 2019-08-03 | 2000
40 | Valuka | 98 | 4 | 2019-08-03 | 1930
41 | Tangail | 217 | 5 | 2019-08-03 | 2100
42 | Mymensing | 258 | 29 | 2019-08-03 | 2000
43 | Kishorganj | 140 | 28 | 2019-08-03 | 21:00
44 | Netrokona | 112 | 3 | 2019-08-03 | 2400
45 | Jamalpur | 143 | 12 | 2019-08-03 | 2200
46 | Sherpur | 114 | 3 | 2019-08-03 | 2300
47 | Srimongal | 47 | 2 | 2019-08-03 | 2200
48 | Shahjibazar | 129 | 21 | 2019-08-03 | 2100
49 | Fenchuganj | 54 | 27 | 2019-08-03 | 1900
50 | Kulawara | 51 | 10 | 2019-08-03 | 1900
51 | Sylhet | 161 | 22 | 2019-08-03 | 1930
52 | Chatak | 42 | 6 | 2019-08-03 | 2300
53 | Sunamganj | 49 | 26 | 2019-08-03 | 2100
54 | Bianibazar | 62 | 11 | 2019-08-03 | 2200
55 | Cumilla (S) | 192 | 31 | 2019-08-03 | 2000
56 | Cumilla(N) | 162 | 5 | 2019-08-03 | 2000
57 | Chandpur | 116 | 20 | 2019-08-03 | 2200
58 | Feni | 157 | 5 | 2019-08-03 | 1900
59 | Chowmuhani | 188 | 22 | 2019-08-03 | 2200
60 | Ashuganj | 63 | 6 | 2019-08-03 | 2300
61 | Daudkandi | 158 | 6 | 2019-08-03 | 1930
62 | B.Baria | 151 | 27 | 2019-08-03 | 2200
63 | Ramganj | 112 | 11 | 2019-08-03 | 2200
64 | Madanhat | 72 | 5 | 2019-08-03 | 2100
65 | Hathazari | 109 | 31 | 2019-08-03 | 1900
66 | Khulshi | 204 | 21 | 2019-08-03 | 1400
67 | Halishahar | 148 | 26 | 2019-08-03 | 1500
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 171 | 4 | 2019-08-03 | 1930
69 | Sikalbaha | 37 | 3 | 2019-08-03 | 1500
70 | Dohazari | 100 | 5 | 2019-08-03 | 2100
71 | Cox'sbazar | 99 | 15 | 2019-08-03 | 1930
72 | Chandraghona | 35 | 12 | 2019-08-03 | 2100
73 | Kaptai | 5 | 1 | 2019-08-03 | 1930
74 | A. Khaer Stl. | 16 | 1 | 2019-08-03 | 1000
75 | Bakulia | 119 | 31 | 2019-08-03 | 1600
76 | Julda | 23 | 22 | 2019-08-03 | 2400
77 | TK chemical | 19 | 25 | 2019-08-03 | 1830
78 | Modern Steel | 16 | 28 | 2019-08-03 | 1000
79 | Shahmirpur | 34 | 5 | 2019-08-03 | 2400
80 | Khagrachhari | 22 | 5 | 2019-08-03 | 2000
81 | Matarbari | 30 | 4 | 2019-08-03 | 2100
82 | Baroiar Hat | 52 | 19 | 2019-08-03 | 2100
83 | Rangamati | 30 | 17 | 2019-08-03 | 2100
84 | Abul Khair 230 | 180 | 26 | 2019-08-03 | 600
85 | BSRM | 162 | 22 | 2019-08-03 | 1830
86 | Goalpara | 29 | 5 | 2019-08-03 | 1930
87 | Central s/s | 99 | 5 | 2019-08-03 | 2000
88 | Noapara | 102 | 4 | 2019-08-03 | 1930
89 | Jashore | 122 | 5 | 2019-08-03 | 20:00
90 | Benapol | 46 | 3 | 2019-08-03 | 20:00
91 | Jhenidah | 118 | 10 | 2019-08-03 | 1930
92 | Bottail | 142 | 5 | 2019-08-03 | 1930
93 | G.K Project | 69 | 29 | 2019-08-03 | 1900
94 | Faridpur | 186 | 6 | 2019-08-03 | 2100
95 | Madaripur | 126 | 3 | 2019-08-03 | 2100
96 | Sariatpur | 54 | 8 | 2019-08-03 | 1930
97 | Gopalganj | 99 | 11 | 2019-08-03 | 1930
98 | Bagerhat | 94 | 31 | 2019-08-03 | 1900
99 | Mongla | 42 | 5 | 2019-08-03 | 1200
100 | Satkhira | 111 | 5 | 2019-08-03 | 1930
101 | Gallamari | 55 | 5 | 2019-08-03 | 1930
102 | Magura | 58 | 21 | 2019-08-03 | 1930
103 | Norail | 31 | 25 | 2019-08-03 | 1930
104 | Chuadanga | 101 | 5 | 2019-08-03 | 2000
105 | Barsal(N) | 47 | 3 | 2019-08-03 | 2300
106 | Barsal(S) | 118 | 3 | 2019-08-03 | 2300
107 | Patuakhali | 127 | 28 | 2019-08-03 | 2200
108 | Bhandaria | 62 | 11 | 2019-08-03 | 2100
109 | Borhan Uddin | 43 | 14 | 2019-08-03 | 2200
110 | Ishurdi | 74 | 5 | 2019-08-03 | 2100
111 | Ruppur Paromanobik | 2 | 3 | 2019-08-03 | 1930
112 | Natore | 145 | 6 | 2019-08-03 | 2000
113 | Bogura | 270 | 6 | 2019-08-03 | 2000
114 | Naogaon | 132 | 3 | 2019-08-03 | 2100
115 | Rajshahi | 167 | 19 | 2019-08-03 | 2100
116 | C.Nawabganj | 87 | 4 | 2019-08-03 | 2100
117 | Amnura | 41 | 23 | 2019-08-03 | 1930
118 | Pabna | 127 | 5 | 2019-08-03 | 2000
119 | Shahjadpur | 117 | 6 | 2019-08-03 | 2000
120 | Serajganj | 125 | 5 | 2019-08-03 | 2100
121 | Niyamatpur | 77 | 5 | 2019-08-03 | 2100
122 | Joypurhat | 60 | 3 | 2019-08-03 | 2100
123 | Mohastangar | 18 | 6 | 2019-08-03 | 2000
124 | Rangpur | 153 | 20 | 2019-08-03 | 2000
125 | Lalmonirhat | 72 | 24 | 2019-08-03 | 2000
126 | Saidpur | 122 | 21 | 2019-08-03 | 2000
127 | Purbasadipur | 110 | 28 | 2019-08-03 | 300
128 | Thakurgaon | 79 | 7 | 2019-08-03 | 1930
129 | Palshbari | 129 | 26 | 2019-08-03 | 2100
130 | Barapukuria | 56 | 28 | 2019-08-03 | 2000
131 | Panchugar | 49 | 8 | 2019-08-03 | 2000
132 | Joldhaka | 31 | 27 | 2019-08-03 | 2000
133 | Kurigram | 41 | 30 | 2019-08-03 | 200
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:August' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4487 | 05.08.19 | 19:30
Chattogram | 1349 | 26.08.19 | 24:00
Khulna | 1524 | 05.08.19 | 21:00
Rajshahi | 1349 | 05.08.19 | 21:00
Cumilla | 1191 | 31.08.19 | 3:00
Mymensingh | 1097 | 01.08.19 | 22:00
Sylhet | 687 | 09.08.19 | 19:00
Barisal | 748 | 28.08.19 | 1:00
Rangpur | 849 | 24.08.19 | 16:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 383 | 395 | 15 | 2019-08-03 | 6:00 | 362 | 19 | 2019-06-03 | 20:00
2 | Bheramara | 388 | 409 | 6 | 2019-08-03 | 3:00 | 383 | 20 | 2019-06-03 | 19:30
3 | Ashuganj(N) | 376 | 393 | 13 | 2019-08-03 | 1:00 | 369 | 18 | 2019-06-03 | 15:00
4 | Kaliakoir | 400 | 378 | 13 | 2019-08-03 | 1:00 | 307 | 24 | 2019-06-03 | 13:00
5 | Bhulta | 400 | 394 | 13 | 2019-08-03 | 22:00 | 364 | 29 | 2019-06-03 | 10:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 1 | 2019-08-03 | 1:00 | 220 | 6 | 2019-08-03 | 14:00
2 | Ishurdi | 230 | 238 | 13 | 2019-08-03 | 9:00 | 220 | 2 | 2019-08-03 | 22:00
3 | Ashuganj | 230 | 240 | 4 | 2019-08-03 | 1:00 | 227 | 30 | 2019-08-03 | 10:00
4 | Serajganj | 230 | 233 | 2 | 2019-08-03 | 18:30 | 220 | 5 | 2019-08-03 | 22:00
5 | Baghabari | 230 | 237 | 13 | 2019-08-03 | 17:00 | 223 | 5 | 2019-08-03 | 1:00
6 | Barapukuria | 230 | 237 | 8 | 2019-08-03 | 10:00 | 209 | 5 | 2019-08-03 | 22:00
7 | Bogra | 230 | 233 | 3 | 2019-08-03 | 18:00 | 200 | 5 | 2019-08-03 | 22:00
8 | Khulna South | 230 | 231 | 6 | 2019-08-03 | 8:00 | 204 | 10 | 2019-08-03 | 7:00
9 | Rampura | 230 | 225 | 13 | 2019-08-03 | 7:00 | 210 | 6 | 2019-08-03 | 14:00
10 | Haripur | 230 | 226 | 13 | 2019-08-03 | 18:00 | 210 | 6 | 2019-08-03 | 16:00
11 | Hasnabad | 230 | 230 | 12 | 2019-08-03 | 7:00 | 209 | 31 | 2019-08-03 | 16:00
12 | Aminbazar | 230 | 227 | 14 | 2019-08-03 | 8:00 | 208 | 25 | 2019-08-03 | 12:00
13 | Tongi | 230 | 226 | 15 | 2019-08-03 | 10:00 | 208 | 25 | 2019-08-03 | 12:00
14 | Comilla (N) | 230 | 232 | 12 | 2019-08-03 | 9:00 | 221 | 26 | 2019-08-03 | 15:00
15 | Hathazari | 230 | 222 | 1 | 2019-08-03 | 18:00 | 212 | 24 | 2019-08-03 | 11:00
16 | Megnaghat | 230 | 231 | 13 | 2019-08-03 | 16:00 | 210 | 31 | 2019-08-03 | 16:00
17 | Fenchuganj | 230 | 238 | 15 | 2019-08-03 | 9:00 | 229 | 19 | 2019-08-03 | 7:00
18 | Siddhirganj | 230 | 228 | 13 | 2019-08-03 | 5:00 | 209 | 29 | 2019-08-03 | 10:00
19 | Maniknagar | 230 | 227 | 13 | 2019-08-03 | 7:00 | 207 | 29 | 2019-08-03 | 10:00
20 | Old Airport | 230 | 226 | 15 | 2019-08-03 | 9:00 | 205 | 29 | 2019-08-03 | 10:00
21 | Barisal | 230 | 242 | 11 | 2019-08-03 | 15:00 | 201 | 10 | 2019-08-03 | 11:00
22 | AKSML | 230 | 221 | 12 | 2019-08-03 | 16:00 | 208 | 20 | 2019-08-03 | 15:00
23 | BSRM | 230 | 224 | 12 | 2019-08-03 | 6:00 | 210 | 19 | 2019-08-03 | 15:00
24 | Bibiyana | 230 | 235 | 15 | 2019-08-03 | 8:00 | 224 | 29 | 2019-08-03 | 9:00
25 | Bhulta | 230 | 229 | 13 | 2019-08-03 | 7:00 | 209 | 29 | 2019-08-03 | 10:00
26 | Ashuganj (S) | 230 | 236 | 3 | 2019-08-03 | 5:00 | 225 | 30 | 2019-08-03 | 10:00
27 | Kaliakoir | 230 | 229 | 13 | 2019-08-03 | 7:00 | 206 | 29 | 2019-08-03 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 136 | 12 | 2019-08-03 | 11:00 | 123 | 4 | 2019-08-03 | 11:00
2 | Munsiganj | 132 | 136 | 20 | 2019-08-03 | 20:00 | 122 | 7 | 2019-08-03 | 1000
3 | Megnaghat | 132 | 135 | 9 | 2019-08-03 | 21:00 | 120 | 7 | 2019-08-03 | 700
4 | Shyampur | 132 | 137 | 11 | 2019-08-03 | 800 | 122 | 7 | 2019-08-03 | 1100
5 | Bhulta | 132 | 131 | 11 | 2019-08-03 | 900 | 115 | 3 | 2019-08-03 | 15:00
6 | Madanganj | 132 | 138 | 3 | 2019-08-03 | 21:00 | 120 | 1 | 2019-08-03 | 10:00
7 | Shitalakhya | 132 | 140 | 5 | 2019-08-03 | 22:00 | 121 | 1 | 2019-08-03 | 10:00
8 | Rahim Steal | 132 | 136 | 12 | 2019-08-03 | 1200 | 124 | 7 | 2019-08-03 | 11:00
9 | Matuail | 132 | 135 | 12 | 2019-08-03 | 1000 | 122 | 4 | 2019-08-03 | 12:00
10 | Ghorasal | 132 | 138 | 5 | 2019-08-03 | 1600 | 130 | 3 | 2019-08-03 | 15:00
11 | Narsinghdi | 132 | 135 | 13 | 2019-08-03 | 1700 | 118 | 1 | 2019-08-03 | 12:00
12 | Haripur (SBU) | 132 | 136 | 12 | 2019-08-03 | 900 | 124 | 7 | 2019-08-03 | 11:00
13 | Ullon | 132 | 137 | 13 | 2019-08-03 | 700 | 121 | 29 | 2019-08-03 | 15:00
14 | Hasnabad | 132 | 137 | 4 | 2019-08-03 | 2400 | 123 | 3 | 2019-08-03 | 12:00
15 | Magbazar | 132 | 137 | 12 | 2019-08-03 | 12:00 | 121 | 26 | 2019-08-03 | 16:00
16 | Maniknagar | 132 | 140 | 13 | 2019-08-03 | 1700 | 125 | 4 | 2019-08-03 | 12:00
17 | Bangabhaban | 132 | 140 | 13 | 2019-08-03 | 1700 | 125 | 4 | 2019-08-03 | 12:00
18 | Narinda | 132 | 140 | 13 | 2019-08-03 | 1700 | 125 | 4 | 2019-08-03 | 12:00
19 | Dhanmondi | 132 | 138 | 18 | 2019-08-03 | 600 | 121 | 29 | 2019-08-03 | 15:00
20 | Lalbag | 132 | 137 | 15 | 2019-08-03 | 9:00 | 120 | 1 | 2019-08-03 | 10:00
21 | Madartek | 132 | 137 | 13 | 2019-08-03 | 600 | 121 | 27 | 2019-08-03 | 13:00
22 | Mirpur | 132 | 139 | 15 | 2019-08-03 | 1000 | 124 | 24 | 2019-08-03 | 1200
23 | Kalyanpur | 132 | 139 | 2 | 2019-08-03 | 100 | 126 | 24 | 2019-08-03 | 1300
24 | Gulshan | 132 | 136 | 12 | 2019-08-03 | 900 | 120 | 27 | 2019-08-03 | 12:00
25 | Uttara | 132 | 138 | 15 | 2019-08-03 | 7:00 | 121 | 29 | 2019-08-03 | 10:00
26 | Uttara(New) | 132 | 134 | 5 | 2019-08-03 | 200 | 122 | 7 | 2019-08-03 | 11:00
27 | Kamrangirchar | 132 | 136 | 5 | 2019-08-03 | 1930 | 120 | 1 | 2019-08-03 | 10:00
28 | Savar | 132 | 136 | 13 | 2019-08-03 | 6:00 | 122 | 28 | 2019-08-03 | 9:00
29 | Bhasantec | 132 | 137 | 9 | 2019-08-03 | 2000 | 116 | 23 | 2019-08-03 | 6:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 138 | 9 | 2019-08-03 | 19:30 | 123 | 29 | 2019-08-03 | 1000
31 | Satmosjid | 132 | 138 | 11 | 2019-08-03 | 6:00 | 123 | 29 | 2019-08-03 | 1000
32 | Tongi | 132 | 137 | 15 | 2019-08-03 | 10:00 | 125 | 6 | 2019-08-03 | 1500
33 | Kabirpur | 132 | 137 | 13 | 2019-08-03 | 1800 | 123 | 24 | 2019-08-03 | 2100
34 | Basundhara | 132 | 133 | 13 | 2019-08-03 | 1800 | 120 | 22 | 2019-08-03 | 1200
35 | Manikganj | 132 | 140 | 7 | 2019-08-03 | 1600 | 125 | 2 | 2019-08-03 | 1500
36 | Joydevpur | 132 | 141 | 5 | 2019-08-03 | 17:00 | 127 | 24 | 2019-08-03 | 1600
37 | New Tongi | 132 | 136 | 13 | 2019-08-03 | 6:00 | 122 | 6 | 2019-08-03 | 1500
38 | Kodda | 132 | 138 | 5 | 2019-08-03 | 1:00 | 120 | 3 | 2019-08-03 | 800
39 | Dhamrai | 132 | 137 | 15 | 2019-08-03 | 9:00 | 123 | 26 | 2019-08-03 | 1900
40 | Valuka | 133 | 133 | 7 | 2019-08-03 | 1600 | 108 | 6 | 2019-08-03 | 1900
41 | Tangail | 132 | 137 | 7 | 2019-08-03 | 1600 | 117 | 1 | 2019-08-03 | 15:00
42 | Mymensing | 132 | 135 | 7 | 2019-08-03 | 1700 | 110 | 6 | 2019-08-03 | 1900
43 | Kishorganj | 132 | 136 | 7 | 2019-08-03 | 1700 | 115 | 26 | 2019-08-03 | 2100
44 | Netrokona | 132 | 136 | 7 | 2019-08-03 | 1700 | 108 | 6 | 2019-08-03 | 1900
45 | Jamalpur | 132 | 140 | 12 | 2019-08-03 | 2100 | 115 | 2 | 2019-08-03 | 900
46 | Sherpur | 132 | 141 | 12 | 2019-08-03 | 2100 | 114 | 2 | 2019-08-03 | 900
47 | Srimongal | 132 | 138 | 31 | 2019-08-03 | 10:00 | 128 | 21 | 2019-08-03 | 2200
48 | Shahjibazar | 132 | 138 | 12 | 2019-08-03 | 600 | 121 | 21 | 2019-08-03 | 2200
49 | Fenchuganj | 132 | 136 | 2 | 2019-08-03 | 900 | 128 | 21 | 2019-08-03 | 1800
50 | Khulawara | 132 | 135 | 3 | 2019-08-03 | 2000 | 127 | 21 | 2019-08-03 | 1830
51 | Sylhet | 132 | 135 | 1 | 2019-08-03 | 500 | 124 | 19 | 2019-08-03 | 2000
52 | Chattak | 132 | 135 | 3 | 2019-08-03 | 600 | 121 | 19 | 2019-08-03 | 1900
53 | Sunamganj | 132 | 136 | 12 | 2019-08-03 | 2100 | 119 | 19 | 2019-08-03 | 2000
54 | Biani Bazar | 132 | 134 | 2 | 2019-08-03 | 600 | 119 | 27 | 2019-08-03 | 1830
55 | Comilla(South) | 132 | 135 | 29 | 2019-08-03 | 600 | 113 | 25 | 2019-08-03 | 1500
56 | Comilla (North) | 132 | 137 | 7 | 2019-08-03 | 1930 | 121 | 29 | 2019-08-03 | 1400
57 | Chandpur | 132 | 140 | 7 | 2019-08-03 | 2100 | 122 | 10 | 2019-08-03 | 1600
58 | Feni | 132 | 135 | 24 | 2019-08-03 | 700 | 119 | 13 | 2019-08-03 | 1500
59 | Chowmuhani | 132 | 128 | 6 | 2019-08-03 | 1100 | 113 | 10 | 2019-08-03 | 1900
60 | Ashuganj | 132 | 139 | 11 | 2019-08-03 | 1700 | 130 | 1 | 2019-08-03 | 2400
61 | Daudkandi | 132 | 136 | 6 | 2019-08-03 | 2100 | 122 | 27 | 2019-08-03 | 1200
62 | Brahminbaria | 132 | 136 | 3 | 2019-08-03 | 700 | 123 | 20 | 2019-08-03 | 1900
63 | Ramganj | 132 | 132 | 7 | 2019-08-03 | 1700 | 115 | 15 | 2019-08-03 | 2100
64 | Madanhat | 132 | 134 | 7 | 2019-08-03 | 600 | 127 | 19 | 2019-08-03 | 1200
65 | Hathazari | 132 | 132 | 1 | 2019-08-03 | 1800 | 126 | 19 | 2019-08-03 | 900
66 | Khulshi | 132 | 131 | 7 | 2019-08-03 | 500 | 123 | 24 | 2019-08-03 | 1100
67 | Halishahar | 132 | 134 | 1 | 2019-08-03 | 1930 | 120 | 11 | 2019-08-03 | 2100
68 | Baraulia | 132 | 132 | 12 | 2019-08-03 | 800 | 124 | 8 | 2019-08-03 | 1200
69 | Sikalbaha | 132 | 135 | 1 | 2019-08-03 | 1930 | 119 | 21 | 2019-08-03 | 1300
70 | Dohazari | 132 | 133 | 1 | 2019-08-03 | 1930 | 116 | 19 | 2019-08-03 | 800
71 | Cox'sbazar | 132 | 130 | 2 | 2019-08-03 | 1300 | 112 | 5 | 2019-08-03 | 1000
72 | Chandraghona | 132 | 134 | 1 | 2019-08-03 | 1800 | 128 | 1 | 2019-08-03 | 1600
73 | Kaptai | 132 | 134 | 6 | 2019-08-03 | 700 | 125 | 12 | 2019-08-03 | 300
74 | A. Khaer Stl. | 132 | 131 | 1 | 2019-08-03 | 1900 | 125 | 5 | 2019-08-03 | 2300
75 | Bakulia | 132 | 133 | 1 | 2019-08-03 | 1930 | 124 | 1 | 2019-08-03 | 1600
76 | Julda | 132 | 134 | 1 | 2019-08-03 | 2000 | 126 | 8 | 2019-08-03 | 1400
77 | TK Chemical | 132 | 136 | 1 | 2019-08-03 | 1830 | 126 | 24 | 2019-08-03 | 900
78 | Modern Steel | 132 | 134 | 1 | 2019-08-03 | 1930 | 126 | 8 | 2019-08-03 | 1700
79 | Shahmirpur | 132 | 133 | 1 | 2019-08-03 | 1900 | 125 | 24 | 2019-08-03 | 1100
80 | Khagrachhari | 132 | 133 | 7 | 2019-08-03 | 600 | 126 | 25 | 2019-08-03 | 800
81 | Matarbari | 132 | 132 | 23 | 2019-08-03 | 2100 | 118 | 5 | 2019-08-03 | 1000
82 | Baroiar Hat | 132 | 134 | 27 | 2019-08-03 | 5:00 | 120 | 11 | 2019-08-03 | 1900
83 | Rangamati | 133 | 136 | 6 | 2019-08-03 | 400 | 127 | 24 | 2019-08-03 | 1100
84 | Goalpara | 132 | 140 | 2 | 2019-08-03 | 100 | 122 | 10 | 2019-08-03 | 1300
85 | Khulna Central | 132 | 140 | 5 | 2019-08-03 | 300 | 121 | 10 | 2019-08-03 | 1300
86 | Noapara | 132 | 136 | 5 | 2019-08-03 | 1800 | 117 | 1 | 2019-08-03 | 2100
87 | Jessore | 132 | 132 | 7 | 2019-08-03 | 700 | 110 | 10 | 2019-08-03 | 1300
88 | Benapol | 132 | 134 | 2 | 2019-08-03 | 800 | 112 | 1 | 2019-08-03 | 2100
89 | Jhenida | 132 | 137 | 7 | 2019-08-03 | 1300 | 106 | 1 | 2019-08-03 | 2100
90 | Bottail | 132 | 139 | 23 | 2019-08-03 | 1200 | 116 | 1 | 2019-08-03 | 2100
91 | G.K Project | 132 | 143 | 14 | 2019-08-03 | 1800 | 125 | 1 | 2019-08-03 | 200
92 | Faridpur | 132 | 135 | 2 | 2019-08-03 | 700 | 110 | 5 | 2019-08-03 | 2000
93 | Madaripur | 132 | 137 | 24 | 2019-08-03 | 1830 | 109 | 5 | 2019-08-03 | 2000
94 | Sariatpur | 132 | 138 | 29 | 2019-08-03 | 1830 | 104 | 5 | 2019-08-03 | 2200
95 | Gopalganj | 132 | 142 | 13 | 2019-08-03 | 1900 | 117 | 5 | 2019-08-03 | 2200
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Bagerhat | 132 | 138 | 6 | 2019-08-03 | 700 | 120 | 1 | 2019-08-03 | 2100
97 | Mongla | 132 | 135 | 6 | 2019-08-03 | 1500 | 115 | 10 | 2019-08-03 | 1300
98 | Satkhira | 132 | 138 | 3 | 2019-08-03 | 9:00 | 119 | 1 | 2019-08-03 | 100
99 | Gallamari | 132 | 140 | 5 | 2019-08-03 | 300 | 122 | 10 | 2019-08-03 | 1300
100 | Magura | 132 | 131 | 9 | 2019-08-03 | 1000 | 103 | 1 | 2019-08-03 | 2100
101 | Norail | 132 | 130 | 8 | 2019-08-03 | 8:00 | 105 | 10 | 2019-08-03 | 1900
102 | Chuadanga | 132 | 129 | 3 | 2019-08-03 | 900 | 98 | 1 | 2019-08-03 | 2100
103 | Barisal(N) | 132 | 140 | 11 | 2019-08-03 | 1600 | 119 | 5 | 2019-08-03 | 2200
104 | Barisal(S) | 132 | 141 | 11 | 2019-08-03 | 1600 | 110 | 10 | 2019-08-03 | 1100
105 | Patuakhali | 132 | 136 | 17 | 2019-08-03 | 700 | 114 | 5 | 2019-08-03 | 2200
106 | Bhandaria | 132 | 137 | 3 | 2019-08-03 | 900 | 118 | 5 | 2019-08-03 | 1900
107 | Ishurdi | 132 | 140 | 18 | 2019-08-03 | 1830 | 126 | 1 | 2019-08-03 | 1930
108 | Ruppur paromanobik | 132 | 140 | 15 | 2019-08-03 | 1830 | 128 | 1 | 2019-08-03 | 2000
109 | Natore | 132 | 138 | 18 | 2019-08-03 | 1830 | 121 | 5 | 2019-08-03 | 2000
110 | Bogra | 132 | 137 | 8 | 2019-08-03 | 1700 | 115 | 5 | 2019-08-03 | 2000
111 | Noagaon | 132 | 132 | 7 | 2019-08-03 | 1800 | 107 | 4 | 2019-08-03 | 2000
112 | Rajshahi | 132 | 135 | 21 | 2019-08-03 | 1830 | 120 | 5 | 2019-08-03 | 2100
113 | C.Nawabganj | 132 | 134 | 18 | 2019-08-03 | 1830 | 114 | 19 | 2019-08-03 | 1500
114 | Amnura | 132 | 139 | 18 | 2019-08-03 | 1830 | 115 | 19 | 2019-08-03 | 1500
115 | Pabna | 132 | 139 | 23 | 2019-08-03 | 1800 | 125 | 5 | 2019-08-03 | 1930
116 | Shahjadpur | 132 | 142 | 22 | 2019-08-03 | 1500 | 126 | 9 | 2019-08-03 | 2100
117 | Serajganj | 132 | 138 | 22 | 2019-08-03 | 1600 | 122 | 9 | 2019-08-03 | 2100
118 | Niyamatpur | 132 | 132 | 8 | 2019-08-03 | 1700 | 101 | 4 | 2019-08-03 | 2000
119 | Joypurhat | 132 | 135 | 8 | 2019-08-03 | 1700 | 104 | 4 | 2019-08-03 | 2000
120 | Mohastangor | 132 | 137 | 8 | 2019-08-03 | 1830 | 110 | 5 | 2019-08-03 | 700
121 | Rangpur | 132 | 134 | 8 | 2019-08-03 | 600 | 100 | 5 | 2019-08-03 | 600
122 | Lalmonirhat | 132 | 134 | 3 | 2019-08-03 | 2100 | 96 | 5 | 2019-08-03 | 600
123 | Saidpur | 132 | 135 | 3 | 2019-08-03 | 2100 | 100 | 5 | 2019-08-03 | 600
124 | Purbasadipur | 132 | 134 | 8 | 2019-08-03 | 800 | 95 | 5 | 2019-08-03 | 600
125 | Thakurgaon | 132 | 133 | 3 | 2019-08-03 | 2100 | 90 | 5 | 2019-08-03 | 600
126 | Palashbari | 132 | 135 | 29 | 2019-08-03 | 800 | 106 | 5 | 2019-08-03 | 700
127 | Barapukuria | 132 | 137 | 8 | 2019-08-03 | 1000 | 109 | 5 | 2019-08-03 | 600
128 | Panchagar | 132 | 130 | 3 | 2019-08-03 | 2100 | 82 | 5 | 2019-08-03 | 600
129 | Joldhaka | 132 | 135 | 3 | 2019-08-03 | 2100 | 98 | 5 | 2019-08-03 | 700
130 | Kurigram | 133 | 132 | 12 | 2019-08-03 | 1800 | 90 | 5 | 2019-08-03 | 500
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:August' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 115 | 400
IP-299421 | Hasnabad | TR2 | 225 | 102 | 400 | 28.08.19 | 10:00
|  | TR3 | 225 | 100 | 350
|  | TR1 | 225 | 165 | 495
IP-299866 | Tongi | TR2 | 225 | 165 | 495 | 02.08.19 | 09:00
|  | TR3 | 225 | 165 | 495
|  | TR1 | 225 | 100 | 385
IP-299427 | Haripur | TR2 | 225 |  |  | 29.08.19 | 10:00 | S/D
|  | TR3 | 225 | 100 | 385
|  | TR1 | 225 | 180 | 540
IP-299728 | Rampura | TR2 | 225 | 180 | 540 | 05.08.19 | 15:00
|  | TR3 | 225 | 180 | 540
|  | TR1 | 225 | 143 | 394
IP-299264 | Aminbazar | TR2 | 225 | 143 | 394 | 01.08.19 | 11:00
|  | TR3 | 225 | 149 | 435
| Maniknagar | TR1 | 300 | 123 | 410 | 27.08.19 | 13:00
|  | TR2 | 300 | 123 | 410
IP-399266 | Cumilla (N) | TR1 | 225 | 160 | 500 | 14.08.19 | 14:00
|  | TR2 | 225 | 161 | 545
| Fenchuganj | TR1 | 300 | 172 | 450 | 21.08.19 | 22:00
|  | MT1 | 150 | 76 | 205
IP-399428 | Hathazari | MT2 | 150 | 76 | 205 | 08.08.19 | 10:00
|  | MT3 | 150 | 76 | 205
|  | MT4 | 150 | 76 | 205
|  | TR1 | 225 | 160 | 460
| Ishurdi | TR2 | 225 | 160 | 460 | 02.08.19 | 21:00
IP-499474 |  | TR3 | 225 | 160 | 460
| Khulna(S) | TR1 | 225 | 134 | 390
IP-58001/58002 |  | TR2 | 225 | 133 | 390 | 02.08.19 | 12:00
|  | TR3 | 300 | 175 | 502
| Bogra | TR1 | 225 | 169 | 466 | 03.08.19 | 21:00
|  | TR2 | 225 | 169 | 466
IP-43002/499264 |  | TR3 | 225 | 231 | 785
IP-499224 | Baghabari | TR1 | 225 | 189 | 580 | 03.08.19 | 20:00
| Barapukuria | TR1 | 225 | 160 | 720 | 25.08.19 | 21:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 225 | 157 | 760 |  |  | 132 kV current is being provided
|  | TR6 | 300 | 227 | 1118
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 198 | 368 | 03.08.19 | 10:15
|  | TR2(400/230 kV) | 520 | 198 | 368
|  | TR1(400/132 kV) | 325 | 250 | 442 | 27.08.19 | 19:15
|  | TR2(400/132 kV) | 325 | 250 | 442
| Bibiyana | ICT1(400/230 kV) | 520 | 86.5 | 169.5 | 26.08.19 | 15:00
|  | ICT2(400/230kV) | 520 | 85.9 | 170
| Bhulta | ATR1(400/230 kV) | 520 | 217 | 381 | 08.08.19 | 16:30
|  | ATR2(400/230kV) | 520 | 217 | 381
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:August' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:August' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-08-19 | 12016 | 12016 | - | - | - | - | - | - | - | - | - | - | - | - | 01-08-19 | 9267.5 | 9267.5 | - | - | - | - | - | - | - | - | - | - | - | -
02-08-19 | 11466 | 11466 | - | - | - | - | - | - | - | - | - | - | - | - | 02-08-19 | 8455.8 | 8455.8 | - | - | - | - | - | - | - | - | - | - | - | -
03-08-19 | 12035 | 12035 | - | - | - | - | - | - | - | - | - | - | - | - | 03-08-19 | 8875 | 8875 | - | - | - | - | - | - | - | - | - | - | - | -
04-08-19 | 12655 | 12655 | - | - | - | - | - | - | - | - | - | - | - | - | 04-08-19 | 10152.8 | 10152.8 | - | - | - | - | - | - | - | - | - | - | - | -
05-08-19 | 12738 | 12738 | - | - | - | - | - | - | - | - | - | - | - | - | 05-08-19 | 10530.1 | 10530.1 | - | - | - | - | - | - | - | - | - | - | - | -
06-08-19 | 12342 | 12342 | - | - | - | - | - | - | - | - | - | - | - | - | 06-08-19 | 10072.7 | 10072.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-08-19 | 10771 | 10771 | - | - | - | - | - | - | - | - | - | - | - | - | 07-08-19 | 8703.3 | 8703.3 | - | - | - | - | - | - | - | - | - | - | - | -
08-08-19 | 10781 | 10781 | - | - | - | - | - | - | - | - | - | - | - | - | 08-08-19 | 8721.1 | 8721.1 | - | - | - | - | - | - | - | - | - | - | - | -
09-08-19 | 11235 | 11235 | - | - | - | - | - | - | - | - | - | - | - | - | 09-08-19 | 8101.8 | 8101.8 | - | - | - | - | - | - | - | - | - | - | - | -
10-08-19 | 11049 | 11049 | - | - | - | - | - | - | - | - | - | - | - | - | 10-08-19 | 8225 | 8225 | - | - | - | - | - | - | - | - | - | - | - | -
11-08-19 | 10615 | 10615 | - | - | - | - | - | - | - | - | - | - | - | - | 11-08-19 | 7916.3 | 7916.3 | - | - | - | - | - | - | - | - | - | - | - | -
12-08-19 | 9818 | 9818 | - | - | - | - | - | - | - | - | - | - | - | - | 12-08-19 | 6792.8 | 6792.8 | - | - | - | - | - | - | - | - | - | - | - | -
13-08-19 | 9274 | 9274 | - | - | - | - | - | - | - | - | - | - | - | - | 13-08-19 | 6666 | 6666 | - | - | - | - | - | - | - | - | - | - | - | -
14-08-19 | 9666 | 9666 | - | - | - | - | - | - | - | - | - | - | - | - | 14-08-19 | 6456.3 | 6456.3 | - | - | - | - | - | - | - | - | - | - | - | -
15-08-19 | 9552 | 9552 | - | - | - | - | - | - | - | - | - | - | - | - | 15-08-19 | 6501.3 | 6501.3 | - | - | - | - | - | - | - | - | - | - | - | -
16-08-19 | 9808 | 9808 | - | - | - | - | - | - | - | - | - | - | - | - | 16-08-19 | 6940.2 | 6940.2 | - | - | - | - | - | - | - | - | - | - | - | -
17-08-19 | 10792 | 10792 | - | - | - | - | - | - | - | - | - | - | - | - | 17-08-19 | 7885.4 | 7885.4 | - | - | - | - | - | - | - | - | - | - | - | -
18-08-19 | 11188 | 11188 | - | - | - | - | - | - | - | - | - | - | - | - | 18-08-19 | 8778.9 | 8778.9 | - | - | - | - | - | - | - | - | - | - | - | -
19-08-19 | 11757 | 11757 | - | - | - | - | - | - | - | - | - | - | - | - | 19-08-19 | 9420.4 | 9420.4 | - | - | - | - | - | - | - | - | - | - | - | -
20-08-19 | 12142 | 12142 | - | - | - | - | - | - | - | - | - | - | - | - | 20-08-19 | 9749.8 | 9749.8 | - | - | - | - | - | - | - | - | - | - | - | -
21-08-19 | 12450 | 12450 | - | - | - | - | - | - | - | - | - | - | - | - | 21-08-19 | 10148.2 | 10148.2 | - | - | - | - | - | - | - | - | - | - | - | -
22-08-19 | 12021 | 12021 | - | - | - | - | - | - | - | - | - | - | - | - | 22-08-19 | 10539.2 | 10539.2 | - | - | - | - | - | - | - | - | - | - | - | -
23-08-19 | 11577 | 11577 | - | - | - | - | - | - | - | - | - | - | - | - | 23-08-19 | 8559.2 | 8559.2 | - | - | - | - | - | - | - | - | - | - | - | -
24-08-19 | 11814 | 11814 | - | - | - | - | - | - | - | - | - | - | - | - | 24-08-19 | 9182.7 | 9182.7 | - | - | - | - | - | - | - | - | - | - | - | -
25-08-19 | 12187 | 12187 | - | - | - | - | - | - | - | - | - | - | - | - | 25-08-19 | 9825.94 | 9825.94 | - | - | - | - | - | - | - | - | - | - | - | -
26-08-19 | 12461 | 12461 | - | - | - | - | - | - | - | - | - | - | - | - | 26-08-19 | 10071.8 | 10071.8 | - | - | - | - | - | - | - | - | - | - | - | -
27-08-19 | 12539 | 12539 | - | - | - | - | - | - | - | - | - | - | - | - | 27-08-19 | 10255.6 | 10255.6 | - | - | - | - | - | - | - | - | - | - | - | -
28-08-19 | 12693 | 12693 | - | - | - | - | - | - | - | - | - | - | - | - | 28-08-19 | 10335.4 | 10335.4 | - | - | - | - | - | - | - | - | - | - | - | -
29-08-20 | 12526 | 12526 | - | - | - | - | - | - | - | - | - | - | - | - | 29-08-20 | 10372.2 | 10372.2 | - | - | - | - | - | - | - | - | - | - | - | -
30-08-19 | 12272 | 12272 | - | - | - | - | - | - | - | - | - | - | - | - | 30-08-19 | 9230.2 | 9230.2 | - | - | - | - | - | - | - | - | - | - | - | -
31-08-19 | 12443 | 12443 | - | - | - | - | - | - | - | - | - | - | - | - | 31-08-19 | 9526.5 | 9526.5

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:August' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12738 | 05/08/19 | 19:30
2 | Maximum day peak Genaration | MW | 10539.2 | 22/08/19 | 21:00
3 | Maximum Evening Peak Demand | MW | 12738 | 05/08/19 | 19:30
4 | Minimum Generation | MW | 6449 | 14/08/19 | 8:00
5 | Average of the daily evening peak Genaration | MW | 11474.6667
6 | Average of the daily day peak Genaration | MW | 8911.5948
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 7325.6048
12 | Total Generation by IPP | MKWH | 2049.3772 | % of total Gen. | 27.98%
13 | Total Generation by BPDB | MKWH | 3752.2923 | " | 51.22%
14 | A) Total Generation by RPCL | MKWH | 152.5351 | '' | 2.082%
| B) Total Generation by REB | MKWH | 171.4948 | " | 2.341%
| C) Total Generation by RENTAL | MKWH | 460.4374 | " | 6.285%
| D) Total Imported from India (HVDC) | MKWH | 631.3461 | " | 8.618%
| E) Total Imported from Tripura, India (A.C) | MKWH | 108.1219 | " | 1.476%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4666.7708 | % of total Gen. | 63.7%
| B) Oil | MKWH | 1540.7738 | '' | 21.03%
| C) Hydro | MKWH | 151.3983 | '' | 2.067%
| D) Solar | MKWH | 4.1565 | '' | 0.05674%
| E) Coal | MKWH | 223.0374 | '' | 3.045%
| F) HVDC (Import from India) | MKWH | 631.3461 | '' | 8.618%
| G) A.C (Import from Tripura, India) | MKWH | 108.1219 | '' | 1.476%
16 | Maximun of the daily total Generation . | MKWH | 270.4339 | 29/08/19
17 | Monthly Load factor | % | 77.3075
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 18732.1703
| A) Gas | M.Taka | 5069.1195
| B) Liquid fuel | M.Taka | 12650.2345
| C) Coal | M.Taka | 1012.8163
| D) HVDC (Import from India) | M.Taka | 3219.865
| E) Tripura(Import from India) | M.Taka | 739.5539
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1144.5406 | 06/08/19
| A) Gas | M.Taka | 711.3402 | 06/08/19
| B) Liquid fuel | M.Taka | 767.6111 | 05/08/19
| C) Coal | M.Taka | 44.5198 | 19/08/19
| D) HVDC (Import from India) | M.Taka | 113.7986 | 02-08-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.3283
| B) Excluding Hydro & Solar | Taka/KWHR | 3.4005
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.67 | 31/08/19 | 06:00
b) | Actual | FT (MSL) | 105.37 | 31/08/19 | 06:00
22 | Peak Genaration of August 2018 | MW | 11217 | 13/08/18 | 22:00
23 | Peak Demand of August 2018 | MW | 11174 | 13/08/18 | 21:00
24 | Maximum peak Generation recorded upto 31/08/19 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/08/19 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/08/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.