## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:July' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | July 2019 |  | June 2019 |  | July 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12436 | 21/07/19 | 12780 | 24/06/19 | 11387 | 18/07/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 21:00
2 | Minimum Generation (MW) | 6202 | 14/07/19 | 5341 | 06/06/19 | 6777 | 03/07/18 | - | -
|  |  | 6:00 |  | 7:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12436 | 21/07/19 | 12780 | 06/06/19 | 11306 | 14/07/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10285.4 | 22/07/19 | 10554 | 24/06/19 | 9735.4 | 19/07/18 | 10364.4 | 29/05/19
|  |  | 12:00 |  | 12:00 |  | 11:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12436 | 21/07/19 | 12780 | 24/06/19 | 11306 | 14/07/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11518.3226 |  | 11184.63 |  | 10632.13 |  | 11518.32 | July -19
7 | Average Generation (MW) at Day Peak | 9293.471 |  | 8726.57 |  | 8546.27 |  | 9293.47 | July -19
8 | Maximum Power Import from India, HVDC (MW) | 936 | 26/07/19 | 949 | 09/06/19 | 476 | 27/07/18 | 956 | 27/3/2019
|  |  | 5:30 |  | 2:00 |  | 14:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 194 | 21/07/19 | 194 | 12/06/19 | 172 | 25/07/18 | 194 | 12/06/19
|  |  | 22:00 |  | 19:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3406.3279 |  | 3440.2 |  | 3249.92 |  | 3572.91 | May-19
21 | Station Use of BPDB (MKWH) | 125.0884 |  | 104.84 |  | 101.95
22 | Net Generation of BPDB (MKWH) | 3281.2394 |  | 3335.35 |  | 3147.97
23 | Net Generation of IPP & RPCL (MKWH) | 2468.1236 |  | 2092.34 |  | 2054.67
24 | Net Generation of REB (MKWH) | 143.6788 |  | 134.16 |  | 145.54
24 | Net Generation of Rental Power Plant (MKWH) | 572.3521 |  | 497.09 |  | 793.03
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6465.3939 |  | 6058.94 |  | 6141.21 |  | 6465.39 | July-19
26 | Energy Generation by Gas (MKWH) | 4492.67 |  | 4367.25 |  | 3894.56 |  | 4635.99 | May-19
27 | Energy Generation by Diesel (MKWH) | 279.0809 |  | 300.73 |  | 736.56 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1524.0229 |  | 1287.74 |  | 1413.49 |  | 1524.02.49 | July-19
29 | Energy Generation by Hydro (MKWH) | 102.8917 |  | 26.9 |  | 118.24 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 3.1773 |  | 5.1 |  | 0.26 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 189.3114 |  | 180.89 |  | 80.03 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 736.9925 |  | 695.73 |  | 435.2 |  | 736.99 | July-19
33 | Monthly Load Factor (%) | 79.2028 |  | 74.57 |  | 78.83 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12436 | 21/07/19 | 21:00
Generation Period
| Dhaka | MW | 4414
| Chattogram | MW | 1152
| Cumilla | MW | 1162
| Mymensingh | MW | 899
| Sylhet | MW | 515
a) | Total supply in East zone | MW | 8142
| Khulna | MW | 1470
| Barisal | MW | 316
| Rajshahi | MW | 1293
| Rangpur | MW | 658
b) | Total supply in West zone | MW | 3737
c) | Total supply in both zone ( a+b) | MW | 11879
Ref: | 27.21.2604.603.16.086.18.182 | Date: 14/08/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 860 | 19/07/19 | 1:00
| b) Ishurdi end | MW | 250 | 18/07/19 | 18:30
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 420 | 18/07/19 | 18:30
| b) Ishurdi end | MW | 320 | 19/07/19 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.9142 | 07/07/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 3.7125 | 07/07/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 56.4472
| b) Ishurdi end | MKWH | 10.8058
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 10.4816
| b) Ishurdi end | MKWH | 54.8031
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 07/07/19 | 22:00
| b)Serajganj end | MW | 340 | 26/07/19 | 11:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 320 | 26/07/19 | 11:00
| b)Sirajganj end | MW | 400 | 07/07/19 | 22:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.92 | 07/07/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 6.862 | 07/07/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 18.356
| b)Sirajganj end | MKWH | 96.818
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 18.192
| b)Sirajganj end | MKWH | 95.938
30 | Transmission loss of EWI /NO-2 | % | 0.906
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 132/33 kV Transformer-T1 | 2019-07-02 07:50 | 2019-07-02 08:20 | 0:30 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T1 , T2 T3 | 2019-07-02 10:14 | 2019-07-02 10:31 | 0:17 | T | Tripped showing 33 kV feeder fault | 106 | 30.0333 | Power interruption
Jodevpur | 132/33 kV Transformers-T4 & T3 | 2019-07-08 20:43 | 2019-07-08 20:44 | 0:01 | T | Tripped showing 33 kV feeder fault | 70 | 70 | Power interruption
Sherpur | 132/33 kV Transformer-T3 | 2019-07-10 14:35 | 2019-07-10 15:10 | 0:35 | E/O | Due to Oil leakage 33 kV side | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 & 33 kV bus | 2019-07-13 20:47 | 2019-07-13 21:21 | 0:34 | E/O | Due to red hot maintenance at 33 kV side | 50 | 28.3333 | Power interruption
Valuka | 132/33 kV Transformers-T1 & T2 | 2019-07-14 08:26 | 2019-07-14 20:51 | 12:25 | E/O | Due to bursting of CB & CT at 33 kV feeder | 80 | 993.3333 | Power interruption
Jamalpur | 132/33 kV Transformer-T1 | 2019-07-15 17:10 | 2019-07-15 18:32 | 1:22 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 & T3 | 2019-07-16 16:02 | 2019-07-16 16:10 | 0:08 | T | Tripped showing 33 kV feeder fault | 25 | 3.3333 | Power interruption
Tongi | 132/33 kV Transformers-T1 & T2 | 2019-07-21 22:07 | 2019-07-21 22:25 | 0:18 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2019-07-24 11:05 | 2019-07-24 11:25 | 0:20 | T | Tripped showing O/C relay at 33 kV side | 70 | 23.3333 | Power interruption
Joydevpur | 132/33 kV Transformers-T3 & T4 | 2019-07-30 18:35 | 2019-07-30 18:39 | 0:04 | T | Tripped showing O/C relay at 33 kV side | 80 | 53.3333 | Power interruption
|  |  | Total : | 16:34 |  | Unserved Energy: |  | 1201.7
Dhaka (South) Grid Circle :
Madartek | 132/33 kV Transformer-T1 | 2019-07-07 09:45 | 2019-07-07 11:52 | 2:07 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformers-T1 & T2 | 2019-07-09 05:43 | 2019-07-09 06:01 | 0:18 | T | Tripped showing O/C relay at 33 kV side | 101 | 30.3 | Power interruption
Munshuganj | 132/33 kV Transformer-T1 | 2019-07-12 08:05 | 2019-07-12 09:58 | 1:53 | E/O | Due to red hot maintenance | 40 | 75.3333 | Power interruption
Madanganj | 132/33 kV Transformer-T2 | 2019-07-28 11:15 | 2019-07-28 12:53 | 1:38 | T | Tripped showing buchhloz relay | 0 | 0 | No interruption
|  |  | Total : | 5:56 |  | Unserved Energy: |  | 105.6333
Chattogram Grid Circle :
Bakulia | 132/33 kV Transformer-T2 | 2019-07-01 08:15 | 2019-07-01 09:05 | 0:50 | E/O | Due to red hot maintenance 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 | 2019-07-01 15:05 | 2019-07-01 15:20 | 4:22 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-07-01 15:05 | 2019-07-01 15:21 | 5:22 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-07-01 15:05 | 2019-07-01 15:22 | 0:17 | T | Tripped showing diff. relay | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2019-07-01 21:20 | 2019-07-01 23:05 | 1:45 | E/O | Due to red hot maintenance at 33 kV side | 60 | 105 | Power interruption
Juldah | 132 kV main bus | 2019-07-03 06:05 | 2019-07-03 08:35 | 2:30 | E/O | Due to red hot maintenance | 16 | 40 | Power interruption
| 132/33 kV Transformer-T1 | 2019-07-05 10:10 | 2019-07-05 11:14 | 1:04 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2019-07-06 18:28 | 2019-07-06 18:40 | 0:12 | T | Tripped showing E/F relay 33 kV side | 48 | 9.6 | Power interruption
Kagrachari | 132/33 kV Transformer-T2 | 2019-07-08 07:22 | 2019-07-08 07:32 | 0:10 | T | Tripped showing diff. relay | 15 | 2.5 | Power interruption
Baraulia | 132/33 kV Transformer-T2 | 2019-07-10 17:39 | 2019-07-10 19:19 | 1:40 | T | Tripped showing O/C relay | 10 | 16.6667 | Power interruption
Shahmirpur | 132/33 kV Transformer-T1 | 2019-07-12 11:47 | 2019-07-12 17:20 | 5:33 | T | Tripped showing PRD relay | 15 | 83.25 | Power interruption
Juldah | 132/33 kV Transformer-T2 | 2019-07-12 21:00 | 2019-07-12 23:36 | 2:36 | T | Tripped showing diff. relay | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T1 | 2019-07-13 10:17 | 2019-07-13 10:59 | 0:42 | T | Tripped showing 33 kV feeder fault | 100 | 70 | Power interruption
| 132/33 kV Transformer-T2 | 2019-07-13 10:59 | 2019-07-13 13:29 | 2:30 | T |  | 40 | 100 | Power interruption
Sikalbaha | 132/33 kV Transformer-T4 | 2019-07-13 11:40 | 2019-07-13 13:02 | 4:22 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T2 | 2019-07-16 11:05 | 2019-07-16 12:13 | 1:08 | T | Tripped showing diff. relay | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformers-T1,T2 & T3 | 2019-07-21 18:57 | 2019-07-21 19:55 | 0:58 | T | Tripped showing E/F & O/C relay 33 kV side | 100 | 96.6667 | Power interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2019-07-23 08:18 | 2019-07-23 08:46 | 0:28 | T | Tripped showing without any . relay | 0 | 0 | No interruption
|  |  | Total : | 36:29 |  | Unserved Energy: |  | 523.6833
Cumilla Grid Circle :
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2019-07-07 | 2019-07-07 00:25 | 0:25 | T | Tripped showing O/C relay | 100 | 41.6667 | Power interruption
Feni | 132/33 kV Transformer-T2 | 2019-07-08 10:50 | 2019-07-08 11:50 | 1:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-07-13 05:20 | 2019-07-13 08:52 | 3:32 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2019-07-18 09:35 | 2019-07-18 09:52 | 0:17 | T | Tripped showing 33 kV feeder fault | 44 | 19.0667 | Power interruption 09:35 to 10:01
Fenchuganj | 132/33 kV Transformer-T2 | 2019-07-20 02:19 | 2019-07-20 03:25 | 1:06 | T | Tripped showing backup protection relay | 20 | 22 | Power interruption
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2019-07-20 04:26 | 2019-07-20 05:21 | 0:55 | T | Tripped showing diff. relay | 48 | 44 | Power interruption
Ramganj | 33 kV full Bus | 2019-07-22 07:09 | 2019-07-22 08:11 | 1:02 | E/O | Due to red hot maintenance at 33 kV side | 60 | 62 | Power interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-07-27 09:30 | 2019-07-27 10:12 | 0:42 | E/O | Due to red hot maintenance at 132 kV side | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformers-T1 | 2019-07-31 13:31 | 2019-07-31 13:40 | 0:09 | T | Tripped showing PRD relay | 63 | 9.45 | Power interruption 13:31 to 13:40
| 132/33 kV Transformers-T2 | 2019-07-31 13:31 | 2019-07-31 16:16 | 2:45 | T
|  |  | Total : | 11:53 |  | Unserved Energy: |  | 198.1833
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Khulna© | 132/33 kV Transformer-T3 | 2019-07-01 09:52 | 2019-07-01 11:30 | 1:38 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformer-T5 | 2019-07-01 22:38 | 2019-07-02 09:42 | 0:37 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformers-T1 & T2 | 2019-07-02 10:58 | 2019-07-02 11:03 | 0:05 | T | Tripped showing inst. O/C relay | 74 | 6.1667 | Power interruption
Bagerhat | 132/33 kV Transformer-T1 & T3 | 2019-07-04 10:22 | 2019-07-04 10:34 | 0:12 | T | Tripped showing O/C & E/F relay | 30 | 6 | Power interruption
Goalpara | 132/33 kV Transformer-T5 | 2019-07-04 16:18 | 2019-07-04 16:30 | 0:12 | T | Tripped showing O/C & E/F relay at 33kV side | 12 | 2.4 | Power interruption
Mongla | 132/33 kV Transformers-T1 | 2019-07-10 19:41 | 2019-07-10 19:59 | 0:18 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-07-10 19:41 | 2019-07-10 20:05 | 0:24 | T |  | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformers-T1 & T2 | 2019-07-11 05:56 | 2019-07-11 06:06 | 0:10 | T | Due to 33 kV feeder fault | 35 | 5.8333 | Power interruption
Patuakhali | 132/33 kV Transformer-T3 | 2019-07-09 09:05 | 2019-07-09 10:17 | 1:12 | T | Due to red hot maintenance 33 kV side | 10 | 12 | No interruption
Goalpara | 33 kV Bus | 2019-07-13 07:50 | 2019-07-13 10:53 | 3:03 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-07-16 17:05 | 2019-07-16 17:12 | 0:07 | T | Due to 33 kV feeder fault | 15 | 1.75 | Power interruption
Barisal(S) | 132/33 kV Transformers-T1 & T2 | 2019-07-18 08:16 | 2019-07-18 08:30 | 0:14 | T | Due to 33 kV feeder fault | 20 | 4.6667 | Power interruption
Khulna© | 132/33 kV Transformer-T1 | 2019-07-20 07:23 | 2019-07-20 09:51 | 0:37 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-07-23 05:32 | 2019-07-23 06:01 | 0:29 | T | Due to 33 kV feeder fault | 10 | 4.8333 | Power interruption
Khulna© | 132/33 kV Transformer-T3 | 2019-07-24 16:46 | 2019-07-24 18:25 | 1:39 | E/O | Due to red hot maintenance ae 33 kV side | 5 | 8.25 | Power interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-07-25 06:03 | 2019-07-25 06:26 | 0:23 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2019-07-29 08:44 | 2019-07-29 10:00 | 3:37 | E/O | Due to red hot maintenance ae 33 kV side | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformer-T1 | 2019-07-29 18:24 | 2019-07-29 19:04 | 0:40 | T | Due to 33 kV feeder fault | 15 | 10 | Power interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-07-30 07:39 | 2019-07-30 08:39 | 1:00 | E/O | Due to red hot maintenance ae 33 kV side | 15 | 15 | Power interruption
Patuakhali | 132/33 kV Transformers-T1 & T2 | 2019-07-30 07:32 | 2019-07-30 08:20 | 0:48 | E/O | Due to red hot maintenance ae 33 kV side | 25 | 20 | Power interruption
Napara | 132/33 kV Transformer-T4 | 2019-07-31 13:00 | 2019-07-31 14:00 | 1:00 | E/O | Due to red hot maintenance ae 33 kV side | 25 | 25 | Power interruption
|  |  | Total : | 18:25 |  | Unserved Energy: |  | 121.9
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T1 | 2019-07-04 06:09 | 2019-07-04 10:40 | 4:31 | T | Tripped showing differential relay | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2019-07-07 07:37 | 2019-07-07 09:52 | 2:15 | E/O | Due to red hot maintenance at 33 kV side | 15 | 36.25 | Power interruption
Bottail | 132/33 kV Transformer-T1 | 2019-07-09 04:25 | 2019-07-09 04:48 | 0:23 | E/O | Due to 33 kV CB burst | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-07-09 23:06 | 2019-07-09 23:13 | 0:07 | T | Due to winding tempterature high | 98 | 11.4333 | Power interruption
Ishurdi | 132/33 kV Transformers-T2 | 2019-07-19 09:56 | 2019-07-19 12:11 | 2:15 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2019-07-20 09:30 | 2019-07-20 10:10 | 0:40 | E/O | Due to red hot maintenance at 33 kV side | 5 | 3.3333 | Power interruption
Jhenidah | 132/33 kV Transformers-T1 & T2 | 2019-07-20 10:59 | 2019-07-20 11:13 | 0:14 | T | Tripped showing O/C relay at kV side | 72 | 16.8 | Power interruption
Bottail | 132/33 kV Transformer-T1 | 2019-07-22 07:24 | 2019-07-22 08:32 | 1:08 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Patuakhali | 33 kV Bus-1 | 2019-07-24 08:08 | 2019-07-24 08:52 | 0:44 | E/O | Due to red hot maintenance work | 30 | 22 | Power interruption
|  |  | Total : | 12:17 |  |  |  | 89.8167
Bogura Grid Circle:
Rajshahi | 132/33 kV Transformer-T1 | 2019-07-02 10:42 | 2019-07-02 11:28 | 0:46 | E/O | Due to red hot maintenance at 33 kV side | 18 | 13.8 | Power interruption
Rangpur | 132/33 kV Transformer-T1 | 2019-07-02 11:25 | 2019-07-02 12:15 | 0:50 | E/O | Due to red hot maintenance | 15 | 12.5 | Power interruption
| 132/33 kV Transformer-T2 | 2019-07-02 10:45 | 2019-07-02 11:24 | 0:39 | E/O | Due to red hot maintenance | 15 | 9.75 | Power interruption
Ishurdi | 132/33 kV Transformer-T1 | 2019-07-04 06:09 | 2019-07-04 10:40 | 4:31 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T2 | 2019-07-08 07:08 | 2019-07-08 10:54 | 3:46 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Rangpur | 33 kV Bus-1 & 2 | 2019-07-11 21:30 | 2019-07-11 22:08 | 0:38 | E/O | Due to red hot maintenance | 70 | 44.3333 | Power interruption
Ishurdi | 132/33 kV Transformer-T2 | 2019-07-14 13:57 | 2019-07-14 15:08 | 1:11 | T | Tripped showing no relay | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-07-15 10:38 | 2019-07-15 13:14 | 2:36 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 | 2019-07-15 20:50 | 2019-07-15 23:30 | 2:40 | E/O | Due to red hot maintenance | 20 | 53.3333 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-07-18 10:01 | 2019-07-18 10:05 | 0:04 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Rangpur | 33 kV Bus | 2019-07-19 15:30 | 2019-07-19 16:40 | 1:10 | E/O | Due to red hot maintenance at 33 kV side | 80 | 93.3333 | Power interruption
Rajshahi | 132/33 kV Transformer-T1 | 2019-07-20 21:45 | 2019-07-20 23:10 | 1:25 | E/O | Due to red hot maintenance at 33 kV side | 24 | 34 | Power interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2019-07-24 13:20 | 2019-07-24 13:31 | 0:11 | T | Tripped showing O/C relay at 33 kV side | 5 | 0.91667 | Power interruption
Rangpur | 132/33 kV Transformer-T3 | 2019-07-24 16:40 | 2019-07-24 23:15 | 6:35 | T | Tripped showing 33kV feeder fault | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T4 | 2019-07-28 20:14 | 2019-07-28 20:45 | 0:31 | E/O | Due to red hot maintenance at 33 kV side | 10 | 5.1667 | Power interruption
|  |  | Total : | 27:33 |  | Unserved Energy: |  | 267.1333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 129:07 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-1 | 2019-07-01 20:01 | 2019-07-01 20:31 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| 230 kV Breaker | 2019-07-02 10:02 | 2019-07-02 10:35 | 1:51 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2019-07-09 16:33 | 2019-07-09 16:53 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Kabirpur-Kadda 132 kV line-2 | 2019-07-09 16:33 | 2019-07-09 16:54 | 0:21 | T |  | 0 | 0 | No interruption
| Kabirpur-Manikganj 132 kV line-1 | 2019-07-09 16:38 | 2019-07-09 16:54 | 0:16 | T |  | 250 | 66.6667 | Power interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2019-07-11 00:54 | 2019-07-11 01:03 | 0:09 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2019-07-12 21:47 | 2019-07-12 22:48 | 1:51 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-07-16 12:18 | 2019-07-16 12:33 | 0:15 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2019-07-24 13:01 | 2019-07-24 13:07 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-07-24 13:01 | 2019-07-24 13:17 | 0:16 | T |  | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-kabirpur 132 kV line-1 | 2019-07-25 10:31 | 2019-07-25 10:40 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:04 |  | Unserved Energy: |  | 66.6667
Dhaka (South) Grid Circle :
Madanganj | Madanganj-Haripur 132 kV line-1 | 2019-07-07 11:14 | 2019-07-07 12:56 | 1:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj (S) 230 kV line-1 | 2019-07-07 12:27 | 2019-07-07 13:47 | 1:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
APR | APR-Shyampur (N) 230 kV line | 2019-07-13 17:54 | 2019-07-13 18:04 | 0:10 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 V line-2 | 2019-07-13 18:04 | 2019-07-13 18:16 | 0:12 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2019-07-14 23:29 | 2019-07-15 00:02 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Haripur-Bhulta 132 kV line | 2019-07-14 23:29 | 2019-07-14 23:48 | 0:19 | T | Tripped showing dist. relay | 114 | 36.1 | Power interruption
Siddhirganj | Siddhirganj-Dautch Bangla 132 kV line | 2019-07-14 23:21 | 2019-07-14 23:54 | 0:33 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Siddhirganj-SiddhirganjPeaking 132 132 kV line | 2019-07-14 23:21 | 2019-07-14 23:49 | 0:28 | T | Tripped showing master trip relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2019-07-16 15:35 | 2019-07-16 16:35 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2019-07-24 16:55 | 2019-07-24 17:33 | 0:38 | T | Tripped showing PTAW,PD3,signal | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-2 | 2019-07-26 08:13 | 2019-07-26 11:53 | 3:40 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 6:38 |  | Unserved Energy: |  | 36.1
Chittagong Grid Circle :
Hathazari | Hathazari-Baroihat 132 kV line-1 | 2019-07-01 09:02 | 2019-07-01 09:20 | 0:18 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
| Hathazari-Baroihat 132 kV line-1 | 2019-07-01 09:02 | 2019-07-01 09:20 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hathazari-Baroihat 132 kV line-1 | 2019-07-01 09:43 | 2019-07-01 12:36 | 2:53 | T |  | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha GIS 132 kV line | 2019-07-01 15:05 | 2019-07-01 15:09 | 0:04 | T | Tripped showing O/C relay | 235 | 15.6667 | Power interruption
| Madunaghat-T.K chemical 132 kV line | 2019-07-01 15:05 | 2019-07-01 15:10 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2019-07-01 15:05 | 2019-07-01 16:10 | 1:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line | 2019-07-01 15:05 | 2019-07-01 15:17 | 0:12 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV line | 2019-07-02 06:30 | 2019-07-02 08:34 | 2:04 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV line-2 | 2019-07-03 09:01 | 2019-07-03 11:07 | 2:06 | E/O | Due to gas filling | 0 | 0 | No interruption
Hathazari | Hathazari-Baroihat 132 kV line-1 | 2019-07-10 13:07 | 2019-07-10 13:23 | 0:16 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Hathazari-Baroihat 132 kV line-2 | 2019-07-10 13:07 | 2019-07-10 13:29 | 0:22 | T |  | 0 | 0 | No interruption
| Hathazari-Khulshi 132 kV line | 2019-07-10 13:07 | 2019-07-10 13:24 | 0:17 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-07-10 13:07 | 2019-07-10 13:31 | 0:24 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV line-2 | 2019-07-10 13:07 | 2019-07-10 13:21 | 0:14 | T |  | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2019-07-13 15:12 | 2019-07-13 15:36 | 0:24 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line | 2019-07-16 07:10 | 2019-07-16 18:10 | 11:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 132 kV line | 2019-07-16 13:18 | 2019-07-16 14:53 | 1:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line | 2019-07-16 22:05 | 2019-07-17 00:33 | 2:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-2 | 2019-07-22 06:03 | 2019-07-22 06:50 | 0:47 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-2 | 2019-07-27 15:55 | 2019-07-27 17:51 | 1:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2019-07-27 22:39 | 2019-07-27 23:53 | 1:14 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-1 | 2019-07-28 06:04 | 2019-07-28 07:57 | 1:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 31:55 |  | Unserved Energy: |  | 15.6667
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-1 | 2019-07-10 22:56 | 2019-07-10 23:56 | 1:00 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2019-07-12 10:55 | 2019-07-12 11:20 | 0:25 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-2 | 2019-07-12 10:55 | 2019-07-12 12:57 | 2:02 | T |  | 0 | 0 | No interruption
| Bibiyana-Cumilla(N) 230 kV line-1 & 2 | 2019-07-12 10:55 | 2019-07-12 12:39 | 1:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 132 line | 2019-07-12 10:26 | 2019-07-12 11:00 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line | 2019-07-15 07:40 | 2019-07-15 07:47 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
B.Baria | B.Baria-Narsinghdi 132 kV line-1 | 2019-07-15 09:15 | 2019-07-15 09:22 | 0:07 | T | Tripped showing dist. relay | 25 | 2.9167 | Power interruption 09:15 to 9:22
| B.Baria-Narsinghdi 132 kV line-2 | 2019-07-15 09:15 | 2019-07-15 09:23 | 0:08 | T
| B.Baria-Ashuganj 132 kV line-2 | 2019-07-17 11:30 | 2019-07-18 12:35 | 25:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 | 2019-07-17 12:37 | 2019-07-17 12:49 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line | 2019-07-22 11:02 | 2019-07-22 18:03 | 7:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 | 2019-07-24 08:18 | 2019-07-24 08:37 | 0:19 | T | Tripped showing dist. & O/C relay | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-2 | 2019-07-31 18:27 | 2019-07-31 21:29 | 3:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 41:46 |  | Unserved Energy: |  | 2.9167
Khulna Grid Circle :
Barisal(N) | Barisal(N)-Madaripur 132 kV line-2 | 2019-07-13 12:27 | 2019-07-13 12:42 | 0:15 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-07-17 07:14 | 2019-07-17 11:10 | 3:56 | E/O | Due to red hot maintenance | 40 | 157.3333 | Power interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-07-17 19:22 | 2019-07-18 18:59 | 23:37 | T | Tripped showing dist. relay | 32 | 755.7333 | Power interruption
Goalpara | Goalpara-orion P/S 132 kV line | 2019-07-20 15:50 | 2019-07-20 16:20 | 0:30 | T | Tripped showing diff. relay | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-2 | 2019-07-20 15:50 | 2019-07-20 16:20 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-2 | 2019-07-31 10:47 | 2019-07-31 11:14 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj P/S | Gopalganj P/S-Gopalganj S/S 132 kV line | 2019-07-31 10:49 | 2019-07-31 14:40 | 3:51 | T | Tripped showing TCSR relay | 0 | 0 | No interruption
|  |  | Total : | 33:06 |  | Unserved Energy: |  | 913.0667
HVDC Grid Circle :
Jhenidah | Jhenidah-Chuadanga 132 kV line | 2019-07-06 11:29 | 2019-07-06 11:40 | 0:11 | T | Tripped showing dist. relay | 46 | 8.4333 | Power interruption
HVDC | HVDC-Khulna(S) 230 kV line-1 | 2019-07-11 13:16 | 2019-07-11 15:49 | 2:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Khulna(S) 230 kV line-2 | 2019-07-16 05:14 | 2019-07-16 08:11 | 2:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2019-07-18 15:34 | 2019-07-18 16:06 | 0:32 | T | Tripped showing dist. PTaW,PD3 signal | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-2 | 2019-07-25 09:47 | 2019-07-25 12:01 | 2:14 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
|  |  | Total : | 8:27 |  | Unserved Energy: |  | 8.4333
Bogura Grid Circle :
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2019-07-01 20:45 | 2019-07-01 20:50 | 0:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2019-07-02 20:45 | 2019-07-02 20:52 | 0:07 | T |  | 22 | 2.5667 | Power interruption
Ishurdi | Ishurdi-Ghorashal 132 kV line-2 | 2019-07-07 20:52 | 2019-07-07 21:45 | 1:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 132 kV line-1 | 2019-07-15 03:26 | 2019-07-16 11:07 | 31:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Natore | Natore-Rajsahahi 132 kV line-1 | 2019-07-17 08:01 | 2019-07-17 08:16 | 0:15 | T | Tripped showing E/F. relay | 170 | 39.6667 | Power interruption 08:01 to 08:16
| Natore-Rajsahahi 132 kV line-2 | 2019-07-17 08:01 | 2019-07-17 17:05 | 9:04 | T
Saidpur | Saidpur-Purbasadipur 132 kV line | 2019-07-22 09:20 | 2019-07-22 09:31 | 0:11 | T | Tripped showing O/C. relay | 134 | 24.5667 | Power interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2019-07-25 15:10 | 2019-07-25 15:16 | 0:06 | T | Tripped showing dist.(C-phase) relay | 64 | 6.4 | Power interruption
| Rangpur-Lalmonirhat 132 kV line | 2019-07-30 12:05 | 2019-07-30 12:38 | 0:33 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2019-07-31 01:59 | 2019-07-31 10:40 | 8:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 51:48 |  | Unserved Energy: |  | 73.2
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2019-07-15 01:58 | 2019-07-16 08:18 | 30:20 | T | Tripped showing main protection relay | 0 | 0 | No interruption
|  |  | Total : | 30:20 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 210:04 | Hours |  |  | Executive Engineer
T = Tripping | [7 empty] | Information Management Division
E/O = Emergency Outage | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV Transformer-T3 | 2019-07-03 16:40 | 2019-07-03 17:32 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 33 kV Bus &132/33 kV Transformer-T2 | 2019-07-05 06:11 | 2019-07-05 08:10 | 1:59 | S/O | Due to C/M work | 25 | 49.5833 | Power interruption
| 132/33 kV Transformer-T1 | 2019-07-05 08:41 | 2019-07-05 10:24 | 1:43 | S/O | Due to C/M work | 40 | 68.6667 | Power interruption
Tongi | 33 kV Bus | 2019-07-06 10:50 | 2019-07-06 12:15 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-ICT2 | 2019-07-06 08:59 | 2019-07-06 17:58 | 8:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2019-07-12 06:09 | 2019-07-12 09:07 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamarai | 132/33 kV Transformer-T2 | 2019-07-13 08:34 | 2019-07-13 17:28 | 8:54 | S/O | Due to 33 kV bus extension work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-07-13 10:30 | 2019-07-13 13:30 | 3:00 | S/O | Due to T-connection of bus section-4 | 60 | 180 | Power interruption
| 132/33 kV Transformer-T4 | 2019-07-15 13:30 | 2019-07-15 14:35 | 1:05 | S/O | Due to LT fault | 10 | 10.8333 | Power interruption
Sherpur | 132/33 kV Transformer-T2 | 2019-07-16 11:36 | 2019-07-16 13:05 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2019-07-17 07:04 | 2019-07-17 08:59 | 1:55 | S/O | Due to C/M work | 60 | 115 | Power interruption
Bibiyana | 400/230 kV Transformer-ICT1 | 2019-07-17 08:15 | 2019-07-17 15:11 | 6:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-07-17 10:31 | 2019-07-17 17:05 | 6:34 | S/O | Due to PBS work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2019-07-18 06:30 | 2019-07-18 07:32 | 1:02 | S/O | Due to maintenance work at 33 kV side | 45 | 46.5 | Power interruption
Dhamarai | 132/33 kV Transformer-T1 | 2019-07-19 08:56 | 2019-07-19 16:10 | 7:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-07-20 09:51 | 2019-07-20 13:48 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamarai | 132/33 kV Transformer-T2 | 2019-07-21 08:27 | 2019-07-21 16:23 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-07-21 10:40 | 2019-07-21 11:24 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 33 kV Bus -1 | 2019-07-22 01:20 | 2019-07-22 02:58 | 1:38 | S/O | Due to maintenance work at 33 kV side | 41 | 66.9667 | Power interruption
Mirpur | 132/33 kV Transformer-T3 | 2019-07-23 09:34 | 2019-07-23 15:50 | 6:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-07-24 08:02 | 2019-07-24 10:02 | 2:00 | S/O | Due to replacement of PT | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2019-07-24 13:33 | 2019-07-24 15:16 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-07-24 09:18 | 2019-07-24 12:35 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-07-24 15:58 | 2019-07-24 16:55 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamarai | 132/33 kV Transformer-T1 | 2019-07-26 09:15 | 2019-07-26 16:48 | 7:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2019-07-27 06:31 | 2019-07-27 08:07 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2019-07-27 07:22 | 2019-07-27 08:35 | 1:13 | S/O | Due to C/M work | 70 | 85.1667 | Power interruption
Kishorganj | 132/33 kV Transformer-T3 | 2019-07-28 23:20 | 2019-07-28 23:45 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 33 kV Bus-2 | 2019-07-29 11:20 | 2019-07-29 12:54 | 1:34 | S/O | Due to PBS work | 0 | 0 | No interruption
|  |  | Total : | 96:54 |  | Unserved Energy: |  | 622.7167
Dhaka (South) Grid Circle :
Narsinghdi | 132/33 kV Transformer-T1 | 2019-07-01 17:47 | 2019-07-01 19:07 | 1:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shyampur | 230/132 kV Transformer-T1 | 2019-07-05 11:13 | 2019-07-05 17:02 | 5:49 | S/O | Due to project work | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T2 | 2019-07-06 07:05 | 2019-07-06 15:46 | 8:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2019-07-13 05:14 | 2019-07-13 08:34 | 3:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-07-20 05:08 | 2019-07-20 08:38 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2019-07-26 07:38 | 2019-07-26 10:20 | 2:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2019-07-26 07:35 | 2019-07-26 10:02 | 2:27 | S/O | Due to C/M work | 15 | 9.75 | Power interruption
Gulshan | 132/33 kV Transformer-T1 | 2019-07-27 05:31 | 2019-07-27 06:48 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2019-07-27 06:37 | 2019-07-27 13:10 | 6:33 | S/O | Due to D/W work | 15 | 98.25 | Power interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2019-07-27 06:52 | 2019-07-27 13:20 | 6:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132 kV main Bus | 2019-07-29 10:27 |  |  | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 42:07 |  | Unserved Energy: |  | 108
Page: 2/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformer-T1 | 2019-07-01 08:20 | 2019-07-01 08:45 | 0:25 | S/O | Due to CB pole maintenance | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2019-07-01 12:36 | 2019-07-01 17:49 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-07-04 06:14 | 2019-07-04 06:22 | 0:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus-2 | 2019-07-05 11:39 | 2019-07-05 14:42 | 3:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230 kV main Bus | 2019-07-12 06:47 | 2019-07-12 15:30 | 8:43 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | 132 kV GIS Bus-2 | 2019-07-12 08:51 | 2019-07-12 10:00 | 1:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T2 | 2019-07-12 09:03 | 2019-07-12 16:11 | 7:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV Transformer-T1 | 2019-07-14 13:22 | 2019-07-14 13:58 | 0:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
Halishahar | 33 kV Bus | 2019-07-16 13:29 | 2019-07-16 13:38 | 0:09 | S/O | Due to C/M work | 40 | 6 | Power interruption
T.K chemical | 132 kV Bus | 2019-07-16 08:12 | 2019-07-16 16:52 | 8:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132 kV Bus | 2019-07-19 06:18 | 2019-07-19 10:34 | 4:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT2 | 2019-07-21 18:24 | 2019-07-21 18:24 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 | 2019-07-22 15:46 | 2019-07-22 16:55 | 1:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2019-07-25 14:52 | 2019-07-25 16:01 | 1:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV Transformer-T3 | 2019-07-27 14:24 | 2019-07-27 15:30 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformers-T1 & T2 | 2019-07-29 15:01 | 2019-07-29 16:38 | 1:37 | S/O | Due to replacement work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2019-07-30 14:47 | 2019-07-30 15:25 | 0:38 | S/O | Due to replacement work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2019-07-31 15:13 | 2019-07-31 16:36 | 1:23 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 46:32 |  | Unserved Energy : |  | 6
Cumilla Grid Circle :
Biyanibazar | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-07-10 11:09 | 2019-07-10 14:17 | 3:08 | S/O | Due to D/W by PBS | 10 | 146.6667 | Power interruption
Chandpur | 132/33 kV Transformer-T1 & 33 kV Bus-1 | 2019-07-12 09:15 | 2019-07-12 13:00 | 3:45 | S/O |  | 15 | 56.25 | Power interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-07-13 09:11 | 2019-07-13 12:20 | 3:09 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-07-13 13:13 | 2019-07-13 15:25 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-07-14 09:30 | 2019-07-14 11:19 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2019-07-14 15:17 | 2019-07-14 19:27 | 4:10 | S/O | Due to replacement work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2019-07-16 10:08 | 2019-07-16 12:51 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2019-07-17 15:24 | 2019-07-17 19:04 | 3:40 | S/O | Due to C/M work at 33 kV side | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 | 2019-07-19 14:13 | 2019-07-19 14:13 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-07-20 07:12 | 2019-07-20 19:01 | 11:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-07-27 16:15 | 2019-07-27 16:55 | 0:40 | S/O | Due to C/M work | 55 | 36.6667 | Power interruption
|  |  | Total : | 37:05 |  | Unserved Energy : |  | 239.5833
Khulna Grid Circle :
Barisal(N) | 132/33 kV Transformers-T1 & T2 | 2019-07-04 12:35 | 2019-07-04 13:35 | 1:00 | S/O | Due to maintenance of 33 kV feeder | 11 | 11 | Power interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-07-09 06:19 | 2019-07-09 07:24 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformer-T2 | 2019-07-10 06:26 | 2019-07-10 07:49 | 1:23 | S/O | Due to replacement work | 0 | 0 | No interruption
Bagerhat | 33 kV Bus | 2019-07-12 06:29 | 2019-07-12 12:20 | 5:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformer-T2 | 2019-07-12 06:20 | 2019-07-12 08:03 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2019-07-12 08:24 | 2019-07-12 09:11 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2019-07-13 08:05 | 2019-07-13 09:44 | 1:39 | S/O | Due to D/W work | 25 | 41.25 | Power interruption
| 132/33 kV Transformer-T1 | 2019-07-13 10:42 | 2019-07-13 12:31 | 1:49 | S/O | Due to C/M work | 20 | 36.3333 | Power interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-07-13 15:20 | 2019-07-13 15:44 | 0:24 | S/O | Due to changing work | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Noapara | 132/33 kV Transformer-T4 | 2019-07-15 09:57 | 2019-07-15 11:14 | 1:17 | S/O | Due to temperature of high at 33 kV Breaker | 30 | 38.5 | Power interruption
Khulna(S) | 230/132 kV Transformer-T3 | 2019-07-17 14:36 | 2019-07-17 14:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sariatpur | 33 kV full Bus | 2019-07-20 08:11 | 2019-07-20 14:15 | 6:04 | S/O | Due to D/W work | 20 | 121.3333 | Power interruption
Barisal(N) | 33 kV Bus | 2019-07-20 08:25 | 2019-07-20 11:10 | 2:45 | S/O | Due to replacement work | 20 | 55 | Power interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2019-07-21 09:27 | 2019-07-21 10:27 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2019-07-27 08:05 | 2019-07-27 10:12 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-07-27 10:44 | 2019-07-27 14:10 | 3:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformers-T4 ,T5 & 33 kV Bus | 2019-07-27 09:13 | 2019-07-27 17:52 | 8:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2019-07-28 09:14 | 2019-07-28 14:36 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-07-28 15:19 | 2019-07-28 17:45 | 2:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T3 | 2019-07-31 11:47 | 2019-07-31 13:50 | 2:03 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 49:50 |  | Unserved Energy : |  | 303.4167
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T2 | 2019-07-11 22:25 | 2019-07-13 18:10 | 43:45 | S/O | Due to project work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T2 | 2019-07-12 07:08 | 2019-07-13 08:25 | 25:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Kustia | 132/33 kV Transformer-T1 | 2019-07-12 07:21 | 2019-07-12 12:21 | 5:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Benapole | 132/33 kV Transformer-T2 | 2019-07-20 09:52 | 2019-07-20 15:50 | 5:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-07-24 16:18 | 2019-07-24 20:48 | 4:30 | S/O | Due to protection test | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-07-27 08:40 | 2019-07-27 10:38 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-07-27 08:30 | 2019-07-27 09:13 | 0:43 | S/O | Due to 33 kV feeder maintenance | 35 | 25.0833 | Power interruption
Jessore | 132/33 kV Transformer-T3 | 2019-07-28 12:05 | 2019-08-03 17:44 | 149:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | 230/33 kV auxiliary Transformer | 2019-07-29 10:58 | 2019-07-29 16:42 | 5:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T2 | 2019-07-31 07:24 | 2019-07-31 07:43 | 0:19 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 199:08 |  | Unserved Energy : |  | 25.0833
Bogura Grid Circle:
Bogura | 132 kV main bus | 2019-07-03 08:35 | 2019-07-03 13:30 | 4:55 | S/O | Due to C/M work | 60 | 97 | Power interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-07-03 09:28 | 2019-07-03 13:52 | 4:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV Transformer-T2 | 2019-07-03 12:15 | 2019-07-03 17:00 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-07-04 09:35 | 2019-07-04 17:50 | 8:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T1 | 2019-07-05 08:42 | 2019-07-15 17:27 | 248:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 33 kV main bus | 2019-07-05 09:31 | 2019-07-05 09:52 | 0:21 | S/O | Due to changing work | 35 | 12.25 | Power interruption
Jaldhaka | 132/33 kV Transformer-T2 | 2019-07-06 09:45 | 2019-07-06 17:30 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T2 | 2019-07-08 15:45 | 2019-07-08 16:20 | 0:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jaldhaka | 132 kV main bus-1 & 2 | 2019-07-10 10:05 | 2019-07-10 17:55 | 7:50 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main bus-1 & 2 | 2019-07-11 09:57 | 2019-07-11 16:52 | 6:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Palasbari | 33 kV bus | 2019-07-11 09:20 | 2019-07-11 10:40 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132 kV bus-A | 2019-07-12 07:30 | 2019-07-12 09:05 | 1:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 |  | 2019-07-12 10:50 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T03 | 2019-07-13 12:57 | 2019-07-13 16:53 | 3:56 | S/O | Due to DFR work by Energypac | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2(New) |  | 2019-07-13 18:10 |  |  | Due to maintenance work | 0 | 0 | No interruption
Page: 4/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Natore | 132/33 kV Transformer-T3 | 2019-07-13 22:14 | 2019-07-13 23:17 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 |  | 2019-07-15 17:27 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T1 | 2019-07-18 11:56 | 2019-07-18 12:11 | 0:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ishurdi | 33 kV main bus | 2019-07-19 06:34 | 2019-07-19 09:10 | 2:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | 132 kV bus-A | 2019-07-19 09:45 | 2019-07-19 17:30 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV bus & 132/33 kV Transformer T2 | 2019-07-20 07:20 | 2019-07-20 09:20 | 2:00 | S/O | Due to C/M work | 40 | 80 | Power interruption
Kurigram | 132/33 kV Transformer-T1 | 2019-07-21 20:20 | 2019-07-21 21:38 | 1:18 | S/O | Due to Oil leavel checking | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-07-24 07:22 | 2019-07-24 10:45 | 3:23 | S/O | Due to replacement work at 33 kV side | 18 | 60.9 | Power interruption
Sirajganj | 132/33 kV Transformer-T1 | 2019-07-25 15:17 | 2019-07-25 15:32 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 |  | 2019-07-25 14:35 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T1 | 2019-07-26 07:11 | 2019-07-26 10:43 | 3:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2019-07-28 15:26 | 2019-07-28 17:03 | 1:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T1 |  | 2019-07-29 16:24 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 325:05 |  | Unserved Energy : |  | 250.15
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 796:41 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2019-07-01 06:06 | 2019-07-01 10:08 | 4:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-1 | 2019-07-13 06:13 | 2019-07-13 07:27 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2019-07-17 09:30 | 2019-07-17 23:17 | 13:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Bibiyana P/S 132 kV line | 2019-07-17 10:42 | 2019-07-17 11:20 | 0:38 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-07-20 09:38 | 2019-07-20 19:15 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Valuka | Valuka-Mymensingh 132 kV line-1 & 2 | 2019-07-20 14:39 | 2019-07-20 14:50 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line | 2019-07-21 08:43 | 2019-07-21 19:08 | 10:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2019-07-22 09:40 | 2019-07-22 11:56 | 2:16 | S/O | Due to energy meter commissioning | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-07-22 13:18 | 2019-07-22 14:37 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2019-07-23 10:04 | 2019-07-23 14:56 | 4:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-07-24 09:25 | 2019-07-24 12:39 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2019-07-25 06:14 | 2019-07-25 10:56 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 51:03 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-07-06 06:53 | 2019-07-07 00:05 | 17:12 | S/O | Due to project work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar 132 kV line | 2019-07-06 06:53 | 2019-07-06 23:52 | 16:59 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Madartek 132 kV line-2 | 2019-07-07 12:08 | 2019-07-07 18:07 | 5:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-07-07 13:05 | 2019-07-07 15:40 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-2 | 2019-07-08 09:03 | 2019-07-08 15:22 | 6:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line |  | 2019-07-15 23:39 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-B.baria 132 kV line-1 | 2019-07-19 14:45 | 2019-07-19 20:26 | 5:41 | S/O | Due to project work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-07-21 08:53 | 2019-07-21 17:14 | 8:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-2 | 2019-07-22 06:47 | 2019-07-22 16:50 | 10:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-07-22 08:08 | 2019-07-22 13:30 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-2 | 2019-07-23 08:40 | 2019-07-23 12:01 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-07-24 07:55 | 2019-07-24 14:55 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Dautch Bangla 132 kV line | 2019-07-24 06:13 | 2019-07-24 12:07 | 5:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-07-26 07:41 | 2019-07-26 10:20 | 2:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-2 | 2019-07-30 06:57 | 2019-07-30 09:39 | 2:42 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 100:07 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2019-07-01 09:16 | 2019-07-01 16:43 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV line-2 | 2019-07-03 09:25 | 2019-07-03 10:58 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sikalbaha-Juldah 132 kV line-1 | 2019-07-09 09:12 | 2019-07-09 12:22 | 3:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV line-1 | 2019-07-10 09:32 | 2019-07-10 11:19 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K.chemical 132 kV line 132 kV line | 2019-07-11 08:50 | 2019-07-11 10:48 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line | 2019-07-12 05:32 | 2019-07-12 06:47 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line | 2019-07-13 06:04 | 2019-07-13 17:10 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2019-07-15 13:43 | 2019-07-15 13:54 | 2:17 | S/O | Due to tree trimming | 0 | 0 | No interruption
Sikalbaha GIS | Sikalbaha GIS-TK 132 kV line | 2019-07-17 10:34 | 2019-07-17 11:48 | 1:14 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha -Anwara 230 kV line-2 | 2019-07-18 09:23 | 2019-07-18 11:30 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Anwara | Anwara-Silkalbaha 230 kV line-2 | 2019-07-19 10:55 | 2019-07-19 12:40 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-1 | 2019-07-19 06:12 | 2019-07-19 17:57 | 11:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madunaghat-TK. chemical 132 kV line | 2019-07-22 08:15 | 2019-07-22 11:22 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-B.Baria 132 kV line-2 | 2019-07-23 10:02 | 2019-07-23 18:55 | 8:53 | S/O | Due to replacement work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-1 | 2019-07-26 05:54 | 2019-07-26 18:11 | 12:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line-1 | 2019-07-27 08:52 | 2019-07-27 13:08 | 4:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2019-07-28 05:52 | 2019-07-28 07:57 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2019-07-29 06:16 | 2019-07-29 08:33 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 | 2019-07-30 06:57 | 2019-07-30 08:10 | 1:13 | S/O | Due to winding temperature high | 0 | 0 | No interruption
|  |  | Total : | 68:45 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj | Ashuganj -Kishoreganj 132 kV line-2 | 2019-07-18 09:24 | 2019-07-18 16:31 | 7:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj -CumillaN) 230 kV line-1 | 2019-07-19 11:24 | 2019-07-19 19:26 | 8:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj -CumillaN) 230 kV line-2 | 2019-07-19 11:26 | 2019-07-19 19:28 | 8:02 | S/O |  | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV line | 2019-07-20 08:40 | 2019-07-20 21:05 | 12:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroarhat 132 kV line-2 | 2019-07-22 08:48 | 2019-07-22 15:52 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| Feni-Baroarhat 132 kV line-1 | 2019-07-22 07:51 | 2019-07-22 14:58 | 7:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-07-23 14:30 | 2019-07-23 17:17 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 52:34 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | Barisal-Bhandaria 132 kV line | 2019-07-06 11:53 | 2019-07-06 13:54 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakahli | Patuakahli-Paira 132 kV line-1 | 2019-07-13 17:47 | 2019-07-13 17:47 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barisal | Barisal-Paira 132 kV line-1 | 2019-07-14 07:37 | 2019-07-15 11:01 | 27:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-07-14 08:48 | 2019-07-14 08:57 | 0:09 | S/O | Due to replacement work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2019-07-17 13:07 |  |  | S/O | Due to reconductioning work for about 20 days | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2019-07-28 09:57 | 2019-07-28 12:20 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| Faridpur-Madaripur 132 kV line-2 | 2019-07-28 12:47 | 2019-07-28 15:33 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 34:43 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ruppur 132 kV line-1 | 2019-07-01 12:42 | 2019-07-01 16:47 | 4:05 | S/O | Due to project ork | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV line-2 | 2019-07-01 16:50 | 2019-07-01 18:27 | 1:37 | S/O | Due to project work | 0 | 0 | No interruption
| Ishurdi-Baghabari 230 kV line-2 | 2019-07-13 11:06 | 2019-07-13 12:14 | 1:08 | S/O | Due to remove nest at Baghabari S/S | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-1 | 2019-07-17 18:03 | 2019-07-17 20:20 | 2:17 | S/O | Due to project work | 0 | 0 | No interruption
| Jessore-Benapole 132 kV line-1 | 2019-07-18 10:30 | 2019-07-18 16:22 | 5:52 | S/O | Due to project work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2019-07-19 08:17 | 2019-07-19 18:49 | 10:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-2 | 2019-07-20 09:56 | 2019-07-24 15:34 | 101:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jessore-Benapole 132 kV line-1 | 2019-07-24 15:58 | 2019-07-24 20:42 | 4:44 | S/O | Due to protection test | 0 | 0 | No interruption
|  |  | Total : | 131:53 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura-Natore 132 kV line-2 | 2019-07-03 08:50 | 2019-07-03 13:57 | 5:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Joldhaka 132 kV line-2 | 2019-07-05 10:15 | 2019-07-05 18:10 | 7:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Joldhaka | Joldhaka-Saidpur 132 kV line-1 | 2019-07-07 09:50 | 2019-07-07 23:41 | 13:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohathangar 132 kV line-2 | 2019-07-08 08:10 | 2019-07-08 10:23 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2019-07-11 13:31 | 2019-07-11 13:55 | 0:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line-1 & 2 | 2019-07-19 06:05 | 2019-07-19 12:06 | 6:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura -Sirajganj 132 kV line-1 & 2 | 2019-07-19 06:07 | 2019-07-19 12:13 | 6:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2019-07-19 09:10 | 2019-07-19 14:07 | 4:57 | S/O | Due to D/W work | 50 | 247.5 | Power interruption
| Rangpur-Saidpur 132 kV line-1 | 2019-07-20 17:30 | 2019-07-20 22:45 | 5:15 | S/O | Due to CB problem | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2019-07-23 14:40 | 2019-07-23 15:36 | 0:56 | S/O | Due to replacement work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line-1 | 2019-07-24 08:15 | 2019-07-24 10:55 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2019-07-30 05:52 | 2019-07-30 08:57 | 3:05 | S/O | Due to C/M work | 65 | 200.4167 | Power interruption
Bogura(O) | Bogura(O)-Mohastanghor 132 kV line-1 | 2019-07-30 06:06 | 2019-07-30 07:42 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line-1 | 2019-07-31 09:26 | 2019-07-31 10:46 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 61:26 |  | Unserved Energy: |  | 447.9167
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 500:31 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July' 2019
| Area | Previous Month (June 2019) |  |  |  | Current Month (July 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 24 | 11 | 33 | 68 | 13 | 7 | 41 | 61
2 | Dhaka (South) Grid Circle. | 9 | 8 | 20 | 37 | 12 | 3 | 26 | 41
3 | Chattogram Grid Circle. | 7 | 10 | 23 | 40 | 29 | 12 | 36 | 77
4 | Cumilla Grid Circle. | 17 | 9 | 24 | 50 | 20 | 3 | 18 | 41
5 | Khulna Grid Circle. | 9 | 16 | 12 | 37 | 15 | 10 | 28 | 53
6 | Bheramara HVDC Grid Circle | 8 | 3 | 6 | 17 | 10 | 7 | 18 | 35
7 | Bogura Grid Circle. | 15 | 10 | 12 | 37 | 13 | 12 | 42 | 67
8 | Others |  | 1 | 1 | 2 | 1 |  |  | 1
9 | Total | 89 | 68 | 131 | 288 | 113 | 54 | 209 | 376
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July' 2019
| Area | Previous Month (June 2019) |  |  |  | Current Month (July 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 376.05 | 68.34 | 473.67 | 918.06 | 246.7 | 1021.66 | 622.72 | 1891.08
2 | Dhaka (South) Grid Circle. | 20.08 | 11 | 244.2 | 275.28 | 66.4 | 75.33 | 108 | 249.73
3 | Chattogram Grid Circle. | 180.25 | 192.37 | 72 | 444.62 | 394.35 | 145 | 6 | 545.35
4 | Cumilla Grid Circle. | 186.11 | 160.9 | 227.92 | 574.93 | 139.1 | 62 | 239.58 | 440.68
5 | Khulna Grid Circle. | 13.56 | 641.63 | 55.73 | 710.92 | 809.38 | 225.58 | 303.42 | 1338.38
6 | Bheramara HVDC Grid Circle | 29.5 | - | - | 29.5 | 36.66 | 61.58 | 25.08 | 123.32
7 | Bogura Grid Circle. | 263.33 | 179.42 | 325 | 767.75 | 74.12 | 266.22 | 698.07 | 1038.41
8 | Others | - | 313.2 | - | 313.2 | - | - | - | 0
9 | Total | 1068.88 | 1566.86 | 1398.52 | 4034.26 | 1766.71 | 1857.37 | 2002.87 | 5626.95
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 7 | 8 | 15 | 5 | 1 | 9 | 1824.42
2 | Dhaka (South) | 5031.6 | 2 | 2 | 4 | 1 | - | 3 | 213.63
3 | Chattogram | 2042 | 9 | 1 | 10 | 3 | 2 | 5 | 529.68
4 | Khulna | 2434 | 12 | 6 | 18 | 7 | 5 | 6 | 425.32
5 | Bheramara (HVDC) | 2423.3 | 3 | 1 | 4 | 1 | 1 | 2 | 114.89
6 | Bogura | 3145.6 | 9 | 4 | 13 | 1 | 5 | 7 | 517.28
7 | Cumilla | 2981 | 6 | 3 | 9 | 3 | 2 | 4 | 437.76
| Total | 23365.5 | [6 empty] | 4062.98
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.92%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.83%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.94% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 | 1 | - | - | 66.67
2 | Dhaka (South) | 990.29 |  | 1 |  | 1 | 1 | - |  | 36.1
3 | Chattogram | 917 | 20+9(Partial) | 1 | - | 1 | 1 | - | - | 15.67
4 | Khulna | 1238.4 | 21 | 2 | - | 2 | - | - | 2 | 913.07
5 | Bheramara (HVDC) | 598.7 |  | 1 | - | 1 | 1 | - | - | 8.43
6 | Bogura | 1803.3 | 38 | 4 | 2 | 6 | 4 |  | 2 | 521.12
7 | Cumilla | 1648.16 | 17 | 1 |  | 1 | 1 |  | - | 2.92
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1563.98
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.91%
4 | Khulna | 99.91%
5 | Bheramara (HVDC) | 99.76% | [7 empty] | Executive Engineer
6 | Bogura | 99.78% | [7 empty] | Information Management Division
7 | Cumilla | 99.9% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-07-18 | 18 |  | 4 | 03hr47min | 1 | 3hr56min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:July' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 0:17 | 106 | 30.0333 | Due to tripping of 132/33 kV Transformers T1, T2 & T3
Jodevpur |  | 0:01 | 70 | 70 | Due to tripping of 132/33 kV Transformers T3,& T4
Jamalpur | 1 | 0:34 | 50 | 28.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Valuka | 1 | 12:25 | 80 | 993.3333 | Due to tripping of 132/33 kV Transformers T1,& T2
Jodevpur | 1 | 0:08 | 25 | 3.3333 | Due to tripping of 132/33 kV Transformers T3 & T4
Mirpur | 1 | 0:20 | 70 | 23.3333 | Due to tripping of 132/33 kV Transformer T2
Jodevpur | 1 | 0:04 | 80 | 53.3333 | Due to tripping of 132/33 kV Transformers T3 & T4
Mymensingh | 2 | 1:59 | 25 | 49.5833 | Due to S/D of 132/33 kV Transformer T2
|  | 1:43 | 40 | 68.6667 | Due to S/D of 132/33 kV Transformer T1
Jamalpur |  | 3:00 | 60 | 180 | Due to S/D of 132/33 kV Transformer T4
|  | 1:05 | 10 | 10.8333 | Due to S/D of 132/33 kV Transformer T4
Tangail | 1 | 1:55 | 60 | 115 | Due to S/D of 132/33 kV Transformer T2
Kabirpur |  | 1:02 | 45 | 46.5 | Due to S/D of 132/33 kV Transformer T3
|  | 0:16 | 250 | 66.6667 | Due to tripping of Kabirpur-Manikganj 132 kV line-1
Tongi | 1 | 1:38 | 41 | 66.9667 | Due to S/D of 33 kV Bus-1
Mymensingh | 1 | 1:13 | 70 | 85.1667 | Due to S/D of 132/33 kV Transformer T2
Hasnabad | 1 | 0:18 | 101 | 30.3 | Due to tripping of 132/33 kV Transformers T1,& T2
Munshuganj | 1 | 1:53 | 40 | 75.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Haripur | 1 | 0:19 | 114 | 36.1 | Due to tripping of Haripur-Bhulta 132 kV line
Siddhirganj | 1 | 2:27 | 15 | 9.75 | Due to S/D of 132/33 kV Transformer T2
Maniknagar | 1 | 6:33 | 15 | 98.25 | Due to S/D of 132/33 kV Transformer T2
Hathazari | 1 | 1:45 | 60 | 105 | Due to red-hot maintenance of 132/33 kV Transformer T1
Juldah | 1 | 2:30 | 16 | 40 | Due to red-hot maintenance of 132 kV Bus
Madunaghat |  | 0:12 | 48 | 9.6 | Due to red-hot maintenance of 132/33 kV Transformer T1
Kagrachari |  | 0:10 | 15 | 2.5
Baraulia | 2 | 1:40 | 10 | 16.6667 | Due to tripping of 132/33 kV Transformer T2
Shahmirpur |  | 5:33 | 15 | 83.25 | Due to tripping of 132/33 kV Transformer T1
Khulshi | 2 | 0:42 | 100 | 70 | Due to tripping of 132/33 kV Transformer T1
|  | 2:30 | 40 | 100 | Due to tripping of 132/33 kV Transformer T2
Halishahar | 1 | 0:58 | 100 | 96.6667 | Due to tripping of 132/33 kV Transformers T1 ,T2 & T3
Madunaghat | 1 | 0:04 | 235 | 15.6667 | Due to tripping of Madunaghat-Sikalbaha 132 kV line
Sikalbaha | 1 | 0:09 | 40 | 6 | Due to S/D of 33 kV Bus
Cumilla(N) | 2 | 0:25 | 100 | 41.6667 | Due to tripping of 132/33 kV Transformers T3 & T4
|  | 0:17 | 44 | 19.0667
Fenchuganj | 1 | 1:06 | 20 | 22 | Due to tripping of 132/33 kV Transformer T2
Cumilla(N) | 1 | 0:55 | 48 | 44 | Due to tripping of 132/33 kV Transformers T3 & T4
Ramganj | 1 | 1:02 | 60 | 62 | Due to red-hot maintenance of 33 kV full Bus
Chandpur | 1 | 0:09 | 63 | 9.45 | Due to tripping of 132/33 kV Transformer T1
B.Baria |  | 0:07 | 25 | 2.9167 | Due to tripping of B.Baria-Narsinghdi 132 kV line-1
Biyanibazar | 1 | 3:08 | 10 | 146.6667 | Due to S/D of 132/33 kV Transformer T2 & 33 kV Bus
Chandpur | 1 | 3:45 | 15 | 56.25 | Due to S/D of 132/33 kV Transformer T1 & 33 kV Bus
Cumilla(N) | 1 | 0:40 | 55 | 36.6667 | Due to S/D of 132/33 kV Transformer T3
Barisal(S) |  | 0:05 | 74 | 6.1667 | Due to tripping of 132/33 kV Transformers T1 ,& T2
Bagerhat |  | 0:12 | 30 | 6 | Due to tripping of 132/33 kV Transformers T1 ,& T3
Goalpara |  | 0:12 | 12 | 2.4 | Due to tripping of 132/33 kV Transformer T5
Bagerhat | 2 | 0:10 | 35 | 5.8333 | Due to tripping of 132/33 kV Transformers T1 ,& T2
|  | 0:07 | 15 | 1.75 | Due to tripping of 132/33 kV Transformer T1
Barisal | 1 | 0:14 | 20 | 4.6667 | Due to tripping of 132/33 kV Transformers T1 ,& T2
Madaripur |  | 0:29 | 10 | 4.8333 | Due to tripping of 132/33 kV Transformer T2
Khulna© | 1 | 1:39 | 5 | 8.25 | Due to red-hot maintenance of 132/33 kV Transformer T3
Barisal(S) | 1 | 0:40 | 15 | 10 | Due to tripping of 132/33 kV Transformer T1
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:July' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Gopalganj | 1 | 1:00 | 15 | 15 | Due to red-hot maintenance of 132/33 kV Transformer T1
Patuakhali | 1 | 0:48 | 25 | 20 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Napara | 1 | 1:00 | 25 | 25 | Due to red-hot maintenance of 132/33 kV Transformer T4
Barisal | 1 | 3:56 | 40 | 157.3333 | Due to red-hot maintenance of Barisal-Patuakahli 132 kV line
Bagerhat | 1 | 23:37 | 32 | 755.7333 | Due to tripping of Bagerhat-Mongla 132 kV line
Barisal |  | 1:00 | 11 | 11 | Due to S/D of 132/33 kV TransformerT1 & T2
Gopalganj | 2 | 1:39 | 25 | 41.25 | Due to S/D of 132/33 kV Transformer T2
|  | 1:49 | 20 | 36.3333 | Due to S/D of 132/33 kV Transformer T1
Noapara |  | 1:17 | 30 | 38.5 | Due to S/D of 132/33 kV Transformer T4
Sariatpur |  | 6:04 | 20 | 121.3333 | Due to S/D of 33 kV full Bus
Barisal(N) |  | 2:45 | 20 | 55 | Due to S/D of 33 kV full Bus
Mongla |  | 2:15 | 15 | 36.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
| 2 | 0:40 | 5 | 3.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Jhenidah |  | 0:14 | 72 | 16.8 | Due to tripping of 132/33 kV Transformers T1 ,& T2
Patuakhali | 1 | 0:44 | 30 | 22 | Due to S/D of 33 kV Bus-1
|  | 1:12 | 10 | 12 | Due to red-hot maintenance of 132/33 kV Transformer T3
Jhenidah | 2 | 0:11 | 46 | 8.4333 | Due to tripping of Jhenidah-Chuadanga 132 kV line
|  | 0:43 | 35 | 25.0833 | Due to S/D of 132/33 kV Transformer T1
Bottail | 1 | 0:07 | 98 | 11.4333 | Due to tripping of 132/33 kV Transformer T2
Rajshahi | 1 | 0:46 | 18 | 13.8 | Due to red-hot maintenance of 132/33 kV Transformer T1
Rangpur | 5 | 0:50 | 15 | 12.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:39 | 15 | 9.75 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 0:38 | 70 | 44.3333 | Due to red-hot maintenance of 33 kV Bus
|  | 2:40 | 20 | 53.3333 | Due to red-hot maintenance of 132/33 kV Transformer T3
|  | 1:10 | 80 | 93.3333 | Due to red-hot maintenance of 33 kV Bus
Rajshahi | 1 | 1:25 | 24 | 34 | Due to red-hot maintenance of 132/33 kV Transformer T1
C.nawabganj | 1 | 0:11 | 5 | 0.91667 | Due to tripping of 132/33 kV Transformer T11
Saidpur | 2 | 0:31 | 10 | 5.1667 | Due to red-hot maintenance of 132/33 kV Transformer T4
|  | 0:07 | 22 | 2.5667 | Due to tripping of Saidpur-Purbasadipur 132 kV line-2
Natore | 1 | 0:14 | 170 | 39.6667 | Due to tripping of Natore-Rajshahi 132 kV line-1 & 2
Saidpur | 1 | 0:11 | 134 | 24.5667 | Due to tripping of Saidpur-Purbasadipur 132 kV line
Rangpur | 1 | 0:06 | 64 | 6.4 | Due to tripping of Rangpur-Lalmonirhat-132 kV line
Bogura | 1 | 4:55 | 60 | 97 | Due to S/D of 132 kV Bus
Natore | 1 | 0:21 | 35 | 12.25 | Due to S/D of 33 kV Bus
Rangpur | 1 | 2:00 | 40 | 80 | Due to S/D of 132/33 kV Transformer T2
Naogaon | 1 | 3:23 | 18 | 60.9 | Due to S/D of 132/33 kV Transformer T3
Rangpur | 1 | 4:57 | 50 | 247.5 | Due to S/D of Rangpur-Lalmonirhat-132 kV line
Saidpur | 1 |  | 65 | 200.4167 | Due to S/D of Saidpur-Purbasadipur 132 kV line
Total unserved energy : |  |  |  | 5626.9667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 4 | 2019-07-03 | 16:00
2 | Munsiganj | 144 | 17 | 2019-07-03 | 2100
3 | Sonargaon | 88 | 17 | 2019-07-03 | 1200
4 | Shyampur | 210 | 22 | 2019-07-03 | 2300
5 | Bhulta | 217 | 8 | 2019-07-03 | 2100
6 | Madanganj | 62 | 4 | 2019-07-03 | 1400
7 | Shitalakhya | 121 | 18 | 2019-07-03 | 1600
8 | Rahim steel | 26 | 16 | 2019-07-03 | 11:00
9 | Matuail | 102 | 4 | 2019-07-03 | 1000
10 | Ghorasal | 97 | 21 | 2019-07-03 | 2200
11 | Narsingdi | 149 | 21 | 2019-07-03 | 2100
12 | Haripur (SBU) | 124 | 1 | 2019-07-03 | 100
13 | Ullon | 98 | 21 | 2019-07-03 | 1700
14 | Hasnabad | 217 | 1 | 2019-07-03 | 1930
15 | Magbazar | 157 | 22 | 2019-07-03 | 1700
16 | Maniknagar | 124 | 22 | 2019-07-03 | 1000
17 | Bangabhaban | 41 | 22 | 2019-07-03 | 1300
18 | Narinda | 104 | 6 | 2019-07-03 | 1300
19 | Dhanmondi | 182 | 22 | 2019-07-03 | 1300
20 | Lalbag | 99 | 1 | 2019-07-03 | 1500
21 | Madartek | 69 | 21 | 2019-07-03 | 2100
22 | Mirpur | 121 | 23 | 2019-07-03 | 1900
23 | Kalyanpur | 129 | 16 | 2019-07-03 | 1500
24 | Gulshan | 180 | 23 | 2019-07-03 | 1500
25 | Uttara | 96 | 23 | 2019-07-03 | 2300
26 | Uttara(new) | 21 | 21 | 2019-07-03 | 15:00
27 | Kamrangirchar | 87 | 24 | 2019-07-03 | 1200
28 | Savar | 153 | 23 | 2019-07-03 | 16:00
29 | Bhasantec | 180 | 22 | 2019-07-03 | 1600
30 | Agargaon | 66 | 22 | 2019-07-03 | 1600
31 | Satmosjid | 133 | 23 | 2019-07-03 | 2100
32 | Tongi | 173 | 21 | 2019-07-03 | 1100
33 | Kabirpur | 227 | 8 | 2019-07-03 | 1100
34 | Basundhara | 142 | 21 | 2019-07-03 | 2300
35 | Manikganj | 102 | 19 | 2019-07-03 | 2100
36 | Joydevpur | 237 | 22 | 2019-07-03 | 21:00
37 | New Tongi | 126 | 6 | 2019-07-03 | 1930
38 | Kodda | 271 | 3 | 2019-07-03 | 2100
39 | Dhamrai | 62 | 20 | 2019-07-03 | 20:00
40 | Valuka | 116 | 4 | 2019-07-03 | 2000
41 | Tangail | 201 | 19 | 2019-07-03 | 2100
42 | Mymensing | 255 | 22 | 2019-07-03 | 20:00
43 | Kishorganj | 134 | 20 | 2019-07-03 | 2000
44 | Netrokona | 110 | 3 | 2019-07-03 | 22:00
45 | Jamalpur | 132 | 1 | 2019-07-03 | 22:00
46 | Sherpur | 108 | 4 | 2019-07-03 | 2400
47 | Srimongal | 43 | 30 | 2019-07-03 | 1930
48 | Shahjibazar | 128 | 2 | 2019-07-03 | 2100
49 | Fenchuganj | 57 | 5 | 2019-07-03 | 2100
50 | Kulawara | 49 | 3 | 2019-07-03 | 1930
51 | Sylhet | 157 | 18 | 2019-07-03 | 1930
52 | Chatak | 43 | 18 | 2019-07-03 | 2000
53 | Sunamganj | 41 | 2 | 2019-07-03 | 2100
54 | Bianibazar | 54 | 17 | 2019-07-03 | 2000
55 | Cumilla (S) | 194 | 21 | 2019-07-03 | 2200
56 | Cumilla(N) | 165 | 3 | 2019-07-03 | 1900
57 | Chandpur | 109 | 21 | 2019-07-03 | 2100
58 | Feni | 148 | 17 | 2019-07-03 | 21:00
59 | Chowmuhani | 192 | 22 | 2019-07-03 | 2300
60 | Ashuganj | 62 | 18 | 2019-07-03 | 2300
61 | Daudkandi | 150 | 18 | 2019-07-03 | 1930
62 | B.Baria | 149 | 19 | 2019-07-03 | 2100
63 | Ramganj | 94 | 4 | 2019-07-03 | 1930
64 | Madanhat | 71 | 1 | 2019-07-03 | 1930
65 | Hathazari | 105 | 17 | 2019-07-03 | 2000
66 | Khulshi | 215 | 16 | 2019-07-03 | 1300
67 | Halishahar | 153 | 17 | 2019-07-03 | 1500
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 185 | 28 | 2019-07-03 | 1400
69 | Sikalbaha | 39 | 2 | 2019-07-03 | 2000
70 | Dohazari | 92 | 18 | 2019-07-03 | 2100
71 | Cox'sbazar | 96 | 20 | 2019-07-03 | 1930
72 | Chandraghona | 28 | 1 | 2019-07-03 | 1900
73 | Kaptai | 5 | 17 | 2019-07-03 | 1900
74 | A. Khaer Stl. | 22 | 2 | 2019-07-03 | 1300
75 | Bakulia | 115 | 21 | 2019-07-03 | 1500
76 | Julda | 22 | 18 | 2019-07-03 | 100
77 | TK chemical | 5 | 14 | 2019-07-03 | 1600
78 | Modern Steel | 19 | 20 | 2019-07-03 | 1000
79 | Shahmirpur | 34 | 17 | 2019-07-03 | 100
80 | Khagrachhari | 20 | 2 | 2019-07-03 | 1930
81 | Matarbari | 30 | 21 | 2019-07-03 | 2100
82 | Baroiar Hat | 38 | 2 | 2019-07-03 | 2000
83 | Rangamati | 20 | 7 | 2019-07-03 | 1830
84 | Abul Khair 230 | 160 | 30 | 2019-07-03 | 1800
85 | BSRM | 165 | 23 | 2019-07-03 | 400
86 | Goalpara | 40 | 24 | 2019-07-03 | 1930
87 | Central s/s | 99 | 23 | 2019-07-03 | 1930
88 | Noapara | 109 | 23 | 2019-07-03 | 2000
89 | Jashore | 123 | 23 | 2019-07-03 | 20:00
90 | Benapol | 52 | 10 | 2019-07-03 | 1930
91 | Jhenidah | 130 | 12 | 2019-07-03 | 2200
92 | Bottail | 132 | 21 | 2019-07-03 | 1930
93 | G.K Project | 80 | 12 | 2019-07-03 | 2000
94 | Faridpur | 176 | 25 | 2019-07-03 | 1930
95 | Madaripur | 124 | 18 | 2019-07-03 | 2300
96 | Sariatpur | 40 | 12 | 2019-07-03 | 2100
97 | Gopalganj | 96 | 18 | 2019-07-03 | 2100
98 | Bagerhat | 105 | 4 | 2019-07-03 | 22:00
99 | Mongla | 50 | 12 | 2019-07-03 | 900
100 | Satkhira | 112 | 21 | 2019-07-03 | 2200
101 | Gallamari | 54 | 21 | 2019-07-03 | 2300
102 | Magura | 57 | 23 | 2019-07-03 | 2000
103 | Chuadanga | 107 | 12 | 2019-07-03 | 2000
104 | Barsal(N) | 60 | 12 | 2019-07-03 | 2100
105 | Barsal(S) | 118 | 17 | 2019-07-03 | 22:00
106 | Patuakhali | 109 | 20 | 2019-07-03 | 2200
107 | Bhandaria | 60 | 23 | 2019-07-03 | 2000
108 | Borhan Uddin | 39 | 26 | 2019-07-03 | 2100
109 | Ishurdi | 69 | 30 | 2019-07-03 | 1930
110 | Ruppur Paromanobik | 2 | 1 | 2019-07-03 | 1900
111 | Natore | 136 | 18 | 2019-07-03 | 2100
112 | Bogura | 247 | 22 | 2019-07-03 | 2000
113 | Naogaon | 131 | 1 | 2019-07-03 | 2100
114 | Rajshahi | 172 | 22 | 2019-07-03 | 20:00
115 | C.Nawabganj | 84 | 21 | 2019-07-03 | 2100
116 | Amnura | 41 | 21 | 2019-07-03 | 1930
117 | Pabna | 125 | 18 | 2019-07-03 | 2100
118 | Shahjadpur | 109 | 17 | 2019-07-03 | 2000
119 | Serajganj | 112 | 6 | 2019-07-03 | 21:00
120 | Niyamatpur | 77 | 21 | 2019-07-03 | 2000
121 | Joypurhat | 59 | 20 | 2019-07-03 | 100
122 | Mohastangar | 17 | 1 | 2019-07-03 | 20:00
123 | Rangpur | 149 | 4 | 2019-07-03 | 1930
124 | Lalmonirhat | 94 | 1 | 2019-07-03 | 100
125 | Saidpur | 118 | 2 | 2019-07-03 | 20:00
126 | Purbasadipur | 106 | 29 | 2019-07-03 | 1930
127 | Thakurgaon | 80 | 19 | 2019-07-03 | 1930
128 | Palshbari | 120 | 4 | 2019-07-03 | 2000
129 | Barapukuria | 53 | 1 | 2019-07-03 | 21:00
130 | Panchugar | 46 | 2 | 2019-07-03 | 2000
131 | Joldhaka | 27 | 18 | 2019-07-03 | 2100
132 | Kurigram | 34 | 31 | 2019-07-03 | 2100
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:July' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4528 | 22.07.19 | 16:00
Chattogram | 1317 | 05.07.19 | 01:00
Khulna | 1490 | 23.07.19 | 20:00
Rajshahi | 1295 | 22.07.19 | 21:00
Cumilla | 1168 | 17.07.19 | 21:00
Mymensingh | 974 | 04.07.19 | 21:00
Sylhet | 527 | 03.07.19 | 19:30
Barisal | 439 | 27.07.19 | 23:00
Rangpur | 752 | 02.07.19 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 383 | 393 | 8 | 2019-07-03 | 20:00 | 378 | 17 | 2019-06-03 | 15:00
2 | Bheramara | 388 | 408 | 13 | 2019-07-03 | 7:00 | 338 | 31 | 2019-06-03 | 6:00
3 | Ashuganj(N) | 376 | 394 | 7 | 2019-07-03 | 2:00 | 358 | 21 | 2019-06-03 | 11:00
4 | Kaliakoir | 400 | 393 | 23 | 2019-07-03 | 7:00 | 352 | 24 | 2019-06-03 | 12:00
5 | Bhulta | 400 | 390 | 17 | 2019-07-03 | 24:00' | 362 | 20 | 2019-06-03 | 12:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 235 | 19 | 2019-07-03 | 13:00 | 220 | 24 | 2019-07-03 | 10:00
2 | Ishurdi | 230 | 237 | 1 | 2019-07-03 | 18:30 | 213 | 21 | 2019-07-03 | 7:00
3 | Ashuganj | 230 | 240 | 2 | 2019-07-03 | 19:00 | 229 | 20 | 2019-07-03 | 16:00
4 | Serajganj | 230 | 235 | 26 | 2019-07-03 | 17:00 | 217 | 21 | 2019-07-03 | 21:00
5 | Baghabari | 230 | 237 | 24 | 2019-07-03 | 17:00 | 219 | 20 | 2019-07-03 | 21:00
6 | Barapukuria | 230 | 240 | 14 | 2019-07-03 | 2:00 | 213 | 17 | 2019-07-03 | 22:00
7 | Bogra | 230 | 232 | 14 | 2019-07-03 | 4:00 | 201 | 20 | 2019-07-03 | 21:00
8 | Khulna South | 230 | 235 | 2 | 2019-07-03 | 16:00 | 197 | 19 | 2019-07-03 | 22:00
9 | Rampura | 230 | 224 | 7 | 2019-07-03 | 3:00 | 208 | 24 | 2019-07-03 | 12:00
10 | Haripur | 230 | 223 | 14 | 2019-07-03 | 5:00 | 210 | 24 | 2019-07-03 | 10:00
11 | Hasnabad | 230 | 225 | 12 | 2019-07-03 | 21:00 | 209 | 20 | 2019-07-03 | 11:00
12 | Aminbazar | 230 | 226 | 12 | 2019-07-03 | 20:00 | 208 | 24 | 2019-07-03 | 10:00
13 | Tongi | 230 | 235 | 8 | 2019-07-03 | 21:00 | 210 | 3 | 2019-07-03 | 9:00
14 | Comilla (N) | 230 | 232 | 5 | 2019-07-03 | 18:00 | 221 | 2 | 2019-07-03 | 13:00
15 | Hathazari | 230 | 225 | 8 | 2019-07-03 | 24:00' | 213 | 25 | 2019-07-03 | 9:00
16 | Megnaghat | 230 | 228 | 2 | 2019-07-03 | 22:00 | 212 | 16 | 2019-07-03 | 12:00
17 | Fenchuganj | 230 | 240 | 12 | 2019-07-03 | 20:00 | 229 | 1 | 2019-07-03 | 11:00
18 | Siddhirganj | 230 | 226 | 9 | 2019-07-03 | 2:00 | 209 | 24 | 2019-07-03 | 12:00
19 | Maniknagar | 230 | 310 | 20 | 2019-07-03 | 17:00 | 208 | 21 | 2019-07-03 | 10:00
20 | Old Airport | 230 | 224 | 12 | 2019-07-03 | 20:00 | 206 | 24 | 2019-07-03 | 10:00
21 | Barisal | 230 | 237 | 10 | 2019-07-03 | 15:00 | 214 | 17 | 2019-07-03 | 21:00
22 | AKSML | 230 | 223 | 8 | 2019-07-03 | 14:00 | 208 | 2 | 2019-07-03 | 12:00
23 | BSRM | 230 | 224 | 7 | 2019-07-03 | 17:00 | 211 | 2 | 2019-07-03 | 12:00
24 | Bibiyana | 230 | 235 | 12 | 2019-07-03 | 14:00 | 227 | 1 | 2019-07-03 | 2:00
25 | Bhulta | 230 | 227 | 12 | 2019-07-03 | 20:00 | 210 | 24 | 2019-07-03 | 10:00
26 | Ashuganj (S) | 230 | 237 | 1 | 2019-07-03 | 3:00 | 227 | 4 | 2019-07-03 | 10:00
27 | Kaliakoir | 230 | 228 | 5 | 2019-07-03 | 1:00 | 213 | 16 | 2019-07-03 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 134 | 4 | 2019-07-03 | 19:30 | 123 | 4 | 2019-07-03 | 12:00
2 | Munsiganj | 132 | 136 | 1 | 2019-07-03 | 20:00 | 122 | 20 | 2019-07-03 | 12:00
3 | Megnaghat | 132 | 134 | 12 | 2019-07-03 | 2000 | 120 | 13 | 2019-07-03 | 7:00
4 | Shyampur | 132 | 137 | 12 | 2019-07-03 | 1700 | 122 | 16 | 2019-07-03 | 12:00
5 | Bhulta | 132 | 128 | 12 | 2019-07-03 | 1800 | 114 | 21 | 2019-07-03 | 10:00
6 | Madanganj | 132 | 138 | 15 | 2019-07-03 | 1:00 | 120 | 16 | 2019-07-03 | 12:00
7 | Shitalakhya | 132 | 140 | 5 | 2019-07-03 | 1:00 | 120 | 3 | 2019-07-03 | 9:00
8 | Rahim Steal | 132 | 135 | 4 | 2019-07-03 | 19:30 | 124 | 4 | 2019-07-03 | 12:00
9 | Matuail | 132 | 133 | 4 | 2019-07-03 | 20:00 | 121 | 24 | 2019-07-03 | 13:00
10 | Ghorasal | 132 | 140 | 12 | 2019-07-03 | 100 | 128 | 13 | 2019-07-03 | 1:00
11 | Narsinghdi | 132 | 134 | 12 | 2019-07-03 | 1400 | 109 | 1 | 2019-07-03 | 1:00
12 | Haripur (SBU) | 132 | 135 | 12 | 2019-07-03 | 2000 | 124 | 4 | 2019-07-03 | 12:00
13 | Ullon | 132 | 136 | 2 | 2019-07-03 | 4:00 | 122 | 24 | 2019-07-03 | 12:00
14 | Hasnabad | 132 | 136 | 12 | 2019-07-03 | 2000 | 123 | 21 | 2019-07-03 | 10:00
15 | Magbazar | 132 | 137 | 3 | 2019-07-03 | 5:00 | 122 | 24 | 2019-07-03 | 12:00
16 | Maniknagar | 132 | 136 | 2 | 2019-07-03 | 4:00 | 125 | 4 | 2019-07-03 | 12:00
17 | Bangabhaban | 132 | 136 | 2 | 2019-07-03 | 4:00 | 125 | 4 | 2019-07-03 | 12:00
18 | Narinda | 132 | 136 | 2 | 2019-07-03 | 4:00 | 125 | 4 | 2019-07-03 | 12:00
19 | Dhanmondi | 132 | 136 | 2 | 2019-07-03 | 4:00 | 123 | 20 | 2019-07-03 | 12:00
20 | Lalbag | 132 | 137 | 19 | 2019-07-03 | 20:00 | 119 | 4 | 2019-07-03 | 12:00
21 | Madartek | 132 | 136 | 6 | 2019-07-03 | 7:00 | 122 | 24 | 2019-07-03 | 12:00
22 | Mirpur | 132 | 136 | 9 | 2019-07-03 | 4:00 | 120 | 16 | 2019-07-03 | 12:00
23 | Kalyanpur | 132 | 139 | 12 | 2019-07-03 | 20:00 | 126 | 4 | 2019-07-03 | 12:00
24 | Gulshan | 132 | 136 | 7 | 2019-07-03 | 3:00 | 121 | 24 | 2019-07-03 | 12:00
25 | Uttara | 132 | 135 | 15 | 2019-07-03 | 7:00 | 121 | 4 | 2019-07-03 | 12:00
26 | Uttara(New) | 132 | 138 | 2 | 2019-07-03 | 18:00 | 122 | 3 | 2019-07-03 | 12:00
27 | Kamrangirchar | 132 | 136 | 12 | 2019-07-03 | 20:00 | 118 | 24 | 2019-07-03 | 10:00
28 | Savar | 132 | 135 | 12 | 2019-07-03 | 20:00 | 123 | 4 | 2019-07-03 | 12:00
29 | Bhasantec | 132 | 138 | 5 | 2019-07-03 | 1:00 | 121 | 24 | 2019-07-03 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 139 | 7 | 2019-07-03 | 2:00 | 123 | 21 | 2019-07-03 | 11:00
31 | Satmosjid | 132 | 139 | 7 | 2019-07-03 | 2:00 | 123 | 21 | 2019-07-03 | 10:00
32 | Tongi | 132 | 139 | 12 | 2019-07-03 | 1930 | 125 | 17 | 2019-07-03 | 9:00
33 | Kabirpur | 132 | 136 | 1 | 2019-07-03 | 18:00 | 123 | 16 | 2019-07-03 | 13:00
34 | Basundhara | 132 | 135 | 12 | 2019-07-03 | 2000 | 119 | 21 | 2019-07-03 | 11:00
35 | Manikganj | 132 | 141 | 12 | 2019-07-03 | 2000 | 121 | 6 | 2019-07-03 | 8:00
36 | Joydevpur | 132 | 143 | 7 | 2019-07-03 | 13:00 | 127 | 24 | 2019-07-03 | 1:00
37 | New Tongi | 132 | 137 | 5 | 2019-07-03 | 1:00 | 124 | 16 | 2019-07-03 | 10:00
38 | Kodda | 132 | 141 | 5 | 2019-07-03 | 1:00 | 120 | 7 | 2019-07-03 | 9:00
39 | Dhamrai | 132 | 134 | 1 | 2019-07-03 | 18:00 | 122 | 8 | 2019-07-03 | 11:00
40 | Valuka | 133 | 135 | 14 | 2019-07-03 | 5:00 | 110 | 8 | 2019-07-03 | 1:00
41 | Tangail | 132 | 136 | 14 | 2019-07-03 | 6:00 | 121 | 2 | 2019-07-03 | 23:00
42 | Mymensing | 132 | 136 | 15 | 2019-07-03 | 3:00 | 110 | 18 | 2019-07-03 | 2200
43 | Kishorganj | 132 | 139 | 14 | 2019-07-03 | 6:00 | 116 | 18 | 2019-07-03 | 2100
44 | Netrokona | 132 | 137 | 13 | 2019-07-03 | 14:00 | 112 | 18 | 2019-07-03 | 2100
45 | Jamalpur | 132 | 139 | 2 | 2019-07-03 | 9:00 | 111 | 8 | 2019-07-03 | 100
46 | Sherpur | 132 | 139 | 2 | 2019-07-03 | 8:00 | 111 | 8 | 2019-07-03 | 100
47 | Srimongal | 132 | 140 | 14 | 2019-07-03 | 11:00 | 130 | 23 | 2019-07-03 | 1900
48 | Shahjibazar | 132 | 138 | 6 | 2019-07-03 | 13:00 | 129 | 23 | 2019-07-03 | 1000
49 | Fenchuganj | 132 | 138 | 12 | 2019-07-03 | 1400 | 131 | 17 | 2019-07-03 | 15:00
50 | Khulawara | 132 | 137 | 12 | 2019-07-03 | 1400 | 130 | 30 | 2019-07-03 | 1:00
51 | Sylhet | 132 | 137 | 12 | 2019-07-03 | 500 | 131 | 1 | 2019-07-03 | 19:00
52 | Chattak | 132 | 137 | 12 | 2019-07-03 | 600 | 129 | 2 | 2019-07-03 | 20:00
53 | Sunamganj | 132 | 138 | 6 | 2019-07-03 | 1:00 | 127 | 2 | 2019-07-03 | 21:00
54 | Biani Bazar | 132 | 137 | 12 | 2019-07-03 | 1300 | 128 | 1 | 2019-07-03 | 19:00
55 | Comilla(South) | 132 | 128 | 7 | 2019-07-03 | 7:00 | 118 | 17 | 2019-07-03 | 21:00
56 | Comilla (North) | 132 | 138 | 8 | 2019-07-03 | 24:00' | 131 | 20 | 2019-07-03 | 22:00
57 | Chandpur | 132 | 140 | 6 | 2019-07-03 | 14:00 | 124 | 27 | 2019-07-03 | 5:00
58 | Feni | 132 | 133 | 8 | 2019-07-03 | 14:00 | 117 | 31 | 2019-07-03 | 19:00
59 | Chowmuhani | 132 | 134 | 13 | 2019-07-03 | 19:30 | 115 | 24 | 2019-07-03 | 22:00
60 | Ashuganj | 132 | 140 | 13 | 2019-07-03 | 16:00 | 131 | 2 | 2019-07-03 | 23:00
61 | Daudkandi | 132 | 139 | 1 | 2019-07-03 | 20:00 | 122 | 21 | 2019-07-03 | 11:00
62 | Brahminbaria | 132 | 137 | 15 | 2019-07-03 | 10:00 | 125 | 23 | 2019-07-03 | 22:00
63 | Ramganj | 132 | 136 | 30 | 2019-07-03 | 11:00 | 118 | 20 | 2019-07-03 | 2200
64 | Madanhat | 132 | 135 | 8 | 2019-07-03 | 10:00 | 124 | 26 | 2019-07-03 | 700
65 | Hathazari | 132 | 135 | 10 | 2019-07-03 | 17:00 | 127 | 2 | 2019-07-03 | 12:00
66 | Khulshi | 132 | 133 | 10 | 2019-07-03 | 1:00 | 123 | 1 | 2019-07-03 | 16:00
67 | Halishahar | 132 | 138 | 10 | 2019-07-03 | 13:00 | 125 | 30 | 2019-07-03 | 9:00
68 | Baraulia | 132 | 136 | 5 | 2019-07-03 | 20:00 | 123 | 15 | 2019-07-03 | 16:00
69 | Sikalbaha | 132 | 138 | 10 | 2019-07-03 | 13:00 | 118 | 25 | 2019-07-03 | 9:00
70 | Dohazari | 132 | 137 | 10 | 2019-07-03 | 13:00 | 126 | 17 | 2019-07-03 | 9:00
71 | Cox'sbazar | 132 | 136 | 1 | 2019-07-03 | 13:00 | 116 | 20 | 2019-07-03 | 19:00
72 | Chandraghona | 132 | 137 | 10 | 2019-07-03 | 13:00 | 103 | 22 | 2019-07-03 | 10:00
73 | Kaptai | 132 | 136 | 23 | 2019-07-03 | 1:00 | 120 | 1 | 2019-07-03 | 21:00
74 | A. Khaer Stl. | 132 | 134 | 27 | 2019-07-03 | 19:30 | 124 | 2 | 2019-07-03 | 12:00
75 | Bakulia | 132 | 136 | 10 | 2019-07-03 | 13:00 | 126 | 2 | 2019-07-03 | 12:00
76 | Julda | 132 | 136 | 9 | 2019-07-03 | 19:30 | 123 | 15 | 2019-07-03 | 7:00
77 | TK Chemical | 132 | 136 | 1 | 2019-07-03 | 19:30 | 127 | 2 | 2019-07-03 | 10:00
78 | Modern Steel | 132 | 136 | 7 | 2019-07-03 | 19:30 | 126 | 2 | 2019-07-03 | 11:00
79 | Shahmirpur | 132 | 136 | 24 | 2019-07-03 | 6:00 | 120 | 25 | 2019-07-03 | 9:00
80 | Khagrachhari | 132 | 137 | 10 | 2019-07-03 | 13:00 | 122 | 25 | 2019-07-03 | 10:00
81 | Matarbari | 132 | 136 | 7 | 2019-07-03 | 14:00 | 119 | 31 | 2019-07-03 | 19:00
82 | Baroiar Hat | 132 | 141 | 26 | 2019-07-03 | 5:00 | 121 | 1 | 2019-07-03 | 15:00
83 | Rangamati | 133 | 138 | 25 | 2019-07-03 | 16:00 | 126 | 1 | 2019-07-03 | 16:00
84 | Goalpara | 132 | 139 | 2 | 2019-07-03 | 20:00 | 114 | 19 | 2019-07-03 | 2200
85 | Khulna Central | 132 | 139 | 16 | 2019-07-03 | 17:00 | 114 | 19 | 2019-07-03 | 2200
86 | Noapara | 132 | 137 | 9 | 2019-07-03 | 18:00 | 111 | 19 | 2019-07-03 | 2100
87 | Jessore | 132 | 134 | 26 | 2019-07-03 | 8:00 | 106 | 19 | 2019-07-03 | 2200
88 | Benapol | 132 | 135 | 26 | 2019-07-03 | 7:00 | 106 | 17 | 2019-07-03 | 2100
89 | Jhenida | 132 | 141 | 26 | 2019-07-03 | 8:00 | 102 | 17 | 2019-07-03 | 2100
90 | Bottail | 132 | 141 | 24 | 2019-07-03 | 18:00 | 114 | 17 | 2019-07-03 | 2100
91 | G.K Project | 132 | 141 | 12 | 2019-07-03 | 1700 | 115 | 24 | 2019-07-03 | 400
92 | Faridpur | 132 | 136 | 25 | 2019-07-03 | 6:00 | 110 | 17 | 2019-07-03 | 21:00
93 | Madaripur | 132 | 142 | 25 | 2019-07-03 | 17:00 | 114 | 17 | 2019-07-03 | 21:00
94 | Sariatpur | 132 | 139 | 26 | 2019-07-03 | 5:00 | 110 | 17 | 2019-07-03 | 21:00
95 | Gopalganj | 132 | 143 | 9 | 2019-07-03 | 18:00 | 120 | 3 | 2019-07-03 | 700
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Bagerhat | 132 | 139 | 9 | 2019-07-03 | 3:00 | 110 | 19 | 2019-07-03 | 2200
97 | Mongla | 132 | 141 | 26 | 2019-07-03 | 6:00 | 112 | 19 | 2019-07-03 | 2200
98 | Satkhira | 132 | 137 | 9 | 2019-07-03 | 9:00 | 104 | 24 | 2019-07-03 | 1500
99 | Gallamari | 132 | 139 | 10 | 2019-07-03 | 4:00 | 98 | 24 | 2019-07-03 | 1500
100 | Magura | 132 | 141 | 27 | 2019-07-03 | 9:00 | 100 | 17 | 2019-07-03 | 2200
101 | Chuadanga | 132 | 140 | 1 | 2019-07-03 | 18:00 | 92 | 17 | 2019-07-03 | 2100
102 | Barisal(N) | 132 | 140 | 9 | 2019-07-03 | 11:00 | 121 | 4 | 2019-07-03 | 2100
103 | Barisal(S) | 132 | 140 | 1 | 2019-07-03 | 6:00 | 124 | 17 | 2019-07-03 | 21:00
104 | Patuakhali | 132 | 140 | 10 | 2019-07-03 | 13:00 | 117 | 24 | 2019-07-03 | 100
105 | Bhandaria | 132 | 137 | 9 | 2019-07-03 | 9:00 | 113 | 3 | 2019-07-03 | 700
106 | Ishurdi | 132 | 139 | 2 | 2019-07-03 | 17:00 | 122 | 21 | 2019-07-03 | 2100
107 | Ruppur paromanobik | 132 | 139 | 9 | 2019-07-03 | 9:00 | 123 | 21 | 2019-07-03 | 2000
108 | Natore | 132 | 138 | 15 | 2019-07-03 | 18:00 | 117 | 20 | 2019-07-03 | 2100
109 | Bogra | 132 | 138 | 14 | 2019-07-03 | 4:00 | 116 | 20 | 2019-07-03 | 2100
110 | Noagaon | 132 | 135 | 15 | 2019-07-03 | 4:00 | 107 | 20 | 2019-07-03 | 2100
111 | Rajshahi | 132 | 136 | 23 | 2019-07-03 | 19:30 | 115 | 17 | 2019-07-03 | 2000
112 | C.Nawabganj | 132 | 138 | 26 | 2019-07-03 | 17:00 | 113 | 23 | 2019-07-03 | 1300
113 | Amnura | 132 | 140 | 23 | 2019-07-03 | 20:00 | 115 | 17 | 2019-07-03 | 2100
114 | Pabna | 132 | 138 | 12 | 2019-07-03 | 1700 | 121 | 21 | 2019-07-03 | 21:00
115 | Shahjadpur | 132 | 140 | 1 | 2019-07-03 | 18:30 | 114 | 25 | 2019-07-03 | 2100
116 | Serajganj | 132 | 138 | 6 | 2019-07-03 | 18:00 | 116 | 25 | 2019-07-03 | 2100
117 | Niyamatpur | 132 | 137 | 15 | 2019-07-03 | 2:00 | 103 | 20 | 2019-07-03 | 2100
118 | Joypurhat | 132 | 137 | 10 | 2019-07-03 | 6:00 | 102 | 20 | 2019-07-03 | 1930
119 | Mohastangor | 132 | 137 | 14 | 2019-07-03 | 3:00 | 102 | 21 | 2019-07-03 | 2100
120 | Rangpur | 132 | 136 | 14 | 2019-07-03 | 4:00 | 102 | 17 | 2019-07-03 | 1930
121 | Lalmonirhat | 132 | 136 | 14 | 2019-07-03 | 3:00 | 100 | 17 | 2019-07-03 | 2000
122 | Saidpur | 132 | 137 | 14 | 2019-07-03 | 3:00 | 100 | 17 | 2019-07-03 | 2000
123 | Purbasadipur | 132 | 136 | 7 | 2019-07-03 | 5:00 | 100 | 17 | 2019-07-03 | 1930
124 | Thakurgaon | 132 | 137 | 25 | 2019-07-03 | 7:00 | 95 | 17 | 2019-07-03 | 2000
125 | Palashbari | 132 | 139 | 23 | 2019-07-03 | 18:00 | 108 | 20 | 2019-07-03 | 2100
126 | Barapukuria | 132 | 140 | 14 | 2019-07-03 | 2:00 | 114 | 17 | 2019-07-03 | 1930
127 | Panchagar | 132 | 135 | 14 | 2019-07-03 | 3:00 | 83 | 17 | 2019-07-03 | 2000
128 | Joldhaka | 132 | 136 | 14 | 2019-07-03 | 3:00 | 98 | 17 | 2019-07-03 | 1930
129 | Kurigram | 133 | 111 | 31 | 2019-07-03 | 4:00 | 110 | 31 | 2019-07-03 | 1931
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:July' 2019
| Name of the | Auto transofrmer |  | Recorded Maximum Load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
IP-299421 | Hasnabad | TR1 | 225 | 106 | 325 | 27.07.19 | 10:00
|  | TR2 | 225 | 97 | 325 | 27.07.19
|  | TR3 | 225 | 96 | 300
IP-299866 | Tongi | TR1 | 225 | 160 | 475 | 17.07.19 | 09:00
|  | TR2 | 225 | 160 | 475 | 17.07.19
|  | TR3 | 225 | 160 | 475
IP-299427 | Haripur | TR1 | 225 | 122 | 500 | 01.07.19 | 11:00 | S/D
|  | TR2 | 225 | - | - | 01.07.19
|  | TR3 | 225 | 122 | 500
IP-299728 | Rampura | TR1 | 225 | 178 | 535 | 22.07.19 | 15:00
|  | TR2 | 225 | 178 | 535 | 22.07.19
|  | TR3 | 225 | 178 | 535
IP-299264 | Aminbazar | TR1 | 225 | 160 | 491 | 06.07.19 | 06:00
|  | TR2 | 225 | 160 | 491 | 06.07.19
|  | TR3 | 225 | 167 | 519
| Maniknagar | TR1 | 300 | 126 | 410 | 22.07.19 | 16:00
IP-399266 |  | TR2 | 300 | 126 | 410
| Cumilla (N) | TR1 | 225 | 140 | 386 | 02.07.19 | 12:00
|  | TR2 | 225 | 138 | 400
| Fenchuganj | TR1 | 300 | 167 | 426 | 13.07.19 | 2:00
IP-399428 | Hathazari | MT1 | 150 | 78 | 190 | 26.07.19 | 10:00
|  | MT2 | 150 | 78 | 190 | 26.07.19
|  | MT3 | 150 | 78 | 190
|  | MT4 | 150 | 78 | 190
| Ishurdi | TR1 | 225 | 184 | 740 | 18.07.19 | 1:00
IP-499474 |  | TR2 | 225 | 184 | 740 | 18.07.19
|  | TR3 | 225 | 184 | 740
IP-58001/58002 | Khulna(S) | TR1 | 225 | 125 | 338 | 17.07.19 | 5:00
|  | TR2 | 225 | 125 | 338 | 17.07.19
|  | TR3 | 300 | 158 | 443
| Bogra | TR1 | 225 | 150 | 448 | 31.07.19 | 21:00
IP-43002/499264 |  | TR2 | 225 | 150 | 448
IP-499224 |  | TR3 | 225 | 202 | 594
| Baghabari | TR1 | 225 | 190 | 560 | 31.07.19 | 21:00
| Barapukuria | TR1 | 225 | 180 | 900 | 30.07.19 | 20:00 | Due to unavailability 230 kV side meters 132 kV current is provided
|  | TR2 | 225 | 191 | 850
|  | TR6 | 300 | 207 | 1093
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 292 | 490 | 11.07.19 | 9:30
|  | TR2(400/230 kV) | 520 | 292 | 490
|  | TR1(400/132 kV) | 325 | 245 | 422 | 18.07.19 | 20:15
|  | TR2(400/132 kV) | 325 | 245 | 422
| Bibiyana | ICT1(400/230 kV) | 520 | 119.4 | 209 | 11.07.19 | 12:00
|  | ICT2(400/230kV) | 520 | 117.9 | 207
| Bhulta | ATR1(400/230 kV) | 520 | 207 | 363 | 10.07.19 | 23:15
|  | ATR2(400/230kV) | 520 | 207 | 363
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:July' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:July' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-07-19 | 11634 | 11634 | - | - | - | - | - | - | - | - | - | - | - | - | 01-07-19 | 10117 | 10117 | - | - | - | - | - | - | - | - | - | - | - | -
02-07-19 | 12131 | 12131 | - | - | - | - | - | - | - | - | - | - | - | - | 02-07-19 | 9093.3 | 9093.3 | - | - | - | - | - | - | - | - | - | - | - | -
03-07-19 | 12229 | 12229 | - | - | - | - | - | - | - | - | - | - | - | - | 03-07-19 | 9710.1 | 9710.1 | - | - | - | - | - | - | - | - | - | - | - | -
04-07-19 | 12200 | 12200 | - | - | - | - | - | - | - | - | - | - | - | - | 04-07-19 | 10104.1 | 10104.1 | - | - | - | - | - | - | - | - | - | - | - | -
05-07-19 | 11411 | 11411 | - | - | - | - | - | - | - | - | - | - | - | - | 05-07-19 | 8718.8 | 8718.8 | - | - | - | - | - | - | - | - | - | - | - | -
06-07-19 | 11395 | 11395 | - | - | - | - | - | - | - | - | - | - | - | - | 06-07-19 | 8995.7 | 8995.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-07-19 | 11543 | 11543 | - | - | - | - | - | - | - | - | - | - | - | - | 07-07-19 | 9201.4 | 9201.4 | - | - | - | - | - | - | - | - | - | - | - | -
08-07-19 | 11444 | 11444 | - | - | - | - | - | - | - | - | - | - | - | - | 08-07-19 | 9095.8 | 9095.8 | - | - | - | - | - | - | - | - | - | - | - | -
09-07-19 | 11462 | 11462 | - | - | - | - | - | - | - | - | - | - | - | - | 09-07-19 | 9081.1 | 9081.1 | - | - | - | - | - | - | - | - | - | - | - | -
10-07-19 | 10935 | 10935 | - | - | - | - | - | - | - | - | - | - | - | - | 10-07-19 | 9450.9 | 9450.9 | - | - | - | - | - | - | - | - | - | - | - | -
11-07-19 | 10662 | 10662 | - | - | - | - | - | - | - | - | - | - | - | - | 11-07-19 | 9230 | 9230 | - | - | - | - | - | - | - | - | - | - | - | -
12-07-19 | 9880 | 9880 | - | - | - | - | - | - | - | - | - | - | - | - | 12-07-19 | 7665.7 | 7665.7 | - | - | - | - | - | - | - | - | - | - | - | -
13-07-19 | 9808 | 9808 | - | - | - | - | - | - | - | - | - | - | - | - | 13-07-19 | 8654.2 | 8654.2 | - | - | - | - | - | - | - | - | - | - | - | -
14-07-19 | 10815 | 10815 | - | - | - | - | - | - | - | - | - | - | - | - | 14-07-19 | 8342.8 | 8342.8 | - | - | - | - | - | - | - | - | - | - | - | -
15-07-19 | 10637 | 10637 | - | - | - | - | - | - | - | - | - | - | - | - | 15-07-19 | 8193.1 | 8193.1 | - | - | - | - | - | - | - | - | - | - | - | -
16-07-19 | 11654 | 11654 | - | - | - | - | - | - | - | - | - | - | - | - | 16-07-19 | 9268.9 | 9268.9 | - | - | - | - | - | - | - | - | - | - | - | -
17-07-19 | 12150 | 12150 | - | - | - | - | - | - | - | - | - | - | - | - | 17-07-19 | 9853.9 | 9853.9 | - | - | - | - | - | - | - | - | - | - | - | -
18-07-19 | 12186 | 12186 | - | - | - | - | - | - | - | - | - | - | - | - | 18-07-19 | 10120.6 | 10120.6 | - | - | - | - | - | - | - | - | - | - | - | -
19-07-19 | 11477 | 11477 | - | - | - | - | - | - | - | - | - | - | - | - | 19-07-19 | 8841.1 | 8841.1 | - | - | - | - | - | - | - | - | - | - | - | -
20-07-19 | 12162 | 12162 | - | - | - | - | - | - | - | - | - | - | - | - | 20-07-19 | 9451.3 | 9451.3 | - | - | - | - | - | - | - | - | - | - | - | -
21-07-19 | 12436 | 12436 | - | - | - | - | - | - | - | - | - | - | - | - | 21-07-19 | 10257 | 10257 | - | - | - | - | - | - | - | - | - | - | - | -
22-07-19 | 12270 | 12270 | - | - | - | - | - | - | - | - | - | - | - | - | 22-07-19 | 10285.4 | 10285.4 | - | - | - | - | - | - | - | - | - | - | - | -
23-07-19 | 11640 | 11640 | - | - | - | - | - | - | - | - | - | - | - | - | 23-07-19 | 10178.8 | 10178.8 | - | - | - | - | - | - | - | - | - | - | - | -
24-07-19 | 11559 | 11559 | - | - | - | - | - | - | - | - | - | - | - | - | 24-07-19 | 9704.1 | 9704.1 | - | - | - | - | - | - | - | - | - | - | - | -
25-07-19 | 12033 | 12033 | - | - | - | - | - | - | - | - | - | - | - | - | 25-07-19 | 9894.8 | 9894.8 | - | - | - | - | - | - | - | - | - | - | - | -
26-07-19 | 10913 | 10913 | - | - | - | - | - | - | - | - | - | - | - | - | 26-07-19 | 8081.6 | 8081.6 | - | - | - | - | - | - | - | - | - | - | - | -
27-07-19 | 11508 | 11508 | - | - | - | - | - | - | - | - | - | - | - | - | 27-07-19 | 8619.5 | 8619.5 | - | - | - | - | - | - | - | - | - | - | - | -
28-07-19 | 11578 | 11578 | - | - | - | - | - | - | - | - | - | - | - | - | 28-07-19 | 9180.3 | 9180.3 | - | - | - | - | - | - | - | - | - | - | - | -
29-07-20 | 11791 | 11791 | - | - | - | - | - | - | - | - | - | - | - | - | 29-07-20 | 9544.9 | 9544.9 | - | - | - | - | - | - | - | - | - | - | - | -
30-07-19 | 11663 | 11663 | - | - | - | - | - | - | - | - | - | - | - | - | 30-07-19 | 9406.8 | 9406.8 | - | - | - | - | - | - | - | - | - | - | - | -
31-07-19 | 11862 | 11862 | - | - | - | - | - | - | - | - | - | - | - | - | 31-07-19 | 9754.6 | 9754.6

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:July' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12436 | 21/07/19 | 21:00
2 | Maximum day peak Genaration | MW | 10285.4 | 22/07/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 12436 | 21/07/19 | 21:00
4 | Minimum Generation | MW | 6202 | 14/07/19 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11518.3226
6 | Average of the daily day peak Genaration | MW | 9293.471
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW | -
11 | Total Generation | MKWH | 7327.4749
12 | Total Generation by IPP | MKWH | 2291.3859 | % of total Gen. | 31.27%
13 | Total Generation by BPDB | MKWH | 3406.3279 | " | 46.49%
14 | A) Total Generation by RPCL | MKWH | 176.7376 | '' | 2.412%
| B) Total Generation by REB | MKWH | 143.6788 | " | 1.961%
| C) Total Generation by RENTAL | MKWH | 572.3521 | " | 7.811%
| D) Total Imported from India (HVDC) | MKWH | 640.408 | " | 8.74%
| E) Total Imported from Tripura, India (A.C) | MKWH | 96.5846 | " | 1.318%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4492.67 | % of total Gen. | 61.31%
| B) Oil | MKWH | 1803.1038 | '' | 24.61%
| C) Hydro | MKWH | 102.8917 | '' | 1.404%
| D) Solar | MKWH | 2.5054 | '' | 0.03419%
| E) Coal | MKWH | 189.3114 | '' | 2.584%
| F) HVDC (Import from India) | MKWH | 640.408 | '' | 8.74%
| G) A.C (Import from Tripura, India) | MKWH | 96.5846 | '' | 1.318%
16 | Maximun of the daily total Generation . | MKWH | 262.5004 | 22/07/19
17 | Monthly Load factor | % | 79.2028
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 19816.5408
| A) Gas | M.Taka | 4313.1611
| B) Liquid fuel | M.Taka | 14675.0108
| C) Coal | M.Taka | 828.3688
| D) HVDC (Import from India) | M.Taka | 3266.0806
| E) Tripura(Import from India) | M.Taka | 660.6385
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 960.3959 | 30/07/19
| A) Gas | M.Taka | 398.8514 | 30/07/19
| B) Liquid fuel | M.Taka | 711.0433 | 18/07/19
| C) Coal | M.Taka | 38.4746 | 23/07/19
| D) HVDC (Import from India) | M.Taka | 114.1769 | 25-07-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.5402
| B) Excluding Hydro & Solar | Taka/KWHR | 3.5918
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/19 | 06:00
b) | Actual | FT (MSL) | 105.85 | 31/07/19 | 06:00
22 | Peak Genaration of July 2018 | MW | 11387 | 18/07/18 | 22:00
23 | Peak Demand of July 2018 | MW | 11306 | 14/07/18 | 21:00
24 | Maximum peak Generation recorded upto 31/07/19 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/07/19 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/07/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.