## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:June' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | June 2019 |  | May 2019 |  | June 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12780 | 24/06/19 | 12893 | 29/05/19 | 10949 | 06/06/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 21:00
2 | Minimum Generation (MW) | 5341 | 06/06/19 | 4900 | 25/05/19 | 4876 | 16/06/18 | - | -
|  |  | 7:00 |  | 6:00 |  | 17:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12780 | 24/06/19 | 12893 | 29/05/19 | 10948 | 06/06/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10554 | 24/06/19 | 10364.4 | 29/05/19 | 9178.2 | 07/06/18 | 10364.4 | 29/05/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12780 | 24/06/19 | 12893 | 29/05/19 | 10948 | 06/06/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11184.6333 |  | 11307.07 |  | 9879.5 |  | 11314.04 | May -19
7 | Average Generation (MW) at Day Peak | 8726.5667 |  | 9118.16 |  | 7768.98 |  | 8894.56 | May -19
8 | Maximum Power Import from India, HVDC (MW) | 949 | 09/06/19 | 946 | 08/05/19 | 481 | 17/06/18 | 956 | 27/3/2019
|  |  | 2:00 |  | 1:00 |  | 12:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 194 | 12'/06/19 | 190 | 11/05/19 | 186 | 06/06/18 | 194 | 12/06/19
|  |  | 19:00 |  | 21:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3440.1955 |  | 3572.91 |  | 3122.95 |  | 3572.91 | May-19
21 | Station Use of BPDB (MKWH) | 104.8438 |  | 123.1 |  | 101.45
22 | Net Generation of BPDB (MKWH) | 3335.3516 |  | 3449.81 |  | 3021.5
23 | Net Generation of IPP & RPCL (MKWH) | 2092.3389 |  | 2244.89 |  | 1704.95
24 | Net Generation of REB (MKWH) | 134.161 |  | 136.4 |  | 132.51
24 | Net Generation of Rental Power Plant (MKWH) | 497.087 |  | 497.34 |  | 634.29
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6058.9385 |  | 6328.44 |  | 5493.25 |  | 6328.44 | May-19
26 | Energy Generation by Gas (MKWH) | 4367.2451 |  | 4635.99 |  | 3635.45 |  | 4635.99 | May-19
27 | Energy Generation by Diesel (MKWH) | 300.7306 |  | 292.24 |  | 538.47 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1284.7373 |  | 1321.9 |  | 1128.82 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 26.8955 |  | 24.07 |  | 99.13 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 5.1029 |  | 3.98 |  | 0.32 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 180.8932 |  | 173.67 |  | 192.5 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 695.7256 |  | 762.63 |  | 419.73 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 74.5667 |  | 75.21 |  | 76.29 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:June' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12780 | 24/06/19 | 21:00
Generation Period
| Dhaka | MW | 4331
| Chattogram | MW | 1096
| Cumilla | MW | 1064
| Mymensingh | MW | 958
| Sylhet | MW | 497
a) | Total supply in East zone | MW | 7946
| Khulna | MW | 1324
| Barisal | MW | 349
| Rajshahi | MW | 1262
| Rangpur | MW | 693
b) | Total supply in West zone | MW | 3628
c) | Total supply in both zone ( a+b) | MW | 11574
Ref: | 27.21.2604.603.16.086.18.170 | Date: 14/07/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1400 | 14/06/19 | 1:00
| b) Ishurdi end | MW | 390 | 02/06/19 | 11:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 890 | 02/06/19 | 11:00
| b) Ishurdi end | MW | 520 | 14/06/19 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 7.9035 | 14/06/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 7.5607 | 14/06/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 71.5178
| b) Ishurdi end | MKWH | 14.3185
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 13.889
| b) Ishurdi end | MKWH | 69.4348
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 730 | 14/06/19 | 1:00
| b)Serajganj end | MW | 310 | 18/06/19 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 290 | 18/06/19 | 9:00
| b)Sirajganj end | MW | 670 | 14/06/19 | 1:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 12.266 | 14/06/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 11.968 | 14/06/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 80.824
| b)Sirajganj end | MKWH | 24.154
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 23.918
| b)Sirajganj end | MKWH | 80.006
30 | Transmission loss of EWI /NO-2 | % | 1.004
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV Transformer-T3 | 2019-06-02 23:58 | 2019-06-03 00:35 | 0:37 | T | Tripped showing O/C relay at 33 side | 55 | 33.9167 | Power interruption
Sherpur | 132/33 kV Transformer-T1 | 2019-06-03 10:50 | 2019-06-03 11:14 | 0:24 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2019-06-03 10:50 | 2019-06-03 11:14 | 0:24 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2019-06-05 12:59 | 2019-06-05 14:35 | 1:36 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Tangail | 33 kV all Transformer | 2019-06-05 17:48 | 2019-06-05 17:55 | 0:07 | E/O | Due to33 kV feeder CB burst | 100 | 11.6667 | Power interruption
Aminbazar | 230/132 kV Transformer T01 | 2019-06-08 11:06 | 2019-06-08 13:44 | 2:38 | T | Tripped showing Diff & Buchholz relay | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2019-06-08 10:33 | 2019-06-08 13:19 | 2:46 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Savar | 132/33 kV Transformers-T1 & T2 | 2019-06-13 06:19 | 2019-06-13 06:22 | 0:03 | T | Tripped showing O/C relay at 33 side | 78 | 3.9 | Power interruption
| 132/33 kV Transformer-T1 | 2019-06-15 08:23 | 2019-06-15 08:29 | 0:06 | T | Tripped showing main protection relay | 78 | 7.5 | Power interruption
| 132/33 kV Transformer-T1 | 2019-06-15 08:24 | 2019-06-15 08:29 | 0:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2019-06-15 08:01 | 2019-06-15 09:00 | 0:59 | T | Tripped showing E/F relay at 33 side | 20 | 19.6667 | Power interruption
Dhamrai | 132/33 kV Transformers-T1 & T2 | 2019-06-16 11:43 | 2019-06-16 12:03 | 0:20 | T | Tripped showing 33 kV feeder fault | 40 | 13.3333 | Power interruption
Kabirpur | 132/33 kV Transformer-T2 | 2019-06-16 09:05 | 2019-06-16 10:30 | 1:25 | E/O | Due to red hot maintenance at 33 kV bus isolator | 40 | 56.6667 | Power interruption
Mymensingh | 132/33 kV Transformer-T2 | 2019-06-20 20:50 | 2019-06-20 21:22 | 0:32 | T | Tripped showing E/F relay at 33 side | 60 | 32 | Power interruption
Netrakona | 132/33 kV Transformer-T3 | 2019-06-21 10:05 | 2019-06-21 11:10 | 1:05 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 13:07 |  | Unserved Energy: |  | 178.65
Dhaka (South) Grid Circle :
Siddhirganj | 230/132 kV Transformer-T02 | 2019-06-03 05:47 | 2019-06-03 08:25 | 2:38 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2019-06-17 20:58 | 2019-06-17 21:11 | 0:13 | T | Tripped showing O/C relay at 33 kV side | 65 | 14.0833 | Power interruption
| 132/33 kV Transformer-T1 | 2019-06-29 11:43 | 2019-06-29 11:49 | 0:06 | T | Tripped showing O/C relay | 60 | 6 | Power interruption
|  |  | Total : | 2:57 |  | Unserved Energy: |  | 20.0833
Chattogram Grid Circle :
Kagrachari | 132/33 kV Transformer-T1 | 2019-06-01 08:17 | 2019-06-01 08:42 | 0:25 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2019-06-05 22:12 | 2019-06-05 22:21 | 0:12 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2019-06-06 21:34 | 2019-06-06 22:30 | 0:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | 132/33 kV Transformer-T3 | 2019-06-16 14:37 | 2019-06-16 15:14 | 0:37 | T | Tripped showing E/F & O/C relay | 15 | 9.25 | Power interruption
Hathazari | 230/132 kV Transformer-MT-4 | 2019-06-19 05:48 | 2019-06-19 07:02 | 1:14 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2019-06-20 16:02 | 2019-06-20 17:12 | 1:10 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T2 | 2019-06-22 09:17 | 2019-06-22 09:45 | 0:28 | E/O | Due to red hot maintenance 33 kV side | 6 | 2.8 | Power interruption
| 132/33 kV Transformer-T1 | 2019-06-23 23:32 | 2019-06-24 00:25 | 0:53 | E/O | Due to red hot maintenance | 20 | 17.6667 | Power interruption
| 33 kV Bus & 132/33 kV Transformer T1 | 2019-06-24 13:43 | 2019-06-24 14:38 | 0:55 | E/O | Due to red hot maintenance | 18 | 16.5 | Power interruption
| 132/33 kV Transformer-T2 | 2019-06-26 11:30 | 2019-06-26 12:52 | 1:22 | E/O | Due to red hot maintenance | 36 | 49.2 | Power interruption
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2019-06-29 20:55 | 2019-06-29 22:43 | 1:48 | E/O | Due to bursting of 132/33 kV Transformer T2 | 59 | 106.2 | Power interruption
| 132/33 kV Transformer-T2 | 2019-06-30 17:24 | 2019-06-30 21:12 | 3:48 | T | Tripped showing winding temperature high | 45 | 171 | Power interruption
|  |  | Total : | 13:48 |  | Unserved Energy: |  | 372.6167
Cumilla Grid Circle :
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-06-06 08:04 | 2019-06-06 12:26 | 4:22 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2019-06-10 08:02 | 2019-06-10 09:29 | 1:27 | E/O | Due to red hot maintenance at 33 kV side | 20 | 29 | Power interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2019-06-17 02:53 | 2019-06-17 03:16 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ramganj | 33 kV Bus& 132/33 kV Transformer-T2 | 2019-06-18 06:36 | 2019-06-18 07:52 | 1:16 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-06-20 07:10 | 2019-06-20 10:39 | 3:29 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(S) | 33 kV Bus& 132/33 kV Transformer-T1 | 2019-06-21 21:06 | 2019-06-21 21:45 | 0:39 | E/O | Due to red hot maintenance at 33 kV side | 35 | 22.75 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2019-06-22 16:40 | 2019-06-22 17:38 | 0:58 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2019-06-24 06:30 | 2019-06-24 07:33 | 1:03 | E/O | Due to red hot maintenance | 8 | 66.15 | Power interruption
Chowmuhani | 33 kV Bus &132/33 kV Transformer-T3 | 2019-06-25 06:12 | 2019-06-25 06:55 | 0:43 | E/O | Due to red hot maintenance | 60 | 43 | Power interruption
Sunamganj | 132/33 kV Transformers-T1 | 2019-06-26 02:04 | 2019-06-26 03:57 | 1:53 | T | Tripped showing FEF650at 132 kV sides & REF 630 at 33 kV sides | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-06-26 02:04 | 2019-06-26 03:51 | 1:47 | T |  | 0 | 0 | No interruption
|  |  | Total : | 18:00 |  | Unserved Energy: |  | 160.9
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Noapara | 132/33 kV Transformer-T1 | 2019-06-03 07:12 | 2019-06-03 08:46 | 1:34 | T | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2019-06-03 08:51 | 2019-06-03 09:56 | 1:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2019-06-06 09:03 | 2019-06-06 10:37 | 1:34 | E/O | Due to red hot maintenance | 30 | 47 | Power interruption
Faridpur | 33 kV Bus section -3,4 | 2019-06-10 00:05 | 2019-06-10 00:44 | 0:39 | E/O | Due to red hot maintenance at 33 kV side | 60 | 390 | Power interruption
Noapara | 33 kV Bus-2 | 2019-06-10 07:42 | 2019-06-10 10:03 | 2:21 | E/O | Due to red hot maintenance | 28 | 65.8 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-06-11 21:38 | 2019-06-11 21:42 | 0:04 | T | Tripped showing E/F relay at 33 kV side | 36 | 1.7333 | Power interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-06-13 07:35 | 2019-06-13 09:09 | 1:34 | E/O | Due to red hot maintenance | 25 | 39.1667 | Power interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-06-14 04:45 | 2019-06-14 05:06 | 0:21 | E/O | Due to 33 kV new port feeder fault | 34 | 11.9 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-06-14 09:09 | 2019-06-14 09:43 | 0:34 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2019-06-15 15:04 | 2019-06-15 15:50 | 0:46 | E/O | Due to red hot maintenance | 30 | 23 | Power interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-06-17 06:19 | 2019-06-17 08:25 | 2:06 | E/O | Due to red hot maintenance | 21 | 44.1 | Power interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-06-17 08:12 | 2019-06-17 09:42 | 1:30 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-06-17 09:00 | 2019-06-17 10:24 | 1:24 | E/O | Due to red hot maintenance at 33 kV side | 20 | 11.3333 | Power interruption
Khulna© | 132/33 kV Transformer-T1 | 2019-06-17 08:03 | 2019-06-17 09:41 | 1:38 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-06-18 12:24 | 2019-06-18 13:01 | 0:37 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-06-19 04:42 | 2019-06-19 04:51 | 0:09 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2019-06-20 15:31 | 2019-06-20 15:36 | 0:05 | T | Tripped showing O/C relay | 130 | 10.8333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-06-20 15:31 | 2019-06-20 17:27 | 1:56 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T4 | 2019-06-21 14:12 | 2019-06-21 14:17 | 0:05 | E/O | Due to 33 kV feeder fault | 40 | 3.3333 | Power interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-06-26 17:05 | 2019-06-26 17:11 | 0:06 | T | Tripped showing O/C & E/F relay at 33 kV side | 10 | 1 | Power interruption
| 132/33 kV Transformers-T1 | 2019-06-30 06:08 | 2019-06-30 06:17 | 0:09 | E/O | Due to 33 kV feeder fault | 40 | 6 | Power interruption 06:08 to 6:17
| 132/33 kV Transformers-T3 | 2019-06-30 06:08 | 2019-06-30 06:18 | 0:10 | E/O
|  |  | Total : | 20:27 |  | Unserved Energy: |  | 655.2
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T2 | 2019-06-12 22:39 | 2019-06-13 10:43 | 12:04 | T | Tripped showing differential relay | 0 | 0 | No interruption
| 230/132 kV Transformer-T3 | 2019-06-20 15:20 | 2019-06-20 17:15 | 1:55 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2019-06-22 08:16 | 2019-06-22 09:15 | 0:59 | E/O | Due to red hot maintenance at 33 kV side | 30 | 29.5 | Power interruption
Pabna | 132/33 kV Transformer-T3 | 2019-06-30 10:12 | 2019-06-30 15:05 | 4:53 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 19:51 |  |  |  | 29.5
Bogura Grid Circle:
Naogaon | 132/33 kV Transformer-T2 | 2019-06-01 22:30 | 2019-06-01 23:20 | 0:50 | E/O | Due to red hot maintenance | 25 | 20.8333 | Power interruption
Rangpur | 33 kV Bus section -2 | 2019-06-16 08:40 | 2019-06-16 09:40 | 1:00 | E/O | Due to red hot maintenance at 33 kV CB | 40 | 40 | Power interruption
Lalmonirhat | 132/33 kV Transformer-T4 | 2019-06-16 11:03 | 2019-06-16 12:25 | 1:22 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T3 | 2019-06-20 07:50 | 2019-06-20 08:51 | 1:01 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T2 | 2019-06-22 11:22 | 2019-06-22 11:58 | 0:36 | E/O | Due to red hot maintenance | 6 | 3.6 | Power interruption
Saidpur | 132/33 kV Transformer-T3 | 2019-06-27 05:50 | 2019-06-27 06:30 | 0:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2019-06-27 14:50 | 2019-06-27 17:12 | 2:22 | E/O | Due to red hot maintenance | 22 | 52.0667 | Power interruption
Saidpur | 132/33 kV Transformer-T5 | 2019-06-27 19:28 | 2019-06-27 20:50 | 1:22 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2019-06-28 02:55 | 2019-06-28 03:10 | 0:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformers-T1 & T2 | 2019-06-28 20:01 | 2019-06-28 20:09 | 0:08 | T | Tripped showing 33 kV feeder fault | 120 | 16 | Power interruption
|  |  | Total : | 9:36 |  | Unserved Energy: |  | 132.5
Others :
Bashundhara | 132/33 kV Transformer-T2 | 2019-06-29 16:42 | 2019-06-30 03:30 | 10:48 | E/O | Due to Oil leakage | 29 | 313.2 | Power interruption
|  |  | Total : | 10:48 |  | Unserved Energy: |  | 313.2
Total outage period of Sub-station Equipment : |  |  |  | 108:34 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2019-06-01 23:57 | 2019-06-02 00:36 | 0:39 | T | Tripped showing dist. & directional relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-06-02 10:55 | 2019-06-02 11:04 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir -Tangail132 kV line-1 | 2019-06-02 14:38 | 2019-06-02 20:42 | 6:04 | T | Tripped showing directional ,O/C & E/F relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-06-03 14:22 | 2019-06-03 15:29 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2019-06-05 05:44 | 2019-06-05 05:54 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi(old) | Tongi(old)-New Tongi 132 kV line | 2019-06-05 20:45 | 2019-06-05 20:59 | 0:14 | T | Tripped showing Diff.. relay | 36 | 8.4 | Power interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2019-06-05 22:04 | 2019-06-05 23:26 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Tangail-Kaliakoir 132 kV line-1 | 2019-06-06 06:48 | 2019-06-06 07:47 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2019-06-11 11:21 | 2019-06-11 15:19 | 1:51 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2019-06-16 10:43 | 2019-06-16 12:40 | 1:57 | T | Tripped showing dist.& E/F relay | 40 | 78 | Power interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 & 2 | 2019-06-17 20:53 | 2019-06-17 21:01 | 0:08 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
| Mymensingh-Bhaluka 132 kV line-1 & 2 | 2019-06-17 20:55 | 2019-06-17 21:11 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2019-06-17 10:37 | 2019-06-17 10:47 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-2 | 2019-06-17 10:37 | 2019-06-17 10:53 | 0:16 | T |  | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 | 2019-06-20 09:14 | 2019-06-20 11:52 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 & 2 | 2019-06-22 12:43 | 2019-06-22 13:49 | 1:06 | T | Tripped showing sky wire fail on CKT-1 & 2 | 104 | 114.4 | Power interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-06-23 11:37 | 2019-06-23 11:47 | 0:10 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2019-06-23 11:38 | 2019-06-23 11:47 | 0:09 | T | Tripped showing O/C relay | 144 | 21.6 | Power interruption
Aminbazar | Aminbazar-Basila 132 kV line | 2019-06-24 07:12 | 2019-06-24 09:01 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV line-1 | 2019-06-27 22:20 | 2019-06-27 22:46 | 0:26 | T | Tripped showing dist. relay | 100 | 43.3333 | Power interruption
| Mymensingh-Bhaluka 132 kV line-2 | 2019-06-27 22:20 | 2019-06-27 22:47 | 0:27 | T | Tripped showing dist. relay
|  |  | Total : | 22:39 |  | Unserved Energy: |  | 265.7333
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 230 kV line-2 | 2019-06-03 10:25 | 2019-06-03 12:16 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur (N) 132 kV line-1 | 2019-06-08 06:42 | 2019-06-08 08:13 | 1:31 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Shyampur(O)-Shyampur (N) 132 kV line | 2019-06-08 13:04 | 2019-06-08 13:06 | 0:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-2 | 2019-06-12 00:02 | 2019-06-12 09:20 | 9:18 | T | Tripped showing C-phase voltage failure | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-2 | 2019-06-15 07:42 | 2019-06-15 10:49 | 3:07 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2019-06-15 08:18 | 2019-06-15 09:51 | 1:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalakhya 132 kV line | 2019-06-15 08:40 | 2019-06-15 09:09 | 0:29 | T | Tripped showing main protection . relay | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi 132 kV line-2 | 2019-06-19 14:33 | 2019-06-19 21:29 | 6:56 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
| Bashundhara-Tongi 132 kV line-1 | 2019-06-19 14:33 | 2019-06-19 14:45 | 0:12 | E/O |  | 55 | 11 | Power interruption
| Bashudhara-Tongi 132 kV line-1 | 2019-06-21 08:23 | 2019-06-21 09:20 | 0:57 | T | Tripped showing temperature high | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2019-06-22 07:33 | 2019-06-22 09:22 | 1:49 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line | 2019-06-24 11:10 | 2019-06-24 11:34 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bashundhara | Bashundhara-Tongi 132 kV line-2 | 2019-06-26 11:00 | 2019-06-26 14:25 | 3:25 | T | Tripped showing diff.relay | 0 | 0 | No interruption
|  |  | Total : | 15:45 |  | Unserved Energy: |  | 11
Chittagong Grid Circle :
Sikalbaha S/S | Sikalbaha S/S-Sikalbaha P/S 132 kV line | 2019-06-06 11:15 | 2019-06-06 11:45 | 0:30 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K. chemical 132 kV line | 2019-06-10 08:40 | 2019-06-10 10:47 | 2:07 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line-2 | 2019-06-14 02:54 | 2019-06-14 03:28 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hathazari-Baroihat 132 kV line-2 | 2019-06-15 13:33 | 2019-06-15 13:52 | 0:19 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line | 2019-06-30 14:09 | 2019-06-30 14:39 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 4:00 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-06-02 13:26 | 2019-06-02 14:13 | 0:47 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV line-2 | 2019-06-02 13:26 | 2019-06-02 13:36 | 0:10 | T |  | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.baria 132 kV line | 2019-06-04 09:30 | 2019-06-04 09:45 | 0:15 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur Desh 132 kV line | 2019-06-05 12:44 | 2019-06-05 14:51 | 2:07 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-06-02 12:24 | 2019-06-02 12:40 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj -Sirajganj 230 kV line-2 | 2019-06-10 19:29 | 2019-06-10 19:39 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2019-06-11 04:38 | 2019-06-11 18:13 | 13:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-06-11 11:49 | 2019-06-11 12:22 | 0:33 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2019-06-12 09:20 | 2019-06-12 12:17 | 2:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-06-19 11:34 | 2019-06-19 11:46 | 0:12 | T | Tripped showing dist. O/C & E/F relay | 0 | 0 | No interruption
Chandpur | ChandpurCumilla(N) 132 kV line-2 | 2019-06-20 13:40 | 2019-06-20 13:49 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2019-06-20 23:15 | 2019-06-20 23:36 | 0:21 | T | Tripped showing dir.& O/C. relay | 232 | 81.2 | Power interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV line-1 &2 | 2019-06-22 13:36 | 2019-06-22 14:22 | 0:46 | T | Tripped showing dist. relay | 136 | 104.2667 | Power interruption
Chatak | Chatak-Sunamganj 132 kV line-1 | 2019-06-25 23:12 | 2019-06-26 00:29 | 1:17 | T | Tripped showing dist.(B-phase) relay | 0.5 | 0.64167 | Power interruption
Surjamoninagar | Surjamoninagar-Cumilla(S) 132 kV line-1 & 2 | 2019-06-27 03:32 | 2019-06-27 04:17 | 0:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 24:20 |  | Unserved Energy: |  | 186.1083
Khulna Grid Circle :
Khulna(C) | Khulna©-Noapara 132 kV line-2 | 2019-06-05 13:49 | 2019-06-05 14:23 | 0:34 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2019-06-09 13:24 | 2019-06-09 14:17 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Barisal(N)-Bhola 230 kV line-1 | 2019-06-22 12:51 | 2019-06-22 13:34 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 2:10 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2019-06-05 05:44 | 2019-06-05 05:55 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV line | 2019-06-05 05:44 | 2019-06-05 06:34 | 0:50 | T | Tripped showing dist.CSW,CAS,CD & CE signal | 0 | 0 | No interruption
| Ishurdi-Baghabari 132 kV line | 2019-06-05 05:45 | 2019-06-05 06:20 | 0:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV line | 2019-06-05 05:44 | 2019-06-05 06:41 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Bheramara P/S 132 kV line | 2019-06-06 15:04 | 2019-06-06 15:14 | 1:36 | E/O | Tripped showing Oil leakage | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2019-06-14 01:01 | 2019-06-14 01:17 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 | 2019-06-29 10:35 | 2019-06-29 11:02 | 0:27 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
|  |  | Total : | 4:52 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Naogaon | Naogaon-Niyamatpur 132 kV line | 2019-06-17 22:30 | 2019-06-17 22:39 | 0:09 | T | Tripped showing dist. relay | 40 | 6 | Power interruption
Bogura | Bogura -Mohasthanghar 132 kV line-1 | 2019-06-19 10:02 | 2019-06-19 14:20 | 4:18 | T | Tripped showing dist. relay | 20 | 86 | Power interruption
Palashbari | Palashbari-Mahasthangar 132 kV line-2 | 2019-06-19 14:33 | 2019-06-19 14:51 | 0:18 | T | Tripped showing dist. relay | 30 | 9 | Power interruption
Rangpur | Rangpur-Rangpur confidance 132 kV line-2 | 2019-06-20 10:10 | 2019-06-20 10:33 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mohasthangar | Mohasthangar-Bogura 132 kV line-2 | 2019-06-22 23:15 | 2019-06-23 00:14 | 0:59 | E/O | Due to red hot maintenance | 35 | 34.4167 | Power interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2019-06-24 12:21 | 2019-06-24 13:18 | 0:57 | E/O | Due to red hot maintenance | 30 | 28.5 | Power interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2019-06-24 20:12 | 2019-06-24 20:15 | 0:03 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-1 & 2 | 2019-06-25 10:20 | 2019-06-25 10:42 | 0:22 | T | Tripped showing dist. relay | 170 | 62.3333 | Power interruption
| Rangpur-Saidpur 132 kV line-1 & 2 | 2019-06-25 20:54 | 2019-06-25 21:22 | 0:28 | T | Tripped showing dist.(B-phase) relay | 30 | 14 | Power interruption
| Rangpur-Barapukuria 132 kV line-1 & 2 | 2019-06-25 20:59 | 2019-06-25 21:29 | 0:30 | T | Tripped showing dist. relay | 140 | 70 | Power interruption
Natore | Natore-Rajsahahi 132 kV line-1 | 2019-06-27 02:37 | 2019-06-27 02:45 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Natore-Ishurdi 132 kV line | 2019-06-27 02:37 | 2019-06-27 03:04 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-2 | 2019-06-27 19:28 | 2019-06-27 20:12 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 & 2 | 2019-06-27 19:38 | 2019-06-27 20:12 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mahasthangar 132 kV line | 2019-06-28 15:58 | 2019-06-28 16:09 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 11:02 |  | Unserved Energy: |  | 310.25
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 84:48 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV Transformer-T3 | 2019-06-03 11:24 | 2019-06-03 13:41 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2019-06-06 08:06 | 2019-06-06 08:53 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2019-06-06 10:26 | 2019-06-06 19:04 | 8:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2019-06-07 07:33 | 2019-06-07 10:26 | 2:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-06-07 10:31 | 2019-06-07 11:48 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 33 kV Bus with132/33 kV Transformers-T1 & T2 | 2019-06-08 06:29 | 2019-06-08 08:31 | 2:02 | S/O | Due to C/M work | 60 | 122 | Power interruption
Kaliakoir | 400/132 kV Transformer-TR1 | 2019-06-08 07:07 | 2019-06-08 08:29 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-2 | 2019-06-09 11:55 | 2019-06-09 15:29 | 3:34 | S/O | Due to isolator maintenance | 0 | 0 | No interruption
| 230/132 kV Transformer-T-1 | 2019-06-10 10:35 | 2019-06-10 14:26 | 3:51 | S/O | Due to protection work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-06-12 09:18 | 2019-06-12 13:05 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2019-06-14 12:25 | 2019-06-14 12:50 | 0:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | 132 kV Bus &132/33 kV Transformer-T3 | 2019-06-19 10:22 | 2019-06-19 11:38 | 1:16 | S/O | Due to changing of 33 kV Bus | 0 | 0 | No interruption
Bibiyana | 230 kV Bus-2 | 2019-06-20 09:06 | 2019-06-20 17:31 | 8:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2019-06-21 06:37 | 2019-06-21 09:20 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 33 kV Bus &132/33 kV Transformers-T1 & T2 | 2019-06-22 06:04 | 2019-06-22 09:35 | 3:31 | S/O | Due to replacement work | 100 | 351.6667 | Power interruption
Savar | 132 kV main Bus | 2019-06-28 06:30 | 2019-06-28 08:22 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2019-06-30 15:18 | 2019-06-30 15:18 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 48:40 |  | Unserved Energy: |  | 473.6667
Dhaka (South) Grid Circle :
Siddhirganj | 230/132 kV Transformer-TR-1 | 2019-06-04 06:54 | 2019-06-04 10:10 | 3:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 | 2019-06-08 10:15 | 2019-06-08 10:43 | 0:28 | S/O | Due to changing work | 0 | 0 | No interruption
Madartak | 132/33 kV Transformer-T2 | 2019-06-16 18:34 | 2019-06-16 18:34 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2019-06-22 07:09 | 2019-06-22 08:47 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsinghdi | 132 kV Bus-1 | 2019-06-27 10:19 | 2019-06-27 15:10 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-GT2 | 2019-06-27 16:41 | 2019-06-27 17:30 | 0:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-TR-2 | 2019-06-28 05:12 | 2019-06-28 11:25 | 6:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T2 | 2019-06-28 07:32 | 2019-06-28 12:50 | 5:18 | S/O | Due to C/M work | 40 | 212 | Power interruption
Siddhirganj | 230/132 kV Transformer-MTR-2 | 2019-06-29 06:29 | 2019-06-29 08:40 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 24:44 |  | Unserved Energy: |  | 212
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformer-T2 | 2019-06-06 14:50 | 2019-06-06 15:30 | 0:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Modern steel | 132/33 kV Transformer-Tr | 2019-06-08 10:38 | 2019-06-08 10:50 | 0:12 | S/O | Due to replacement work at 33 kV bushing | 0 | 0 | No interruption
T.K.chemical | 132/33 kV Transformer-Tr | 2019-06-09 12:18 | 2019-06-09 17:22 | 5:04 | S/O | Due to 33 kV cable problem | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2019-06-11 07:07 | 2019-06-11 11:34 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132 kV main bus-2 | 2019-06-14 06:00 | 2019-06-14 08:00 | 2:00 | S/O | Due to C/M work | 36 | 72 | Power interruption
T.K.chemical | 132/33 kV Transformer-T1 | 2019-06-21 07:07 | 2019-06-21 11:34 | 4:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2019-06-21 08:18 | 2019-06-21 11:54 | 3:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 230/132 kV Transformer-MTR-2 | 2019-06-28 09:38 | 2019-06-28 13:37 | 3:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Khagrachari | 132/33 kV Transformer-T2 | 2019-06-28 11:57 | 2019-06-28 12:40 | 0:43 | S/O | Due to sparking at 33 kV CT point | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2019-06-29 06:24 | 2019-06-29 18:07 | 11:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 230/132 kV Transformer-TR-1 | 2019-06-29 09:23 | 2019-06-29 11:21 | 1:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2019-06-29 09:41 | 2019-06-29 16:15 | 6:34 | S/O | Due to maintenance of 33 kV feeder | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2019-06-30 17:20 | 2019-06-30 17:30 | 0:10 | S/O | Due to 33 CB pole maintenance | 0 | 0 | No interruption
|  |  | Total : | 45:33 |  | Unserved Energy : |  | 72
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ramganj | 132/33 kV Transformer-T2 | 2019-06-01 10:34 | 2019-06-01 11:58 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T1 | 2019-06-01 13:13 | 2019-06-01 16:08 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 & 33 kV bus | 2019-06-03 06:25 | 2019-06-03 09:40 | 3:15 | S/O | Due to C/M work by PBS | 25 | 81.25 | Power interruption
Sreemongal | 132/33 kV Transformer-T1 | 2019-06-09 09:29 | 2019-06-09 10:58 | 1:29 | S/O | Due to gounding connection problem | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2019-06-15 07:04 | 2019-06-15 20:25 | 13:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2019-06-18 08:47 | 2019-06-18 10:43 | 1:56 | S/O | Due to replacement work | 0 | 0 | No interruption
Bianibazar | 132/33 kV Transformer-T2 & 33 kV bus | 2019-06-20 08:01 | 2019-06-20 12:00 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T3 | 2019-06-21 07:10 | 2019-06-21 07:55 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400 kV main bus-1 | 2019-06-24 09:00 | 2019-06-24 17:05 | 8:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Sunamganj | 33 kV Bus | 2019-06-26 15:47 | 2019-06-26 18:25 | 2:38 | S/O | Due to replacement work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-06-28 09:06 | 2019-06-28 12:46 | 3:40 | S/O | Due to extension work | 40 | 146.6667 | Power interruption
Feni | 132/33 kV Transformer-T2 | 2019-06-30 13:11 | 2019-06-30 21:36 | 8:25 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 51:52 |  | Unserved Energy : |  | 227.9167
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformer-T1 | 2019-06-01 12:27 | 2019-06-01 13:09 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T2 | 2019-06-06 12:35 | 2019-06-06 13:19 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformers-T4 & T5 | 2019-06-06 10:49 | 2019-06-06 11:51 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-06-06 14:22 | 2019-06-06 17:25 | 3:03 | S/O | Due to DC failure | 0 | 0 | No interruption
Patuakhali | 132 kV main bus | 2019-06-11 07:05 | 2019-06-11 09:51 | 2:46 | S/O | Due to D/W work | 44 | 55.7333 | Power interruption
Bagerhat | 33 kV Bus | 2019-06-14 06:10 | 2019-06-14 07:09 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-06-24 07:18 | 2019-06-24 10:06 | 2:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-06-24 07:46 | 2019-06-24 12:58 | 5:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-06-24 10:08 | 2019-06-24 11:52 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 19:00 |  | Unserved Energy : |  | 55.7333
HVDC Grid Circle :
Shahjadpur | 132/33 kV Transformer-T1 | 2019-06-02 12:07 | 2019-06-02 12:43 | 12:04 | S/O | Due to 33 kV incoming CT Oil fiting | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T2 | 2019-06-02 11:10 | 2019-06-02 13:10 | 2:00 | S/O | Due to 33 kV CT change | 0 | 0 | No interruption
|  |  | Total : | 14:04 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Bogura | 33 kV Bus of 132/33 kV Transformer T3 & T4 | 2019-06-08 07:10 | 2019-06-08 08:47 | 1:37 | S/O | Due to C/M work | 60 | 97 | Power interruption
Barapukuria | 230/132 kV Transformer-T01 | 2019-06-12 08:30 | 2019-06-12 18:09 | 9:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2019-06-21 06:04 | 2019-06-21 15:16 | 9:12 | S/O |  | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T2 | 2019-06-22 09:05 | 2019-06-30 18:20 | 201:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-06-28 06:01 | 2019-06-28 11:43 | 5:42 | S/O | Due to D/W work | 40 | 228 | Power interruption
|  |  | Total : | 227:25 |  | Unserved Energy : |  | 325
Others :
Dhanmondi | 132/33 kV Transformer-T4 |  | 2019-06-16 20:38 |  | S/O | Due to maintenance work | 0 | 0 | No interruption | No interruption
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 431:18 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: June 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-06-06 10:31 | 2019-06-06 18:47 | 8:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV line-2 | 2019-06-06 10:32 | 2019-06-07 12:50 | 26:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2019-06-08 07:20 | 2019-06-08 09:29 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2019-06-08 09:51 | 2019-06-08 14:30 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2019-06-08 09:33 | 2019-06-08 13:39 | 4:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Mymensingh RPCL 132 kV line-2 | 2019-06-10 11:26 | 2019-06-10 15:03 | 3:37 | S/O | Due to protection test | 0 | 0 | No interruption
| Mymensingh-Mymensingh RPCL 132 kV line-1 | 2019-06-10 15:10 | 2019-06-10 18:20 | 3:10 | S/O | Due to protection test | 0 | 0 | No interruption
United Mymensingh | United Mymensingh-Sherpur 132 kV line-1 & 2 | 2019-06-14 06:30 | 2019-06-14 14:12 | 7:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Tongi(New) 132 kV line-1 | 2019-06-05 20:45 | 2019-06-14 08:45 | 204:00 | S/O |  | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2019-06-21 06:38 | 2019-06-21 11:48 | 5:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-06-22 08:30 | 2019-06-22 10:50 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2019-06-22 17:15 | 2019-06-23 16:39 | 23:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-1 | 2019-06-25 05:32 | 2019-06-25 17:30 | 11:58 | S/O | Due to changing work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-06-26 10:02 | 2019-06-26 17:27 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail -Mymensingh RPCL 132 kV line-1 | 2019-06-27 11:31 | 2019-06-27 16:22 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2019-06-28 06:06 | 2019-06-28 08:39 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 321:38 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-06-06 07:36 | 2019-06-06 13:33 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Siddhirganj-Matuail 132 kV line-1 | 2019-06-06 12:37 | 2019-06-06 18:39 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-3 | 2019-06-07 06:00 | 2019-06-07 21:11 | 15:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-2 | 2019-06-16 10:11 | 2019-06-16 10:11 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sitalakhya | Sitalakhya-Hasnabad 132 kV line | 2019-06-22 16:33 | 2019-06-22 19:37 | 3:04 | S/O | Due to Isolate fire | 10.5 | 32.2 | Power interruption
| Sitalakhya-Madanganj 132 kV line | 2019-06-22 16:28 | 2019-06-22 19:52 | 3:24 | S/O |  | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2019-06-27 08:19 | 2019-06-27 08:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-06-28 07:44 | 2019-06-28 12:02 | 4:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar 132 kV line | 2019-06-28 07:43 | 2019-06-28 11:53 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-APR 132 kV line | 2019-06-29 07:41 | 2019-06-29 20:30 | 12:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Shyampur 230 kV line | 2019-06-30 07:32 | 2019-06-30 15:02 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 62:25 |  | Unserved Energy: |  | 32.2
Chattogram Grid Circle :
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2019-06-01 04:50 | 2019-06-01 06:46 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madunaghat-T.K.chemical 132 kV line 132 kV line | 2019-06-01 06:47 | 2019-06-01 07:54 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madunaghat-T.K.chemical 132 kV line 132 kV line | 2019-06-14 10:54 | 2019-06-14 14:33 | 3:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK.chemical 132 kV line | 2019-06-14 10:54 | 2019-06-14 14:33 | 3:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sikalbaha-TK.chemical 132 kV line | 2019-06-20 07:09 | 2019-06-20 09:57 | 2:48 | S/O | Due to D/W work | 0 | 0 | No interruption
T.K chemical | T.K chemical-Madunaghat 132 kV line | 2019-06-21 07:13 | 2019-06-21 09:59 | 2:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-2 | 2019-06-23 13:35 | 2019-06-23 14:17 | 0:42 | S/O | Due to CB problem | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K.chemical 132 kV line 132 kV line | 2019-06-24 07:16 | 2019-06-24 08:01 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK.chemical 132 kV line | 2019-06-24 07:17 | 2019-06-24 08:02 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2019-06-30 10:54 | 2019-06-30 13:11 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 20:24 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: June 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj Network | Ashuganj Network-Ashuganj(S) 230 kV line-1 | 2019-05-30 19:34 | 2019-06-02 11:53 | 9:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 230 kV Bus coupler breaker | 2019-05-30 19:34 | 2019-06-02 12:19 | 9:48 | S/O |  | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Baraka P/S 132 kV -1 | 2019-06-08 07:50 | 2019-06-08 17:29 | 13:42 | S/O |  | 0 | 0 | No interruption
| Fenchuganj S/S-Fenchuganj P/S 132 kV line-2 | 2019-06-08 07:51 | 2019-06-08 17:39 | 9:48 | S/O | Due to Baraka bay maintenance work | 0 | 0 | No interruption
| Fenchuganj S/S-Fenchuganj P/S 132 kV line-3 | 2019-06-08 07:54 | 2019-06-08 21:36 | 13:42 | S/O |  | 0 | 0 | No interruption
United P/S | United P/S-Ashuganj 230 kV line | 2019-06-10 19:23 | 2019-06-15 16:28 | 117:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2019-06-16 11:05 | 2019-06-16 13:59 | 2:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2019-06-17 13:42 | 2019-06-17 13:55 | 0:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 132 kV line-2 | 2019-06-19 08:35 | 2019-06-19 17:15 | 8:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroarhat 132 kV line-2 | 2019-06-20 09:58 | 2019-06-20 13:30 | 3:32 | S/O | Due to changing work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2019-06-20 22:28 | 2019-06-20 23:49 | 1:21 | S/O | Due to removing antenna | 0 | 0 | No interruption
Ashuganj | Ashuganj S/S-Ashuganj United P/S 132 kV line | 2019-06-23 15:05 | 2019-06-27 00:50 | 81:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 272:09 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | Barisal-Madaripur 132 kV line-2 | 2019-06-22 08:20 | 2019-06-22 11:36 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-NWCCP 132 kV line | 2019-06-28 06:34 | 2019-06-28 09:58 | 3:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2019-06-28 06:49 | 2019-06-28 12:31 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 12:22 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Pabna | Pabna-Shahjadpur 132 kV line | 2019-06-07 22:20 | 2019-07-07 00:47 | 698:27 | S/O | Due to low load | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV line-1 |  | 2019-06-05 17:26 | 6:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bottail | Bottail-Jhenidah 132 kV line-2 | 2019-06-18 17:21 | 2019-06-18 17:58 | 0:37 | S/O | Due to protection work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Bheramara 400 kV line-2 | 2019-06-28 06:01 | 2019-06-28 09:52 | 1:13 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 706:39 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura-Mohastanghor 132 kV line-2 | 2019-06-01 13:45 | 2019-06-01 14:41 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nwabganj | C.nwabganj-Amnura 132 kV line |  | 2019-06-02 12:01 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-1 | 2019-06-15 11:40 | 2019-06-15 17:15 | 5:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-1 | 2019-06-22 09:16 | 2019-06-22 12:01 | 6:22 | S/O | Due to changing work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-2 | 2019-06-22 12:05 | 2019-06-22 14:53 | 6:22 | S/O | Due to changing work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2019-06-27 06:55 | 2019-06-27 13:38 | 6:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Palashbari 132 kV line-1 & 2 | 2019-06-27 23:50 | 2019-06-28 01:30 | 6:22 | S/O | Due to removing work | 0 | 0 | No interruption
|  |  | Total : | 32:20 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 1427:57 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June' 2019
| Area | Previous Month (May 2019) |  |  |  | Current Month (June 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 25 | 11 | 34 | 70 | 24 | 11 | 33 | 68
2 | Dhaka (South) Grid Circle. | 27 | 5 | 34 | 66 | 9 | 8 | 20 | 37
3 | Chattogram Grid Circle. | 15 | 4 | 16 | 35 | 7 | 10 | 23 | 40
4 | Cumilla Grid Circle. | 37 | 19 | 24 | 80 | 17 | 9 | 24 | 50
5 | Khulna Grid Circle. | 33 | 11 | 23 | 67 | 9 | 16 | 12 | 37
6 | Bheramara HVDC Grid Circle | 9 | 5 | 9 | 23 | 8 | 3 | 6 | 17
7 | Bogura Grid Circle. | 21 | 11 | 42 | 74 | 15 | 10 | 12 | 37
8 | Others |  |  | 1 | 1 |  | 1 | 1 | 2
9 | Total | 167 | 66 | 183 | 416 | 89 | 68 | 131 | 288
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June' 2019
| Area | Previous Month (May 2019) |  |  |  | Current Month (June 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 1679.46 | 114.85 | 213.35 | 2007.66 | 376.05 | 68.34 | 473.67 | 918.06
2 | Dhaka (South) Grid Circle. | 113.6 | 34.33 | 209 | 356.93 | 20.08 | 11 | 244.2 | 275.28
3 | Chattogram Grid Circle. | 17.6 | 32.5 | 526.63 | 576.73 | 180.25 | 192.37 | 72 | 444.62
4 | Cumilla Grid Circle. | 106.98 | 158.43 | 809.17 | 1074.58 | 186.11 | 160.9 | 227.92 | 574.93
5 | Khulna Grid Circle. | 95.67 | 42.75 | 385.13 | 523.55 | 13.56 | 641.63 | 55.73 | 710.92
6 | Bheramara HVDC Grid Circle | 9.45 | 8.4 | 13.67 | 31.52 | 29.5 | - | - | 29.5
7 | Bogura Grid Circle. | 107.05 | 115.7 | 22.18 | 244.93 | 263.33 | 179.42 | 325 | 767.75
8 | Others | - | - | - | 0 | - | 313.2 | - | 313.2
9 | Total | 2129.81 | 506.96 | 2179.13 | 4815.9 | 1068.88 | 1566.86 | 1398.52 | 4034.26
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 7 | 2 | 9 | 4 | 2 | 3 | 652.32
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 | 2 | - | 1 | 232.08
3 | Chattogram | 2042 | 7 | 1 | 8 | 1 | 3 | 4 | 444.62
4 | Khulna | 2434 | 12 | 1 | 13 | 5 | 2 | 6 | 710.93
5 | Bheramara (HVDC) | 2423.3 | 1 |  | 1 | 1 |  |  | 29.5
6 | Bogura | 3145.6 | 4 | 2 | 6 | 2 | 1 | 3 | 457.5
7 | Cumilla | 2981 | 4 | 2 | 6 | 1 | 1 | 4 | 388.82
| Total | 23365.5 | [6 empty] | 2915.77
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.94%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.69% | [6 empty] | Executive Engineer
6 | Bogura | 99.98% | [6 empty] | Information Management Division
7 | Cumilla | 99.98% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 5 | - | 5 | 3 | - | 2 | 265.73
2 | Dhaka (South) | 990.29 |  | 1 | 1 | 2 | 1 | - | 1 | 43.2
3 | Chattogram | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 7 |  | 7 | 4 | 2 | 1 | 310.25
7 | Cumilla | 1648.16 | 17 | 2 |  | 2 | 1 | 1 | - | 186.11
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 805.29
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.94%
2 | Dhaka (South) | 99.84%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.96% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.93% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-06-18 | 20 |  | 10 | 16hr27min | 1 | 2hr8min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:June' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 1 | 0:37 | 55 | 33.9167 | Due to tripping of 132/33 kV Transformer T1
Tangail |  | 0:07 | 100 | 11.6667 | Due to bursting of 33 kV CB
Savar |  | 0:03 | 78 | 3.9 | Due to tripping of 132/33 kV Transformers T1,& T2
| 2 | 0:06 | 78 | 7.5 | Due to tripping of 132/33 kV Transformer T1
Tongi | 1 | 0:59 | 20 | 19.6667 | Due to tripping of 132/33 kV Transformer T3
Dhamrai | 1 | 0:20 | 40 | 13.3333 | Due to tripping of 132/33 kV Transformers T1,& T2
Kabirpur | 1 | 1:25 | 40 | 56.6667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Mymensingh | 1 | 0:32 | 60 | 32 | Due to tripping of 132/33 kV Transformer T2
Tongi(O) |  | 0:14 | 36 | 8.4 | Due to tripping of Tongi-New Tongi 132 kV line
Kaliakoir |  | 1:57 | 40 | 78 | Due to tripping of Kaliakoir-Kabirpur 132 kV line-1
Aminbazar |  | 1:06 | 104 | 114.4 | Due to tripping of Aminbazar-Savar 132 kV line-1 & 2
Mymensingh | 2 | 0:09 | 144 | 21.6 | Due to tripping of Mymensingh-Jamalpur 132 kV line-2
|  | 0:26 | 100 | 43.3333 | Due to tripping of Mymensingh-Bhluka 132 kV line-1
Jamalpur | 1 | 2:02 | 60 | 122 | Due to S/D of 132/33 kV Transformers T1 & T2
Mymensingh | 1 | 3:31 | 100 | 351.6667
Narsinghdi | 2 | 0:13 | 65 | 14.0833 | Due to tripping of 132/33 kV Transformer T2
|  | 0:06 | 60 | 6 | Due to tripping of 132/33 kV Transformer T1
Bashundhara | 2 | 0:12 | 55 | 11 | Due to tripping of Bashundhara-Tongi 132 kV line-1
|  | 10:48 | 29 | 313.2 | Due to Oil eakage of 132/33 kV Transformer T2
Narsinghdi | 1 | 5:18 | 40 | 212 | Due to S/D of 132/33 kV Transformer T2
Sitalakhya | 1 | 3:04 | 10.5 | 32.2 | Due to S/D of Sitalakhya -Hasnabad 132 kV line
Sikalbaha |  | 0:37 | 15 | 9.25 | Due to tripping of 132/33 kV Transformer T3
Dohazari | 3 | 0:28 | 6 | 2.8 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 0:53 | 20 | 17.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:55 | 18 | 16.5
|  | 1:22 | 36 | 49.2
Madunaghat | 2 | 1:48 | 59 | 106.2 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 3:48 | 45 | 171 | Due to tripping of 132/33 kV Transformer T2
Hathazari | 1 | 2:00 | 36 | 72
Ramganj | 1 | 1:27 | 20 | 29 | Due to red-hot maintenance of 132/33 kV Transformer T1
Cumilla(S) |  | 0:39 | 35 | 22.75 | Due to red-hot maintenance of 132/33 kV Transformer T1
Sreemongal |  | 1:03 | 8 | 66.15
Chowmuhani |  | 0:43 | 60 | 43 | Due to red-hot maintenance of 132/33 kV Transformer T3
Sylhet |  | 0:21 | 232 | 81.2 | Due to tripping of Sylhet-Fenchuganj
Cumilla(S) | 1 | 0:36 | 136 | 104.2667 | Due to tripping of Cumilla(S)-Surjamoninagar 132 kV line-1 & 2
Chatak | 1 | 0:14 | 0.5 | 0.64167 | Due to tripping of Chatak-Sunamganj 132 kV line
Ramganj | 1 | 3:15 | 25 | 81.25 | Due to S/D of 132/33 kV Transformer T2
Cumilla(N) | 1 | 3:40 | 40 | 146.6667 | Due to S/D of 132/33 kV Transformer T3
Satkhira |  | 1:34 | 30 | 47 | Due to red-hot maintenance of 132/33 kV Transformer T1
Faridpur |  | 0:39 | 60 | 390 | Due to red-hot maintenance of 33 kV Bus
Noapara | 2 | 2:21 | 28 | 65.8 | Due to red-hot maintenance of 33 kV Bus-2
|  | 0:04 | 36 | 1.7333 | Due to tripping of 132/33 kV Transformers T1 & T2
Gopalganj |  | 1:34 | 25 | 39.1667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Moongla |  | 0:21 | 34 | 11.9 | Due to 33 kV feeder fault of 132/33 kV Transformers T1 & T2
Faridpur |  | 0:46 | 30 | 23 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bagerhat |  | 2:06 | 21 | 44.1 | Due to red-hot maintenance of 132/33 kV Transformer T2
Faridpur | 2 | 1:24 | 20 | 11.3333
|  | 0:05 | 130 | 10.8333 | Due to tripping of 132/33 kV Transformer T1
Noapara | 1 | 0:05 | 40 | 3.3333 | Due to 33 kV feeder fault of 132/33 kV Transformer T4
Bagerhat | 2 | 0:06 | 10 | 1 | Due to tripping of 132/33 kV Transformer T2
|  | 0:09 | 40 | 6 | Due to 33 kV feeder fault of 132/33 kV Transformer T1
Patuakhali | 1 | 2:46 | 44 | 55.7333 | Due to S/D of 132 kV Bus
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:June' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Bottail | 1 | 0:59 | 30 | 29.5 | Due to red-hot maintenance of 132/33 kV Transformer T2
Naogaon | 1 | 0:50 | 25 | 20.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Rangpur | 1 | 1:00 | 40 | 40 | Due to red-hot maintenance of 33 kV Bus-2
Purbasadipur | 2 | 0:40 | 6 | 3.6 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 2:22 | 22 | 52.0667 | Due to red-hot maintenance of 132/33 kV Transformer T3
Rajshahi |  | 0:08 | 120 | 16 | Due to tripping of 33 kV feeder fault
Naogaon |  | 0:06 | 40 | 6 | Due to tripping of Naogaon-Niyamatpur 132 kV line
Bogura |  | 4:18 | 20 | 86 | Due to tripping of Bogura-Mohastangar 132 kV line-1
Palashbari |  | 0:18 | 30 | 9 | Due to tripping of Palashbari -Mohastangar 132 kV line-2
Mohasthangar |  | 0:59 | 35 | 34.4167 | Due to re-hot maintenance of Mohastangar-Bogura 132 kV line-2
Barapukuria |  | 0:57 | 30 | 28.5 | Due to re-hot maintenance of Barapukuria-Saidpur 132 kV line-1
Saidpur |  | 0:22 | 170 | 62.3333 | Due to tripping of Saidpur-Purbasadipur 132 kV line-1 & 2
Rangpur | 2 | 0:28 | 30 | 14 | Due to tripping of Rangpur-Saidpur 132 kV line-1 & 2
|  | 0:30 | 140 | 70 | Due to tripping of Rangpur-Barapukuria 132 kV line-1 & 2
Bogura | 1 | 1:37 | 60 | 97 | Due to S/D of 132/33 kV TransformersT3 & T4
C.nawabganj |  | 5:42 | 40 | 228 | Due to S/D of 132/33 kV TransformerT1
| Total unserved energy : |  |  | 4034.2583 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 24 | 2019-06-03 | 15:00
2 | Munsiganj | 130 | 29 | 2019-06-03 | 21:00
3 | Sonargaon | 84 | 29 | 2019-06-03 | 21:00
4 | Shyampur | 204 | 27 | 2019-06-03 | 24:00
5 | Bhulta | 212 | 25 | 2019-06-03 | 13:00
6 | Madanganj | 70 | 24 | 2019-06-03 | 15:00
7 | Shitalakhya | 118 | 29 | 2019-06-03 | 16:00
8 | Rahim steel | 23 | 24 | 2019-06-03 | 11:00
9 | Matuail | 102 | 30 | 2019-06-03 | 12:00
10 | Ghorasal | 96 | 26 | 2019-06-03 | 19:30
11 | Narsingdi | 146 | 30 | 2019-06-03 | 20:00
12 | Haripur (SBU) | 106 | 30 | 2019-06-03 | 12:00
13 | Ullon | 102 | 26 | 2019-06-03 | 16:00
14 | Hasnabad | 225 | 25 | 2019-06-03 | 20:00
15 | Magbazar | 162 | 24 | 2019-06-03 | 16:00
16 | Maniknagar | 122 | 17 | 2019-06-03 | 17:00
17 | Bangabhaban | 40 | 17 | 2019-06-03 | 15:00
18 | Narinda | 104 | 26 | 2019-06-03 | 17:00
19 | Dhanmondi | 193 | 17 | 2019-06-03 | 12:00
20 | Lalbag | 99 | 27 | 2019-06-03 | 11:00
21 | Madartek | 67 | 25 | 2019-06-03 | 23:00
22 | Mirpur | 125 | 25 | 2019-06-03 | 19:30
23 | Kalyanpur | 138 | 25 | 2019-06-03 | 19:30
24 | Gulshan | 188 | 25 | 2019-06-03 | 12:00
25 | Uttara | 99 | 17 | 2019-06-03 | 19:00
26 | Uttara(new) | 21 | 25 | 2019-06-03 | 15:00
27 | Kamrangirchar | 95 | 17 | 2019-06-03 | 17:00
28 | Savar | 158 | 24 | 2019-06-03 | 16:00
29 | Bhasantec | 189 | 25 | 2019-06-03 | 15:00
30 | Agargaon | 81 | 12 | 2019-06-03 | 14:00
31 | Satmosjid | 121 | 26 | 2019-06-03 | 19:30
32 | Tongi | 169 | 25 | 2019-06-03 | 16:00
33 | Kabirpur | 232 | 30 | 2019-06-03 | 16:00
34 | Basundhara | 144 | 25 | 2019-06-03 | 16:00
35 | Manikganj | 106 | 22 | 2019-06-03 | 20:00
36 | Joydevpur | 264 | 26 | 2019-06-03 | 21:00
37 | New Tongi | 116 | 20 | 2019-06-03 | 9:00
38 | Kodda | 271 | 24 | 2019-06-03 | 19:30
39 | Dhamrai | 65 | 29 | 2019-06-03 | 20:00
40 | Valuka | 120 | 23 | 2019-06-03 | 19:30
41 | Tangail | 208 | 30 | 2019-06-03 | 22:00
42 | Mymensing | 239 | 18 | 2019-06-03 | 20:00
43 | Kishorganj | 137 | 13 | 2019-06-03 | 21:00
44 | Netrokona | 115 | 25 | 2019-06-03 | 22:00
45 | Jamalpur | 142 | 30 | 2019-06-03 | 22:00
46 | Sherpur | 116 | 18 | 2019-06-03 | 22:00
47 | Srimongal | 45 | 18 | 2019-06-03 | 22:00
48 | Shahjibazar | 131 | 17 | 2019-06-03 | 21:00
49 | Fenchuganj | 56 | 19 | 2019-06-03 | 20:00
50 | Kulawara | 50 | 24 | 2019-06-03 | 19:00
51 | Sylhet | 157 | 24 | 2019-06-03 | 20:00
52 | Chatak | 35 | 20 | 2019-06-03 | 21:00
53 | Sunamganj | 40 | 12 | 2019-06-03 | 21:00
54 | Bianibazar | 52 | 19 | 2019-06-03 | 19:30
55 | Cumilla (S) | 194 | 12 | 2019-06-03 | 19:00
56 | Cumilla(N) | 153 | 30 | 2019-06-03 | 20:00
57 | Chandpur | 112 | 1 | 2019-06-03 | 23:00
58 | Feni | 149 | 17 | 2019-06-03 | 21:00
59 | Chowmuhani | 194 | 24 | 2019-06-03 | 22:00
60 | Ashuganj | 62 | 18 | 2019-06-03 | 24:00
61 | Daudkandi | 151 | 24 | 2019-06-03 | 21:00
62 | B.Baria | 160 | 17 | 2019-06-03 | 21:00
63 | Ramganj | 104 | 1 | 2019-06-03 | 21:00
64 | Madanhat | 72 | 13 | 2019-06-03 | 21:00
65 | Hathazari | 110 | 18 | 2019-06-03 | 19:00
66 | Khulshi | 233 | 17 | 2019-06-03 | 15:00
67 | Halishahar | 161 | 25 | 2019-06-03 | 11:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 188 | 22 | 2019-06-03 | 23:00
69 | Sikalbaha | 42 | 25 | 2019-06-03 | 19:30
70 | Dohazari | 104 | 30 | 2019-06-03 | 19:00
71 | Cox'sbazar | 103 | 25 | 2019-06-03 | 21:00
72 | Chandraghona | 36 | 22 | 2019-06-03 | 22:00
73 | Kaptai | 5 | 9 | 2019-06-03 | 19:30
74 | A. Khaer Stl. | 20 | 30 | 2019-06-03 | 9:00
75 | Bakulia | 119 | 30 | 2019-06-03 | 20:00
76 | Julda | 21 | 17 | 2019-06-03 | 9:00
77 | TK chemical | 5 | 17 | 2019-06-03 | 16:00
78 | Modern Steel | 16 | 26 | 2019-06-03 | 4:00
79 | Shahmirpur | 36 | 22 | 2019-06-03 | 24:00
80 | Khagrachhari | 21 | 17 | 2019-06-03 | 20:00
81 | Matarbari | 33 | 18 | 2019-06-03 | 21:00
82 | Baroiar Hat | 54 | 20 | 2019-06-03 | 21:00
83 | Rangamati | 14 | 13 | 2019-06-03 | 21:00
84 | Abul Khair 230 | 174 | 13 | 2019-06-03 | 14:00
85 | BSRM | 159 | 26 | 2019-06-03 | 14:00
86 | Goalpara | 38 | 26 | 2019-06-03 | 22:00
87 | Central s/s | 102 | 17 | 2019-06-03 | 20:00
88 | Noapara | 110 | 25 | 2019-06-03 | 20:00
89 | Jashore | 122 | 17 | 2019-06-03 | 19:30
90 | Jhenida | 130 | 30 | 2019-06-03 | 19:30
91 | Bottail | 138 | 19 | 2019-06-03 | 20:00
92 | G.K Project | 62 | 25 | 2019-06-03 | 22:00
93 | Faridpur | 184 | 17 | 2019-06-03 | 20:00
94 | Madaripur | 129 | 17 | 2019-06-03 | 21:00
95 | Gopalganj | 99 | 13 | 2019-06-03 | 22:00
96 | Bagerhat | 103 | 30 | 2019-06-03 | 22:00
97 | Mongla | 51 | 30 | 2019-06-03 | 13:00
98 | Satkhira | 116 | 1 | 2019-06-03 | 22:00
99 | Gallamari | 56 | 19 | 2019-06-03 | 13:00
100 | Magura | 56 | 19 | 2019-06-03 | 19:30
101 | Chuadanga | 96 | 24 | 2019-06-03 | 19:30
102 | Barishal | 120 | 18 | 2019-06-03 | 1:00
103 | Patuakhali | 113 | 25 | 2019-06-03 | 22:00
104 | Bhandaria | 60 | 10 | 2019-06-03 | 22:00
105 | Barisal (N) | 46 | 24 | 2019-06-03 | 22:00
106 | Sariatpur | 42 | 4 | 2019-06-03 | 21:00
107 | Benapol | 45 | 17 | 2019-06-03 | 21:00
108 | Borhan Uddin | 40 | 1 | 2019-06-03 | 22:00
109 | Ishurdi | 68 | 20 | 2019-06-03 | 21:00
110 | Ruppur Paromanobik | 3 | 24 | 2019-06-03 | 13:00
111 | Natore | 135 | 9 | 2019-06-03 | 21:00
112 | Bogura | 256 | 19 | 2019-06-03 | 21:00
113 | Noagaon | 137 | 25 | 2019-06-03 | 21:00
114 | Rajshahi | 176 | 30 | 2019-06-03 | 20:00
115 | C.Nawabganj | 84 | 27 | 2019-06-03 | 1:00
116 | Amnura | 40 | 28 | 2019-06-03 | 4:00
117 | Pabna | 131 | 19 | 2019-06-03 | 20:00
118 | Shahjadpur | 108 | 23 | 2019-06-03 | 19:30
119 | Serajganj | 119 | 30 | 2019-06-03 | 21:00
120 | Niyamatpur | 66 | 25 | 2019-06-03 | 21:00
121 | Joypurhat | 55 | 11 | 2019-06-03 | 1:00
122 | Mohastangor | 17 | 9 | 2019-06-03 | 20:00
123 | Rangpur | 145 | 19 | 2019-06-03 | 21:00
124 | Lalmonirhat | 96 | 13 | 2019-06-03 | 20:00
125 | Saidpur | 117 | 24 | 2019-06-03 | 20:00
126 | Purbasadipur | 108 | 21 | 2019-06-03 | 20:00
127 | Thakurgaon | 82 | 17 | 2019-06-03 | 1:00
128 | Palashbari | 133 | 11 | 2019-06-03 | 1:00
129 | Barapukuria | 54 | 20 | 2019-06-03 | 21:00
130 | Panchagar | 47 | 1 | 2019-06-03 | 21:00
131 | Joldhaka | 20 | 12 | 2019-06-03 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:June' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4616 | 24.06.19 | 16:00
Chattogram | 1391 | 22.06.19 | 24:00
Khulna | 1539 | 20.06.19 | 21:00
Rajshahi | 1314 | 24.06.19 | 21:00
Cumilla | 1206 | 24.06.19 | 22:00
Mymensingh | 998 | 25.06.19 | 21:00
Sylhet | 549 | 24.06.19 | 21:00
Barisal | 386 | 19.06.19 | 4:00
Rangpur | 746 | 24.06.19 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 383 | 402 | 6 | 2019-06-03 | 6:00 | 373 | 1 | 2019-06-03 | 13:00
2 | Bheramara | 388 | 407 | 2 | 2019-06-03 | 13:00 | 378 | 1 | 2019-06-03 | 15:00
3 | Ashuganj(N) | 376 | 403 | 11 | 2019-06-03 | 6:00 | 357 | 1 | 2019-06-03 | 13:00
4 | Kaliakoir | 400 | 387 | 6 | 2019-06-03 | 7:00 | 352 | 23 | 2019-06-03 | 12:00
5 | Bhulta | 400 | 399 | 7 | 2019-06-03 | 18:00 | 361 | 25 | 2019-06-03 | 11:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 238 | 8 | 2019-06-03 | 14:00 | 220 | 18 | 2019-06-03 | 13:00
2 | Ishurdi | 230 | 238 | 20 | 2019-06-03 | 21:00 | 220 | 8 | 2019-06-03 | 21:00
3 | Ashuganj | 230 | 244 | 12 | 2019-06-03 | 4:00 | 225 | 23 | 2019-06-03 | 15:00
4 | Serajganj | 230 | 235 | 4 | 2019-06-03 | 12:00 | 217 | 14 | 2019-06-03 | 1:00
5 | Baghabari | 230 | 236 | 1 | 2019-06-03 | 5:00 | 219 | 8 | 2019-06-03 | 21:00
6 | Barapukuria | 230 | 241 | 11 | 2019-06-03 | 7:00 | 214 | 8 | 2019-06-03 | 21:00
7 | Bogra | 230 | 236 | 2 | 2019-06-03 | 8:00 | 203 | 8 | 2019-06-03 | 21:00
8 | Khulna South | 230 | 238 | 26 | 2019-06-03 | 18:00 | 207 | 30 | 2019-06-03 | 21:00
9 | Rampura | 230 | 230 | 5 | 2019-06-03 | 11:00 | 210 | 25 | 2019-06-03 | 11:00
10 | Haripur | 230 | 231 | 7 | 2019-06-03 | 17:00 | 210 | 25 | 2019-06-03 | 11:00
11 | Hasnabad | 230 | 234 | 6 | 2019-06-03 | 8:00 | 208 | 25 | 2019-06-03 | 10:00
12 | Aminbazar | 230 | 232 | 6 | 2019-06-03 | 5:00 | 209 | 23 | 2019-06-03 | 12:00
13 | Tongi | 230 | 230 | 7 | 2019-06-03 | 07:00 | 209 | 24 | 2019-06-03 | 11:00
14 | Comilla (N) | 230 | 237 | 7 | 2019-06-03 | 18:00 | 213 | 1 | 2019-06-03 | 14:00
15 | Hathazari | 230 | 227 | 14 | 2019-06-03 | 7:00 | 212 | 2 | 2019-06-03 | 11:00
16 | Megnaghat | 230 | 236 | 1 | 2019-06-03 | 6:00 | 210 | 18 | 2019-06-03 | 18:30
17 | Fenchuganj | 230 | 241 | 6 | 2019-06-03 | 18:00 | 215 | 1 | 2019-06-03 | 15:00
18 | Siddhirganj | 230 | 233 | 6 | 2019-06-03 | 3:00 | 210 | 25 | 2019-06-03 | 11:00
19 | Maniknagar | 230 | 232 | 7 | 2019-06-03 | 17:00 | 207 | 25 | 2019-06-03 | 11:00
20 | Old Airport | 230 | 233 | 1 | 2019-06-03 | 12:00 | 206 | 25 | 2019-06-03 | 11:00
21 | Barisal | 230 | 236 | 12 | 2019-06-03 | 5:00 | 210 | 1 | 2019-06-03 | 9:00
22 | AKSML | 230 | 224 | 8 | 2019-06-03 | 8:00 | 209 | 2 | 2019-06-03 | 13:00
23 | BSRM | 230 | 233 | 1 | 2019-06-03 | 6:00 | 209 | 2 | 2019-06-03 | 13:00
24 | Bibiyana | 230 | 239 | 6 | 2019-06-03 | 6:00 | 216 | 1 | 2019-06-03 | 12:00
25 | Bhulta | 230 | 236 | 1 | 2019-06-03 | 06:00 | 210 | 25 | 2019-06-03 | 11:00
26 | Ashuganj (S) | 230 | 242 | 12 | 2019-06-03 | 18:00 | 217 | 1 | 2019-06-03 | 12:00
27 | Kaliakoir | 230 | 235 | 6 | 2019-06-03 | 6:00 | 211 | 27 | 2019-06-03 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 14 | 2019-06-03 | 3:00 | 120 | 25 | 2019-06-03 | 10:00
2 | Munsiganj | 132 | 137 | 10 | 2019-06-03 | 20:00 | 121 | 20 | 2019-06-03 | 11:00
3 | Megnaghat | 132 | 136 | 7 | 2019-06-03 | 17:00 | 119 | 25 | 2019-06-03 | 10:00
4 | Shyampur | 132 | 138 | 6 | 2019-06-03 | 6:00 | 121 | 25 | 2019-06-03 | 10:00
5 | Bhulta | 132 | 132 | 5 | 2019-06-03 | 14:00 | 112 | 23 | 2019-06-03 | 10:00
6 | Madanganj | 132 | 140 | 10 | 2019-06-03 | 20:00 | 120 | 18 | 2019-06-03 | 14:00
7 | Shitalakhya | 132 | 142 | 10 | 2019-06-03 | 20:00 | 122 | 20 | 2019-06-03 | 10:00
8 | Rahim Steal | 132 | 137 | 7 | 2019-06-03 | 18:00 | 122 | 23 | 2019-06-03 | 10:00
9 | Matuail | 132 | 136 | 7 | 2019-06-03 | 16:00 | 120 | 18 | 2019-06-03 | 16:00
10 | Ghorasal | 132 | 142 | 14 | 2019-06-03 | 17:00 | 125 | 2 | 2019-06-03 | 8:00
11 | Narsinghdi | 132 | 137 | 29 | 2019-06-03 | 20:00 | 114 | 23 | 2019-06-03 | 12:00
12 | Haripur (SBU) | 132 | 137 | 7 | 2019-06-03 | 12:00 | 122 | 22 | 2019-06-03 | 16:00
13 | Ullon | 132 | 137 | 29 | 2019-06-03 | 6:00 | 122 | 17 | 2019-06-03 | 15:00
14 | Hasnabad | 132 | 140 | 5 | 2019-06-03 | 13:00 | 123 | 3 | 2019-06-03 | 12:00
15 | Magbazar | 132 | 137 | 4 | 2019-06-03 | 7:00 | 120 | 25 | 2019-06-03 | 15:00
16 | Maniknagar | 132 | 136 | 4 | 2019-06-03 | 7:00 | 123 | 16 | 2019-06-03 | 16:00
17 | Bangabhaban | 132 | 136 | 4 | 2019-06-03 | 7:00 | 119 | 25 | 2019-06-03 | 10:00
18 | Narinda | 132 | 136 | 4 | 2019-06-03 | 7:00 | 121 | 25 | 2019-06-03 | 12:00
19 | Dhanmondi | 132 | 137 | 29 | 2019-06-03 | 7:00 | 121 | 25 | 2019-06-03 | 12:00
20 | Lalbag | 132 | 142 | 6 | 2019-06-03 | 6:00 | 118 | 23 | 2019-06-03 | 12:00
21 | Madartek | 132 | 138 | 4 | 2019-06-03 | 6:00 | 122 | 18 | 2019-06-03 | 12:00
22 | Mirpur | 132 | 140 | 9 | 2019-06-03 | 6:00 | 123 | 27 | 2019-06-03 | 17:00
23 | Kalyanpur | 132 | 140 | 8 | 2019-06-03 | 7:00 | 126 | 18 | 2019-06-03 | 11:00
24 | Gulshan | 132 | 136 | 4 | 2019-06-03 | 5:00 | 121 | 17 | 2019-06-03 | 15:00
25 | Uttara | 132 | 136 | 6 | 2019-06-03 | 8:00 | 121 | 18 | 2019-06-03 | 11:00
26 | Uttara(New) | 132 | 137 | 5 | 2019-06-03 | 16:00 | 120 | 25 | 2019-06-03 | 11:00
27 | Kamrangirchar | 132 | 140 | 5 | 2019-06-03 | 16:00 | 120 | 2 | 2019-06-03 | 11:00
28 | Savar | 132 | 136 | 6 | 2019-06-03 | 7:00 | 122 | 24 | 2019-06-03 | 10:00
29 | Bhasantec | 132 | 138 | 5 | 2019-06-03 | 8:00 | 119 | 18 | 2019-06-03 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 139 | 19 | 2019-06-03 | 6:00 | 121 | 17 | 2019-06-03 | 15:00
31 | Satmosjid | 132 | 138 | 5 | 2019-06-03 | 8:00 | 121 | 17 | 2019-06-03 | 15:00
32 | Tongi | 132 | 139 | 11 | 2019-06-03 | 4:00 | 124 | 18 | 2019-06-03 | 11:00
33 | Kabirpur | 132 | 139 | 6 | 2019-06-03 | 18:30 | 119 | 18 | 2019-06-03 | 10:00
34 | Basundhara | 132 | 136 | 20 | 2019-06-03 | 1:00 | 118 | 17 | 2019-06-03 | 15:00
35 | Manikganj | 132 | 142 | 14 | 2019-06-03 | 5:00 | 126 | 27 | 2019-06-03 | 12:00
36 | Joydevpur | 132 | 142 | 1 | 2019-06-03 | 6:00 | 123 | 18 | 2019-06-03 | 11:00
37 | New Tongi | 132 | 137 | 1 | 2019-06-03 | 6:00 | 122 | 18 | 2019-06-03 | 9:00
38 | Kodda | 132 | 140 | 19 | 2019-06-03 | 13:00 | 117 | 18 | 2019-06-03 | 8:00
39 | Dhamrai | 132 | 139 | 15 | 2019-06-03 | 7:00 | 123 | 23 | 2019-06-03 | 12:00
40 | Valuka | 133 | 138 | 1 | 2019-06-03 | 5:00 | 107 | 23 | 2019-06-03 | 12:00
41 | Tangail | 132 | 140 | 1 | 2019-06-03 | 6:00 | 118 | 24 | 2019-06-03 | 21:00
42 | Mymensing | 132 | 137 | 1 | 2019-06-03 | 5:00 | 110 | 24 | 2019-06-03 | 20:00
43 | Kishorganj | 132 | 138 | 1 | 2019-06-03 | 5:00 | 116 | 24 | 2019-06-03 | 21:00
44 | Netrokona | 132 | 139 | 1 | 2019-06-03 | 6:00 | 110 | 24 | 2019-06-03 | 20:00
45 | Jamalpur | 132 | 140 | 26 | 2019-06-03 | 18:30 | 114 | 6 | 2019-06-03 | 8:00
46 | Sherpur | 132 | 139 | 26 | 2019-06-03 | 7:00 | 116 | 15 | 2019-06-03 | 14:00
47 | Srimongal | 132 | 140 | 10 | 2019-06-03 | 1:00 | 130 | 20 | 2019-06-03 | 24:00
48 | Shahjibazar | 132 | 140 | 14 | 2019-06-03 | 9:00 | 128 | 23 | 2019-06-03 | 21:00
49 | Fenchuganj | 132 | 138 | 9 | 2019-06-03 | 6:00 | 128 | 20 | 2019-06-03 | 24:00
50 | Khulawara | 132 | 136 | 5 | 2019-06-03 | 8:00 | 128 | 20 | 2019-06-03 | 24:00
51 | Sylhet | 132 | 137 | 14 | 2019-06-03 | 7:00 | 128 | 26 | 2019-06-03 | 11:00
52 | Chattak | 132 | 137 | 14 | 2019-06-03 | 5:00 | 123 | 20 | 2019-06-03 | 24:00
53 | Sunamganj | 132 | 137 | 17 | 2019-06-03 | 3:00 | 121 | 20 | 2019-06-03 | 24:00
54 | Biani Bazar | 132 | 137 | 10 | 2019-06-03 | 5:00 | 124 | 20 | 2019-06-03 | 24:00
55 | Comilla(South) | 132 | 135 | 1 | 2019-06-03 | 7:00 | 117 | 12 | 2019-06-03 | 24:00
56 | Comilla (North) | 132 | 140 | 14 | 2019-06-03 | 9:00 | 129 | 1 | 2019-06-03 | 23:00
57 | Chandpur | 132 | 140 | 14 | 2019-06-03 | 17:00 | 120 | 1 | 2019-06-03 | 19:00
58 | Feni | 132 | 133 | 14 | 2019-06-03 | 18:00 | 119 | 26 | 2019-06-03 | 19:00
59 | Chowmuhani | 132 | 131 | 14 | 2019-06-03 | 8:00 | 113 | 2 | 2019-06-03 | 14:00
60 | Ashuganj | 132 | 140 | 1 | 2019-06-03 | 7:00 | 129 | 24 | 2019-06-03 | 23:00
61 | Daudkandi | 132 | 136 | 4 | 2019-06-03 | 12:00 | 120 | 25 | 2019-06-03 | 10:00
62 | Brahminbaria | 132 | 138 | 1 | 2019-06-03 | 6:00 | 123 | 24 | 2019-06-03 | 21:00
63 | Ramganj | 132 | 132 | 12 | 2019-06-03 | 18:00 | 111 | 1 | 2019-06-03 | 19:00
64 | Madanhat | 132 | 135 | 18 | 2019-06-03 | 20:00 | 126 | 2 | 2019-06-03 | 11:00
65 | Hathazari | 132 | 136 | 30 | 2019-06-03 | 10:00 | 125 | 1 | 2019-06-03 | 12:00
66 | Khulshi | 132 | 132 | 15 | 2019-06-03 | 19:30 | 122 | 2 | 2019-06-03 | 13:00
67 | Halishahar | 132 | 137 | 18 | 2019-06-03 | 19:30 | 125 | 1 | 2019-06-03 | 10:00
68 | Baraulia | 132 | 136 | 18 | 2019-06-03 | 18:30 | 123 | 12 | 2019-06-03 | 13:00
69 | Sikalbaha | 132 | 137 | 18 | 2019-06-03 | 19:30 | 119 | 22 | 2019-06-03 | 15:00
70 | Dohazari | 132 | 136 | 18 | 2019-06-03 | 20:00 | 115 | 3 | 2019-06-03 | 18:00
71 | Cox'sbazar | 132 | 129 | 15 | 2019-06-03 | 14:00 | 112 | 3 | 2019-06-03 | 19:00
72 | Chandraghona | 132 | 136 | 24 | 2019-06-03 | 1:00 | 126 | 2 | 2019-06-03 | 10:00
73 | Kaptai | 132 | 135 | 18 | 2019-06-03 | 19:30 | 125 | 2 | 2019-06-03 | 9:00
74 | A. Khaer Stl. | 132 | 131 | 4 | 2019-06-03 | 12:00 | 124 | 18 | 2019-06-03 | 16:00
75 | Bakulia | 132 | 136 | 29 | 2019-06-03 | 19:30 | 124 | 2 | 2019-06-03 | 11:00
76 | Julda | 132 | 136 | 18 | 2019-06-03 | 18:30 | 126 | 1 | 2019-06-03 | 13:00
77 | TK Chemical | 132 | 137 | 14 | 2019-06-03 | 16:00 | 127 | 18 | 2019-06-03 | 9:00
78 | Modern Steel | 132 | 140 | 18 | 2019-06-03 | 18:30 | 126 | 2 | 2019-06-03 | 11:00
79 | Shahmirpur | 132 | 136 | 18 | 2019-06-03 | 18:30 | 125 | 13 | 2019-06-03 | 17:00
80 | Khagrachhari | 132 | 136 | 29 | 2019-06-03 | 9:00 | 116 | 29 | 2019-06-03 | 19:00
81 | Matarbari | 132 | 132 | 15 | 2019-06-03 | 14:00 | 114 | 3 | 2019-06-03 | 2:00
82 | Baroiar Hat | 132 | 133 | 14 | 2019-06-03 | 8:00 | 119 | 1 | 2019-06-03 | 19:00
83 | Rangamati | 133 | 135 | 18 | 2019-06-03 | 18:30 | 125 | 2 | 2019-06-03 | 13:00
84 | Goalpara | 132 | 140 | 5 | 2019-06-03 | 16:00 | 122 | 30 | 2019-06-03 | 12:00
85 | Khulna Central | 132 | 139 | 5 | 2019-06-03 | 14:00 | 121 | 30 | 2019-06-03 | 21:00
86 | Noapara | 132 | 137 | 12 | 2019-06-03 | 14:00 | 116 | 30 | 2019-06-03 | 21:00
87 | Jessore | 132 | 135 | 2 | 2019-06-03 | 10:00 | 110 | 29 | 2019-06-03 | 21:00
88 | Jhenida | 132 | 136 | 2 | 2019-06-03 | 10:00 | 107 | 24 | 2019-06-03 | 21:00
89 | Bottail | 132 | 139 | 29 | 2019-06-03 | 17:00 | 116 | 24 | 2019-06-03 | 21:00
90 | G.K.Project | 132 | 142 | 2 | 2019-06-03 | 13:00 | 120 | 30 | 2019-06-03 | 22:00
91 | Faridpur | 132 | 138 | 18 | 2019-06-03 | 9:00 | 115 | 24 | 2019-06-03 | 21:00
92 | Madaripur | 132 | 141 | 29 | 2019-06-03 | 4:00 | 120 | 24 | 2019-06-03 | 21:00
93 | Gopalganj | 132 | 144 | 19 | 2019-06-03 | 20:00 | 121 | 27 | 2019-06-03 | 21:00
94 | Bagerhat | 132 | 142 | 28 | 2019-06-03 | 18:00 | 114 | 30 | 2019-06-03 | 21:00
95 | Mongla | 132 | 140 | 28 | 2019-06-03 | 11:00 | 119 | 16 | 2019-06-03 | 22:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Satkhira | 132 | 140 | 5 | 2019-06-03 | 17:00 | 103 | 30 | 2019-06-03 | 21:00
97 | Gallamari | 132 | 140 | 2 | 2019-06-03 | 13:00 | 96 | 30 | 2019-06-03 | 21:00
98 | Magura | 132 | 139 | 2 | 2019-06-03 | 10:00 | 104 | 24 | 2019-06-03 | 20:00
99 | Chuadanga | 132 | 136 | 2 | 2019-06-03 | 10:00 | 98 | 24 | 2019-06-03 | 21:00
100 | Barisal | 132 | 139 | 2 | 2019-06-03 | 12:00 | 103 | 27 | 2019-06-03 | 12:00
101 | Patuakhali | 132 | 140 | 5 | 2019-06-03 | 14:00 | 121 | 24 | 2019-06-03 | 21:00
102 | Bhandaria | 132 | 142 | 28 | 2019-06-03 | 13:00 | 112 | 30 | 2019-06-03 | 22:00
103 | Barisal(N) | 132 | 142 | 28 | 2019-06-03 | 15:00 | 128 | 24 | 2019-06-03 | 21:00
104 | Sariatpur | 132 | 139 | 28 | 2019-06-03 | 9:00 | 117 | 24 | 2019-06-03 | 22:00
105 | Benapol | 132 | 136 | 6 | 2019-06-03 | 18:30 | 105 | 30 | 2019-06-03 | 21:00
106 | Ishurdi | 132 | 140 | 2 | 2019-06-03 | 9:00 | 126 | 8 | 2019-06-03 | 2100
107 | Ruppur paromanobik | 132 | 141 | 7 | 2019-06-03 | 17:00 | 127 | 24 | 2019-06-03 | 2100
108 | Natore | 132 | 139 | 2 | 2019-06-03 | 8:00 | 118 | 8 | 2019-06-03 | 2100
109 | Bogra | 132 | 142 | 2 | 2019-06-03 | 8:00 | 117 | 8 | 2019-06-03 | 2100
110 | Noagaon | 132 | 140 | 2 | 2019-06-03 | 7:00 | 112 | 8 | 2019-06-03 | 2100
111 | Rajshahi | 132 | 137 | 26 | 2019-06-03 | 18:00 | 114 | 8 | 2019-06-03 | 2100
112 | C.Nawabganj | 132 | 135 | 26 | 2019-06-03 | 18:00 | 112 | 8 | 2019-06-03 | 2100
113 | Amnura | 132 | 140 | 1 | 2019-06-03 | 18:30 | 115 | 8 | 2019-06-03 | 2100
114 | Pabna | 132 | 140 | 2 | 2019-06-03 | 900 | 124 | 24 | 2019-06-03 | 21:00
115 | Shahjadpur | 132 | 144 | 2 | 2019-06-03 | 900 | 129 | 8 | 2019-06-03 | 2100
116 | Serajganj | 132 | 139 | 2 | 2019-06-03 | 900 | 122 | 8 | 2019-06-03 | 2100
117 | Niyamatpur | 132 | 142 | 2 | 2019-06-03 | 800 | 107 | 24 | 2019-06-03 | 2100
118 | Joypurhat | 132 | 142 | 2 | 2019-06-03 | 800 | 110 | 8 | 2019-06-03 | 2100
119 | Mohastangor | 132 | 140 | 2 | 2019-06-03 | 800 | 113 | 8 | 2019-06-03 | 2100
120 | Rangpur | 132 | 138 | 2 | 2019-06-03 | 800 | 106 | 8 | 2019-06-03 | 2100
121 | Lalmonirhat | 132 | 137 | 2 | 2019-06-03 | 900 | 98 | 8 | 2019-06-03 | 2100
122 | Saidpur | 132 | 138 | 2 | 2019-06-03 | 800 | 105 | 8 | 2019-06-03 | 2100
123 | Purbasadipur | 132 | 142 | 11 | 2019-06-03 | 600 | 105 | 8 | 2019-06-03 | 2100
124 | Thakurgaon | 132 | 137 | 11 | 2019-06-03 | 600 | 94 | 8 | 2019-06-03 | 2100
125 | Palashbari | 132 | 138 | 2 | 2019-06-03 | 800 | 108 | 8 | 2019-06-03 | 2100
126 | Barapukuria | 132 | 141 | 11 | 2019-06-03 | 700 | 114 | 8 | 2019-06-03 | 2100
127 | Panchagar | 132 | 136 | 11 | 2019-06-03 | 600 | 90 | 8 | 2019-06-03 | 2100
128 | Joldhaka | 132 | 138 | 11 | 2019-06-03 | 500 | 104 | 8 | 2019-06-03 | 2100
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:June' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 108 | 410
IP-299421 | Hasnabad | TR2 | 225 | 95 | 400 | 01.06.19 | 12:00
|  | TR3 | 225 | 95 | 360
|  | TR1 | 225 | 165 | 490
IP-299866 | Tongi | TR2 | 225 | 165 | 490 | 17.06.19 | 09:00
|  | TR3 | 225 | 165 | 490
|  | TR1 | 225 | 137 | 475
IP-299427 | Haripur | TR2 | 225 |  |  | 28.06.19 | 17:00 | S/D
|  | TR3 | 225 | 137 | 475
|  | TR1 | 225 | 145 | 600
IP-299728 | Rampura | TR2 | 225 | 145 | 600 | 25.06.19 | 11:00
|  | TR3 | 225 | 145 | 600
|  | TR1 | 225 | 155 | 470
IP-299264 | Aminbazar | TR2 | 225 | 155 | 470 | 28.06.19 | 11:00
|  | TR3 | 225 | 162 | 492
| Maniknagar | TR1 | 300 | 126 | 410 | 26.06.19 | 17:00
|  | TR2 | 300 | 126 | 410
IP-399266 | Cumilla (N) | TR1 | 225 | 170 | 520 | 27.06.19 | 7:00
|  | TR2 | 225 | 173 | 505
| Fenchuganj | TR1 | 300 | 193 | 491 | 24.06.19 | 19:00
|  | TR1 | 150 | 150 | 300
IP-399428 | Hathazari | TR3 | 150 | 150 | 300 | 11.06.19 | 9:00
|  | TR4 | 150 | 150 | 300
|  | TR1 | 225 | 170 | 500
| Ishurdi | TR2 | 225 | 170 | 500 | 14.06.19 | 22:00
IP-499474 |  | TR3 | 225 | 170 | 500
| Khulna(S) | TR1 | 225 | 128 | 330
IP-58001/58002 |  | TR2 | 225 | 128 | 330 | 17.0.19 | 6:00
|  | TR3 | 300 | 160 | 416
| Bogra | TR1 | 225 | 148 | 443 | 06.06.19 | 21:00
|  | TR2 | 225 | 148 | 443
IP-43002/499264 |  | TR3 | 225 | 200 | 595
IP-499224 | Baghabari | TR1 | 225 | 195 | 580 | 08.06.19 | 20:00
| Barapukuria | TR1 | 225 | 190 | 950 | 22.06.19 | 24:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 225 | 160 | 820 |  |  | 132 kV current is being provided
|  | TR6 | 300 | 205 | 1063
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 192 | 358 | 24.06.19 | 8:15
|  | TR2(400/230 kV) | 520 | 192 | 358
|  | TR1(400/132 kV) | 325 | 245 | 435 | 24.06.19 | 19:45
|  | TR2(400/132 kV) | 325 | 245 | 435
| Bibiyana | ICT1(400/230 kV) | 520 | 230 | 207 | 14.06.19 | 16:00
|  | ICT2(400/230kV) | 520 | 129 | 208
| Bhulta | ATR1(400/230 kV) | 520 | 201 | 351 | 29.06.19 | 10:30
|  | ATR2(400/230kV) | 520 | 201 | 351
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:June' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:June' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-06-19 | 11784 | 11784 | - | - | - | - | - | - | - | - | - | - | - | - | 01-06-19 | 8817.7 | 8817.7 | - | - | - | - | - | - | - | - | - | - | - | -
02-06-19 | 10254 | 10254 | - | - | - | - | - | - | - | - | - | - | - | - | 02-06-19 | 6994 | 6994 | - | - | - | - | - | - | - | - | - | - | - | -
03-06-19 | 9977 | 9977 | - | - | - | - | - | - | - | - | - | - | - | - | 03-06-19 | 7525.5 | 7525 | - | - | - | - | - | - | - | - | - | - | - | -
04-06-19 | 8678 | 8678 | - | - | - | - | - | - | - | - | - | - | - | - | 04-06-19 | 5919.6 | 5919.6 | - | - | - | - | - | - | - | - | - | - | - | -
05-06-19 | 8188 | 8188 | - | - | - | - | - | - | - | - | - | - | - | - | 05-06-19 | 5635.8 | 5635.8 | - | - | - | - | - | - | - | - | - | - | - | -
06-06-19 | 9009 | 9009 | - | - | - | - | - | - | - | - | - | - | - | - | 06-06-19 | 6075.7 | 6075.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-06-19 | 8889 | 8889 | - | - | - | - | - | - | - | - | - | - | - | - | 07-06-19 | 6229.4 | 6229.4 | - | - | - | - | - | - | - | - | - | - | - | -
08-06-19 | 9585 | 9585 | - | - | - | - | - | - | - | - | - | - | - | - | 08-06-19 | 6806.7 | 6806.7 | - | - | - | - | - | - | - | - | - | - | - | -
09-06-19 | 10187 | 10187 | - | - | - | - | - | - | - | - | - | - | - | - | 09-06-19 | 7550.4 | 7550.4 | - | - | - | - | - | - | - | - | - | - | - | -
10-06-19 | 11089 | 11089 | - | - | - | - | - | - | - | - | - | - | - | - | 10-06-19 | 8389 | 8389 | - | - | - | - | - | - | - | - | - | - | - | -
11-06-19 | 11482 | 11482 | - | - | - | - | - | - | - | - | - | - | - | - | 11-06-19 | 9054.9 | 9054.9 | - | - | - | - | - | - | - | - | - | - | - | -
12-06-19 | 11870 | 11870 | - | - | - | - | - | - | - | - | - | - | - | - | 12-06-19 | 9927 | 9927 | - | - | - | - | - | - | - | - | - | - | - | -
13-06-19 | 11960 | 11960 | - | - | - | - | - | - | - | - | - | - | - | - | 13-06-19 | 10134.3 | 10134.3 | - | - | - | - | - | - | - | - | - | - | - | -
14-06-19 | 11343 | 11343 | - | - | - | - | - | - | - | - | - | - | - | - | 14-06-19 | 8562 | 8562 | - | - | - | - | - | - | - | - | - | - | - | -
15-06-19 | 10606 | 10606 | - | - | - | - | - | - | - | - | - | - | - | - | 15-06-19 | 8259.6 | 8259.6 | - | - | - | - | - | - | - | - | - | - | - | -
16-06-19 | 12094 | 12094 | - | - | - | - | - | - | - | - | - | - | - | - | 16-06-19 | 9487 | 9487 | - | - | - | - | - | - | - | - | - | - | - | -
17-06-19 | 11602 | 11602 | - | - | - | - | - | - | - | - | - | - | - | - | 17-06-19 | 10049.1 | 10049.1 | - | - | - | - | - | - | - | - | - | - | - | -
18-06-19 | 12063 | 12063 | - | - | - | - | - | - | - | - | - | - | - | - | 18-06-19 | 9641.4 | 9641.4 | - | - | - | - | - | - | - | - | - | - | - | -
19-06-19 | 12355 | 12355 | - | - | - | - | - | - | - | - | - | - | - | - | 19-06-19 | 10508.4 | 10508.4 | - | - | - | - | - | - | - | - | - | - | - | -
20-06-19 | 12362 | 12362 | - | - | - | - | - | - | - | - | - | - | - | - | 20-06-19 | 10190.8 | 10190.8 | - | - | - | - | - | - | - | - | - | - | - | -
21-06-19 | 11369 | 11369 | - | - | - | - | - | - | - | - | - | - | - | - | 21-06-19 | 8416.2 | 8416.2 | - | - | - | - | - | - | - | - | - | - | - | -
22-06-19 | 12182 | 12182 | - | - | - | - | - | - | - | - | - | - | - | - | 22-06-19 | 9135.5 | 9135.5 | - | - | - | - | - | - | - | - | - | - | - | -
23-06-19 | 12451 | 12451 | - | - | - | - | - | - | - | - | - | - | - | - | 23-06-19 | 10320.7 | 10320.7 | - | - | - | - | - | - | - | - | - | - | - | -
24-06-19 | 12780 | 12780 | - | - | - | - | - | - | - | - | - | - | - | - | 24-06-19 | 10554 | 10554 | - | - | - | - | - | - | - | - | - | - | - | -
25-06-19 | 12457 | 12457 | - | - | - | - | - | - | - | - | - | - | - | - | 25-06-19 | 10529.3 | 10529.3 | - | - | - | - | - | - | - | - | - | - | - | -
26-06-19 | 11796 | 11796 | - | - | - | - | - | - | - | - | - | - | - | - | 26-06-19 | 9930.2 | 9930.2 | - | - | - | - | - | - | - | - | - | - | - | -
27-06-19 | 11897 | 11897 | - | - | - | - | - | - | - | - | - | - | - | - | 27-06-19 | 9382 | 9382 | - | - | - | - | - | - | - | - | - | - | - | -
28-06-19 | 10964 | 10964 | - | - | - | - | - | - | - | - | - | - | - | - | 28-06-19 | 8068.2 | 8068.2 | - | - | - | - | - | - | - | - | - | - | - | -
29-06-20 | 12234 | 12234 | - | - | - | - | - | - | - | - | - | - | - | - | 29-06-20 | 9256.6 | 9256.6 | - | - | - | - | - | - | - | - | - | - | - | -
30-06-19 | 12032 | 12032 | - | - | - | - | - | - | - | - | - | - | - | - | 30-06-19 | 10446 | 10446 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:June' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12780 | 24/06/19 | 21:00
2 | Maximum day peak Genaration | MW | 10554 | 24/06/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 12780 | 24/06/19 | 21:00
4 | Minimum Generation | MW | 5341 | 06/06/19 | 7:00
5 | Average of the daily evening peak Genaration | MW | 11184.6333
6 | Average of the daily day peak Genaration | MW | 8726.5667
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW | -
11 | Total Generation | MKWH | 6859.5079
12 | Total Generation by IPP | MKWH | 1947.3335 | % of total Gen. | 28.39%
13 | Total Generation by BPDB | MKWH | 3440.1955 | " | 50.15%
14 | A) Total Generation by RPCL | MKWH | 145.0054 | '' | 2.114%
| B) Total Generation by REB | MKWH | 134.161 | " | 1.956%
| C) Total Generation by RENTAL | MKWH | 497.087 | " | 7.247%
| D) Total Imported from India (HVDC) | MKWH | 596.1985 | " | 8.692%
| E) Total Imported from Tripura, India (A.C) | MKWH | 99.527 | " | 1.451%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4367.2451 | % of total Gen. | 63.67%
| B) Oil | MKWH | 1585.4679 | '' | 23.11%
| C) Hydro | MKWH | 26.8955 | '' | 0.3921%
| D) Solar | MKWH | 3.2807 | '' | 0.04783%
| E) Coal | MKWH | 180.8932 | '' | 2.637%
| F) HVDC (Import from India) | MKWH | 596.1985 | '' | 8.692%
| G) A.C (Import from Tripura, India) | MKWH | 99.527 | '' | 1.451%
16 | Maximun of the daily total Generation . | MKWH | 271.3337 | 25/06/19
17 | Monthly Load factor | % | 74.5667
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 15019.0525
| A) Gas | M.Taka | 3011.475
| B) Liquid fuel | M.Taka | 11246.4262
| C) Coal | M.Taka | 761.1513
| D) HVDC (Import from India) | M.Taka | 3040.6126
| E) Tripura(Import from India) | M.Taka | 680.765
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 728.4627 | 27/06/19
| A) Gas | M.Taka | 109.3795 | 13/06/19
| B) Liquid fuel | M.Taka | 604.5826 | 26/06/19
| C) Coal | M.Taka | 32.7819 | 18/06/19
| D) HVDC (Import from India) | M.Taka | 115.7051 | 09-06-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.507
| B) Excluding Hydro & Solar | Taka/KWHR | 3.5225
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/06/19 | 06:00
b) | Actual | FT (MSL) | 77.78 | 30/06/19 | 06:00
22 | Peak Genaration of June 2018 | MW | 10949 | 06/06/18 | 22:00
23 | Peak Demand of June 2018 | MW | 10948 | 06/06/18 | 21:00
24 | Maximum peak Generation recorded upto 30/06/19 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 30/06/19 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 30/06/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.