## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:May' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | May 2019 |  | April 2019 |  | May 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12893 | 29/05/19 | 12200 | 29/04/19 | 10958 | 28/05/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 21:00 |  | 19:30
2 | Minimum Generation (MW) | 4900 | 25/05/19 | 4404 | 07/04/19 | 4453.1 | 01/05/18 | - | -
|  |  | 6:00 |  | 1:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12893 | 29/05/19 | 12200 | 29/04/19 | 10958 | 28/05/18 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 21:00 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 10364.4 | 29/05/19 | 10057 | 24/04/19 | 9123.3 | 30/05/18 | 10364.4 | 29/05/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12893 | 29/04/19 | 12200 | 29/04/19 | 10958 | 28/05/18 | 12893 | 29/04/19
|  |  | 21:00 |  | 19:30 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11307.071 |  | 10379.33 |  | 9278.4 |  | 11314.04 | May -19
7 | Average Generation (MW) at Day Peak | 9118.159 |  | 8450.52 |  | 7343.17 |  | 8894.56 | May -19
8 | Maximum Power Import from India, HVDC (MW) | 946 | 08/05/19 | 954 | 16/04/19 | 493 | 12/05/18 | 956 | 27/3/2019
|  |  | 1:00 |  | 20:30 |  | 8:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 190 | 2019-11-05 | 188 | 28/04/19 | 188 | 29/05/18 | 190 | 11/05/19
|  |  | 21:00 |  | 22:00 |  | 21:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3572.9103 |  | 3100.97 |  | 2983.89 |  | 3572.91 | May-19
21 | Station Use of BPDB (MKWH) | 123.0983 |  | 126.29 |  | 99.22
22 | Net Generation of BPDB (MKWH) | 3449.812 |  | 2974.68 |  | 2884.67
23 | Net Generation of IPP & RPCL (MKWH) | 2244.8907 |  | 1935.4 |  | 1500.97
24 | Net Generation of REB (MKWH) | 136.4 |  | 128.62 |  | 139.44
24 | Net Generation of Rental Power Plant (MKWH) | 497.3361 |  | 427.5 |  | 661.35
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6328.4388 |  | 5466.19 |  | 5186.44 |  | 6328.44 | May-19
26 | Energy Generation by Gas (MKWH) | 4635.99 |  | 4100.99 |  | 3455.5 |  | 4635.99 | MAy-19
27 | Energy Generation by Diesel (MKWH) | 292.2378 |  | 237.4 |  | 444.89 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1321.8953 |  | 1029.05 |  | 1095.13 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 24.0671 |  | 51.48 |  | 61.25 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 3.9774 |  | 4 |  | 0.34 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 173.674 |  | 169.56 |  | 228.54 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 762.9273 |  | 626.12 |  | 428.88 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 75.2134 |  | 70.79 |  | 70.09 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:May' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12893 | 29/05/19 | 21:00
Generation Period
| Dhaka | MW | 4451
| Chattogram | MW | 1108
| Cumilla | MW | 1216
| Mymensingh | MW | 928
| Sylhet | MW | 511
a) | Total supply in East zone | MW | 8214
| Khulna | MW | 1542
| Barisal | MW | 357
| Rajshahi | MW | 1297
| Rangpur | MW | 699
b) | Total supply in West zone | MW | 3895
c) | Total supply in both zone ( a+b) | MW | 12109
Ref: | 27.21.2604.603.16.086.18.161 | Date: 13/06/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 520 | 03/05/19 | 2:00
| b) Ishurdi end | MW | 400 | 23/05/19 | 4:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1050 | 23/05/19 | 4:00
| b) Ishurdi end | MW | 250 | 03/05/19 | 2:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 1.9404 | 01/05/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 1.6335 | 01/05/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 18.6095
| b) Ishurdi end | MKWH | 43.1062
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 41.813
| b) Ishurdi end | MKWH | 18.0675
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 25/05/19 | 10:00
| b)Serajganj end | MW | 250 | 26/05/19 | 20:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 240 | 26/05/19 | 20:00
| b)Sirajganj end | MW | 440 | 25/05/19 | 10:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 2.04 | 01/05/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 2.032 | 01/05/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 68.54
| b)Sirajganj end | MKWH | 20.682
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 20.636
| b)Sirajganj end | MKWH | 67.588
30 | Transmission loss of EWI /NO-2 | % | 1.119
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | 132/33 kV Transformer-T4 | 2019-05-03 00:28 | 2019-05-03 00:34 | 0:06 | T | Tripped showing O/C relay at 33 side | 112 | 11.2 | Power interruption
Kabirpur | 132/33 kV Transformers-T1 & T2 | 2019-05-07 02:21 | 2019-05-07 02:46 | 0:25 | E/O | Due to 33 kV feeder loop burnt | 75 | 31.25 | Power interruption
Aminbazar | 230/132 kV Transformer-TR1 | 2019-05-08 07:09 | 2019-05-08 18:00 | 10:51 | T | Tripped showing differential relay | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 | 2019-05-08 08:27 | 2019-05-08 08:48 | 0:21 | T | Due to 33 kV feeder fault | 36 | 12.6 | Power interruption
Manikganj | 132/33 kV Transformer-T2 | 2019-05-08 11:11 | 2019-05-08 11:56 | 0:45 | E/O | Due to re hot maintenance | 15 | 11.25 | Power interruption
Aminbazar | 230/132 kV Transformer-T-2 | 2019-05-09 16:58 | 2019-05-09 22:20 | 5:22 | T | Tripped showing general trip | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2019-05-13 06:12 | 2019-05-13 08:34 | 2:22 | E/O | Due to re hot maintenance at 33 kV side | 18 | 39.6 | Power interruption
Tangail | 132/33 kV Transformers-T1 , T2 & T3 | 2019-05-13 08:40 | 2019-05-13 08:53 | 0:13 | T | Tripped showing O/C & E/F relay at 33 side | 130 | 28.1667 | Power interruption
Savar | 132/33 kV Transformers-T1 & T2 | 2019-05-17 19:09 | 2019-05-17 19:44 | 0:35 | T | Tripped showing IDMT signal | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1 & T2 | 2019-05-18 11:54 | 2019-05-18 14:10 | 2:16 | T | Due to 33 kV feeder fault | 30 | 68 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2019-05-19 22:36 | 2019-05-20 00:08 | 1:32 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-05-20 19:35 | 2019-05-20 20:10 | 0:35 | E/O | Due to re hot maintenance | 15 | 8.75 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2019-05-21 06:27 | 2019-05-21 07:12 | 0:45 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformers-GT3 GT4 | 2019-05-21 20:17 | 2019-05-21 20:22 | 0:05 | T | Tripped showing O/C& L/O relay | 110 | 9.1667 | Power interruption
Kabirpur | 132/33 kV Transformers-T1 , T2 & T3 | 2019-05-23 14:18 | 2019-05-23 14:36 | 0:18 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2019-05-24 17:20 | 2019-05-24 18:05 | 0:45 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2019-05-25 02:28 | 2019-05-25 17:53 | 15:25 | T | Tripped showing general trip | 90 | 588 | Power interruption 02:28 to 9:00
Tongi | 132/33 kV Transformer-T1 | 2019-05-26 17:38 | 2019-05-26 18:44 | 1:06 | E/O | Due to high temperature at Y-phase CB loop | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T1 & T2 | 2019-05-26 19:32 | 2019-05-26 19:46 | 0:14 | T | Tripped showing O/C & E/F relay | 119 | 27.7667 | Power interruption
Jamalpur | 132/33 kV Transformers-T1 & T2 | 2019-05-27 22:57 | 2019-05-28 07:00 | 8:03 | T | Tripped showing O/C& L/O relay | 115 | 925.75 | Power interruption
Mirpur | 132/33 kV Transformer-T1 | 2019-05-30 09:23 | 2019-05-30 15:17 | 5:54 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-05-31 20:23 | 2019-05-31 21:35 | 1:12 | E/O | Due to re hot maintenance at 33 kV side | 20 | 24 | Power interruption
|  |  | Total : | 59:10 |  | Unserved Energy: |  | 1785.5
Dhaka (South) Grid Circle :
Madanganj | 132/33 kV Transformer-T1 | 2019-05-04 04:08 | 2019-05-04 11:50 | 7:42 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2019-05-13 17:33 | 2019-05-13 17:57 | 0:24 | E/O | Due to 33 kV feeder fault | 60 | 24 | Power interruption
| 132/33 kV Transformer-T2 | 2019-05-13 18:50 | 2019-05-13 19:19 | 0:29 | T | Due to post insulator problem at 33 kV PBS feeder | 26 | 12.5667 | Power interruption
Shyampur | 230/132 kV Transformers-T1 & T2 | 2019-05-23 08:53 | 2019-05-23 10:55 | 0:00 | T | Tripped showing without any relay | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2019-05-31 02:35 | 2019-05-31 02:45 | 0:10 | E/O | Due to Oil leakage | 62 | 10.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-05-31 20:32 | 2019-05-31 20:42 | 0:10 | T | Tripped showing dist.N51 intertrip relay | 59 | 9.8333 | Power interruption
|  |  | Total : | 1:22 |  | Unserved Energy: |  | 56.7333
Chittagong Grid Circle :
Madunaghat | 132/33 kV Transformer-T1 | 2019-05-24 09:50 | 2019-05-24 11:15 | 1:25 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformers-T1 | 2019-05-28 21:01 | 2019-05-28 21:13 | 0:12 | T | Tripped showing O/C relay | 58 | 11.6 | Power interruption 21:01 to 21:13
| 132/33 kV Transformers-T2 | 2019-05-28 21:01 | 2019-05-28 21:25 | 0:24 | T
Dohazari | 132/33 kV Transformer-T1 | 2019-05-30 23:12 | 2019-05-31 00:17 | 1:05 | E/O | Due to re hot maintenance at 33 kV side | 30 | 32.5 | Power interruption
|  |  | Total : | 3:06 |  | Unserved Energy: |  | 44.1
Page: 2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Daudkandi | 132/33 kV Transformer-T1 | 2019-05-03 07:32 | 2019-05-03 08:41 | 1:09 | E/O | Due to re hot maintenance at 33 kV side | 20 | 23 | Power interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2019-05-05 20:25 | 2019-05-05 21:06 | 0:41 | E/O | Due to re hot maintenance at 33 kV side | 15 | 10.25 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T03 | 2019-05-05 23:33 | 2019-05-06 11:59 | 12:26 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T2 | 2019-05-07 01:40 | 2019-05-07 02:25 | 0:45 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2019-05-07 10:19 | 2019-05-07 10:42 | 0:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer TR1 | 2019-05-08 02:16 | 2019-05-08 03:10 | 0:54 | T | Tripped showing no signal | 0 | 0 | No interruption
| 230/132 kV Transformer TR1 | 2019-05-09 01:48 | 2019-05-09 02:23 | 0:35 | T | Tripped showing without relay | 0 | 0 | No interruption
Ashuganj | 132/33 kV Transformer-T3 | 2019-05-10 05:11 | 2019-05-11 05:55 | 24:44 | T | Tripped showing buchholz& Diff. relay | 34 | 24.9333 | Power interruption 05:11 to 5:55
| 132/33 kV Transformer-T3 | 2019-05-11 08:56 | 2019-05-11 18:16 | 9:20 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-05-12 12:18 | 2019-05-12 13:08 | 0:50 | E/O |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-05-12 16:04 | 2019-05-12 16:17 | 0:13 | E/O |  | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-05-12 22:24 | 2019-05-12 23:27 | 1:03 | E/O | Due to re hot maintenance at 33 kV side | 80 | 84 | Power interruption
Fenchuganj | 230/132 kV Transformer AT2 | 2019-05-14 11:59 | 2019-05-14 12:11 | 0:12 | T | Tripped showing PRV-1 signal | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2019-05-16 08:05 | 2019-05-16 09:52 | 1:47 | E/O | Due to re hot maintenance at 33 kV side | 13 | 23.1833 | Power interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-05-18 21:27 | 2019-05-18 21:59 | 0:32 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2019-05-21 23:14 | 2019-05-21 23:50 | 0:36 | E/O | Due to re hot maintenance at 33 kV side | 30 | 18 | Power interruption
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2019-05-23 20:35 | 2019-05-23 22:02 | 1:27 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2019-05-23 23:03 | 2019-05-24 00:02 | 0:59 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-05-25 12:48 | 2019-05-25 13:43 | 0:55 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-1 | 2019-05-30 18:25 | 2019-05-30 19:35 | 1:10 | E/O | Due to Ashuganj CT of OAT11(New Transformer) blast & fire spread around the Transformer | 0 | 0 | No interruption
| 230 kV Bus-1,2 | 2019-05-30 18:25 | 2019-05-30 20:14 | 1:49 | E/O |  | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2019-05-31 10:50 | 2019-05-31 18:00 | 7:10 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
|  |  | Total : | 69:40 |  | Unserved Energy: |  | 183.3667
Khulna Grid Circle :
Bhandaria | 132/33 kV Transformers-T1 & T2 | 2019-05-01 13:14 | 2019-05-01 13:35 | 0:21 | T | Tripped showing SPS relay | 19 | 6.65 | Power interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-05-02 18:02 | 2019-05-02 18:27 | 0:25 | E/O | Due to re hot maintenance 33 kV side | 15 | 6.25 | Power interruption
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-05-03 04:25 | 2019-05-03 05:25 | 1:00 | T | Due to Auxiliary transformer fault of WZPDCL | 36 | 36 | Power interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-05-03 08:48 | 2019-05-03 10:07 | 1:19 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Barisal(O) | 132/33 kV Transformer-T2 | 2019-05-04 12:01 | 2019-05-04 13:23 | 1:22 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2019-05-05 11:19 | 2019-05-05 11:59 | 0:40 | E/O | Due to re hot maintenance 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T2 | 2019-05-05 15:39 | 2019-05-05 15:42 | 0:03 | T | Due to SPS operation | 15 | 0.75 | Power interruption
Barisal(N) | 230/132 kV Transformer-T2 | 2019-05-06 08:27 | 2019-05-09 16:32 | 80:05 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformers-T1 & T2 | 2019-05-06 13:32 | 2019-05-06 13:49 | 0:17 | T | Tripped showing E/F & O/C relay at 33 kV side | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-05-08 07:43 | 2019-05-08 08:38 | 0:55 | E/O | Due to re hot maintenance | 28 | 25.6667 | Power interruption
Barisal(N) | 230/132 kV Transformer-TR2 | 2019-05-09 16:55 | 2019-05-09 17:27 | 0:32 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T3 | 2019-05-12 17:46 | 2019-05-12 17:52 | 0:06 | T | Due to Bhola -33 MW Rental line fail | 11 | 1.1 | Power interruption
Barisal(N) | 132/33 kV Transformer-T4 | 2019-05-13 21:19 | 2019-05-13 22:02 | 0:43 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T1 & T2 | 2019-05-13 23:40 | 2019-05-14 00:04 | 0:24 | T | Tripped showing Oil leakage | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2019-05-14 08:11 | 2019-05-14 08:59 | 0:48 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-05-14 11:14 | 2019-05-14 12:59 | 1:45 | T | Tripped showing Oil leakage at 33 kV Y-phase CT | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T2 | 2019-05-16 17:21 | 2019-05-16 17:30 | 0:09 | T | Tripped showing 33 kV feeder fault | 68 | 10.2 | Power interruption
Barisal(N) | 132/33 kV Transformer-T4 | 2019-05-23 00:39 | 2019-05-23 03:46 | 3:07 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-05-23 00:20 | 2019-05-23 04:12 | 3:52 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-23 00:27 | 2019-05-23 07:35 | 7:08 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 | 2019-05-23 23:42 | 2019-05-23 23:54 | 0:12 | T | Tripped showing diff.& O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-05-23 23:42 | 2019-05-23 23:50 | 0:08 | T |  | 0 | 0 | No interruption
Barisal(Old) | 132/33 kV Transformers-T1 & T2 | 2019-05-23 00:27 | 2019-05-23 00:33 | 0:06 | T | Tripped showing E/F & O/C relay | 44 | 4.4 | Power interruption
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Magura | 132/33 kV Transformers-T1 & T2 | 2019-05-25 05:59 | 2019-05-25 06:09 | 0:10 | T | Tripped showing E/F & O/C relay at 33 kV side | 28 | 4.6667 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-05-25 06:01 | 2019-05-25 06:12 | 0:11 | T | Tripped showing E/F relay 33 kV side | 12 | 2.2 | Power interruption
Bhandaria | 132/33 kV Transformers-T1 & T3 | 2019-05-26 11:17 | 2019-05-26 11:20 | 0:03 | T | Tripped showing operating SPS relay 33 kV side | 25 | 1.25 | Power interruption
Khulna© | 132/33 kV Transformers-T1 ,T2 & T3 | 2019-05-29 21:08 | 2019-05-29 21:16 | 0:08 | T | Due to 33 kV feeder fault | 99 | 13.2 | Power interruption
Bhandaria | 132/33 kV Transformers-T1 | 2019-05-31 06:42 | 2019-05-31 06:48 | 0:06 | T | Due to 33 kV feeder fault | 4 | 0.4 | Power interruption
Madaripur | 132/33 kV Transformers-T2 | 2019-05-31 08:40 | 2019-05-31 09:45 | 1:05 | E/O | Due to re hot maintenance at 33 kV side | 10 | 10.8333 | Power interruption
|  |  | Total : | 107:10 |  | Unserved Energy: |  | 123.5667
HVDC Grid Circle :
Kustia | 132/33 kV Transformer-T2 | 2019-05-03 07:32 | 2019-05-03 09:05 | 0:08 | T | Due to red hot maintenance at 33 kV Bus | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-05-05 00:17 | 2019-05-05 20:33 | 20:16 | T | Tripped showing differential relay | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T1 | 2019-05-15 16:10 | 2019-05-15 17:18 | 1:08 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2019-05-16 07:41 | 2019-05-16 17:17 | 9:36 | T | Tripped showing differential relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-16 16:46 | 2019-05-16 17:08 | 0:22 | T | Due to winding temperature high | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2019-05-18 11:50 | 2019-05-18 11:59 | 0:09 | T | Tripped showing O/C relay | 69 | 9.45 | Power interruption
Bottail | 132/33 kV Transformer-T2 | 2019-05-21 09:04 | 2019-05-21 10:35 | 1:31 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2019-05-31 11:12 | 2019-05-31 12:36 | 1:24 | E/O | Due to re hot maintenance at 33 kV side | 6 | 8.4 | Power interruption
|  |  | Total : | 162:27 |  |  |  | 17.85
Bogura Grid Circle:
Barapukuria | 230/132 kV Transformer-T1 | 2019-05-04 06:35 | 2019-05-04 17:58 | 11:23 | T | Tripped showing supervision relay | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T1 | 2019-05-04 22:35 | 2019-05-04 22:50 | 0:15 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 | 2019-05-06 10:15 | 2019-05-06 11:55 | 1:40 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-08 09:45 | 2019-05-08 11:30 | 1:45 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2019-05-09 08:22 | 2019-05-09 10:05 | 1:43 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bogura(N) | 132/33 kV Transformers-T1 & T2 | 2019-05-09 15:44 | 2019-05-09 20:40 | 4:56 | T | Tripped showing no signal | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 | 2019-05-10 10:30 | 2019-05-10 13:32 | 3:02 | E/O | Due to re hot maintenance at 33 kv Bus | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T1 | 2019-05-13 19:58 | 2019-05-13 20:53 | 0:55 | T | Tripped showing high voltage | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-13 20:15 | 2019-05-14 12:58 | 16:43 | T | Tripped showing PRD relay | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T3 | 2019-05-13 20:25 | 2019-05-13 20:55 | 0:30 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T4 | 2019-05-15 12:38 | 2019-05-15 12:45 | 0:07 | T | Due to Bagmara feeder fault at 33 kV side | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 | 2019-05-16 11:50 | 2019-05-16 14:05 | 2:15 | E/O | Due to re hot maintenance at 33 kV CB | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2019-05-18 11:50 | 2019-05-18 11:59 | 0:09 | T | Tripped showing O/C relay | 69 | 9.45 | Power interruption
Amnura | 132/33 kV Transformer-T1 | 2019-05-22 21:30 | 2019-05-22 21:49 | 0:19 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T2 | 2019-05-28 11:05 | 2019-05-28 13:02 | 1:57 | E/O | Due to Oil leakage | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformers-T1 & T2 & 33 kV Bus | 2019-05-29 07:04 | 2019-05-29 07:33 | 0:29 | E/O | Due to re hot maintenance at 33 kv Bus | 25 | 12.0833 | Power interruption
Natore | 132/33 kV Transformer-T2 | 2019-05-30 11:02 | 2019-05-30 11:24 | 0:22 | E/O | Due to re hot maintenance at 33 kv Bus | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T4 | 2019-05-30 11:24 | 2019-05-30 12:38 | 1:14 | E/O | Due to re hot maintenance at 33 kv Bus | 5 | 6.1667 | Power interruption
|  |  | Total : | 49:44 |  | Unserved Energy: |  | 27.7
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 452:39 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2019-05-09 20:29 | 2019-05-09 20:34 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishireganj 132 kv line-1 & 2 | 2019-05-13 17:49 | 2019-05-13 17:57 | 0:08 | T | Tripped showing dist. relay | 66 | 8.8 | Power interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-2 | 2019-05-17 18:58 | 2019-05-17 20:02 | 1:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kadda 230 kV line-1 | 2019-05-17 18:52 | 2019-05-17 20:20 | 1:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-1 | 2019-05-17 18:53 | 2019-05-17 19:53 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-2 | 2019-05-17 19:20 | 2019-05-17 19:45 | 0:25 | T |  | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2019-05-17 18:12 | 2019-05-17 19:32 | 1:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Mymensingh 132 kV line-2 | 2019-05-21 16:10 | 2019-05-21 16:35 | 0:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2019-05-22 12:39 | 2019-05-23 01:19 | 12:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2019-05-22 12:35 | 2019-05-23 00:20 | 11:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2019-05-23 00:32 | 2019-05-23 01:32 | 1:00 | T | Tripped showing dist.67N,DTT signal | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-2 | 2019-05-23 00:32 | 2019-05-23 01:46 | 1:14 | T |  | 0 | 0 | No interruption
Gazipur RPCL | Gazipur RPCL-Tangail 132 kV line-2 | 2019-05-25 02:02 | 2019-05-25 03:10 | 1:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2019-05-31 00:41 | 2019-05-31 01:00 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV line-1 | 2019-05-31 01:24 | 2019-05-31 02:12 | 0:48 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
|  |  | Total : | 34:36 |  | Unserved Energy: |  | 8.8
Dhaka (South) Grid Circle :
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-05-04 11:46 | 2019-05-04 11:55 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2019-05-09 05:55 | 2019-05-09 06:54 | 0:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2019-05-17 08:38 | 2019-05-17 08:51 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-2 | 2019-05-17 08:38 | 2019-05-17 09:10 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2019-05-17 18:49 | 2019-05-17 20:12 | 1:23 | T | Tripped showing DT,L96 & PTAW,PD3 signal | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2019-05-17 19:04 | 2019-05-17 19:05 | 0:01 | T | Tripped showing dist. (Z1) relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2019-05-17 19:03 | 2019-05-17 19:32 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line | 2019-05-17 19:14 | 2019-05-17 19:29 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-05-17 19:07 | 2019-05-17 19:27 | 0:20 | T | Tripped showing dist. (Z1) relay | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV line-1 | 2019-05-17 19:57 | 2019-05-17 21:11 | 1:14 | T | Tripped showing dist. (Z1) relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsingdi 132 kV line | 2019-05-19 16:20 | 2019-05-19 16:54 | 0:34 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2019-05-22 16:09 | 2019-05-22 16:16 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line | 2019-05-22 23:43 | 2019-05-23 01:51 | 2:08 | T | Tripped showing diff.& E/F. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV line | 2019-05-22 23:37 | 2019-05-23 00:32 | 0:55 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2019-05-22 23:39 | 2019-05-22 23:59 | 0:20 | T | Tripped showing O/C.& E/F relay | 84 | 28 | Power interruption
Haripur | Haripur-Shyampur 132 kV line | 2019-05-22 23:45 | 2019-05-22 23:57 | 0:12 | T | Tripped showing dist. (Z1) relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2019-05-22 23:43 | 2019-05-22 23:51 | 0:08 | T | Tripped showing dist. relay | 74 | 9.8667 | Power interruption
Shyampur(New) | Shyampur(New)-Shyampur (Old) 132 kV line-1 | 2019-05-22 23:36 | 2019-05-23 07:04 | 7:28 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Meghangaht | Meghangaht-Shyampur 230 kV line-1 | 2019-05-22 23:36 | 2019-05-23 14:10 | 14:34 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Meghangaht-Shyampur 230 kV line-2 | 2019-05-22 23:36 | 2019-05-23 13:42 | 14:06 | T |  | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2019-05-22 22:45 | 2019-05-22 23:04 | 0:19 | T | Tripped showing no signal | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Haripur 132 kV line | 2019-05-23 08:53 | 2019-05-23 09:13 | 0:20 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Shyampur(N)-Bramongaon 132 kV line | 2019-05-23 08:53 | 2019-05-23 09:13 | 0:20 | T | Tripped showing without any relay | 160 | 53.3333 | Power interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2019-05-26 10:26 | 2019-05-26 10:31 | 0:05 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-2 | 2019-05-27 22:18 | 2019-05-27 23:22 | 1:04 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 44:59 |  | Unserved Energy: |  | 91.2
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Baraulia | Baraulia-Hathazari 132 kV line-2 | 2019-05-02 22:23 | 2019-05-03 00:05 | 1:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line | 2019-05-04 01:40 | 2019-05-04 02:18 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Baraulia | Baraulia-Khulshi 132 kV line | 2019-05-04 12:50 | 2019-05-04 13:07 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-AKSTL 132 kV line | 2019-05-04 12:50 | 2019-05-04 13:39 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Khulshi-Madunaghat 132 kV line-1 | 2019-05-05 21:06 | 2019-05-06 00:06 | 3:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-05-15 09:53 | 2019-05-15 10:13 | 0:20 | T | Tripped showing dist. relay | 18 | 6 | Power interruption
Hathazari | Hathazari-Baroierhat 132 kV line-1 | 2019-05-19 07:26 | 2019-05-19 07:46 | 0:20 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 & 2 | 2019-05-19 08:43 | 2019-05-19 08:51 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-05-19 08:53 | 2019-05-19 08:54 | 0:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2019-05-22 11:26 | 2019-05-22 11:43 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rangamati-Kagracahari 132 kV line-1 & 2 | 2019-05-22 11:26 | 2019-05-22 11:47 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Abul khair 230 kV line-1 | 2019-05-24 11:42 | 2019-05-24 12:33 | 0:51 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line | 2019-05-24 20:16 | 2019-05-24 20:35 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khagrachari | Khagrachari-Kaptai 132 kV line-1 & 2 | 2019-05-24 19:46 | 2019-05-24 20:47 | 1:01 | T | Tripped showing dist.(R-phase) & E/F relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-1 | 2019-05-24 19:22 | 2019-05-24 19:34 | 0:12 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
|  |  | Total : | 10:16 |  | Unserved Energy: |  | 6
Cumilla Grid Circle :
Chandpur | Chandpur-Chandpur Desh Energy 132 kV line-1 | 2019-05-02 06:28 | 2019-05-02 06:56 | 0:28 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Chatak | Chatak-Sylhet 132 kV line-1 | 2019-05-03 09:27 | 2019-05-03 11:17 | 1:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-2 | 2019-05-04 08:39 | 2019-05-04 09:12 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-2 | 2019-05-04 08:54 | 2019-05-04 09:04 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-2 | 2019-05-05 11:25 | 2019-05-05 12:07 | 1:42 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2019-05-05 20:38 | 2019-05-05 14:13 | 1:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-2 | 2019-05-08 02:06 | 2019-05-08 11:34 | 9:28 | T | Tripped showing A/R block relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2019-05-08 02:16 | 2019-05-08 02:30 | 0:14 | T | Tripped showing dist. relay | 125 | 29.1667 | Power interruption
FenchuganjS/S | FenchuganjS/S-Fechuganj P/S 132 kV line | 2019-05-08 02:15 | 2019-05-08 03:20 | 1:05 | T | Tripped showing dist. O/C & E/F relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-05-08 23:52 | 2019-05-09 00:09 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj-Sylhet 132 kV line-2 | 2019-05-09 22:06 | 2019-05-09 22:48 | 0:42 | T | Tripped showing dist. relay | 41 | 28.7 | Power interruption
| FenchuganjS/S-Fenchuganj P/S 132 kV line-1 | 2019-05-11 23:29 | 2019-05-12 00:25 | 0:56 | T |  | 0 | 0 | No interruption
| FenchuganjS/S-Fenchuganj P/S 132 kV line-2 | 2019-05-11 23:29 | 2019-05-12 00:22 | 0:53 | T |  | 0 | 0 | No interruption
| FenchuganjS/S-Fenchuganj P/S 132 kV line-3 | 2019-05-11 23:29 | 2019-05-12 00:21 | 0:52 | T |  | 0 | 0 | No interruption
| Fenchuganj S/S-Sylhet 132 kV line | 2019-05-11 23:29 | 2019-05-12 00:27 | 0:58 | T | Tripped showing dist.(Z2) relay | 0 | 0 | No interruption
| Fenchuganj S/S-Sylhet 132 kV line | 2019-05-11 23:29 | 2019-05-11 23:38 | 0:09 | T |  | 9 | 1.35 | Power interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-05-11 22:43 | 2019-05-12 00:29 | 1:46 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-05-13 17:32 | 2019-05-13 17:59 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2019-05-13 17:49 | 2019-05-13 18:06 | 0:17 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption | #REF!
| Ashuganj-Kishoreganj 132 kV line-1 | 2019-05-13 17:32 | 2019-05-13 18:04 | 0:32 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
B.Baria | B.Baria-Narsinghdi 132 kV line-1 | 2019-05-14 00:30 | 2019-05-14 23:10 | 22:40 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2019-05-15 10:40 | 2019-05-15 10:54 | 0:14 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-1 | 2019-05-16 12:33 | 2019-05-16 12:57 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2019-05-17 21:32 | 2019-05-18 10:31 | 12:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2019-05-19 14:48 | 2019-05-19 22:37 | 7:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2019-05-20 11:13 | 2019-05-20 11:23 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 & 2 | 2019-05-21 19:28 | 2019-05-21 19:44 | 0:16 | T | Tripped showing dist.& O/C relay | 65 | 17.3333 | Power interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2019-05-22 06:48 | 2019-05-22 06:52 | 0:04 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2019-05-23 01:55 | 2019-05-23 06:20 | 4:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line-1 | 2019-05-23 23:18 | 2019-05-23 23:51 | 0:33 | T | Tripped showing Auto reclose relay | 10 | 5.5 | Power interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-05-24 09:51 | 2019-05-24 10:12 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-2 | 2019-05-25 04:44 | 2019-05-25 06:42 | 1:58 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2019-05-30 06:27 | 2019-05-30 06:29 | 0:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line-1 | 2019-05-31 04:01 | 2019-05-31 04:33 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 77:20 |  | Unserved Energy: |  | 82.05
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal(N) | Barisal-Patuakhali 132 kV line | 2019-05-04 04:40 | 2019-05-04 04:52 | 0:12 | T | Tripped showing E/F relay | 3 | 0.6 | Power interruption
Madaripur | Madaripur-Faridpur 132 kV line-1 | 2019-05-13 22:20 | 2019-05-14 00:37 | 2:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-1 | 2019-05-15 15:31 | 2019-05-15 16:15 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-05-15 15:47 | 2019-05-15 16:15 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sherpur | Sherpur-United Mymensingh P/S 132 kV line-1 | 2019-05-18 23:35 | 2019-05-18 23:52 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-05-23 02:56 | 2019-05-23 04:08 | 1:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 & 2 | 2019-05-23 13:35 | 2019-05-23 13:45 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-05-25 03:36 | 2019-05-25 03:39 | 0:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-Faridpur P/S 132 kV line | 2019-05-25 03:02 | 2019-05-25 10:30 | 7:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-05-26 11:16 | 2019-05-26 11:35 | 0:19 | T | Tripped showing E/F relay | 45 | 14.25 | Power interruption
Madaripur | Madaripur-Faridpur 132 kV line-2 | 2019-05-26 11:16 | 2019-05-26 11:53 | 0:37 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Faridpur | Faridpur -Madaripur 132 kV line-1 | 2019-05-26 11:16 | 2019-05-26 12:01 | 0:45 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Khulna NWPGCL | Khulna NWPGCL-Goalpara 132 kV line | 2019-05-28 10:19 | 2019-05-28 17:35 | 1:36 | E/O | Due to snapping of Y-phase loop | 0 | 0 | No interruption
Faridpur | Faridpur -Madaripur 132 kV line-1 | 2019-05-30 13:04 | 2019-05-30 13:12 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-05-31 05:00 | 2019-05-31 05:04 | 0:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur -Madaripur 132 kV line-1 | 2019-05-31 09:50 | 2019-05-31 10:01 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 16:31 |  | Unserved Energy: |  | 14.85
HVDC Grid Circle :
Bheramara HVDC | Bheramara HVDC-Khulna(S) 230 kV line-1 | 2019-05-03 10:47 | 2019-05-03 11:17 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV line-2 | 2019-05-04 07:38 | 2019-05-04 08:06 | 0:28 | T | Tripped showing DTT. relay | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 &,2 | 2019-05-15 21:20 | 2019-05-15 22:15 | 0:55 | E/O | Due to R-phase line DS burn | 0 | 0 | No interruption
| Shahjadpur-Baghabari 132 kV line-1 | 2019-05-18 15:08 | 2019-05-18 23:34 | 8:26 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2019-05-22 06:53 | 2019-05-22 09:20 | 1:36 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
| Ishurdi-Baghabari 132 kV line | 2019-05-25 02:10 | 2019-05-25 03:18 | 1:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 13:03 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
C.nawabganj | 132 kV Bus | 2019-05-06 05:56 | 2019-05-06 07:32 | 1:36 | E/O | Due to re hot maintenance | 55 | 88 | Power interruption
Bogura (N) | Bogura (N)-Barapukuria -Sirajganj 230 kV line-1 | 2019-05-09 15:44 | 2019-05-09 16:01 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bogura-Bogura(N) 132 kV line-1 | 2019-05-10 08:15 | 2019-05-10 09:19 | 1:36 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV line-1 | 2019-05-10 11:29 | 2019-05-10 12:27 | 0:58 | T | Tripped showing no signal | 0 | 0 | No interruption
Palashbari | Palashbari-Confidence 132 kV line-2 | 2019-05-13 22:15 | 2019-05-13 23:10 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2019-05-16 00:19 | 2019-05-16 00:29 | 0:10 | T | Tripped showing dist. relay | 7 | 1.1667 | Power interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2019-05-17 06:25 | 2019-05-17 06:45 | 0:20 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2019-05-17 16:26 | 2019-05-17 17:05 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sirajganj | Sirajagnj -Bogura 132 kV line-1 | 2019-05-17 17:22 | 2019-05-17 20:02 | 2:40 | T | Tripped showing power showing | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2019-05-21 20:18 | 2019-05-21 20:26 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2019-05-22 02:44 | 2019-05-22 02:58 | 0:14 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2019-05-22 02:42 | 2019-05-22 02:58 | 0:16 | T | Tripped showing dist. relay | 155 | 41.3333 | Power interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2019-05-22 22:24 | 2019-05-22 23:11 | 0:47 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line-1 | 2019-05-30 20:59 | 2019-05-30 22:30 | 1:31 | T | Tripped showing directional & E/F. relay | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line-1 | 2019-05-30 20:59 | 2019-05-30 22:50 | 1:51 | T | Tripped showing dist. relay | 40 | 74 | Power interruption
|  |  | Total : | 13:58 |  | Unserved Energy: |  | 204.5
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 210:43 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132 kV Bus &132/33 kV Transformer-T2 | 2019-05-01 10:20 | 2019-05-01 12:36 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Valuka | 132 kV Bus | 2019-05-02 09:20 | 2019-05-02 18:19 | 8:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T4 |  | 2019-05-02 20:47 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T2 |  | 2019-05-02 21:36 | 43587.9 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi(New) | 132/33 kV Transformer-T2 | 2019-05-05 07:44 | 2019-05-05 17:10 | 9:26 | S/O | Due to replacement work | 15 | 141.5 | Power interruption
Valuka | 132/33 kV Transformer-T1 | 2019-05-09 08:27 | 2019-05-14 12:40 | 124:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2019-05-10 08:16 | 2019-05-10 17:52 | 9:36 | S/O | Due to replacement work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2019-05-12 11:58 | 2019-05-12 17:18 | 5:20 | S/O | Due to CB hydraulic pressure low | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-05-13 09:40 | 2019-05-13 11:04 | 1:24 | S/O | Due to temperature of 132 kV Y-phase CB high | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-05-13 11:31 | 2019-05-13 16:44 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-05-16 07:10 | 2019-05-16 10:18 | 3:08 | S/O | Due to C/M work | 12 | 37.6 | Power interruption
| 132/33 kV Transformer-T1 | 2019-05-16 10:35 | 2019-05-16 11:47 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-05-16 09:04 | 2019-05-16 10:32 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-05-16 10:44 | 2019-05-16 16:33 | 5:49 | S/O | Due to protection work | 0 | 0 | No interruption
Jamalpur | 33 kV Bus with132/33 kV Transformer-T2 | 2019-05-17 06:29 | 2019-05-17 09:25 | 2:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2019-05-17 08:25 | 2019-05-17 10:40 | 2:15 | S/O | Due to maintenance by 33 kV feeder | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T2 | 2019-05-21 10:12 | 2019-05-21 17:00 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/230 kV Transformer-T2 | 2019-05-22 09:01 | 2019-05-22 18:02 | 9:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2019-05-25 17:53 | 2019-05-25 17:53 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 & 33 kV Bus-2 & 3 | 2019-05-27 08:38 | 2019-05-27 09:46 | 1:08 | S/O | Due to maintenance by PDB | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-T2 & 230 kV Bus-2 | 2019-05-27 08:41 | 2019-05-27 16:36 | 7:55 | S/O | Due to project work | 0 | 0 | No interruption
| 400/230 kV Transformer-T2 & 230 kV Bus-2 | 2019-05-28 08:16 | 2019-05-28 17:07 | 8:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-05-29 09:27 | 2019-05-29 11:40 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-05-29 11:58 | 2019-05-29 12:29 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-05-29 12:40 | 2019-05-29 13:13 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
New(Tongi) | 132/33 kV Transformer-T1 | 2019-05-30 07:48 | 2019-05-30 12:20 | 4:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 & 33 kV Bus-1 | 2019-05-31 05:55 | 2019-05-31 08:12 | 2:17 | S/O | Due to C/M work | 15 | 34.25 | Power interruption
|  |  | Total : | 57:29 |  | Unserved Energy: |  | 213.35
Dhaka (South) Grid Circle :
Narsingdi | 132/33 kV Transformer-T2 | 2019-05-03 11:45 | 2019-05-03 13:07 | 1:22 | S/O | Due to project work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-MT2 |  | 2019-05-03 08:13 |  | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-06 05:03 | 2019-05-06 05:56 | 0:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsingdi | 132 kV Bus-1& 2 | 2019-05-09 10:17 | 2019-05-09 15:40 | 5:23 | S/O | Due to maintenance by 33 kV feeder | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-GT-1 | 2019-05-09 08:27 | 2019-05-09 08:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsingdi | 132 kV Bus-2 | 2019-05-09 15:44 | 2019-05-09 17:02 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T1 | 2019-05-11 09:17 | 2019-05-11 13:31 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2019-05-11 09:00 | 2019-05-11 14:05 | 5:05 | S/O | Due to D/W work | 30 | 152.5 | Power interruption
Siddhirganj | 230 kV Bus-1 | 2019-05-12 05:41 | 2019-05-12 09:24 | 3:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargon | 230/132 kV Transformer-T-1 |  | 2019-05-14 08:24 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Narsingdi | 132 kV Bus |  | 2019-05-15 09:59 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T-2 | 2019-05-17 06:31 | 2019-05-18 09:01 | 26:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T1 | 2019-05-17 08:48 | 2019-05-17 18:32 | 9:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Sonargaon | 132/33 kV Transformer-T2 | 2019-05-18 08:20 | 2019-05-18 10:49 | 2:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-20 08:48 | 2019-05-20 10:00 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-26 11:15 | 2019-05-26 11:40 | 0:25 | S/O | Due to maintenance by 33 kV Breaker | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T2 | 2019-05-26 17:14 | 2019-05-26 18:06 | 0:52 | S/O | Due to high temperature at Y-phase LT bushing | 0 | 0 | No interruption
Bhulta | 400/230/33 kV Transformer ATR-01 | 2019-05-28 09:28 | 2019-05-29 11:52 | 26:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2019-05-29 08:07 | 2019-05-29 10:00 | 1:53 | S/O | Due to C/M work | 30 | 56.5 | Power interruption
|  |  | Total : | 91:27 |  | Unserved Energy: |  | 209
Chattogram Grid Circle :
Hathazari | 132 kV Full Bus | 2019-05-08 05:58 | 2019-05-08 07:35 | 1:37 | S/O | Due to C/M work | 70 | 113.1667 | Power interruption
| 230 kV Breaker | 2019-05-09 08:12 | 2019-05-30 09:55 | 505:43 | S/O | Due to replacement work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T3 | 2019-05-13 06:11 | 2019-05-13 09:11 | 3:00 | S/O | Due to 33 kV ReB feeder extension work | 42 | 126 | Power interruption
Madunaghat | 132 kV CB-904 | 2019-05-14 09:41 | 2019-05-14 09:57 | 0:16 | S/O | Due to remove polythene from chandraghona 132 kV line-1 | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 & 2 | 2019-05-18 12:10 | 2019-05-18 13:10 | 1:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-05-20 06:32 | 2019-05-20 08:58 | 2:26 | S/O | Due to D/W work | 38 | 92.4667 | Power interruption
Chandraghona | 132/33 kV Transformer-T2 | 2019-05-21 09:03 | 2019-05-26 17:03 | 128:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132 kV 602B & 622B CB (New) |  | 2019-05-21 06:22 |  |  | Due to maintenance work | 0 | 0 | No interruption
Halishahar | 33 kV Bus | 2019-05-22 14:46 | 2019-05-22 16:42 | 1:56 | S/O | Due to Bus Isolator damage | 0 | 0 | No interruption
| 132 kV Bus | 2019-05-31 06:08 | 2019-05-31 08:18 | 2:10 | S/O | Due to C/M work | 90 | 195 | Power interruption
|  |  | Total : | 737:35 |  | Unserved Energy : |  | 526.6333
Cumilla Grid Circle :
Daudkandi | 132 kV main Bus | 2019-05-01 07:26 | 2019-05-01 14:27 | 7:01 | S/O | Due to D/W work | 94 | 658 | Power interruption
Fenchuganj | 230/132 kV Transformer T02 | 2019-05-02 09:03 | 2019-05-02 10:55 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 33 kV Bus | 2019-05-04 08:30 | 2019-05-04 09:44 | 1:14 | S/O | Due to 33 kV feeder maintenance | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3(New) |  | 2019-05-06 16:28 |  |  | New Commissioning | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-05-11 23:49 | 2019-05-12 00:38 | 0:49 | S/O | Due to 33 kV feeder maintenance | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer T02 | 2019-05-13 14:54 | 2019-05-13 18:07 | 3:13 | S/O | Due to protection work | 0 | 0 | No interruption
Kulaura | 132/33 kV Transformer-T2 | 2019-05-15 12:40 | 2019-05-15 12:48 | 0:08 | S/O | Due to protection work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T2 | 2019-05-15 17:45 | 2019-05-15 19:28 | 1:43 | S/O | Due to 33 kV bushing spark | 10 | 17.1667 | Power interruption
Kulaura | 132/33 kV Transformer-T2 | 2019-05-16 09:10 | 2019-05-16 18:14 | 9:04 | S/O | Due to relay test | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-05-16 14:45 | 2019-05-16 16:28 | 1:43 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-05-20 06:56 | 2019-05-20 10:20 | 3:24 | S/O | Due to C/M work | 10 | 34 | Power interruption
| 132/33 kV Transformer-T2 | 2019-05-20 14:11 | 2019-05-20 16:41 | 2:30 | S/O | Due to C/M work | 40 | 100 | Power interruption
Chowmuhani | 132/33 kV Transformer-T3 | 2019-05-25 12:08 | 2019-05-25 13:55 | 1:47 | S/O | Due to CB spring test | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-05-27 08:28 | 2019-05-27 10:45 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2019-05-31 07:16 | 2019-05-31 09:39 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 39:08 |  | Unserved Energy : |  | 809.1667
Khulna Grid Circle :
Barisal(N) | 132/33 kV Transformers-T4 & T5 | 2019-05-01 10:13 | 2019-05-01 11:44 | 1:31 | S/O | Due to 33 kV Bus maintenance | 12 | 18.2 | Power interruption
Shariatpur | 132/33 kV Transformer-T2 |  | 2019-05-02 15:19 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2019-05-03 06:40 | 2019-05-03 12:19 | 5:39 | S/O | Due to D/W work | 45 | 254.25 | Power interruption
Bagerhat | 132/33 kV Transformer-T1 |  | 2019-05-03 12:10 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2019-05-06 17:10 | 2019-05-06 18:41 | 1:31 | S/O | Due to changing work | 17 | 25.7833 | Power interruption
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal(N) | 230/132 kV Transformer-TR-2 | 2019-05-07 08:27 | 2019-05-07 15:06 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T2 | 2019-05-11 08:32 | 2019-05-11 11:59 | 3:27 | S/O | Due to replacement work at 33 kV CB | 7 | 24.15 | Power interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-05-15 07:09 | 2019-05-15 08:41 | 1:32 | S/O | Due to chandonimahol 33 kV feeder work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-05-15 08:08 | 2019-05-15 11:15 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2019-05-15 08:42 | 2019-05-15 09:17 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-05-25 10:08 | 2019-05-25 11:10 | 1:02 | S/O | Due to CB problem | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-05-25 14:08 | 2019-05-25 19:57 | 5:49 | S/O | Due to put scaling at CB pole | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 |  | 2019-05-26 14:56 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformer-T1 | 2019-05-27 06:07 | 2019-05-27 08:42 | 2:35 | S/O | Due to C/M work | 15 | 38.75 | Power interruption
Satkhira | 132/33 kV Transformers-T1 & T2 | 2019-05-27 11:32 | 2019-05-27 11:37 | 0:05 | S/O | Due to removing kites | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-05-27 10:15 | 2019-05-27 10:26 | 0:11 | S/O | Due to changing work | 0 | 0 | No interruption
Barisal(O) | 132/33 kV Transformer-T1 | 2019-05-29 05:17 | 2019-05-29 06:29 | 1:12 | S/O | Due to C/M work | 20 | 24 | Power interruption
Khulna© | 132/33 kV Transformer-T3 | 2019-05-31 09:23 | 2019-05-31 10:05 | 0:42 | S/O | Due to replacement work at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 99:19 |  | Unserved Energy : |  | 385.1333
HVDC Grid Circle :
Benapole | 132/33 kV Transformer-T2 |  | 2019-05-14 16:59 | 1:33 |  | Due to new trasnformer connection | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T2 | 2019-05-14 22:29 | 2019-05-14 23:10 | 0:41 | S/O | Due to 33 kV PBS feeder work | 20 | 13.6667 | Power interruption
Pabna | 132/33 kV Transformer-T2 | 2019-05-25 09:42 | 2019-05-25 21:52 | 12:10 | S/O | Due to 33 kV loop connection | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 & T3 | 2019-05-28 09:15 | 2019-05-28 12:10 | 2:55 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 17:19 |  | Unserved Energy : |  | 13.6667
Bogura Grid Circle:
Naogaon | 132/33 kV Transformer-T02 | 2019-05-02 10:08 | 2019-05-02 10:32 | 0:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 |  | 2019-05-04 17:58 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-& 33 kV Bus | 2019-05-05 10:43 | 2019-05-05 11:15 | 0:32 | S/O | Due to D/W work | 8 | 4.2667 | Power interruption
Natore | 132/33 kV Transformer-T4 |  | 2019-05-06 13:25 |  | S/O | Due to reconducting work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 |  | 2019-05-06 15:14 |  | S/O |  | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-05-11 07:05 | 2019-05-11 07:52 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-05-11 11:45 | 2019-05-11 14:05 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T3 | 2019-05-14 09:15 | 2019-05-14 20:15 | 11:00 | S/O | Due to L/A changing | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 |  | 2019-05-14 18:05 |  | S/O |  | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T2 | 2019-05-15 09:20 | 2019-05-15 09:45 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132 kV Bus-2 | 2019-05-16 07:02 | 2019-05-16 09:15 | 2:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T1 | 2019-05-18 11:17 | 2019-05-18 12:01 | 0:44 | S/O | Due to Oil level low | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 |  | 2019-05-18 16:18 |  |  | Due to reconducting work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-05-19 11:28 |  |  | S/O |  | 0 | 0 | No interruption
Mohastanghaoar | 132/33 kV Transformer-T2 | 2019-05-19 12:03 | 2019-05-19 13:43 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 33 kV Bus | 2019-05-19 12:26 | 2019-05-19 13:35 | 1:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132 kV main Bus | 2019-05-21 07:20 | 2019-05-21 12:33 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-05-21 09:28 | 2019-05-21 10:33 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-05-21 10:36 | 2019-05-21 11:49 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 |  | 2019-05-21 15:39 |  |  | Due to reconducting work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-05-22 09:28 | 2019-05-22 15:32 | 6:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T1 |  | 2019-05-22 11:00 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T1 | 2019-05-27 10:25 | 2019-05-27 11:10 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-05-29 08:15 | 2019-05-29 08:58 | 0:43 | S/O | Due to C/M work | 25 | 17.9167 | Power interruption
|  |  | Total : | 36:17 |  | Unserved Energy : |  | 22.1833
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 1078:34 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: May 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Valuka 132 kV line-1 | 2019-05-14 13:55 | 2019-05-14 17:06 | 3:11 | S/O | Due to protection work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2019-05-15 10:16 | 2019-05-15 12:47 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh PPL | Mymensingh PPL-Jamalpur 132 kV line-1 | 2019-05-16 11:54 | 2019-05-16 12:54 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh PPL-Jamalpur 132 kV line-2 | 2019-05-16 12:01 | 2019-05-16 14:16 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2019-05-17 06:11 | 2019-05-17 06:55 | 0:44 | S/O | Due to temperature high on reserve bus | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-05-19 09:55 | 2019-05-19 15:45 | 5:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2019-05-30 07:28 | 2019-05-30 11:08 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 19:11 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 230 kV line-2 | 2019-05-02 08:21 | 2019-05-02 17:35 | 9:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar132 kV line-2 | 2019-05-03 05:32 | 2019-05-03 07:41 | 2:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2019-05-03 09:05 | 2019-05-03 11:30 | 2:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-2 | 2019-05-05 05:37 | 2019-05-05 07:48 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2019-05-05 08:48 | 2019-05-05 21:05 | 12:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2019-05-10 06:26 | 2019-05-10 16:26 | 10:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Siddhirganj-Maniknagar 230 kV line-1 | 2019-05-11 06:19 | 2019-05-11 17:42 | 11:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| Siddhirganj-Maniknagar 230 kV line-2 | 2019-05-12 04:40 | 2019-05-12 09:56 | 5:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| Siddhirganj-Haripur 230 kV line-1 | 2019-05-12 05:38 | 2019-05-12 09:41 | 4:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-Haripur 132 kV line |  | 2019-05-15 09:43 |  | S/O | Due to reconducting work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2019-05-16 15:39 | 2019-05-16 17:31 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2019-05-17 06:31 | 2019-05-18 08:59 | 26:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar132 kV line-2 | 2019-05-18 04:55 | 2019-05-18 09:44 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara -Tongi 132 kV line-1 | 2019-05-23 16:16 | 2019-05-23 16:49 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2019-05-31 17:01 | 2019-05-31 22:24 | 5:23 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 88:49 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Juldah | Juldah-Halishahar 132 kV line | 2019-05-10 07:01 | 2019-05-10 11:02 | 4:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikakbaha | Sikakbaha-Barapukuria 230 kV line |  | 2019-05-10 16:03 |  |  | Due to reconducting work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line | 2019-05-11 09:50 | 2019-05-11 10:01 | 0:11 | S/O | Due to safe entrance of a crain | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV express line |  | 2019-05-11 17:35 |  |  | Due to reconducting work | 0 | 0 | No interruption
Sikakbaha | Sikakbaha-Shahmirpur 132 kV line-1 & 2 | 2019-05-12 08:11 | 2019-05-12 16:10 | 7:59 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikakbaha-Bakulia 132 kV line-1 | 2019-05-29 07:07 | 2019-05-29 20:20 | 13:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSM 230 kV line | 2019-05-31 07:52 | 2019-05-31 11:02 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 215:26 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ghoarshal 132 kV line-2 | 2019-05-05 10:36 | 2019-05-05 15:49 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-1 | 2019-05-07 06:21 | 2019-05-07 12:37 | 6:22 | S/O | Due to project work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-2 | 2019-05-08 05:05 | 2019-05-08 13:43 | 6:22 | S/O | Due to project work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV line-3 |  | 2019-05-18 18:04 | 6:22 | S/O | Due to project work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-05-16 10:58 | 2019-05-16 12:49 | 1:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2019-05-17 08:23 | 2019-05-17 18:00 | 9:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana S/S | Bibiyana S/S-Bibiyana 400 kV line | 2019-05-17 09:30 | 2019-05-17 10:10 | 0:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1 | 2019-05-19 11:07 | 2019-05-19 13:16 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 |  | 2019-05-17 11:46 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1 | 2019-05-29 07:47 | 2019-05-29 15:14 | 7:27 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 46:03 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: May 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Shariatpur 132 kV line-2(New) |  | 2019-02-05 15:18 |  | S/O | Due to reconducting work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2019-05-05 06:05 | 2019-05-05 16:52 | 10:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Barisal(GT) 132 kV line | 2019-05-09 09:55 | 2019-05-09 15:36 | 6:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Barisal(S)-Barisal(N) 132 kV line-1 | 2019-05-11 10:52 | 2019-05-11 11:55 | 6:22 | S/O | Due to L/A checking | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-05-24 11:03 | 2019-05-24 12:16 | 1:13 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 1:13 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2019-05-01 06:24 | 2019-05-01 18:52 | 12:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ruppur 132 kV line-2 | 2019-05-01 11:33 | 2019-05-02 16:15 | 28:42 | S/O | Due to project work | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-1 | 2019-05-02 07:38 | 2019-05-02 10:14 | 34:50 | S/O |  | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-2 | 2019-05-13 17:57 | 2019-05-13 17:57 | 0:00 |  | New commissioning | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 & 2 | 2019-05-17 15:05 | 2019-05-17 15:55 | 0:50 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Ruppur 132 kV line-1 | 2019-05-20 07:15 | 2019-05-20 20:40 | 13:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-1 & 2 | 2019-05-31 08:47 | 2019-05-31 09:02 | 0:15 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 90:30 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Rangpur | Rangpur-Palashbari 132 kV line-1 | 2019-05-02 06:05 | 2019-05-03 10:05 | 28:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line | 2019-05-03 06:50 | 2019-05-03 07:50 | 1:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 132 kV line-2 | 2019-05-03 06:42 | 2019-05-03 18:42 | 12:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ruppur | Ruppur-Ishurdi 132 kV line-1 |  | 2019-05-03 12:53 |  |  | New commissioning |  |  | No interruption
Rangpur | Rangpur-Palashbari 132 line-2 | 2019-05-04 06:40 | 2019-05-04 08:30 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur 132 kV line-2 | 2019-05-05 05:45 | 2019-05-05 14:55 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 132 kV line-2 | 2019-05-09 05:25 | 2019-05-09 17:02 | 11:37 | S/O | Due to project work | 0 | 0 | No interruption
| Bogura -Sirajganj 132 kV line-2 | 2019-05-09 05:09 | 2019-05-09 06:13 | 1:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura -Natore 132 kV line-2 | 2019-05-10 07:08 | 2019-05-10 15:45 | 8:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 132 kV line-1 | 2019-05-10 05:05 | 2019-05-10 16:58 | 11:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sirajganj-Bogura 132 kV line-1 | 2019-05-11 05:11 | 2019-05-11 17:27 | 12:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 132 kV line-1 | 2019-05-12 05:20 | 2019-05-12 16:46 | 11:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 132 kV line-1 | 2019-05-13 05:10 | 2019-05-21 14:59 | 201:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 132 kV line-2 | 2019-05-15 05:15 | 2019-05-18 12:06 | 78:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura -Mahastangar 132 kV line-1 | 2019-05-21 07:29 | 2019-05-21 09:18 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura -Sirajganj 132 kV line-2 | 2019-05-22 06:38 | 2019-05-22 11:29 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura 230 kV S/S-Bogura Confidence 132 kV line-2 | 2019-05-22 07:42 | 2019-05-22 17:42 | 10:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura -Confidence 132 kV line | 2019-05-23 07:44 | 2019-05-23 18:20 | 10:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line-1 |  | 2019-05-31 10:05 |  | S/O | Due to reconducting work | 0 | 0 | No interruption
|  |  | Total : | 416:49 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Narindah 132 kV line-1 | 2019-05-17 06:29 | 2019-05-17 11:06 | 4:37 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 4:37 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 882:38 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May' 2019
| Area | Previous Month (April 2019) |  |  |  | Current Month (May 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 20 | 20 | 30 | 70 | 25 | 11 | 34 | 70
2 | Dhaka (South) Grid Circle. | 28 | 4 | 30 | 62 | 27 | 5 | 34 | 66
3 | Chattogram Grid Circle. | 5 | 8 | 35 | 48 | 15 | 4 | 16 | 35
4 | Cumilla Grid Circle. | 38 | 11 | 23 | 72 | 37 | 19 | 24 | 80
5 | Khulna Grid Circle. | 48 | 8 | 23 | 79 | 33 | 11 | 23 | 67
6 | Bheramara HVDC Grid Circle | 21 | 9 | 16 | 46 | 9 | 5 | 9 | 23
7 | Bogura Grid Circle. | 5 | 16 | 28 | 49 | 21 | 11 | 42 | 74
8 | Others | bar: Total number of S/O to Total number of Total; Total number of S/O to Total number of Total
9 | Total | 165 | 76 | 186 | 427 | 167 | 66 | 183 | 416
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May' 2019
| Area | Previous Month (April 2019) |  |  |  | Current Month (May 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 67.43 | 388.67 | 687.6 | 1143.7 | 1679.46 | 114.85 | 213.35 | 2007.66
2 | Dhaka (South) Grid Circle. | 342.5 | 53.06 | 154.58 | 550.14 | 113.6 | 34.33 | 209 | 356.93
3 | Chattogram Grid Circle. | 18 |  | 89.25 | 107.25 | 17.6 | 32.5 | 526.63 | 576.73
4 | Cumilla Grid Circle. | 556.33 | 367.17 | 1346.67 | 2270.17 | 106.98 | 158.43 | 809.17 | 1074.58
5 | Khulna Grid Circle. | 123.38 | 216.68 | 219.83 | 559.89 | 95.67 | 42.75 | 385.13 | 523.55
6 | Bheramara HVDC Grid Circle | 357.5 | 139.25 | 486 | 982.75 | 9.45 | 8.4 | 13.67 | 31.52
7 | Bogura Grid Circle. |  | 491.97 | 448 | 939.97 | 107.05 | 115.7 | 22.18 | 244.93
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 1465.14 | 1656.8 | 3431.93 | 6553.87 | 2129.81 | 506.96 | 2179.13 | 4815.9
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 12 | 3 | 15 | 6 | 2 | 7 | 1998.85
2 | Dhaka (South) | 5031.6 | 4 | 2 | 6 | 4 | - | 2 | 265.73
3 | Chattogram | 2042 | 2 | 4 | 6 | 1 |  | 5 | 570.73
4 | Khulna | 2434 | 14 | 6 | 20 | 11 | 3 | 6 | 508.7
5 | Bheramara (HVDC) | 2423.3 | 2 | 1 | 3 | 1 | 1 | 1 | 31.52
6 | Bogura | 3145.6 | 2 | 2 | 4 | 1 | 2 | 1 | 40.43
7 | Cumilla | 2981 | 6 | 4 | 10 | - | 2 | 8 | 992.54
| Total | 23365.5 | [6 empty] | 4408.5
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.82%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 98.59%
5 | Bheramara (HVDC) | 98.38% | [6 empty] | Executive Engineer
6 | Bogura | 99.82% | [6 empty] | Information Management Division
7 | Cumilla | 99.89% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 | 1 | - |  | 8.8
2 | Dhaka (South) | 990.29 |  | 3 |  | 3 | 3 | - | - | 91.2
3 | Chattogram | 917 | 20+9(Partial) | 1 | - | 1 | 1 | - | - | 6
4 | Khulna | 1238.4 | 21 | 2 | - | 2 | 2 | - | - | 14.85
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 4 |  | 4 | 2 | - | 2 | 204.5
7 | Cumilla | 1648.16 | 17 | 5 |  | 5 | 3 | 2 | - | 82.05
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 407.4
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.96%
4 | Khulna | 99.94%
5 | Bheramara (HVDC) | 99.94% | [7 empty] | Executive Engineer
6 | Bogura | 99.95% | [7 empty] | Information Management Division
7 | Cumilla | 99.84% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-05-18 | 12 |  | 2 | 45min | 1 | 1hr36min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:May' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Joydevpur | 1 | 0:06 | 112 | 11.2 | Due to tripping of 132/33 kV Transformer T4
Kabirpur | 1 | 0:25 | 75 | 31.25 | Due to tripping of 132/33 kV TransformersT1 & T2
Joydevpur | 1 | 0:21 | 36 | 12.6 | Due to red-hot maintenance of 33 kV Bus
Mymensingh | 1 | 2:22 | 18 | 42.6 | Due to red-hot maintenance of 132/33 kV Transformer T1
Tangail | 1 | 0:13 | 130 | 28.1667 | Due to tripping of 132/33 kV Transformers T1,T2 & T3
Tongi | 1 | 2:16 | 30 | 68 | Due to tripping of 132/33 kV Transformers T1,& T2
Kishoreganj | 1 | 0:35 | 15 | 8.75 | Due to red-hot maintenance of 132/33 kV Transformer T1
Joydevpur | 1 | 0:05 | 110 | 9.1667 | Due to tripping of 132/33 kV Transformers GT3,& GT4
Kabirpur | 1 | 6:32 | 90 | 588 | Due to tripping of 132/33 kV Transformer T2
Kishoreganj | 1 | 0:07 | 119 | 27.7667 | Due to tripping of 132/33 kV Transformers T1 & T2
Jamalpur | 1 | 0:11 | 115 | 925.75
Kishoreganj | 1 | 1:12 | 20 | 24 | Due to tripping of 132/33 kV Transformer T2
Mymensingh | 1 | 0:08 | 66 | 8.8 | Due to tripping of Mymensingh-Kishoreganj 132 kV line-1 & 2
Tongi(new) | 1 | 9:26 | 15 | 141.5 | Due to S/D of 132/33 kV Transformer T2
Jamalpur | 1 | 3:08 | 12 | 37.6 | Due to S/D of 132/33 kV Transformer T2
Mymensingh | 1 | 2:17 | 15 | 34.25 | Due to S/D of 132/33 kV Transformer T1
Manikganj | 1 | 0:45 | 15 | 11.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
Narsingdi | 4 | 0:24 | 60 | 24 | Due to tripping of 132/33 kV Transformer T2
|  | 0:29 | 26 | 12.5667
|  | 0:10 | 62 | 10.3333
|  | 0:10 | 59 | 9.8333
Siddhirganj |  | 0:20 | 84 | 28 | Dueto tripping of Siddhirganj-Matuial 132 kV line
Hasnabad | 1 | 0:08 | 74 | 9.8667 | Due to tripping of Hasnabad-Kamrangirchar 132 kV line
Shyampur | 1 | 0:20 | 160 | 53.3333 | Due to tripping of Shyampur-Bramongaon 132 kV line
Sonargaon | 2 | 5:05 | 30 | 152.5 | Due to S/D of 132/33 kV Transformer T2
|  | 1:53 | 30 | 56.5
Cox'sbazar |  | 0:12 | 58 | 11.6 | Due to tripping of 132/33 kV Transformers T1 & T2
Dohazari | 1 | 1:05 | 30 | 32.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:20 | 18 | 6 | Due to tripping of Dohazari--Coxsbazar 132 kV line-1
Hathazari |  | 1:37 | 70 | 113.1667 | Due to S/D of 132 kV full Bus
Cox'sbazar | 1 | 3:00 | 42 | 126 | Due to S/D of 132/33 kV Transformer T3
Dohazari | 1 | 2:26 | 38 | 92.4667 | Due to S/D of 132/33 kV Transformer T2
Halishahar | 1 | 2:10 | 90 | 195 | Due to S/D of 132 kV Bus
Daudkandi |  | 1:09 | 20 | 23 | Due to red-hot maintenance of 132/33 kV Transformer T1
Chowmuhani |  | 0:41 | 15 | 10.25 | Due to red-hot maintenance of 132/33 kV Transformer T3
Ashuganj |  | 0:44 | 34 | 24.9333 | Due to tripping of 132/33 kV Transformer T3
B.baria |  | 1:03 | 80 | 84 | Due to red-hot maintenance of 132/33 kV Transformer T3
Sylhet |  | 1:47 | 13 | 23.1833
Chowmuhani |  | 0:36 | 30 | 18 | Due to tripping of 132/33 kV Transformer T3
Sylhet |  | 0:14 | 125 | 29.1667 | Due to tripping of Sylhet--Fenchuganj 132 kV line
Fenchuganj | 2 | 0:42 | 41 | 28.7 | Due to tripping of Fenchuganj-Sylhet 132 kV line-2
|  | 0:09 | 9 | 1.35
Sylhet |  | 0:16 | 65 | 17.3333 | Due to tripping of Sylhet-Chatak 132 kV line-1 & 2
Chatak |  | 0:33 | 10 | 5.5 | Due to tripping of Chatak-Sunamganj 132 kV line-1
Daudkandi |  | 7:01 | 94 | 658 | Due to S/D of 132 kV main Bus
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:April' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Chowmuhani |  | 1:43 | 10 | 17.1667 | Due to S/D of 132/33 kV Transformer T2
B.Baria | 2 | 3:24 | 10 | 34 | Due to S/D of 132 kV bus
|  | 2:30 | 40 | 100
Bhandaria | 1 | 0:21 | 19 | 6.65 | Due to tripping of 132/33 kV Transformers T1 & T2
Faridpur | 1 | 0:25 | 15 | 6.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
Mongla |  | 1:00 | 36 | 36 | Due to tripping of 132/33 kV Transformers T1 & T2
Bhandaria | 1 | 0:03 | 15 | 0.75
Gopalganj |  | 0:55 | 28 | 25.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Patuakhali |  | 0:06 | 11 | 1.1 | Due to tripping of 132/33 kV Transformer T1
Madaripur |  | 0:09 | 68 | 10.2 | Due to tripping of 132/33 kV Transformers T1 & T2
Barisal |  | 0:06 | 44 | 4.4
Magura |  | 0:10 | 28 | 4.6667
Mongla |  | 0:11 | 12 | 2.2 | Due to tripping of 132/33 kV Transformers T1 & T2
Bhandaria |  | 0:03 | 25 | 1.25 | Due to tripping of 132/33 kV Transformers T1 & T3
Khulna© |  | 0:08 | 99 | 13.2 | Due to tripping of 132/33 kV Transformers T1 ,T2 & T3
Bhandaria |  | 0:06 | 4 | 0.4 | Due to tripping of 132/33 kV Transformer T1
Madaripur |  | 1:05 | 10 | 10.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Barisal |  | 0:12 | 3 | 0.6 | Due to tripping of Barisal-Patuakhali 132 kV line
Madaripur |  | 0:19 | 45 | 14.25 | Due to tripping of Madaripur-Gopalganj 132 kV line
Barisal |  | 1:31 | 12 | 18.2 | Due to S/D of 33 kV bus
Faridpur |  | 5:39 | 45 | 254.25 | Due to S/D of 132/33 kV Transformer T1
Gallamari |  | 1:31 | 17 | 25.7833 | Due to S/D of 132/33 kV Transformer T2
Patuakhali |  | 3:27 | 7 | 24.15
Barisal(S) |  | 2:35 | 15 | 38.75 | Due to S/D of 132/33 kV Transformer T1
Barisal(O) |  | 1:12 | 20 | 24
Gallamari |  | 1:24 | 6 | 8.4 | Due to red-hot maintenance of 132/33 kV Transformer T2
Jessore |  | 0:41 | 20 | 13.6667 | Due to S/D of 132/33 kV Transformer T2
Pabna |  | 0:09 | 69 | 9.45 | Due to tripping of 132/33 kV Transformer T2
C.nawabganj |  | 0:29 | 25 | 12.0833 | Due to tripping of 132/33 kV Transformers T1 ,T2 & 33 kV Bus
Saidpur |  | 1:14 | 5 | 6.1667 | Due to red-hot maintenance of 132/33 kV Transformer T4
C.nawabganj |  | 1:36 | 55 | 88 | Due to red-hot maintenance of 132 kV Bus
Naogaon |  | 0:10 | 7 | 1.1667 | Due to tripping of Naogaon-Niyamatpur 132 kV line
Saidpur |  | 0:16 | 155 | 41.3333 | Due to tripping of Saidpur-Purbasadipur 132 kV line
Amnura |  | 1:51 | 40 | 74 | Due to tripping of Amnura-C.nawabganj 132 kV line-1
Purbasadipur |  | 0:32 | 8 | 4.2667 | Due to S/D of 33 kV Bus
Naogaon |  | 0:43 | 25 | 17.9167 | Due to S/D of Transformer T &33 kV Bus
| Total unserved energy : |  |  | 4818.9 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 13 | 2019-05-03 | 15:00
2 | Munsiganj | 135 | 30 | 2019-05-03 | 21:00
3 | Sonargaon | 75 | 2 | 2019-05-03 | 19:30
4 | Shyampur | 204 | 19 | 2019-05-03 | 12:00
5 | Bhulta | 212 | 26 | 2019-05-03 | 23:00
6 | Madanganj | 67 | 28 | 2019-05-03 | 18:00
7 | Shitalakhya | 128 | 28 | 2019-05-03 | 16:00
8 | Rahim steel | 31 | 16 | 2019-05-03 | 9:00
9 | Matuail | 105 | 11 | 2019-05-03 | 10:00
10 | Ghorasal | 94 | 11 | 2019-05-03 | 21:00
11 | Narsingdi | 140 | 29 | 2019-05-03 | 19:30
12 | Haripur (SBU) | 111 | 15 | 2019-05-03 | 9:00
13 | Ullon | 104 | 8 | 2019-05-03 | 19:30
14 | Hasnabad | 240 | 12 | 2019-05-03 | 21:00
15 | Magbazar | 159 | 21 | 2019-05-03 | 15:00
16 | Maniknagar | 120 | 7 | 2019-05-03 | 12:00
17 | Bangabhaban | 44 | 13 | 2019-05-03 | 10:00
18 | Narinda | 104 | 12 | 2019-05-03 | 14:00
19 | Dhanmondi | 187 | 19 | 2019-05-03 | 12:00
20 | Lalbag | 94 | 18 | 2019-05-03 | 13:00
21 | Madartek | 84 | 29 | 2019-05-03 | 19:30
22 | Mirpur | 125 | 8 | 2019-05-03 | 19:30
23 | Kalyanpur | 135 | 21 | 2019-05-03 | 19:30
24 | Gulshan | 178 | 2 | 2019-05-03 | 15:00
25 | Uttara | 96 | 21 | 2019-05-03 | 19:30
26 | Uttara(new) | 20 | 7 | 2019-05-03 | 15:00
27 | Kamrangirchar | 85 | 18 | 2019-05-03 | 14:00
28 | Savar | 157 | 11 | 2019-05-03 | 15:00
29 | Bhasantec | 186 | 9 | 2019-05-03 | 15:00
30 | Agargaon | 76 | 19 | 2019-05-03 | 15:00
31 | Satmosjid | 127 | 11 | 2019-05-03 | 19:30
32 | Tongi | 164 | 5 | 2019-05-03 | 17:00
33 | Kabirpur | 269 | 13 | 2019-05-03 | 14:00
34 | Basundhara | 146 | 12 | 2019-05-03 | 19:00
35 | Manikganj | 110 | 11 | 2019-05-03 | 21:00
36 | Joydevpur | 239 | 11 | 2019-05-03 | 19:30
37 | New Tongi | 118 | 11 | 2019-05-03 | 15:00
38 | Kodda | 263 | 26 | 2019-05-03 | 12:00
39 | Dhamrai | 60 | 21 | 2019-05-03 | 20:00
40 | Valuka | 104 | 28 | 2019-05-03 | 21:00
41 | Tangail | 215 | 11 | 2019-05-03 | 21:00
42 | Mymensing | 248 | 11 | 2019-05-03 | 22:00
43 | Kishorganj | 138 | 22 | 2019-05-03 | 21:00
44 | Netrokona | 105 | 20 | 2019-05-03 | 20:00
45 | Jamalpur | 144 | 9 | 2019-05-03 | 22:00
46 | Sherpur | 104 | 6 | 2019-05-03 | 23:00
47 | Srimongal | 42 | 23 | 2019-05-03 | 21:00
48 | Shahjibazar | 132 | 21 | 2019-05-03 | 22:00
49 | Fenchuganj | 52 | 20 | 2019-05-03 | 22:00
50 | Kulawara | 50 | 21 | 2019-05-03 | 19:00
51 | Sylhet | 149 | 20 | 2019-05-03 | 22:00
52 | Chatak | 36 | 29 | 2019-05-03 | 22:00
53 | Sunamganj | 39 | 29 | 2019-05-03 | 21:00
54 | Bianibazar | 50 | 11 | 2019-05-03 | 18:30
55 | Cumilla (S) | 190 | 11 | 2019-05-03 | 21:00
56 | Cumilla(N) | 149 | 26 | 2019-05-03 | 20:00
57 | Chandpur | 121 | 28 | 2019-05-03 | 19:30
58 | Feni | 165 | 30 | 2019-05-03 | 22:00
59 | Chowmuhani | 208 | 20 | 2019-05-03 | 21:00
60 | Ashuganj | 63 | 9 | 2019-05-03 | 23:00
61 | Daudkandi | 162 | 30 | 2019-05-03 | 22:00
62 | B.Baria | 164 | 12 | 2019-05-03 | 23:00
63 | Ramganj | 104 | 29 | 2019-05-03 | 21:00
64 | Madanhat | 72 | 29 | 2019-05-03 | 15:00
65 | Hathazari | 106 | 21 | 2019-05-03 | 22:00
66 | Khulshi | 226 | 21 | 2019-05-03 | 12:00
67 | Halishahar | 161 | 30 | 2019-05-03 | 15:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 186 | 15 | 2019-05-03 | 01:00
69 | Sikalbaha | 42 | 30 | 2019-05-03 | 20:00
70 | Dohazari | 112 | 30 | 2019-05-03 | 21:00
71 | Cox'sbazar | 99 | 27 | 2019-05-03 | 20:00
72 | Chandraghona | 31 | 12 | 2019-05-03 | 19:30
73 | Kaptai | 4.3 | 22 | 2019-05-03 | 19:30
74 | A. Khaer Stl. | 16 | 5 | 2019-05-03 | 22:00
75 | Bakulia | 126 | 18 | 2019-05-03 | 21:00
76 | Julda | 22 | 2 | 2019-05-03 | 10:00
77 | TK chemical | 7.8 | 16 | 2019-05-03 | 09:00
78 | Modern Steel | 16 | 6 | 2019-05-03 | 11:00
79 | Shahmirpur | 39 | 1 | 2019-05-03 | 01:00
80 | Khagrachhari | 20 | 1 | 2019-05-03 | 19:30
81 | Matarbari | 34 | 5 | 2019-05-03 | 20:00
82 | Baroiar Hat | 32 | 30 | 2019-05-03 | 19:30
83 | Rangamati | 12 | 1 | 2019-05-03 | 19:00
84 | Abul Khair 230 | 168 | 25 | 2019-05-03 | 12:00
85 | BSRM | 193 | 23 | 2019-05-03 | 5:00
86 | Goalpara | 31 | 27 | 2019-05-03 | 8:00
87 | Central s/s | 102 | 8 | 2019-05-03 | 21:00
88 | Noapara | 111 | 28 | 2019-05-03 | 20:00
89 | Jashore | 170 | 13 | 2019-05-03 | 21:00
90 | Jhenida | 124 | 30 | 2019-05-03 | 23:00
91 | Bottail | 142 | 22 | 2019-05-03 | 21:00
92 | G.K Project | 62 | 30 | 2019-05-03 | 22:00
93 | Faridpur | 192 | 13 | 2019-05-03 | 21:00
94 | Madaripur | 140 | 6 | 2019-05-03 | 20:00
95 | Gopalganj | 104 | 29 | 2019-05-03 | 22:00
96 | Bagerhat | 92 | 13 | 2019-05-03 | 21:00
97 | Mongla | 42 | 8 | 2019-05-03 | 12:00
98 | Satkhira | 112 | 13 | 2019-05-03 | 21:00
99 | Gallamari | 56 | 28 | 2019-05-03 | 19:30
100 | Magura | 62 | 29 | 2019-05-03 | 22:00
101 | Chuadanga | 96 | 24 | 2019-05-03 | 19:30
102 | Barishal | 132 | 7 | 2019-05-03 | 20:00
103 | Patuakhali | 121 | 21 | 2019-05-03 | 22:00
104 | Bhandaria | 60 | 24 | 2019-05-03 | 22:00
105 | Barisal (N) | 48 | 30 | 2019-05-03 | 20:00
106 | Sariatpur | 42 | 29 | 2019-05-03 | 22:00
107 | Benapol | 47 | 30 | 2019-05-03 | 22:00
108 | Borhan Uddin | 37 | 29 | 2019-05-03 | 22:00
109 | Ishurdi | 71 | 28 | 2019-05-03 | 1:00
110 | Ruppur Paromanobik | 2 | 8 | 2019-05-03 | 20:00
111 | Natore | 138 | 28 | 2019-05-03 | 20:00
112 | Bogura | 251 | 27 | 2019-05-03 | 21:00
113 | Noagaon | 128 | 1 | 2019-05-03 | 1:00
114 | Rajshahi | 169 | 27 | 2019-05-03 | 21:00
115 | C.Nawabganj | 78 | 13 | 2019-05-03 | 21:00
116 | Amnura | 39 | 13 | 2019-05-03 | 20:00
117 | Pabna | 134 | 13 | 2019-05-03 | 20:00
118 | Shahjadpur | 112 | 8 | 2019-05-03 | 19:30
119 | Serajganj | 120 | 11 | 2019-05-03 | 20:00
120 | Niyamatpur | 75 | 1 | 2019-05-03 | 20:00
121 | Joypurhat | 57 | 22 | 2019-05-03 | 21:00
122 | Mohastangor | 24 | 26 | 2019-05-03 | 19:30
123 | Rangpur | 140 | 29 | 2019-05-03 | 19:00
124 | Lalmonirhat | 93 | 1 | 2019-05-03 | 20:00
125 | Saidpur | 111 | 29 | 2019-05-03 | 21:00
126 | Purbasadipur | 114 | 12 | 2019-05-03 | 20:00
127 | Thakurgaon | 78 | 7 | 2019-05-03 | 19:30
128 | Palashbari | 124 | 12 | 2019-05-03 | 21:00
129 | Barapukuria | 55 | 29 | 2019-05-03 | 21:00
130 | Panchagar | 44 | 9 | 2019-05-03 | 20:00
131 | Joldhaka | 17 | 11 | 2019-05-03 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:May' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4542 | 21.05.19 | 5:00
Chattogram | 1394 | 30.05.19 | 23:00
Khulna | 1593 | 30.05.19 | 22:00
Rajshahi | 1326 | 27.05.19 | 21:00
Cumilla | 1216 | 29.05.19 | 22:00
Mymensingh | 980 | 11.05.19 | 21:00
Sylhet | 529 | 30.05.19 | 21:00
Barisal | 364 | 30.05.19 | 23:00
Rangpur | 715 | 28.05.19 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  | Hour | Minm | Date |  | Hour
No. |  | Voltage | Voltage |  |  |  | Voltage |  |  |  | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 396 | 4 | 2019-05-03 | 05:00 | 371 | 28 | 2019-05-03 | 11:00
2 | Bheramara | 400 | 409 | 4 | 2019-05-03 | 4:00 | 383 | 2 | 2019-05-03 | 19:30
3 | Ashuganj(N) | 400 | 408 | 4 | 2019-05-03 | 4:00 | 358 | 18 | 2019-05-03 | 17:00
4 | Kaliakoir | 400 | 389 | 17 | 2019-05-03 | 19:00 | 347 | 28 | 2019-05-03 | 12:00
5 | Bhulta | 400 | 407 | 4 | 2019-05-03 | 4:00 | 363 | 22 | 2019-05-03 | 18:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 17 | 2019-05-03 | 18:30 | 215 | 18 | 2019-05-03 | 12:00
2 | Ishurdi | 230 | 248 | 4 | 2019-05-03 | 04:00 | 217 | 9 | 2019-05-03 | 21:00
3 | Ashuganj | 230 | 241 | 10 | 2019-05-03 | 5:00 | 224 | 5 | 2019-05-03 | 11:00
4 | Serajganj | 230 | 238 | 23 | 2019-05-03 | 6:00 | 225 | 21 | 2019-05-03 | 21:00
5 | Baghabari | 230 | 241 | 4 | 2019-05-03 | 9:00 | 220 | 2 | 2019-05-03 | 19:00
6 | Barapukuria | 230 | 242 | 13 | 2019-05-03 | 2:00 | 213 | 18 | 2019-05-03 | 22:00
7 | Bogra | 230 | 244 | 4 | 2019-05-03 | 7:00 | 205 | 18 | 2019-05-03 | 21:00
8 | Khulna South | 230 | 250 | 4 | 2019-05-03 | 6:00 | 206 | 1 | 2019-05-03 | 13:00
9 | Rampura | 230 | 230 | 17 | 2019-05-03 | 19:30 | 210 | 16 | 2019-05-03 | 11:00
10 | Haripur | 230 | 232 | 17 | 2019-05-03 | 19:30 | 210 | 16 | 2019-05-03 | 11:00
11 | Hasnabad | 230 | 232 | 17 | 2019-05-03 | 19:30 | 207 | 28 | 2019-05-03 | 12:00
12 | Aminbazar | 230 | 236 | 17 | 2019-05-03 | 19:30 | 206 | 28 | 2019-05-03 | 12:00
13 | Tongi | 230 | 231 | 4 | 2019-05-03 | 05:00 | 205 | 28 | 2019-05-03 | 11:00
14 | Comilla (N) | 230 | 236 | 4 | 2019-05-03 | 23:00 | 214 | 18 | 2019-05-03 | 22:00
15 | Hathazari | 230 | 228 | 4 | 2019-05-03 | 13:00 | 209 | 29 | 2019-05-03 | 15:00
16 | Megnaghat | 230 | 238 | 18 | 2019-05-03 | 5:00 | 210 | 28 | 2019-05-03 | 12:00
17 | Fenchuganj | 230 | 241 | 4 | 2019-05-03 | 18:00 | 215 | 18 | 2019-05-03 | 23:00
18 | Siddhirganj | 230 | 235 | 17 | 2019-05-03 | 19:30 | 205 | 27 | 2019-05-03 | 11:00
19 | Maniknagar | 230 | 233 | 17 | 2019-05-03 | 19:30 | 207 | 28 | 2019-05-03 | 12:00
20 | Old Airport | 230 | 236 | 17 | 2019-05-03 | 19:30 | 204 | 28 | 2019-05-03 | 12:00
21 | Barisal | 230 | 248 | 4 | 2019-05-03 | 08:00 | 210 | 7 | 2019-05-03 | 21:00
22 | AKSML | 230 | 225 | 4 | 2019-05-03 | 13:00 | 206 | 25 | 2019-05-03 | 12:00
23 | BSRM | 230 | 235 | 18 | 2019-05-03 | 05:00 | 206 | 29 | 2019-05-03 | 12:00
24 | Bibiyana | 230 | 238 | 4 | 2019-05-03 | 10:00 | 216 | 18 | 2019-05-03 | 21:00
25 | Bhulta | 230 | 238 | 18 | 2019-05-03 | 06:00 | 209 | 28 | 2019-05-03 | 11:00
26 | Ashuganj (S) | 230 | 241 | 1 | 2019-05-03 | 7:00 | 218 | 18 | 2019-05-03 | 22:00
27 | Kaliakoir | 230 | 241 | 17 | 2019-05-03 | 6:00 | 210 | 16 | 2019-05-03 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 141 | 17 | 2019-05-03 | 19:30 | 123 | 6 | 2019-05-03 | 11:00
2 | Munsiganj | 132 | 141 | 17 | 2019-05-03 | 19:30 | 121 | 6 | 2019-05-03 | 12:00
3 | Megnaghat | 132 | 139 | 17 | 2019-05-03 | 19:30 | 121 | 23 | 2019-05-03 | 17:00
4 | Shyampur | 132 | 140 | 17 | 2019-05-03 | 19:30 | 120 | 13 | 2019-05-03 | 10:00
5 | Bhulta | 132 | 131 | 25 | 2019-05-03 | 4:00 | 112 | 27 | 2019-05-03 | 10:00
6 | Madanganj | 132 | 138 | 17 | 2019-05-03 | 19:30 | 103 | 1 | 2019-05-03 | 1:00
7 | Shitalakhya | 132 | 141 | 17 | 2019-05-03 | 19:30 | 118 | 23 | 2019-05-03 | 8:00
8 | Rahim Steal | 132 | 141 | 17 | 2019-05-03 | 19:30 | 123 | 1 | 2019-05-03 | 1:00
9 | Matuail | 132 | 141 | 17 | 2019-05-03 | 19:30 | 121 | 6 | 2019-05-03 | 12:00
10 | Ghorasal | 132 | 145 | 17 | 2019-05-03 | 19:00 | 130 | 30 | 2019-05-03 | 10:00
11 | Narsinghdi | 132 | 138 | 4 | 2019-05-03 | 10:00 | 114 | 30 | 2019-05-03 | 23:00
12 | Haripur (SBU) | 132 | 140 | 17 | 2019-05-03 | 19:30 | 122 | 15 | 2019-05-03 | 9:00
13 | Ullon | 132 | 138 | 17 | 2019-05-03 | 19:00 | 118 | 16 | 2019-05-03 | 11:00
14 | Hasnabad | 132 | 138 | 17 | 2019-05-03 | 20:00 | 120 | 16 | 2019-05-03 | 12:00
15 | Magbazar | 132 | 140 | 17 | 2019-05-03 | 19:00 | 118 | 16 | 2019-05-03 | 12:00
16 | Maniknagar | 132 | 142 | 17 | 2019-05-03 | 19:30 | 123 | 11 | 2019-05-03 | 11:00
17 | Bangabhaban | 132 | 142 | 17 | 2019-05-03 | 19:30 | 117 | 6 | 2019-05-03 | 12:00
18 | Narinda | 132 | 142 | 17 | 2019-05-03 | 19:30 | 119 | 9 | 2019-05-03 | 13:00
19 | Dhanmondi | 132 | 138 | 17 | 2019-05-03 | 19:00 | 118 | 16 | 2019-05-03 | 11:00
20 | Lalbag | 132 | 141 | 17 | 2019-05-03 | 19:30 | 115 | 19 | 2019-05-03 | 13:00
21 | Madartek | 132 | 137 | 17 | 2019-05-03 | 19:30 | 119 | 9 | 2019-05-03 | 13:00
22 | Mirpur | 132 | 139 | 17 | 2019-05-03 | 19:30 | 121 | 28 | 2019-05-03 | 11:00
23 | Kalyanpur | 132 | 145 | 17 | 2019-05-03 | 19:30 | 123 | 28 | 2019-05-03 | 12:00
24 | Gulshan | 132 | 138 | 17 | 2019-05-03 | 19:30 | 119 | 9 | 2019-05-03 | 13:00
25 | Uttara | 132 | 140 | 17 | 2019-05-03 | 19:30 | 119 | 21 | 2019-05-03 | 12:00
26 | Uttara(New) | 132 | 144 | 17 | 2019-05-03 | 19:00 | 120 | 13 | 2019-05-03 | 14:00
27 | Kamrangirchar | 132 | 141 | 17 | 2019-05-03 | 19:30 | 117 | 22 | 2019-05-03 | 12:00
28 | Savar | 132 | 140 | 17 | 2019-05-03 | 19:30 | 120 | 28 | 2019-05-03 | 12:00
29 | Bhasantec | 132 | 145 | 17 | 2019-05-03 | 19:30 | 122 | 21 | 2019-05-03 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2019
|  | Rated | Maxm | Date |  | Hour | Minm | Date |  | Hour
SL. | Substation | Voltage | Voltage |  |  |  | Voltage |  |  |  | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 146 | 17 | 2019-05-03 | 19:30 | 123 | 21 | 2019-05-03 | 12:00
31 | Satmosjid | 132 | 145 | 17 | 2019-05-03 | 19:30 | 123 | 21 | 2019-05-03 | 12:00
32 | Tongi | 132 | 141 | 17 | 2019-05-03 | 19:00 | 125 | 5 | 2019-05-03 | 10:00
33 | Kabirpur | 132 | 143 | 17 | 2019-05-03 | 19:30 | 121 | 30 | 2019-05-03 | 15:00
34 | Basundhara | 132 | 134 | 22 | 2019-05-03 | 24:00 | 115 | 13 | 2019-05-03 | 13:00
35 | Manikganj | 132 | 148 | 17 | 2019-05-03 | 19:00 | 125 | 12 | 2019-05-03 | 5:00
36 | Joydevpur | 132 | 143 | 4 | 2019-05-03 | 14:00 | 127 | 26 | 2019-05-03 | 17:00
37 | New Tongi | 132 | 143 | 17 | 2019-05-03 | 19:30 | 122 | 8 | 2019-05-03 | 14:00
38 | Kodda | 132 | 144 | 17 | 2019-05-03 | 19:00 | 118 | 5 | 2019-05-03 | 11:00
39 | Dhamrai | 132 | 143 | 17 | 2019-05-03 | 19:30 | 122 | 28 | 2019-05-03 | 12:00
40 | Valuka | 133 | 140 | 4 | 2019-05-03 | 10:00 | 114 | 9 | 2019-05-03 | 19:30
41 | Tangail | 132 | 143 | 17 | 2019-05-03 | 19:00 | 120 | 7 | 2019-05-03 | 11:00
42 | Mymensing | 132 | 141 | 4 | 2019-05-03 | 10:00 | 114 | 6 | 2019-05-03 | 22:00
43 | Kishorganj | 132 | 141 | 4 | 2019-05-03 | 10:00 | 116 | 30 | 2019-05-03 | 21:00
44 | Netrokona | 132 | 142 | 4 | 2019-05-03 | 09:00 | 114 | 7 | 2019-05-03 | 21:00
45 | Jamalpur | 132 | 141 | 4 | 2019-05-03 | 10:00 | 119 | 25 | 2019-05-03 | 12:00
46 | Sherpur | 132 | 141 | 4 | 2019-05-03 | 09:00 | 120 | 25 | 2019-05-03 | 11:00
47 | Srimongal | 132 | 141 | 4 | 2019-05-03 | 10:00 | 125 | 30 | 2019-05-03 | 18:30
48 | Shahjibazar | 132 | 140 | 4 | 2019-05-03 | 10:00 | 121 | 30 | 2019-05-03 | 18:30
49 | Fenchuganj | 132 | 138 | 4 | 2019-05-03 | 10:00 | 128 | 30 | 2019-05-03 | 18:30
50 | Khulawara | 132 | 138 | 4 | 2019-05-03 | 10:00 | 128 | 30 | 2019-05-03 | 20:00
51 | Sylhet | 132 | 137 | 4 | 2019-05-03 | 10:00 | 128 | 8 | 2019-05-03 | 9:00
52 | Chattak | 132 | 138 | 4 | 2019-05-03 | 18:00 | 127 | 21 | 2019-05-03 | 20:00
53 | Sunamganj | 132 | 138 | 4 | 2019-05-03 | 10:00 | 125 | 21 | 2019-05-03 | 20:00
54 | Biani Bazar | 132 | 138 | 4 | 2019-05-03 | 18:30 | 126 | 29 | 2019-05-03 | 21:00
55 | Comilla(South) | 132 | 137 | 4 | 2019-05-03 | 7:00 | 117 | 2 | 2019-05-03 | 19:00
56 | Comilla (North) | 132 | 143 | 4 | 2019-05-03 | 10:00 | 126 | 13 | 2019-05-03 | 13:00
57 | Chandpur | 132 | 141 | 4 | 2019-05-03 | 13:00 | 114 | 2 | 2019-05-03 | 24:00
58 | Feni | 132 | 139 | 4 | 2019-05-03 | 10:00 | 117 | 2 | 2019-05-03 | 15:00
59 | Chowmuhani | 132 | 136 | 4 | 2019-05-03 | 10:00 | 109 | 2 | 2019-05-03 | 24:00
60 | Ashuganj | 132 | 144 | 4 | 2019-05-03 | 10:00 | 122 | 30 | 2019-05-03 | 21:00
61 | Daudkandi | 132 | 137 | 4 | 2019-05-03 | 10:00 | 119 | 16 | 2019-05-03 | 11:00
62 | Brahminbaria | 132 | 140 | 4 | 2019-05-03 | 14:00 | 119 | 30 | 2019-05-03 | 23:00
63 | Ramganj | 132 | 138 | 4 | 2019-05-03 | 10:00 | 106 | 2 | 2019-05-03 | 24:00
64 | Madanhat | 132 | 137 | 24 | 2019-05-03 | 20:00 | 125 | 5 | 2019-05-03 | 16:00
65 | Hathazari | 132 | 136 | 4 | 2019-05-03 | 13:00 | 113 | 4 | 2019-05-03 | 17:00
66 | Khulshi | 132 | 135 | 24 | 2019-05-03 | 20:00 | 120 | 2 | 2019-05-03 | 15:00
67 | Halishahar | 132 | 137 | 14 | 2019-05-03 | 03:00 | 123 | 25 | 2019-05-03 | 14:00
68 | Baraulia | 132 | 136 | 4 | 2019-05-03 | 13:00 | 122 | 25 | 2019-05-03 | 12:00
69 | Sikalbaha | 132 | 136 | 24 | 2019-05-03 | 20:00 | 124 | 25 | 2019-05-03 | 12:00
70 | Dohazari | 132 | 135 | 4 | 2019-05-03 | 9:00 | 122 | 29 | 2019-05-03 | 14:00
71 | Cox'sbazar | 132 | 131 | 4 | 2019-05-03 | 13:00 | 111 | 29 | 2019-05-03 | 15:00
72 | Chandraghona | 132 | 137 | 4 | 2019-05-03 | 13:00 | 124 | 2 | 2019-05-03 | 15:00
73 | Kaptai | 132 | 136 | 4 | 2019-05-03 | 13:00 | 124 | 28 | 2019-05-03 | 13:00
74 | A. Khaer Stl. | 132 | 135 | 4 | 2019-05-03 | 13:00 | 120 | 26 | 2019-05-03 | 10:00
75 | Bakulia | 132 | 134 | 4 | 2019-05-03 | 13:00 | 104 | 18 | 2019-05-03 | 21:00
76 | Julda | 132 | 136 | 24 | 2019-05-03 | 20:00 | 123 | 26 | 2019-05-03 | 10:00
77 | TK Chemical | 132 | 137 | 14 | 2019-05-03 | 19:30 | 124 | 25 | 2019-05-03 | 12:00
78 | Modern Steel | 132 | 135 | 24 | 2019-05-03 | 20:00 | 121 | 25 | 2019-05-03 | 14:00
79 | Shahmirpur | 132 | 135 | 4 | 2019-05-03 | 20:00 | 123 | 25 | 2019-05-03 | 13:00
80 | Khagrachhari | 132 | 137 | 4 | 2019-05-03 | 20:00 | 122 | 29 | 2019-05-03 | 15:00
81 | Matarbari | 132 | 134 | 4 | 2019-05-03 | 09:00 | 115 | 29 | 2019-05-03 | 14:00
82 | Baroiar Hat | 132 | 138 | 4 | 2019-05-03 | 09:00 | 117 | 2 | 2019-05-03 | 15:00
83 | Rangamati | 133 | 137 | 24 | 2019-05-03 | 13:00 | 123 | 2 | 2019-05-03 | 15:00
84 | Goalpara | 132 | 143 | 4 | 2019-05-03 | 06:00 | 119 | 18 | 2019-05-03 | 22:00
85 | Khulna Central | 132 | 143 | 4 | 2019-05-03 | 06:00 | 117 | 19 | 2019-05-03 | 13:00
86 | Noapara | 132 | 143 | 4 | 2019-05-03 | 06:00 | 113 | 21 | 2019-05-03 | 20:00
87 | Jessore | 132 | 138 | 4 | 2019-05-03 | 06:00 | 106 | 21 | 2019-05-03 | 21:00
88 | Jhenida | 132 | 140 | 4 | 2019-05-03 | 09:00 | 103 | 21 | 2019-05-03 | 21:00
89 | Bottail | 132 | 142 | 4 | 2019-05-03 | 4:00 | 114 | 21 | 2019-05-03 | 21:00
90 | G.K.Project | 132 | 145 | 4 | 2019-05-03 | 03:00 | 122 | 9 | 2019-05-03 | 22:00
91 | Faridpur | 132 | 142 | 4 | 2019-05-03 | 9:00 | 111 | 7 | 2019-05-03 | 21:00
92 | Madaripur | 132 | 145 | 4 | 2019-05-03 | 8:00 | 119 | 7 | 2019-05-03 | 13:00
93 | Gopalganj | 132 | 149 | 4 | 2019-05-03 | 10:00 | 123 | 24 | 2019-05-03 | 15:00
94 | Bagerhat | 132 | 140 | 4 | 2019-05-03 | 4:00 | 112 | 21 | 2019-05-03 | 21:00
95 | Mongla | 132 | 142 | 4 | 2019-05-03 | 6:00 | 115 | 19 | 2019-05-03 | 13:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Satkhira | 132 | 143 | 4 | 2019-05-03 | 4:00 | 113 | 21 | 2019-05-03 | 21:00
97 | Gallamari | 132 | 143 | 4 | 2019-05-03 | 5:00 | 119 | 19 | 2019-05-03 | 13:00
98 | Magura | 132 | 143 | 4 | 2019-05-03 | 6:00 | 100 | 21 | 2019-05-03 | 21:00
99 | Chuadanga | 132 | 141 | 4 | 2019-05-03 | 4:00 | 93 | 21 | 2019-05-03 | 21:00
100 | Barisal | 132 | 140 | 4 | 2019-05-03 | 5:00 | 122 | 7 | 2019-05-03 | 13:00
101 | Patuakhali | 132 | 144 | 4 | 2019-05-03 | 10:00 | 120 | 7 | 2019-05-03 | 13:00
102 | Bhandaria | 132 | 143 | 4 | 2019-05-03 | 5:00 | 120 | 18 | 2019-05-03 | 21:00
103 | Barisal(N) | 132 | 143 | 23 | 2019-05-03 | 1:00 | 128 | 19 | 2019-05-03 | 13:00
104 | Sariatpur | 132 | 142 | 23 | 2019-05-03 | 1:00 | 117 | 7 | 2019-05-03 | 21:00
105 | Benapol | 132 | 137 | 25 | 2019-05-03 | 6:00 | 106 | 21 | 2019-05-03 | 21:00
106 | Ishurdi | 132 | 144 | 4 | 2019-05-03 | 4:00 | 124 | 21 | 2019-05-03 | 21:00
107 | Ruppur paromanobik | 132 | 144 | 4 | 2019-05-03 | 4:00 | 124 | 21 | 2019-05-03 | 19:30
108 | Natore | 132 | 142 | 4 | 2019-05-03 | 4:00 | 122 | 2 | 2019-05-03 | 21:00
109 | Bogra | 132 | 143 | 4 | 2019-05-03 | 8:00 | 119 | 2 | 2019-05-03 | 21:00
110 | Noagaon | 132 | 141 | 4 | 2019-05-03 | 7:00 | 114 | 2 | 2019-05-03 | 21:00
111 | Rajshahi | 132 | 139 | 4 | 2019-05-03 | 4:00 | 118 | 19 | 2019-05-03 | 13:00
112 | C.Nawabganj | 132 | 138 | 13 | 2019-05-03 | 4:00 | 113 | 22 | 2019-05-03 | 14:00
113 | Amnura | 132 | 140 | 17 | 2019-05-03 | 17:00 | 117 | 12 | 2019-05-03 | 13:00
114 | Pabna | 132 | 141 | 17 | 2019-05-03 | 18:00 | 120 | 2 | 2019-05-03 | 20:00
115 | Shahjadpur | 132 | 148 | 4 | 2019-05-03 | 4:00 | 130 | 8 | 2019-05-03 | 20:00
116 | Serajganj | 132 | 142 | 4 | 2019-05-03 | 6:00 | 121 | 21 | 2019-05-03 | 21:00
117 | Niyamatpur | 132 | 143 | 4 | 2019-05-03 | 6:00 | 109 | 2 | 2019-05-03 | 20:00
118 | Joypurhat | 132 | 145 | 4 | 2019-05-03 | 8:00 | 111 | 2 | 2019-05-03 | 20:00
119 | Mohastangor | 132 | 141 | 4 | 2019-05-03 | 6:00 | 112 | 10 | 2019-05-03 | 15:00
120 | Rangpur | 132 | 143 | 23 | 2019-05-03 | 2:00 | 107 | 21 | 2019-05-03 | 21:00
121 | Lalmonirhat | 132 | 147 | 23 | 2019-05-03 | 5:00 | 100 | 21 | 2019-05-03 | 21:00
122 | Saidpur | 132 | 143 | 23 | 2019-05-03 | 2:00 | 104 | 21 | 2019-05-03 | 21:00
123 | Purbasadipur | 132 | 140 | 4 | 2019-05-03 | 6:00 | 103 | 21 | 2019-05-03 | 21:00
124 | Thakurgaon | 132 | 143 | 23 | 2019-05-03 | 2:00 | 92 | 21 | 2019-05-03 | 21:00
125 | Palashbari | 132 | 141 | 23 | 2019-05-03 | 2:00 | 110 | 21 | 2019-05-03 | 21:00
126 | Barapukuria | 132 | 143 | 23 | 2019-05-03 | 2:00 | 115 | 5 | 2019-05-03 | 19:30
127 | Panchagar | 132 | 142 | 23 | 2019-05-03 | 1:00 | 86 | 21 | 2019-05-03 | 21:00
128 | Joldhaka | 132 | 142 | 23 | 2019-05-03 | 6:00 | 102 | 21 | 2019-05-03 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:May' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 120 | 400
IP-299421 | Hasnabad | TR2 | 225 | 105 | 400 | 28.05.19 | 09:00
|  | TR3 | 225 | 105 | 380
|  | TR1 | 225 | 170 | 530
IP-299866 | Tongi | TR2 | 225 | 170 | 530 | 08.05.19 | 17:00
|  | TR3 | 225 | 170 | 530
|  | TR1 | 225 | 149 | 465
IP-299427 | Haripur | TR2 | 225 |  |  | 23.05.19 | 07:00 | S/D
|  | TR3 | 225 | 149 | 465
|  | TR1 | 225 | 140 | 580
IP-299728 | Rampura | TR2 | 225 | 140 | 580 | 12.05.19 | 15:00
|  | TR3 | 225 | 140 | 580
|  | TR1 | 225 | 146 | 406
IP-299264 | Aminbazar | TR2 | 225 | 146 | 406 | 15.04.19 | 09:00
|  | TR3 | 225 | 145 | 415
| Maniknagar | TR1 | 300 | 126 | 420 | 08.05.19 | 13:00
|  | TR2 | 300 | 126 | 420
IP-399266 | Cumilla (N) | TR1 | 225 | 190 | 570 | 29.05.19 | 19:00
|  | TR2 | 225 | 190 | 557
| Fenchuganj | TR1 | 300 | 183 | 461 | 11.05.19 | 18:30
|  | TR1 | 150 | 125 | 320
IP-399428 | Hathazari | TR3 | 150 | 125 | 320 | 18.05.19 | 22:00
|  | TR4 | 150 | 125 | 320
|  | TR1 | 225 | 170 | 460
| Ishurdi | TR2 | 225 | 170 | 460 | 27.05.19 | 19:30
IP-499474 |  | TR3 | 225 | 170 | 460
| Khulna(S) | TR1 | 225 | 119 | 340
IP-58001/58002 |  | TR2 | 225 | 119 | 340 | 01.05.19 | 15:00
|  | TR3 | 300 | 150 | 434
| Bogra | TR1 | 225 | 155 | 471 | 09.05.19 | 18:00
|  | TR2 | 225 | 155 | 471
IP-43002/499264 |  | TR3 | 225 | 209 | 619
IP-499224 | Baghabari | TR1 | 225 | 178 | 550 | 09.05.19 | 20:00
| Barapukuria | TR1 | 225 | 200 | 1000 | 10.05.19 | 15:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 155 | 780 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 196 | 1007
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 213.9 | 378 | 28.05.19 | 12:45
|  | TR2(400/230 kV) | 520 | 213.9 | 370
|  | TR1(400/132 kV) | 325 | 245.9 | 438 | 30.05.19 | 20:15
|  | TR2(400/132 kV) | 325 | 245.9 | 435
| Bibiyana | ICT1(400/230 kV) | 520 | 113 | 185 | 24.05.19 | 4:00
|  | ICT2(400/230kV) | 520 | 112 | 185
| Bhulta | ATR1(400/230 kV) | 520 | 203 | 363 | 24.05.19 | 12:45
|  | ATR2(400/230kV) | 520 | 203 | 363
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:May' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-05-19 | 11095 | 11095 | - | - | - | - | - | - | - | - | - | - | - | - | 01-05-19 | 7796 | 7796 | - | - | - | - | - | - | - | - | - | - | - | -
02-05-19 | 12008 | 12008 | - | - | - | - | - | - | - | - | - | - | - | - | 02-05-19 | 9934.3 | 9934 | - | - | - | - | - | - | - | - | - | - | - | -
03-05-19 | 7597 | 7597 | - | - | - | - | - | - | - | - | - | - | - | - | 03-05-19 | 7798.3 | 7798.3 | - | - | - | - | - | - | - | - | - | - | - | -
04-05-19 | 7529 | 7529 | - | - | - | - | - | - | - | - | - | - | - | - | 04-05-19 | 4174 | 4174 | - | - | - | - | - | - | - | - | - | - | - | -
05-05-19 | 10884 | 10884 | - | - | - | - | - | - | - | - | - | - | - | - | 05-05-19 | 8465.5 | 8465.5 | - | - | - | - | - | - | - | - | - | - | - | -
06-05-19 | 11813 | 11813 | - | - | - | - | - | - | - | - | - | - | - | - | 06-05-19 | 9380 | 9380 | - | - | - | - | - | - | - | - | - | - | - | -
07-05-19 | 12214 | 12214 | - | - | - | - | - | - | - | - | - | - | - | - | 07-05-19 | 9819.6 | 9819.6 | - | - | - | - | - | - | - | - | - | - | - | -
08-05-19 | 12482 | 12482 | - | - | - | - | - | - | - | - | - | - | - | - | 08-05-19 | 9941.7 | 9941.7 | - | - | - | - | - | - | - | - | - | - | - | -
09-05-19 | 12161 | 12161 | - | - | - | - | - | - | - | - | - | - | - | - | 09-05-19 | 9875.7 | 9875.7 | - | - | - | - | - | - | - | - | - | - | - | -
10-05-19 | 12095 | 12095 | - | - | - | - | - | - | - | - | - | - | - | - | 10-05-19 | 8747.3 | 8747.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-05-19 | 9894 | 9894 | - | - | - | - | - | - | - | - | - | - | - | - | 11-05-19 | 9893.3 | 9893.3 | - | - | - | - | - | - | - | - | - | - | - | -
12-05-19 | 12376 | 12376 | - | - | - | - | - | - | - | - | - | - | - | - | 12-05-19 | 10175.1 | 10175.1 | - | - | - | - | - | - | - | - | - | - | - | -
13-05-19 | 11088 | 11088 | - | - | - | - | - | - | - | - | - | - | - | - | 13-05-19 | 10019.5 | 10019.5 | - | - | - | - | - | - | - | - | - | - | - | -
14-05-19 | 11823 | 11823 | - | - | - | - | - | - | - | - | - | - | - | - | 14-05-19 | 9302.8 | 9302.8 | - | - | - | - | - | - | - | - | - | - | - | -
15-05-19 | 11768 | 11768 | - | - | - | - | - | - | - | - | - | - | - | - | 15-05-19 | 9451.3 | 9451.3 | - | - | - | - | - | - | - | - | - | - | - | -
16-05-19 | 12012 | 12012 | - | - | - | - | - | - | - | - | - | - | - | - | 16-05-19 | 9597.1 | 9597.1 | - | - | - | - | - | - | - | - | - | - | - | -
17-05-19 | 8359.2 | 8359.2 | - | - | - | - | - | - | - | - | - | - | - | - | 17-05-19 | 8410.5 | 8410.5 | - | - | - | - | - | - | - | - | - | - | - | -
18-05-19 | 11179 | 11179 | - | - | - | - | - | - | - | - | - | - | - | - | 18-05-19 | 8583.3 | 8583.3 | - | - | - | - | - | - | - | - | - | - | - | -
19-05-19 | 11244 | 11244 | - | - | - | - | - | - | - | - | - | - | - | - | 19-05-19 | 9670 | 9670 | - | - | - | - | - | - | - | - | - | - | - | -
20-05-19 | 11329 | 11329 | - | - | - | - | - | - | - | - | - | - | - | - | 20-05-19 | 9966.9 | 9966.9 | - | - | - | - | - | - | - | - | - | - | - | -
21-05-19 | 12539 | 12539 | - | - | - | - | - | - | - | - | - | - | - | - | 21-05-19 | 10271 | 10271 | - | - | - | - | - | - | - | - | - | - | - | -
22-05-19 | 12259 | 12259 | - | - | - | - | - | - | - | - | - | - | - | - | 22-05-19 | 9446.2 | 9446.2 | - | - | - | - | - | - | - | - | - | - | - | -
23-05-19 | 11900 | 11900 | - | - | - | - | - | - | - | - | - | - | - | - | 23-05-19 | 8639.4 | 8639.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-05-19 | 9331 | 9331 | - | - | - | - | - | - | - | - | - | - | - | - | 24-05-19 | 8082.1 | 8082.1 | - | - | - | - | - | - | - | - | - | - | - | -
25-05-19 | 10412 | 10412 | - | - | - | - | - | - | - | - | - | - | - | - | 25-05-19 | 7571 | 7571 | - | - | - | - | - | - | - | - | - | - | - | -
26-05-19 | 12399 | 12399 | - | - | - | - | - | - | - | - | - | - | - | - | 26-05-19 | 8529.2 | 8529.2 | - | - | - | - | - | - | - | - | - | - | - | -
27-05-19 | 12336 | 12336 | - | - | - | - | - | - | - | - | - | - | - | - | 27-05-19 | 10172.7 | 10172.7 | - | - | - | - | - | - | - | - | - | - | - | -
28-05-19 | 12380 | 12380 | - | - | - | - | - | - | - | - | - | - | - | - | 28-05-19 | 9847.5 | 9847.5 | - | - | - | - | - | - | - | - | - | - | - | -
29-05-20 | 12893 | 12893 | - | - | - | - | - | - | - | - | - | - | - | - | 29-05-20 | 10364.4 | 10364.4 | - | - | - | - | - | - | - | - | - | - | - | -
30-05-19 | 12022 | 12022 | - | - | - | - | - | - | - | - | - | - | - | - | 30-05-19 | 9928 | 9928 | - | - | - | - | - | - | - | - | - | - | - | -
31-05-20 | 11098 | 11098 | - | - | - | - | - | - | - | - | - | - | - | - | 31-05-20 | 8809.23 | 8809.23

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:May' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12893 | 29/05/19 | 21:00
2 | Maximum day peak Genaration | MW | 10364.4 | 29/05/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 12893 | 29/04/19 | 21:00
4 | Minimum Generation | MW | 4900 | 25/05/19 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11307.071
6 | Average of the daily day peak Genaration | MW | 9118.159
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 7214.4644
12 | Total Generation by IPP | MKWH | 2116.5378 | % of total Gen. | 29.34%
13 | Total Generation by BPDB | MKWH | 3572.9103 | " | 49.52%
14 | A) Total Generation by RPCL | MKWH | 128.3528 | '' | 1.779%
| B) Total Generation by REB | MKWH | 136.4 | " | 1.891%
| C) Total Generation by RENTAL | MKWH | 497.3361 | " | 6.894%
| D) Total Imported from India (HVDC) | MKWH | 656.9702 | " | 9.106%
| E) Total Imported from Tripura, India (A.C) | MKWH | 105.9571 | " | 1.469%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4635.99 | % of total Gen. | 64.26%
| B) Oil | MKWH | 1614.1331 | '' | 22.37%
| C) Hydro | MKWH | 24.0671 | '' | 0.3336%
| D) Solar | MKWH | 3.673 | '' | 0.05091%
| E) Coal | MKWH | 173.674 | '' | 2.407%
| F) HVDC (Import from India) | MKWH | 656.9702 | '' | 9.106%
| G) A.C (Import from Tripura, India) | MKWH | 105.9571 | '' | 1.469%
16 | Maximun of the daily total Generation . | MKWH | 274.9579 | 27/05/19
17 | Monthly Load factor | % | 75.2134
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 446.2257
| A) Gas | M.Taka | 101.5512
| B) Liquid fuel | M.Taka | 317.4265
| C) Coal | M.Taka | 27.248
| D) HVDC (Import from India) | M.Taka | 3350.5479
| E) Tripura(Import from India) | M.Taka | 724.7467
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1089.0066 | 30/05/19
| A) Gas | M.Taka | 466.2744 | 30/05/19
| B) Liquid fuel | M.Taka | 607.5651 | 08/05/19
| C) Coal | M.Taka | 28.8536 | 15/05/19
| D) HVDC (Import from India) | M.Taka | 115.5196 | 08-05-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.3711
| B) Excluding Hydro & Solar | Taka/KWHR | 3.3841
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/19 | 06:00
b) | Actual | FT (MSL) | 73.92 | 31/05/19 | 06:00
22 | Peak Genaration of May 2018 | MW | 10137 | 24/04/18 | 19:30
23 | Peak Demand of May 2018 | MW | 10137 | 24/04/18 | 19:30
24 | Maximum peak Generation recorded upto 31/05/19 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/05/19 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/05/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.