## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:April' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | April 2019 |  | March 2019 |  | April 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12200 | 29/04/19 | 10933 | 30/03/19 | 10137 | 24/04/18 | 12200 | 29/04/19
|  |  | 19:30 |  | 20:00 |  | 21:00 |  | 19:30
2 | Minimum Generation (MW) | 2605 | 2019-04-01 | 4710 | 02/03/19 | 4376 | 18/04/18 | - | -
|  |  | 5:00 |  | 5:00 |  | 4:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12200 | 29/04/19 | 10933 | 30/03/19 | 10137 | 24/04/18 | 12200 | 29/04/19
|  |  | 19:30 |  | 20:00 |  | 21:00 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 10057 | 24/04/19 | 9132.3 | 31/03/19 | 8526.2 | 24/04/18 | 10057 | 24/04/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12200 | 29/04/19 | 10933 | 30/03/19 | 10137 | 24/04/18 | 12200 | 29/04/19
|  |  | 19:30 |  | 19:00 |  | 21:00 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 10379.3333 |  | 9524.16 |  | 8951.2 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 8450.5167 |  | 7899.11 |  | 7375.85 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 954 | 16/04/19 | 956 | 27/03/19 | 486 | 28/04/18 | 956 | 27/3/2019
|  |  | 20:30 |  | 19:00 |  | 14:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 188 | 28'/04/19 | 172 | 25/03/19 | 176 | 05/04/18 | 188 | 29/05/18
|  |  | 22:00 |  | 19:00 |  | 18:30 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3100.9672 |  | 3315.96 |  | 2819.51 |  | 3315.96 | March-19
21 | Station Use of BPDB (MKWH) | 126.2914 |  | 120.74 |  | 81.19
22 | Net Generation of BPDB (MKWH) | 2974.6758 |  | 3195.22 |  | 2738.32
23 | Net Generation of IPP & RPCL (MKWH) | 1935.4012 |  | 1441.94 |  | 1495.62
24 | Net Generation of REB (MKWH) | 128.616 |  | 138.68 |  | 119.68
24 | Net Generation of Rental Power Plant (MKWH) | 427.5001 |  | 370.9 |  | 631.84
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5466.1931 |  | 5146.75 |  | 4985.46 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 4100.9893 |  | 4289.8 |  | 3261.2 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 237.3993 |  | 118.39 |  | 465.99 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1029.0544 |  | 676.8 |  | 1060.14 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 51.4805 |  | 52.33 |  | 64.49 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 4.0002 |  | 3.91 |  | 0.36 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 169.5608 |  | 126.26 |  | 214.46 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 626.1175 |  | 611.47 |  | 280.62 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 70.7946 |  | 72.27 |  | 73.26 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:April' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12200 | 29/04/19 | 19:30
Generation Period
| Dhaka | MW | 4537
| Chattogram | MW | 1087
| Cumilla | MW | 1030
| Mymensingh | MW | 906
| Sylhet | MW | 443
a) | Total supply in East zone | MW | 8003
| Khulna | MW | 1373
| Barisal | MW | 277
| Rajshahi | MW | 1260
| Rangpur | MW | 642
b) | Total supply in West zone | MW | 3552
c) | Total supply in both zone ( a+b) | MW | 11555
Ref: | 27.21.2604.603.16.086.18.151 | Date: 20/05/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 830 | 13/04/19 | 1:00
| b) Ishurdi end | MW | 360 | 13/04/19 | 18:30
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 650 | 13/04/19 | 18:30
| b) Ishurdi end | MW | 360 | 13/04/19 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.5805 | 13/04/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 3.4291 | 13/04/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 27.6118
| b) Ishurdi end | MKWH | 38.5229
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 37.3672
| b) Ishurdi end | MKWH | 26.8076
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 480 | 13/04/19 | 2:00
| b)Serajganj end | MW | 450 | 01/04/19 | 3:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 440 | 01/04/19 | 3:00
| b)Sirajganj end | MW | 410 | 13/04/19 | 2:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.78 | 13/04/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 4.662 | 13/04/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 37.256
| b)Sirajganj end | MKWH | 51.866
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 51.184
| b)Sirajganj end | MKWH | 36.93
30 | Transmission loss of EWI /NO-2 | % | 1.131
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Valuka | 132/33 kV Transformer-T1 | 2019-04-01 15:58 | 2019-04-01 16:40 | 0:42 | E/O | Due to re hot maintenance | 40 | 28 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-04-02 18:40 | 2019-04-03 14:07 | 19:27 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2019-04-04 15:39 | 2019-04-04 15:47 | 0:08 | E/O | Due to 33 kV Poilanpur feeder fault | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T1, T2 & T3 | 2019-04-05 18:55 | 2019-04-05 19:07 | 0:12 | E/O | Due to 33 kV Tangail feeder fault | 125 | 25 | Power interruption
Kadda | 33 kV Bus | 2019-04-07 16:30 | 2019-04-07 17:40 | 1:10 | E/O | Due to re hot maintenance by PBS | 85 | 99.1667 | Power interruption
Joydevpur | 132/33 kV Transformers-T3, & T4 | 2019-04-08 10:19 | 2019-04-08 10:37 | 0:18 | E/O | Due to 33 kV cable fault | 84 | 25.2 | Power interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-04-09 11:35 | 2019-04-09 11:45 | 0:10 | E/O | Due to 33 kV cable fault | 0 | 0 | No interruption
Jamalpur | 33 kV Bus-2& 132/33 kV Transformer T2 | 2019-04-10 06:30 | 2019-04-10 08:48 | 2:18 | E/O | Due to re hot maintenance | 22 | 92 | Power interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-04-16 21:03 | 2019-04-16 23:00 | 1:57 | E/O | Due to re hot maintenance | 0 | 0 | Power interruption
Valuka | 132/33 kV Transformer-T1 | 2019-04-22 21:16 | 2019-04-22 22:33 | 1:17 | E/O | Due to re hot maintenance at 33 kV side | 55 | 64.1667 | Power interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-04-23 09:27 | 2019-04-23 10:25 | 0:58 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T1,& T2 | 2019-04-23 20:30 | 2019-04-23 21:28 | 0:58 | E/O | Due to fire at R-phase CT | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2019-04-25 11:57 | 2019-04-25 12:20 | 0:23 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2019-04-26 06:10 | 2019-04-26 12:10 | 6:00 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2019-04-27 06:54 | 2019-04-27 09:44 | 2:50 | E/O | Due to re hot maintenance | 16 | 45.3333 | Power interruption
Manikganj | 132/33 kV Transformer-T4 | 2019-04-29 07:21 | 2019-04-29 07:38 | 0:17 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 38:48 |  | Unserved Energy: |  | 378.8667
Dhaka (South) Grid Circle :
Hasnabad | 230 kV Bus-2 | 2019-04-03 07:11 | 2019-04-03 10:17 | 3:06 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Ghorasal | 230/132 kV Transformer AT1 | 2019-04-03 07:30 | 2019-04-03 18:30 | 11:00 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T1 | 2019-04-09 11:21 | 2019-04-09 11:32 | 0:11 | T | Tripped showing Vaj,HVPH signal | 0 | 0 | No interruption
Narsingdi | 132 kV Bus-2 | 2019-04-09 14:12 | 2019-04-09 16:46 | 2:34 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-2 | 2019-04-12 15:51 | 2019-04-12 16:05 | 0:14 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-Tr-1 | 2019-04-14 02:44 | 2019-04-14 15:08 | 12:24 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer--T1 | 2019-04-16 23:03 | 2019-04-16 23:40 | 0:37 | E/O | Due to re hot maintenance | 32 | 19.7333 | Power interruption
Narsingdi | 132/33 kV Transformer--T2 | 2019-04-26 19:12 | 2019-04-26 20:02 | 0:50 | E/O | Due to 33 kV cable fault | 40 | 33.3333 | Power interruption
Hasnabad | 132/33 kV Transformers--T1 & T-5 | 2019-04-28 16:56 | 2019-04-28 17:17 | 0:35 | T | Tripped showing O/C relay at 33 kV side | 84 | 49 | Power interruption
|  |  | Total : | 2:37 |  | Unserved Energy: |  | 102.0667
Chittagong Grid Circle :
Halishahar | 33 kV Potenga feeder | 2019-04-04 09:46 | 2019-04-04 15:15 | 5:29 | S/O | Due to server flashing at 33 kV DS | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformers-T1 & T2 | 2019-04-06 09:17 | 2019-04-06 09:35 | 0:18 | T | Tripped showing O/C relay at 33 kV side | 60 | 18 | Power interruption
Madunaghat | 132/33 kV Transformers-T1 | 2019-04-11 16:58 | 2019-04-11 17:40 | 0:42 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-04-11 16:01 | 2019-04-11 16:56 | 0:55 |  |  | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT3 | 2019-04-21 06:25 | 2019-04-21 07:22 | 0:57 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T1 | 2019-04-21 11:02 | 2019-04-21 12:58 | 1:56 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2019-04-21 20:32 | 2019-04-21 21:59 | 1:27 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Modern steel | 132/33 kV Transformer-T1 | 2019-04-24 11:17 | 2019-04-24 11:35 | 0:18 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2019-04-26 07:36 | 2019-04-26 09:18 | 1:42 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 4:38 |  | Unserved Energy: |  | 18
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer T3 | 2019-04-03 08:45 | 2019-04-03 10:45 | 2:00 | E/O | Due to re hot maintenance at 33 kV side | 20 | 40 | Power interruption
Fenchuganj | 230/132 kV Transformer AT1 | 2019-04-05 05:35 | 2019-04-05 06:32 | 2:57 | T | Tripped without showing any relay | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer T1 | 2019-04-06 09:18 | 2019-04-06 18:35 | 3:57 | T | Tripped showing differential relay | 0 | 0 | No interruption
Chandpur | 33 kV Bus | 2019-04-07 05:24 | 2019-04-07 06:30 | 1:06 | E/O | Due to re hot maintenance | 10 | 10.6667 | Power interruption
Daudkandi | 132/33 kV Transformer-T1 | 2019-04-16 11:13 | 2019-04-16 12:06 | 0:53 | E/O | Due to re hot maintenance 33 kV side | 30 | 26.5 | Power interruption
Fenchuganj | 132/33 kV Transformers-T1 | 2019-04-20 13:46 | 2019-04-20 14:45 | 2:57 | T | Tripped without showing any relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-04-24 13:13 | 2019-04-24 13:19 | 2:57 | T | Tripped O/C showing relay | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-04-24 21:00 | 2019-04-24 21:37 | 0:37 | E/O | Due to re hot maintenance 33 kV side | 60 | 37 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T04 | 2019-04-25 12:22 | 2019-04-25 14:04 | 1:42 | E/O | Due to re hot maintenance 33 kV side | 0 | 0 | No interruption
Page:2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
B.Baria | 132/33 kV Transformer-T1 | 2019-04-26 07:34 | 2019-04-26 09:15 | 1:41 | E/O | Due to re hot maintenance 33 kV side | 20 | 33.6667 | Power interruption
Cumilla(N) | 132/33 kV Transformers-T3 | 2019-04-27 19:59 | 2019-04-27 20:55 | 0:56 | E/O | Due to bursting of PT at 33 kV side | 100 | 93.3333 | Power interruption 19:59 to 20:55
| 132/33 kV Transformers-T4 | 2019-04-27 19:59 | 2019-04-27 20:58 | 0:59 | E/O
Fenchuganj | 230/132 kV Transformer AT-2 | 2019-04-28 13:56 | 2019-04-28 15:53 | 1:57 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 24:39 |  | Unserved Energy: |  | 241.1667
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T3 | 2019-04-01 19:29 | 2019-04-01 22:33 | 3:04 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-04-01 21:05 | 2019-04-01 21:11 | 0:06 | T | Tripped showing 33 kV feeder fault | 17 | 1.7 | Power interruption
| 132/33 kV Transformers-T1 | 2019-04-01 03:30 | 2019-04-01 09:16 | 5:46 | T | Due to high Voltage | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-04-01 04:12 | 2019-04-01 04:56 | 0:44 | T |  | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 & T3 | 2019-04-01 04:45 | 2019-04-01 07:56 | 3:11 | T | Due to high Voltage | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-04-01 04:52 | 2019-04-01 06:33 | 1:41 | T |  | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T1 | 2019-04-01 03:38 | 2019-04-01 07:33 | 3:55 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-04-01 03:51 | 2019-04-01 10:12 | 6:21 | T |  | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformers-T1 & T2 | 2019-04-01 04:04 | 2019-04-01 05:53 | 1:49 | T | Due to high Voltage | 0 | 0 | No interruption
Magura | 132/33 kV Transformers-T1 & T2 | 2019-04-01 04:03 | 2019-04-01 06:54 | 2:51 | T | Due to high Voltage | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformers-T1 & T2 | 2019-04-03 09:45 | 2019-04-03 10:20 | 0:35 | T | Due to Tripped from LV showing side SPS relay | 19 | 11.0833 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-04-03 10:28 | 2019-04-03 10:50 | 0:22 | T |  | 19 | 6.9667 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-04-04 12:07 | 2019-04-04 12:57 | 0:50 | T | due to operation of SPS | 10 | 8.3333 | Power interruption
Chuadanga | 132/33 kV Transformers-T1 | 2019-04-06 21:00 | 2019-04-06 23:16 | 2:16 | T | Tripped showing O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-04-06 21:00 | 2019-04-07 00:12 | 3:12 | T |  | 0 | 0 | No interruption
Magura | 132/33 kV Transformers-T1 & T2 | 2019-04-06 19:58 | 2019-04-06 23:29 | 3:31 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformers-T1 & T2 | 2019-04-10 23:22 | 2019-04-11 00:05 | 0:43 | T | Tripped showing 33 kV feeder fault | 40 | 28.6667 | Power interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-04-11 20:08 | 2019-04-11 20:16 | 0:08 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-04-11 19:03 | 2019-04-11 20:11 | 1:08 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2019-04-13 11:34 | 2019-04-13 11:42 | 0:08 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Noapara | 132/33 kV Transformers-T1 | 2019-04-15 07:06 | 2019-04-15 09:52 | 2:46 | E/O | Due to re hot maintenance at 33 kV side | 15 | 41.5 | Power interruption
| 132/33 kV Transformers-T2 | 2019-04-15 07:06 | 2019-04-15 11:10 | 4:04 | E/O
Satkhira | 132/33 kV Transformer-T1 | 2019-04-17 21:15 | 2019-04-17 23:01 | 1:46 | E/O | Due to re hot maintenance | 60 | 26.5 | Power interruption
Madaripur | 132/33 kV Transformers-T1 & T2 | 2019-04-20 07:30 | 2019-04-20 10:11 | 2:41 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Barisal | 132/33 kV Transformers-T1 & T2 | 2019-04-20 17:58 | 2019-04-20 18:02 | 0:04 | T | Tripped showing inst.E/F relay | 80 | 5.3333 | Power interruption
Patuakhali | 132/33 kV all Transformers | 2019-04-24 19:57 | 2019-04-24 20:19 | 0:22 | T | Tripped showing 33 kV feeder fault | 62 | 22.7333 | Power interruption
Bhandaria | 132/33 kV all Transformers | 2019-04-24 20:00 | 2019-04-24 20:03 | 0:03 | T | Tripped showing 33 kV feeder fault | 92 | 4.6 | Power interruption
| 132/33 kV Transformer-T1 | 2019-04-25 10:12 | 2019-04-25 13:25 | 3:13 | E/O | Due to Oil leakage 33 kV side | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-04-25 10:24 | 2019-04-25 11:35 | 1:11 | E/O | Due to re hot maintenance at 33 kV side | 40 | 47.3333 | Power interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-04-25 08:21 | 2019-04-25 08:24 | 0:03 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-04-26 16:56 | 2019-04-26 17:04 | 0:08 | T | Tripped showing inst.E/F relay | 6 | 0.8 | Power interruption
Patuakhali | 132/33 kV Transformers-T1 | 2019-04-27 01:56 | 2019-04-27 02:56 | 1:00 | T | Tripped showing 33 kV feeder fault | 24 | 24 | Power interruption
| 132/33 kV Transformers-T2 | 2019-04-27 01:56 | 2019-04-27 05:59 | 4:03 | T
Bagerhat | 33 kV Bus | 2019-04-29 06:28 | 2019-04-29 08:31 | 2:03 | E/O | Due to re hot maintenance at 33 kV side | 35 | 71.75 | Power interruption
| 132/33 kV Transformer-T1 | 2019-04-29 08:40 | 2019-04-29 08:50 | 0:10 | T | Tripped showing dist.& O/C relay | 55 | 9.1667 | Power interruption
Noapara | 132/33 kV Transformer-T4 | 2019-04-30 11:14 | 2019-04-30 12:28 | 1:14 | E/O | Due to re hot maintenance at 33 kV side | 24 | 29.6 | Power interruption
|  |  | Total : | 65:58 |  | Unserved Energy: |  | 340.0667
HVDC Grid Circle :
Bheramara | 230/132 kV Transformers T01 & T02 | 2019-04-01 03:01 | 2019-04-01 06:21 | 3:20 | T | Tripped showing high Voltage | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2019-04-01 04:04 | 2019-04-01 06:42 | 2:38 | T |  | 0 | 0 | No interruption
Kustia | 132/33 kV Transformer1-T1 | 2019-04-03 07:22 | 2019-04-03 08:10 | 0:48 | E/O | Due to red hot maintenance at 33 kV Bus | 35 | 28 | Power interruption
Ishurdi | 230 kV midbreaker 815B | 2019-04-06 06:43 | 2019-04-06 11:46 | 5:03 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bheramara | 230/132 kV Transformers T1 | 2019-04-06 19:57 | 2019-04-07 01:27 | 5:30 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara | 230/132 kV Transformers T2 | 2019-04-06 19:57 | 2019-04-07 23:13 | 27:16 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2019-04-06 19:58 | 2019-04-06 20:50 | 0:52 | T |  | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2019-04-10 20:32 | 2019-04-10 21:18 | 0:46 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bottail | 132/33 kV Transformers-T1 & T2 | 2019-04-12 19:16 | 2019-04-12 19:41 | 0:25 | T | Tripped showing E/F relay at 33 kV side | 60 | 25 | Power interruption
HVDC | HVDC Bheramara block-1 | 2019-04-15 18:48 | 2019-04-15 19:22 | 0:34 | T | due to external protection trip | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformers-T1 | 2019-04-16 17:21 | 2019-04-16 19:34 | 2:13 | E/O | Due to bursing of (B-phase) PT | 69 | 40.25 | Power interruption 17:21 to 7:56
| 132/33 kV Transformers-T2 | 2019-04-16 17:21 | 2019-04-16 17:56 | 0:35 | E/O
Bottail | 132/33 kV Transformers-T1 & T2 | 2019-04-19 09:11 | 2019-04-19 09:21 | 0:10 | E/O | Due to Meherpur feeder fault | 64 | 10.6667 | Power interruption
Pabna | 132/33 kV Transformer-T1 | 2019-04-19 21:58 | 2019-04-19 22:02 | 0:04 | T | Tripped showing O/C relay | 63 | 4.2 | Power interruption
Bheramara | HVDC pole-1 | 2019-04-20 21:13 | 2019-04-21 01:14 | 4:01 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-04-23 06:24 | 2019-04-23 07:37 | 1:13 | E/O | Due to re hot maintenance | 20 | 24.3333 | Power interruption
Pabna | 132/33 kV Transformer-T3 | 2019-04-28 04:35 | 2019-04-28 05:43 | 1:08 | T | Tripped showing Differential relay | 40 | 45.3333 | Power interruption
Bottail | 132/33 kV Transformer-T1 | 2019-04-30 09:15 | 2019-04-30 10:35 | 1:20 | E/O | Due to re hot maintenance | 27 | 36 | Power interruption
|  |  | Total : | 51:58 |  |  |  | 213.7833
Bogra Grid Circle:
Rajshahi | 132/33 kV Transformer-T2 | 2019-04-01 16:38 | 2019-04-01 17:47 | 1:09 | E/O | Due to re hot maintenance | 15 | 17.25 | Power interruption
Joypurhat | 132/33 kV Transformers-T1 & T2 | 2019-04-01 01:50 | 2019-04-01 05:18 | 3:28 | T | Due to high Voltage | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T1 | 2019-04-06 01:20 | 2019-04-06 01:28 | 0:08 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 | 2019-04-06 15:35 | 2019-04-06 17:45 | 2:10 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T1 | 2019-04-09 09:05 | 2019-04-09 09:40 | 0:35 | E/O | Due to 33 kV feeder fault | 15 | 8.75 | Power interruption
Rajshahi | 132/33 kV Transformer-T2 | 2019-04-09 10:28 | 2019-04-09 14:35 | 4:07 | E/O | Due to re hot maintenance | 10 | 41.1667 | Power interruption
Barapukuria | 132/33 kV Transformer-T5 | 2019-04-20 10:23 | 2019-04-20 11:18 | 0:55 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T1 | 2019-04-20 09:58 | 2019-04-20 15:15 | 5:17 | E/O | Due to capacitor cable burst | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2019-04-20 13:01 | 2019-04-20 13:28 | 0:27 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T2 | 2019-04-21 08:20 | 2019-04-21 09:20 | 1:00 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bogra (Old) | 132/33 kV Transformers-T3 & T4 | 2019-04-26 07:17 | 2019-04-26 08:38 | 1:21 | E/O | Due to re hot maintenance at 33 kV side | 100 | 301.6667 | Power interruption
Natore | 132/33 kV Transformer-T4 | 2019-04-29 07:51 | 2019-04-29 08:45 | 0:54 | E/O | Due to re hot maintenance at 33 kV side | 20 | 18 | Power interruption
|  |  | Total : | 21:31 |  | Unserved Energy: |  | 386.8333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 210:09 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line | 2019-04-01 01:29 | 2019-04-01 01:37 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2019-04-01 02:52 | 2019-04-01 04:10 | 1:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Uttara(New) 132 kV line-1 | 2019-04-02 18:00 | 2019-04-02 18:53 | 0:53 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2019-04-02 18:40 | 2019-04-02 18:48 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-04-06 05:48 | 2019-04-06 06:05 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 | 2019-04-06 08:13 | 2019-04-06 08:33 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2019-04-06 21:10 | 2019-04-06 22:05 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2019-04-06 21:41 | 2019-04-06 22:32 | 0:51 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2019-04-06 21:28 | 2019-04-06 21:37 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV line-1 | 2019-04-06 21:10 | 2019-04-06 21:14 | 0:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-04-06 21:35 | 2019-04-06 21:50 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-04-16 06:20 | 2019-04-16 07:19 | 0:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2019-04-16 04:22 | 2019-04-16 04:33 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Jamalpur S/S | Jamalpur S/S-Jamalpur P/S 132 kV line-1 & 2 | 2019-04-17 02:06 | 2019-04-17 02:17 | 0:11 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Jamalpur S/S-United Mymensingh 132 kV line-1 & 2 | 2019-04-17 19:26 | 2019-04-17 19:34 | 0:08 | T | Tripped showing O/C. relay | 60 | 8 | Power interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-04-20 10:09 | 2019-04-20 11:32 | 1:23 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-04-20 13:01 | 2019-04-20 13:13 | 0:12 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 & 2 | 2019-04-21 03:37 | 2019-04-21 04:01 | 0:24 | E/O | Due to bursting of CT | 147 | 9.8 | Power interruption 17:58 to 18:02
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-04-25 11:56 | 2019-04-25 12:03 | 0:07 | T | Tripped showing dist. relay | 170 | 19.8333 | Power interruption 17:58 to 18:02
| Mymensingh-Jamalpur 132 kV line-2 | 2019-04-25 13:35 | 2019-04-25 13:48 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-1 | 2019-04-25 13:35 | 2019-04-25 13:46 | 0:11 | T | Tripped showing O/C. relay | 216 | 39.6 | Power interruption 13:35 to 13:46
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-04-25 13:35 | 2019-04-25 13:56 | 0:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-04-25 15:50 | 2019-04-25 16:52 | 1:02 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2019-04-27 07:49 | 2019-04-27 14:31 | 6:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 15:56 |  | Unserved Energy: |  | 77.2333
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 230 kV line-1 | 2019-03-31 18:31 | 2019-04-01 03:04 | 8:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-03-31 21:26 | 2019-04-01 10:15 | 12:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-1 | 2019-04-01 11:50 | 2019-04-01 12:24 | 0:34 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-1 | 2019-04-01 14:10 | 2019-04-01 15:00 | 0:50 | T | Tripped showing PTAW signal | 0 | 0 | No interruption
| Ghorasal-Joydevpur 132 kV line-1 | 2019-04-03 07:30 | 2019-04-03 13:50 | 6:20 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-1 | 2019-04-07 07:15 | 2019-04-07 08:15 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-1 | 2019-04-07 16:16 | 2019-04-07 16:39 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj (S) 230 kV line-1 | 2019-04-06 08:25 | 2019-04-06 09:36 | 1:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Tongi 230 kV line-1 | 2019-04-06 12:55 | 2019-04-06 13:11 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-04-08 16:15 | 2019-04-08 17:19 | 1:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2019-04-09 11:25 | 2019-04-09 11:54 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakhya 132 kV line | 2019-04-09 18:15 | 2019-04-09 19:35 | 1:20 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon (Maniknagar-2) 132 kV line | 2019-04-09 18:17 | 2019-04-09 18:31 | 0:14 | T | Tripped showing dist.(Z1-phase) relay | 0 | 0 | No interruption
| Haripur-Ullon (Maniknagar-2) 132 kV line | 2019-04-09 19:44 | 2019-04-09 19:53 | 0:09 | T |  | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line | 2019-04-09 18:18 | 2019-04-09 18:38 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur(N) 132 kV line | 2019-04-09 18:12 | 2019-04-09 18:42 | 0:30 | T | Tripped showing dist. (Z1) relay | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (N) 132 kV line | 2019-04-09 18:12 | 2019-04-09 18:43 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Moghbazar | Moghbazar-Rampura 132 kV line-1 & 2 | 2019-04-09 18:07 | 2019-04-09 18:44 | 0:37 | T | Tripped showing bas bar protection relay | 102 | 62.9 | Power interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2019-04-11 14:45 | 2019-04-11 14:57 | 0:12 | T | Tripped showing dist. relay | 87 | 17.4 | Power interruption
| Lalbagh-Hasnabad 132 kV line | 2019-04-16 23:10 | 2019-04-16 23:29 | 0:19 | T | Tripped showing dist. relay | 65 | 20.5833 | Power interruption
Haripur | Haripur-Ullon 132 kV line-2 | 2019-04-17 00:10 | 2019-04-17 00:20 | 0:10 | T | Tripped showing dist. (B-phase) relay | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (N) 132 kV line | 2019-04-26 05:43 | 2019-04-26 06:32 | 0:49 | T | Tripped showing dir.& O/C relay at 33 kV feeder fault | 163 | 133.1167 | Power interruption
Shyampur(N) | Shyampur (N) -Shyampur 132 kV line -1 & 2 | 2019-04-27 14:21 | 2019-04-27 14:42 | 0:21 | T | Tripped showing E/F. relay | 170 | 59.5 | Power interruption
|  |  | Total : | 17:39 |  | Unserved Energy: |  | 293.5
Chittagong Grid Circle :
Khulshi | Khulshi-AKS Steel 132 kV line | 2019-04-02 23:53 | 2019-04-03 00:35 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-2 | 2019-04-08 12:28 | 2019-04-08 16:21 | 3:53 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line | 2019-04-08 14:00 | 2019-04-08 15:27 | 1:27 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sikalbaha(Old) | Sikalbaha(Old)-ECPV P/P 132 kV line | 2019-04-19 05:56 | 2019-04-19 06:30 | 0:34 | E/O | Due to burting at 132 (R-phase) CT | 0 | 0 | No interruption
Sikalbaha(New) | Sikalbaha(New)-Juldah 132 kV line | 2019-04-19 05:56 | 2019-04-19 18:13 | 12:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 18:53 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2019-04-02 19:03 | 2019-04-02 21:37 | 2:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Cumilla(N) 132 kV line-2 | 2019-04-02 19:30 | 2019-04-02 20:05 | 0:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV line-2 | 2019-04-03 16:30 | 2019-04-03 17:35 | 1:05 | T | Tripped showing dist. relay | 128 | 138.6667 | Power interruption
Sylhet | Sylhet -Fenchuganj 132 kV line | 2019-04-05 03:42 | 2019-04-05 04:05 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2019-04-05 05:37 | 2019-04-05 06:29 | 0:52 | T | Tripped showing dist. (A-phase) relay | 0 | 0 | No interruption
Sylhet | Sylhet -Fenchuganj 132 kV line | 2019-04-05 09:43 | 2019-04-05 10:07 | 0:24 | T | Tripped showing dist. relay | 11 | 4.4 | Power interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV line-1 | 2019-04-05 21:20 | 2019-04-05 23:02 | 1:42 | T | Tripped showing auto reclose relay | 80 | 72 | Power interruption
| Cumilla(S)-Surjamoninagar 132 kV line-2 | 2019-04-05 21:20 | 2019-04-05 22:14 | 0:54 | T
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2019-04-07 00:02 | 2019-04-07 01:00 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Baroiarhat 132 kV line-1 & 2 | 2019-04-07 22:50 | 2019-04-08 00:04 | 1:14 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Feni-Cumilla(N) 132 kV line-2 & T-ckt | 2019-04-07 22:58 | 2019-04-07 23:47 | 0:49 | T |  | 0 | 0 | No interruption
| Feni-Chowmuhani 132 kV line-1 & 2 | 2019-04-07 22:58 | 2019-04-08 00:02 | 1:04 | T |  | 103 | 109.8667 | Power interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2019-04-07 22:58 | 2019-04-07 23:10 | 0:12 | T | Tripped showing E/F relay | 120 | 32 | Power interruption 22:58 to 23:14
| Ramganj-Chowmuhani 132 kV line-2 | 2019-04-07 22:58 | 2019-04-07 23:14 | 0:16 | T
B.Baria | B.Baria-Narsingdi 132 kV line-1 | 2019-04-08 11:50 | 2019-04-08 13:09 | 1:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-1 | 2019-04-08 12:27 | 2019-04-08 12:50 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2019-04-08 14:47 | 2019-04-08 14:57 | 0:10 | T | Tripped showing dist. (A-phase) relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 | 2019-04-09 11:41 | 2019-04-09 11:54 | 0:13 | T | Tripped showing directional & O/C relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line | 2019-04-09 21:20 | 2019-04-09 23:08 | 1:48 | E/O | Due to emergency maintenance | 70 | 126 | Power interruption
| Feni-Cumilla(N) 132 kV line-2 | 2019-04-09 19:29 | 2019-04-09 19:32 | 0:03 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line | 2019-04-09 22:47 | 2019-04-09 23:20 | 0:33 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-2 | 2019-04-15 08:17 | 2019-04-15 09:21 | 1:04 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Cumilla | Cumilla-BSRM 230 kV line-1 | 2019-04-20 10:07 | 2019-04-20 12:22 | 2:15 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1 | 2019-04-20 12:22 | 2019-04-20 23:37 | 11:15 | T | Due to partial tripping of india | 0 | 0 | No interruption
0 | Cumilla(S)-Tripura 132 kV line-2 | 2019-04-20 12:22 | 2019-04-20 23:38 | 11:16 | T |  | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2019-04-20 13:46 | 2019-04-21 11:40 | 21:54 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sareemongal 132 kV line-1 | 2019-04-20 13:46 | 2019-04-20 15:14 | 1:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2019-04-26 19:49 | 2019-04-26 20:02 | 0:13 | T | Tripped showing Dir.& O/C relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line- 1&2 | 2019-04-26 19:49 | 2019-04-26 20:05 | 0:16 | T |  | 0 | 0 | No interruption
| Feni-Chowmuhani 132 kV line- 1 | 2019-04-27 18:33 | 2019-04-27 18:40 | 0:07 | T | Tripped showing O/C relay | 260 | 30.3333 | Power interruption 18:33 to 19:04
| Feni-Chowmuhani 132 kV line- 2 | 2019-04-27 18:33 | 2019-04-27 19:04 | 0:31 | T
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2019-04-27 18:33 | 2019-04-27 18:40 | 0:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2019-04-28 13:56 | 2019-04-28 14:46 | 0:50 | T | Tripped showing dist. relay | 317 | 169.0667 | Power interruption 13:56 to 14:28
| Fenchuganj-Sreemongal 132 kV line-2 | 2019-04-28 13:56 | 2019-04-28 14:28 | 0:32 | T
Sylhet S/S | Sylhet S/S-Fenchuganj P/S 132 kV line | 2019-04-30 00:54 | 2019-04-30 01:20 | 0:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line | 2019-04-30 00:54 | 2019-04-30 01:25 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 70:16 |  | Unserved Energy: |  | 682.3333
Khulna Grid Circle :
Madaripur | Madaripur-Faridpur 132 kV line-2 | 2019-04-01 04:34 | 2019-04-01 08:00 | 3:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2019-04-01 04:15 | 2019-04-01 06:51 | 2:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bhandaria-Barisal(S) 132 kV line | 2019-04-01 04:51 | 2019-04-01 07:14 | 2:23 | T | Tripped showing dist. & O/V relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-04-01 03:56 | 2019-04-01 06:37 | 2:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Patuakhali 132 kV line | 2019-04-01 04:15 | 2019-04-01 05:13 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2019-04-02 23:27 | 2019-04-02 23:47 | 0:20 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2019-04-06 21:02 | 2019-04-06 22:11 | 1:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Madaripur-Barisal 132 kV line | 2019-04-06 21:30 | 2019-04-06 22:21 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barisal 132 kV line | 2019-04-06 21:30 | 2019-04-06 22:21 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bhandaria-Bagerhat 132 kV line | 2019-04-06 21:30 | 2019-04-06 23:19 | 1:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2019-04-06 21:34 | 2019-04-07 12:32 | 14:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-04-06 21:26 | 2019-04-07 21:21 | 23:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-04-06 20:42 | 2019-04-06 21:56 | 1:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Madaripur-Barisal 132 kV line | 2019-04-06 21:02 | 2019-04-06 22:11 | 1:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2019-04-08 10:30 | 2019-04-08 12:07 | 1:37 | T | Tripped showing E/F & lockout relay | 0 | 0 | No interruption
Khulna(C) | Khulna©Noapara 132 kV line-2 | 2019-04-11 09:30 | 2019-04-11 10:11 | 0:41 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2019-04-23 11:16 | 2019-04-23 11:24 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-04-23 18:06 | 2019-04-23 18:17 | 0:11 | T | Tripped showing no. relay | 0 | 0 | No interruption
| Madaripur-Barisal 132 kV line-1 | 2019-04-23 18:06 | 2019-04-23 18:22 | 0:16 | T | Tripped showing no. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-04-26 20:29 | 2019-04-26 20:47 | 0:18 | T | Tripped showing dist. (3-phase) relay | 0 | 0 | No interruption
|  |  | Total : | 49:27 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-ishurdi 132 kV line-1 | 2019-04-02 21:30 | 2019-04-02 23:15 | 1:45 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-1 | 2019-04-02 09:45 | 2019-04-02 10:09 | 0:24 | T | Tripped showing dist. relay | 47 | 18.8 | Power interruption
| Bheramara-Faridpur 132 kV line-1 | 2019-04-03 10:28 | 2019-04-03 15:45 | 5:17 | T |  | 50 | 264.1667 | Power interruption
| Bheramara-Faridpur 132 kV line-2 | 2019-04-04 12:07 | 2019-04-04 12:17 | 0:10 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Ishurdi 230 kV line 2,3 | 2019-04-08 14:01 | 2019-04-08 15:33 | 1:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| HVDC Bheramara-Ishurdi 230 kV line 4 | 2019-04-08 14:01 | 2019-04-08 15:40 | 1:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| HVDC Bheramara-Ishurdi 230 kV line -1 | 2019-04-13 14:17 | 2019-04-13 17:51 | 3:34 | T |  | 0 | 0 | No interruption
| HVDC Bheramara-Ishurdi 230 kV line -3 | 2019-04-13 14:17 | 2019-04-13 14:44 | 0:27 | T |  | 0 | 0 | No interruption
| HVDC Bheramara-Ishurdi 230 kV line -4 | 2019-04-13 14:17 | 2019-04-13 17:52 | 3:35 | T |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2019-04-17 03:45 | 2019-04-17 04:08 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 | 2019-04-23 04:50 | 2019-04-23 06:30 | 1:40 | E/O | Due to bursting of (R-phase) CT | 0 | 0 | No interruption
Bottail | Bottail-Ishurdi 132 kV line-2 | 2019-04-25 10:05 | 2019-04-25 10:14 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 20:35 |  | Unserved Energy: |  | 282.9667
Bogura Grid Circle :
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2019-04-01 03:36 | 2019-04-01 12:43 | 9:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2019-04-06 06:13 | 2019-04-06 06:41 | 0:28 | E/O | Due toY-phase CT burst | 166 | 77.4667 | Power interruption
| Rajshahi-Natore 132 kV line-2 | 2019-04-06 06:13 | 2019-04-06 20:46 | 14:33 | E/O |  | 0 | 0 | No interruption
| Rajshahi-Natore 132 kV line-1 | 2019-04-09 10:52 | 2019-04-09 11:56 | 1:04 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 132 kV line-1 | 2019-04-09 16:20 | 2019-04-09 16:41 | 0:21 | T |  | 0 | 0 | No interruption
| Bogura -Palashbari 132 kV line-1 | 2019-04-12 06:45 | 2019-04-12 07:48 | 1:03 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Panchagar 132 kV line | 2019-04-15 06:40 | 2019-04-15 08:03 | 1:23 | E/O | Due to re hot maintenance | 20 | 27.6667 | Power interruption
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2019-04-17 01:10 | 2019-04-17 02:30 | 1:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Palashbari-Mahastangar 132 kV line-2 | 2019-04-20 21:31 | 2019-04-22 11:00 | 37:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 57:41 |  | Unserved Energy: |  | 105.1333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 250:27 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Sherpur | 132/33 kV Transformer-T1 | 2019-04-01 14:25 | 2019-04-01 16:32 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T02 | 2019-04-05 07:32 | 2019-04-05 18:40 | 11:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 & 33 kV Bus-2 | 2019-04-05 09:05 | 2019-04-05 11:58 | 2:53 | S/O | Due to new feeder connection | 12 | 34.6 | Power interruption
Valuka | 132 kV Bus | 2019-04-07 07:15 | 2019-04-07 07:45 | 0:30 | S/O | Due to removing their permises | 45 | 22.5 | Power interruption
Jamalpur | 132/33 kV Transformers-T1 & T2 | 2019-04-11 06:30 | 2019-04-11 08:48 | 2:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-04-12 06:38 | 2019-04-12 09:36 | 2:58 | S/O | Due to C/M work | 30 | 89 | Power interruption
Kabirpur | 132/33 kV Transformer-T3 | 2019-04-12 12:14 | 2019-04-12 16:17 | 4:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 |  | 2019-04-12 13:36 | 43567.5667 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2019-04-17 10:18 | 2019-04-17 14:03 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2019-04-17 17:48 | 2019-04-18 14:35 | 20:47 | S/O | Due to breaker problem | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2019-04-20 06:44 | 2019-04-20 10:02 | 3:18 | S/O | Due to C/M work | 40 | 132 | Power interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-04-20 10:05 | 2019-04-20 12:19 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2019-04-24 06:49 | 2019-04-24 11:49 | 5:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 |  | 2019-04-25 19:32 | 43580.8139 | S/O | Due to replacememt work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformers-T1 & T2 with 33 kV Bus | 2019-04-25 06:07 | 2019-04-25 09:55 | 3:48 | S/O | Due to C/M work | 60 | 228 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2019-04-26 12:12 | 2019-04-26 15:19 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2019-04-26 12:15 | 2019-04-26 12:35 | 0:20 | S/O | Due to temperature high at 33 kV B-phase CT | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T2(New) |  | 2019-04-26 15:29 |  |  | New commissioning | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2019-04-27 06:59 | 2019-04-27 09:49 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T2 |  | 2019-04-27 12:02 | 43582.5014 | S/O | Due to C/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T1 | 2019-04-30 10:15 | 2019-04-30 14:17 | 4:02 | S/O | Due to C/M work | 45 | 181.5 | Power interruption
|  |  | Total : | 87164.2049 |  | Unserved Energy: |  | 687.6
Dhaka (South) Grid Circle :
Bhulta | 132/33 kV Transformer-GT2 | 2019-04-01 20:38 | 2019-04-01 23:15 | 2:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T2 | 2019-04-05 06:56 | 2019-04-05 09:46 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2019-04-18 09:48 | 2019-04-18 13:03 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2019-04-19 07:24 | 2019-04-19 10:07 | 2:43 | S/O | Due to C/M work | 25 | 67.9167 | Power interruption
| 230 kV Bus-1 | 2019-04-19 09:15 | 2019-04-19 19:01 | 9:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T02 | 2019-04-19 09:08 | 2019-04-19 21:11 | 12:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2019-04-20 09:02 | 2019-04-20 17:37 | 8:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(Old) | 132 kV main Bus | 2019-04-22 09:27 | 2019-04-22 11:57 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2019-04-23 09:45 | 2019-04-23 11:00 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer T1 | 2019-04-24 06:47 | 2019-04-24 10:14 | 3:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T5 | 2019-04-25 08:08 | 2019-04-25 12:30 | 4:22 | S/O | Due to maintenance by 33 kV feeder | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T2 | 2019-04-26 06:07 | 2019-04-26 10:14 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 | 2019-04-26 05:50 | 2019-04-26 09:22 | 3:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 61:02 |  | Unserved Energy: |  | 67.9167
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV Transformer-T2 | 2019-04-02 02:00 | 2019-04-03 18:29 | 40:29 | S/O | Due to CB problem | 0 | 0 | No interruption
Halishahar | 33 kV Potenga feeder | 2019-04-04 09:46 | 2019-04-04 15:15 | 5:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kagrachari | 132/33 kV Transformer-T2 | 2019-04-07 12:53 | 2019-04-07 13:39 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T1 | 2019-04-09 13:10 | 2019-04-09 14:10 | 1:00 | S/O | Due to CB test | 35 | 35 | Power interruption
T.K chemical | 132 kV Bus | 2019-04-12 06:58 | 2019-04-12 17:49 | 10:51 | S/O | Due to D/W work | 5 | 54.25 | Power interruption
Modern Steel | 132/33 kV Transformer-T2 | 2019-04-12 11:10 | 2019-04-12 15:17 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | 132 kV Bus-1 | 2019-04-17 09:53 | 2019-04-17 11:45 | 1:52 | S/O | Due to project work | 0 | 0 | No interruption
| 33 kV Bus-2 | 2019-04-22 08:30 | 2019-04-22 09:00 | 0:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-04-23 10:38 | 2019-04-23 12:43 | 2:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T2 | 2019-04-25 07:09 | 2019-04-26 17:05 | 33:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | 132/33 kV Transformer-T2 | 2019-04-25 09:54 | 2019-04-25 12:35 | 2:41 | S/O | Due to SAS testing | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer T1 | 2019-04-26 08:52 | 2019-04-26 12:19 | 3:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-A | 2019-04-27 08:03 | 2019-04-27 14:06 | 6:03 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 177:50 |  | Unserved Energy : |  | 89.25
Cumilla Grid Circle :
Bibiyana | 400 kV line-1 | 2019-04-01 09:15 | 2019-04-01 17:00 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2019-04-01 13:28 | 2019-04-01 15:50 | 2:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-04-01 15:50 | 2019-04-01 17:53 | 2:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132 kV Bus | 2019-04-13 07:38 | 2019-04-13 17:02 | 9:24 | S/O | Due to D/W work | 90 | 846 | Power interruption
Daudkandi | 132 kV main Bus | 2019-04-19 07:21 | 2019-04-19 12:42 | 5:21 | S/O | Due to new uper bus connection | 60 | 321 | Power interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2019-04-21 07:55 | 2019-04-21 10:55 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2019-04-26 07:18 | 2019-04-26 11:24 | 4:06 | S/O | Due to C/M work | 30 | 123 | Power interruption
Bibiyana | 230 kV dia-5 | 2019-04-27 10:25 | 2019-04-27 12:45 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2019-04-30 06:56 | 2019-04-30 09:46 | 2:50 | S/O | Due to C/M work 33 kV bus | 20 | 56.6667 | Power interruption
|  |  | Total : | 39:11 |  | Unserved Energy : |  | 1346.6667
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T2 | 2019-04-01 19:29 | 2019-04-01 21:10 | 1:41 | S/O | Due to 33 kV Bus maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-04-02 06:59 | 2019-04-02 08:52 | 1:53 | S/O | Due to Breaker problem | 0 | 0 | No interruption
Barisal | 132/33 kV Transformers-T1 & T2 | 2019-04-04 10:28 | 2019-04-04 15:06 | 4:38 | S/O | Due to maintenance of BREB feeder | 15 | 69.5 | Power interruption
Magura | 33 kV Bus | 2019-04-09 07:04 | 2019-04-09 07:32 | 1:41 | S/O | Due to 33 kV feeder fault | 18 | 30.3 | Power interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-04-12 08:01 | 2019-04-12 20:14 | 2:41 | S/O | Due to replacement work | 0 | 0 | No interruption
Goalpara | 33 kV Bus | 2019-04-16 06:59 | 2019-04-16 08:32 | 1:41 | S/O | Due to maintenance of 33 kV feeder | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2019-04-17 06:07 | 2019-04-17 07:39 | 1:32 | S/O | Due to C/M work | 20 | 30.6667 | Power interruption
| 33 kV Bus& 132/33 kV Transformer-T2 | 2019-04-19 09:32 | 2019-04-19 11:37 | 2:05 | S/O | Due to C/M work | 10 | 20.8333 | Power interruption
Barisal(N) | 33 kV Bus | 2019-04-22 08:11 | 2019-04-22 16:45 | 8:34 | S/O | Due to D/W work | 8 | 68.5333 | Power interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-04-23 06:40 | 2019-04-23 12:20 | 5:40 | S/O | Due to shariatpur new trasnformer hook up | 0 | 0 | No interruption
| 132 kV Bus-2 | 2019-04-23 12:30 | 2019-04-23 18:06 | 5:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 | 2019-04-25 07:17 | 2019-04-25 08:57 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal(N) | 33 kV Bus | 2019-04-26 07:24 | 2019-04-26 12:53 | 5:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Sariatpur | 132/33 kV Transformer-T2 |  | 2019-04-29 00:54 |  |  | Due to new trasnformer connection | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-04-29 13:20 | 2019-04-29 13:20 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 84:02 |  | Unserved Energy : |  | 219.8333
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T2 | 2019-04-03 16:22 | 2019-04-03 16:53 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara HVDC | 400 kV converter bay block-2 | 2019-04-05 08:18 | 2019-04-05 10:48 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV & 20D09 diameter | 2019-04-05 09:59 | 2019-04-05 16:43 | 6:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 33 kV Bus section-2 | 2019-04-07 06:17 | 2019-04-07 06:34 | 0:17 | S/O | Due to replacement work | 0 | 0 | No interruption
Bheramara | 132/33 kV Transformer-T2 | 2019-04-19 08:45 | 2019-04-19 11:37 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | 33 kV Bus & 132/33 kV Transformer-T2 | 2019-04-19 09:32 | 2019-04-19 12:05 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132 kV Bus | 2019-04-19 05:21 | 2019-04-19 09:07 | 3:46 | S/O | Due to D/W work | 60 | 226 | Power interruption
Chuadanga | 33 kV Bus | 2019-04-22 08:22 | 2019-04-22 12:42 | 4:20 | S/O | Due to D/W work | 40 | 260 | Power interruption
Jessore | 33 kV Bus | 2019-04-26 07:08 | 2019-04-26 10:14 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 26:39 |  | Unserved Energy : |  | 486
Bogura Grid Circle:
Rangpur | 132/33 kV Transformer-T1 | 2019-04-01 10:53 | 2019-04-01 14:20 | 3:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T5 | 2019-04-04 11:30 | 2019-04-04 14:48 | 3:18 | S/O | Due to reconductoring work | 0 | 0 | No interruption
| 132 kV Bus-B | 2019-04-05 06:45 | 2019-04-05 06:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2019-04-05 09:33 | 2019-04-05 13:58 | 4:25 | S/O | Due to replacement work | 0 | 0 | No interruption
Saidpur | 132 kV Bus-A | 2019-04-06 09:10 | 2019-04-07 16:35 | 31:25 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-04-08 09:10 | 2019-04-09 21:40 | 36:30 | S/O | Due to replacement work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T4 | 2019-04-15 10:40 | 2019-04-15 11:47 | 1:07 | S/O | Due to temperature high | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T1 | 2019-04-17 06:38 | 2019-04-17 07:40 | 1:02 | S/O | Due to D/W work | 20 | 14.4667 | Power interruption
Lalmonirhat | 132/33 kV Transformer-T3 | 2019-04-19 09:14 | 2019-04-19 13:05 | 3:51 | S/O | Due to D/W work | 15 | 57.75 | Power interruption
Pabna | 132/33 kV Transformer-T3(new) |  | 2019-04-20 20:54 | 43575.8708 | S/O | Due to replacement work | 0 | 0 | No interruption
Bogura (N) | 132 kV main Bus | 2019-04-22 14:20 | 2019-04-22 17:45 | 3:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2019-04-25 06:17 | 2019-04-25 07:16 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-04-25 06:17 | 2019-04-25 07:16 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 43579.6403 |  | Unserved Energy : |  | 72.2167
Others :
Maniknagar | Maniknagar-Bagabhaban 132 kV line-1 | 2019-04-12 11:16 | 2019-04-12 15:44 | 4:28 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 4:28 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 130760.2285 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line | 2019-04-01 08:25 | 2019-04-01 15:40 | 7:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2019-04-15 08:46 | 2019-04-15 09:20 | 0:34 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2019-04-17 14:35 | 2019-04-17 17:33 | 2:58 | S/O | Due to investigating temperature of Differential Joint | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-1 | 2019-04-17 17:41 | 2019-04-17 18:24 | 0:43 | S/O | Due to above reason | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-2 | 2019-04-24 08:03 | 2019-04-24 16:26 | 8:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-1 | 2019-04-25 07:40 | 2019-04-25 15:10 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2019-04-25 10:28 | 2019-04-25 17:05 | 6:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2019-04-25 15:18 | 2019-04-25 17:20 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2019-04-29 06:27 | 2019-04-29 18:22 | 11:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Valuka 132 kV line | 2019-04-30 10:15 | 2019-04-30 14:45 | 4:30 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 52:27 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Maniknagar | Maniknagar-Siddhirganj 230 kV line-1 | 2019-03-31 19:35 | 2019-04-01 00:58 | 5:23 | S/O | Due to post insulator broken at Siddhirganj S/S | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV line | 2019-04-02 11:27 | 2019-04-02 20:54 | 9:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2019-04-04 09:10 | 2019-04-04 15:24 | 6:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyamnagar | Shyamnagar 230 kV S/S -Shyamnagar 132 kV line-1 | 2019-04-06 10:21 | 2019-04-06 10:27 | 0:06 | S/O | Due to removing of GI wire | 100 | 10 | Power interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-04-13 20:02 | 2019-04-15 21:36 | 49:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar 132 kV line | 2019-04-15 07:40 | 2019-04-15 18:03 | 10:23 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Hasnabad-Sitalakyha 132 kV line | 2019-04-15 18:10 | 2019-04-15 20:15 | 2:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 132 kV line-1 | 2019-04-17 09:32 | 2019-04-17 15:06 | 5:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Lalbagh 132 kV line | 2019-04-18 08:25 | 2019-04-18 16:02 | 7:37 | S/O | Due to DPDC work | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (New) 132 kV line-2 | 2019-04-19 09:53 | 2019-04-19 11:48 | 1:55 | S/O | Due to DPDC work | 40 | 76.6667 | Power interruption
Siddhirganj | Siddhirganj-Haripur 230 kV line-1 | 2019-04-19 09:06 | 2019-04-19 19:07 | 10:01 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Siddhirganj-Maniknagar 230 kV line-2 | 2019-04-19 09:08 | 2019-04-19 21:11 | 12:03 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV line-1 | 2019-04-19 09:48 | 2019-04-19 11:59 | 2:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2019-04-19 09:02 | 2019-04-19 15:17 | 6:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-2 | 2019-04-25 06:25 | 2019-04-25 17:25 | 11:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-04-25 07:29 | 2019-04-25 09:16 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rampura-Gulshan 132 kV line-1 | 2019-04-27 05:21 | 2019-04-27 06:50 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption | 154.5833
|  |  | Total : | 137:41 |  | Unserved Energy: |  | 86.6667
Chattogram Grid Circle :
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2019-04-01 11:15 | 2019-04-13 13:52 | 290:37 | S/O | Due to reconductoring work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2019-04-09 11:46 | 2019-04-09 12:58 | 1:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroiarhat 132 kV line-2 | 2019-04-09 19:38 | 2019-04-10 01:39 | 6:01 | S/O | Due to TCSR problem | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2019-04-10 09:53 | 2019-04-10 14:51 | 4:58 | S/O | Due to air pressure problem | 0 | 0 | No interruption
Feni | Feni-Baroiarhat 132 kV line-2 | 2019-04-10 16:45 | 2019-04-10 17:17 | 0:32 | S/O | Due to changing work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-04-15 09:25 | 2019-05-04 12:37 | 459:12 | S/O | Due to reconductoring work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-2 | 2019-04-17 08:13 | 2019-04-17 14:50 | 6:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-04-17 09:53 | 2019-04-17 18:43 | 8:50 | S/O | Due to project work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-2 | 2019-04-18 07:52 | 2019-04-18 15:11 | 7:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Baroiarhat 132 kV line-1 | 2019-04-18 19:18 | 2019-04-19 08:24 | 13:06 | S/O | Due to hydraulic pressure low | 0 | 0 | No interruption
| Hathazari-Baroiarhat 132 kV line-2 | 2019-04-19 08:24 | 2019-04-19 20:40 | 12:16 | S/O | Due to altered faulty breaker | 0 | 0 | No interruption
Sikakbaha | Sikakbaha-Shahmirpur 132 kV line-1 & 2 | 2019-04-20 07:14 | 2019-04-20 17:45 | 10:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-1 | 2019-04-20 08:09 | 2019-04-20 14:43 | 6:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikakbaha(New) | Sikakbaha(New)-Sikalbaha 225 MW P/S 132 kV line | 2019-04-20 11:22 | 2019-04-20 12:40 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Sikakbaha | Sikakbaha-Shahmirpur 132 kV line-1 | 2019-04-21 07:48 | 2019-04-21 17:28 | 9:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikakbaha-Shahmirpur 132 kV line-2 | 2019-04-21 07:48 | 2019-04-21 18:41 | 10:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-2 | 2019-04-21 08:12 | 2019-04-21 17:43 | 9:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikakbaha | Sikakbaha-Shahmirpur 132 kV line-1 & 2 | 2019-04-22 09:10 | 2019-04-22 18:03 | 8:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-2 | 2019-04-23 12:27 | 2019-04-23 14:30 | 2:03 | S/O | Due to SAS work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-1 | 2019-04-23 10:15 | 2019-04-23 10:45 | 0:30 | S/O | Due to changing work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2019-04-24 10:20 | 2019-04-24 13:02 | 2:42 | S/O | Due to SAS work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari 132 kV line | 2019-04-27 09:33 | 2019-04-27 11:04 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 584:09 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 132 kV line-1 |  | 2019-04-01 12:43 |  | S/O | Due to reconducting work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2019-04-03 10:55 | 2019-04-05 17:59 | 55:04 | S/O | Due to cable maintenance | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV line-1 & 2 | 2019-04-05 07:00 | 2019-04-05 21:07 | 14:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-1 | 2019-04-05 07:20 | 2019-04-05 07:20 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2019-04-03 10:55 | 2019-04-05 17:59 | 55:04 | S/O | Due to reconducting work | 0 | 0 | No interruption
| Sreemongal-Shahjibazar 132 kV line-1 | 2019-04-03 10:02 | 2019-04-03 11:27 | 1:25 | S/O |  | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-2 | 2019-04-08 19:38 | 2019-04-09 01:39 | 6:01 | S/O | Due to TCSR problem | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2019-04-10 09:54 | 2019-04-11 15:20 | 6:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2019-04-13 08:58 | 2019-04-13 17:27 | 6:22 | S/O | Due to cable maintenance | 0 | 0 | No interruption
| Sreemongal-Shahjibazar 132 kV line-2 | 2019-04-15 07:34 | 2019-04-15 16:43 | 7:22 | S/O |  | 0 | 0 | No interruption
| Sreemongal-Shahjibazar 132 kV line-2 | 2019-04-16 07:33 | 2019-04-16 16:17 | 8:22 | S/O |  | 0 | 0 | No interruption
| Sreemongal-Shahjibazar 132 kV line-2 | 2019-04-17 10:10 | 2019-04-17 15:57 | 9:22 | S/O |  | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-2 | 2019-04-25 16:55 | 2019-04-25 19:15 | 2:20 | S/O | Due to protection test | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 & 2 | 2019-04-29 11:43 | 2019-04-29 19:29 | 7:46 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 179:37 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj | Gopalganj-Modhumoti 132 kV line |  | 2019-04-08 12:42 |  |  | Due to reconducting work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2019-04-11 11:02 | 2019-04-11 20:57 | 9:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna © | Khulna ©-Noapara 132 kV line-1 | 2019-04-12 07:02 | 2019-04-12 17:40 | 10:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2019-04-14 21:34 | 2019-05-07 22:39 | 553:05 | S/O | Due to reconducting work | 0 | 0 | No interruption
Madaripur | Madaripur-Faridpur 132 kV line-2 | 2019-04-23 14:03 | 2019-04-23 16:20 | 2:17 | S/O | Due to carry out bus-2 work | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV line-2(New) |  | 2019-04-25 21:12
Noapara | Noapara-Jessore 132 kV line-1 | 2019-04-26 07:27 | 2019-04-26 08:55 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-1 | 2019-04-27 10:15 | 2019-04-27 12:24 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Sariatpur 132 kV line-2 | 2019-04-29 00:44 | 2019-04-29 00:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barisal(O) 132 kV line-2 | 2019-04-29 07:02 | 2019-04-29 08:16 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV line | 2019-04-27 13:54 | 2019-04-29 00:44 | 34:50 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 41:58 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2019-04-05 14:38 | 2019-04-05 16:00 | 1:22 | S/O | Due to damage string | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2019-04-10 15:49 | 2019-04-10 15:49 | 0:00 | S/O | Due to reconducting work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2019-04-11 07:11 | 2019-04-11 17:50 | 10:39 | S/O | Due to C/M work | 0 | 0
| Bheramara-Faridpur 132 kV line-1 | 2019-04-12 10:15 | 2019-04-12 18:33 | 8:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2019-04-13 11:01 | 2019-04-13 12:08 | 1:07 | S/O | Due to testing work | 0 | 0 | No interruption
| Bheramara-Ishurdi 132 kV line-2 | 2019-04-18 07:06 | 2019-04-18 09:06 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2019-04-20 06:10 | 2019-04-20 07:40 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Ruppur (NPP) 132 kV line-1 & 2 |  | 2019-04-30 18:15 |  |  | Due to new connection
|  |  | Total : | 23:34 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Rajshahi | Rajshahi-Natore 132 kV line-2 |  | 2019-04-01 16:28 |  | S/O | Due to reconducting work | 0 | 0 | No interruption
Rangpur | Rangpur-Palashbari 132 kV line-2 | 2019-04-02 11:25 | 2019-04-02 15:20 | 3:55 | S/O | Due to reconducting work | 0 | 0 | No interruption
Bogura (N) | Bogura (N)-Bogura(Old) 132 kV line-2 | 2019-04-04 14:09 | 2019-04-04 16:12 | 2:03 | S/O | Due to maintenance work | 35 | 95.0833 | Power interruption 09:05 to 15:05
Rangpur | Rangpur-Palashbari 132 kV line-2 | 2019-04-05 07:01 | 2019-04-05 20:12 | 13:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2019-04-05 10:10 | 2019-04-05 10:45 | 0:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura (O) | Bogura (O)-Bogura(New) 132 kV line-2 | 2019-04-12 08:18 | 2019-04-12 15:34 | 7:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogura (O)-Bogura(New) 132 kV line-1 | 2019-04-20 13:22 | 2019-04-20 14:55 | 1:33 | S/O | Due to C/M work | 100 | 56.6667 | Power interruption 13:22 to 15:36
| Bogura (O)-Bogura(New) 132 kV line-2 | 2019-04-20 15:02 | 2019-04-20 15:36 | 0:34 | S/O
Bogura (N) | Bogura (N)-Bogura(Old) 132 kV line- 1& 2 | 2019-04-22 14:11 | 2019-04-22 17:56 | 3:45 | S/O | Due to D/W work | 20 | 75 | Power interruption 13:22 to 15:36
| Bogura (N)-Bogura(Old) 132 kV line-1 | 2019-04-23 07:25 | 2019-04-23 17:29 | 10:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura (N)-Bogura(Old) 132 kV line-1 | 2019-04-24 06:34 | 2019-04-24 19:08 | 12:34 | S/O | Due to D/W work | 0 | 0 | No interruption | 448.9667
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2019-04-24 09:01 | 2019-04-24 17:10 | 8:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura (O) | Bogura (O)-Bogura(New) 132 kV line-2 | 2019-04-25 06:56 | 2019-04-25 18:15 | 11:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura (N) | Bogura (N)-Bogura(Old) 132 kV line- 1& 2 With 132 kV bus | 2019-04-26 06:38 | 2019-04-26 11:38 | 5:00 | S/O | Due to D/W work | 30 | 150 | Power interruption 13:22 to 15:36
Rangpur | Rangpur-palashbari 132 kV line-1 | 2019-04-28 08:30 | 2019-04-28 18:09 | 9:39 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 89:37 |  | Unserved Energy: |  | 376.75
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 1109:03 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April' 2019
| Area | Previous Month (March 2019) |  |  |  | Current Month (April 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 22 | 6 | 54 | 82 | 20 | 20 | 30 | 70
2 | Dhaka (South) Grid Circle. | 32 | 10 | 46 | 88 | 28 | 4 | 30 | 62
3 | Chattogram Grid Circle. | 9 | 9 | 17 | 35 | 5 | 8 | 35 | 48
4 | Cumilla Grid Circle. | 22 | 4 | 55 | 81 | 38 | 11 | 23 | 72
5 | Khulna Grid Circle. | 17 | 8 | 41 | 66 | 48 | 8 | 23 | 79
6 | Bheramara HVDC Grid Circle | 6 | 6 | 13 | 25 | 21 | 9 | 16 | 46
7 | Bogura Grid Circle. | 7 | 11 | 25 | 43 | 5 | 16 | 28 | 49
8 | Others | 1 |  | 4 | 5 |  |  | 1 | 1
9 | Total | 116 | 54 | 255 | 425 | 165 | 76 | 186 | 427
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April' 2019
| Area | Previous Month (March 2019) |  |  |  | Current Month (April 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 292.82 | 35.87 | 412.4 | 741.09 | 67.43 | 388.67 | 687.6 | 1143.7
2 | Dhaka (South) Grid Circle. | 157.43 | 188.99 | 571 | 917.42 | 342.5 | 53.06 | 154.58 | 550.14
3 | Chattogram Grid Circle. | 525 | 21.19 | 511.83 | 1058.02 | 18 |  | 89.25 | 107.25
4 | Cumilla Grid Circle. | 738.46 |  | 400.68 | 1139.14 | 556.33 | 367.17 | 1346.67 | 2270.17
5 | Khulna Grid Circle. | 20.46 | 13 | 1589.89 | 1623.35 | 123.38 | 216.68 | 219.83 | 559.89
6 | Bheramara HVDC Grid Circle | 2.58 | 42.37 | 308.83 | 353.78 | 357.5 | 139.25 | 486 | 982.75
7 | Bogura Grid Circle. | 226.15 | 315.23 | 4163.75 | 4705.13 |  | 491.97 | 448 | 939.97
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 1962.9 | 616.65 | 7958.38 | 10537.93 | 1465.14 | 1656.8 | 3431.93 | 6553.87
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 8 | 6 | 14 | 4 | 1 | 9 | 1066.47
2 | Dhaka (South) | 5031.6 | 3 | 1 | 4 |  | 3 | 1 | 169.99
3 | Chattogram | 2042 | 1 | 2 | 3 | 1 | 1 | 1 | 107.25
4 | Khulna | 2434 | 16 | 5 | 21 | 7 | 4 | 10 | 559.9
5 | Bheramara (HVDC) | 2423.3 | 8 | 2 | 10 | 3 | 1 | 6 | 699.78
6 | Bogura | 3145.6 | 5 | 2 | 7 |  | 2 | 5 | 459.05
7 | Cumilla | 2981 | 6 | 4 | 10 | - | 3 | 7 | 1587.84
| Total | 23365.5 | [6 empty] | 4650.28
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.92%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.97%
4 | Khulna | 99.8%
5 | Bheramara (HVDC) | 99.81% | [6 empty] | Executive Engineer
6 | Bogura | 99.94% | [6 empty] | Information Management Division
7 | Cumilla | 99.89% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 4 | - | 4 | 4 | - |  | 77.23
2 | Dhaka (South) | 990.29 |  | 5 | 2 | 7 | 5 | 1 | 1 | 380.17
3 | Chattogram | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 598.7 |  | 2 |  | 2 | 1 | - | 1 | 282.97
6 | Bogura | 1803.3 | 38 | 2 | 4 | 6 | 1 | - | 4 | 481.88
7 | Cumilla | 1648.16 | 17 | 8 |  | 3 | 3 | 1 | 4 | 682.33
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1904.58
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.45%
3 | Chattogram | 99.98%
4 | Khulna | 99.7%
5 | Bheramara (HVDC) | 99.82% | [7 empty] | Executive Engineer
6 | Bogura | 99.84% | [7 empty] | Information Management Division
7 | Cumilla | 99.82% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-04-18 | 15 |  | 2 | 03hr27 min | 4 | 04hr03 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:April' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Valuka | 1 | 0:42 | 40 | 28 | Due to red-hot maintenance of 132/33 kV Transformer T1
Kabirpur | 1 | 0:12 | 125 | 25 | Due to tripping of 132/33 kV Transformer sT1 T2 & T3
Kadda | 1 | 1:10 | 85 | 99.1667 | Due to red-hot maintenance of 33 kV Bus
Joydevpur | 1 | 0:18 | 84 | 25.2 | Due to tripping of 132/33 kV TransformersT3 & T4
Jamalpur | 1 | 2:18 | 22 | 92 | Due to tripping of 132/33 kV Transformer T2
Valuka | 1 | 1:17 | 55 | 64.1667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Mymensingh | 1 | 2:50 | 16 | 45.3333 | Due to tripping of 132/33 kV Transformer T2
Jamalpur | 1 | 0:08 | 60 | 8 | Due to tripping of Jamalpur-United Mymensingh 132 kV line-1 & 2
| 2 | 2:15 | 147 | 9.8 | Due to tripping of Jamalpur-United Mymensingh 132 kV line-1 & 2
Mymensingh |  | 0:07 | 170 | 19.8333 | Due to tripping of Mymensingh -Jamalpur 132 kV line-2
| 1 | 0:11 | 216 | 39.6 | Due to tripping of Mymensingh -Kishoreganj 132 kV line-1
Netrakona | 1 | 0:33 | 12 | 34.6 | Due to S/D of 132/33 kV Transformer T2
Valuka |  | 0:30 | 45 | 22.5 | Due to S/D of 132 kV bus
Kishoreganj |  | 2:58 | 30 | 89 | Due to S/D of 132/33 kV Transformer T2
Mymensingh |  | 0:53 | 40 | 132 | Due to S/D of 132/33 kV Transformer T2
Jamalpur |  | 3:48 | 60 | 228 | Due to S/D of 132/33 kV Transformers T1 & T2
Valuka | 1 | 4:02 | 45 | 181.5 | Due to S/D of 132/33 kV Transformer T1
Maniknagar | 1 | 0:37 | 32 | 19.7333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Narsingdi |  | 0:50 | 40 | 33.3333 | Due to cable fault of 132/33 kV Transformer T2
Hasnabad |  | 0:35 | 84 | 49 | Due to tripping of 132/33 kV Transformers T1 & T5
Moghbazar |  | 0:37 | 102 | 62.9 | Due to tripping of Moghbazar-Rampura 132 kV line-1 & 2
Lalbagh |  | 0:12 | 87 | 17.4 | Dueto tripping of Lalbagh-Hasnbad 132 kV line
| 1 | 0:19 | 65 | 20.5833 | Due to tripping of Lalbagh-Hasnabad 132 kV line
Shyampur(O) | 1 | 0:49 | 163 | 133.1167 | Due to tripping of Shyampur(O)-Shyampur(N) 132 kV line
Shyampur(N) | 1 | 0:21 | 170 | 59.5 | Due to tripping of Shyampur(N)-Shyampur(O) 132 kV line-1 & 2
Siddhirganj |  | 2:43 | 25 | 67.9167 | Due to S/D of 132/33 kV Transformer T1
Shyampur |  | 0:06 | 100 | 10 | Due to S/D of Shyampur 230 kV -Shyampur-132 kV line-1
Shyampur(O) |  | 1:55 | 40 | 76.6667 | Due to S/D of Shyampur(O)-Shyampur (N) 132 kV line-2
Hathazari | 4 | 0:18 | 60 | 18 | Due to tripping of 132/33 kV Transformers T1 & T2
Halishahar |  | 1:00 | 35 | 35 | Due to S/D of 132/33 kV Transformer T1
T.K chemical |  | 10:51 | 5 | 54.25 | Due to S/D of 132 kV Bus
Due to S/D of 132/33 kV Transformer T2
Chowmuhani |  | 2:00 | 20 | 40 | Due to red-hot maintenance of 132/33 kV Transformer T3
Chandpur |  | 1:06 | 10 | 10.6667 | Due to red-hot maintenance of 33 kV Bus
Daudkandi |  | 0:53 | 30 | 26.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
B.Baria |  | 0:37 | 60 | 37
|  | 1:41 | 20 | 33.6667
Cumilla(N) | 1 | 0:56 | 100 | 93.3333 | Due to PT bursting of 132/33 kV Transformer T3
Cumilla(S) | 1 | 1:05 | 128 | 138.6667 | Due to tripping of Cumilla(S)-Surjamoninagar 132 kV line-2
Sylhet | 1 | 0:24 | 11 | 4.4 | Due to tripping of Sylhet -Fenchuganj 132 kV line
Cumilla(S) |  | 1:42 | 80 | 72 | Due to tripping of Cumilla(S)-Surjamoninagar 132 kV line-1
Feni |  | 1:04 | 103 | 109.8667 | Due to tripping of Feni-Chowmuhani 132 kV line-1 & 2
|  | 0:12 | 120 | 32 | Due to tripping of Ramganj-Chowmuhani 132 kV line-1
|  | 1:48 | 70 | 126 | Due to emergency maintenance of Feni-Chowmuhani 132 kV line
|  | 0:07 | 260 | 30.3333 | Due to tripping of Feni- Chowmuhnai 132 kV line-1 & 2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:April' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Fenchuganj |  | 0:50 | 317 | 169.0667 | Due to tripping of Fenchuganj-Sreemongal 132 kV line-1
Chowmuhani |  | 9:24 | 90 | 846 | Due to S/D of 132 kV bus
Daudkandi |  | 5:21 | 60 | 321
Shahjibazar |  | 4:06 | 30 | 123 | Due to S/D of 132/33 kV Transformer T2
Ramganj |  | 2:50 | 20 | 56.6667 | Due to S/D of 132/33 kV Transformer T2
Bagerhat | 1 | 0:06 | 17 | 1.7 | Due to tripping of 132/33 kV Transformer T2
Bhandaria | 2 | 0:22 | 19 | 11.0833 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:35 | 19 | 6.9667
|  | 0:50 | 10 | 8.3333
Gallamari |  | 0:43 | 40 | 28.6667 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Noapara |  | 2:46 | 15 | 41.5 | Due to tripping of 132/33 kV Transformers T1 & T2
Satkhira |  | 1:46 | 60 | 26.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
Barisal |  | 0:04 | 80 | 5.3333 | Due to tripping of 132/33 kV Transformers T1 & T2
Patuakhali |  | 0:22 | 62 | 22.7333 | Due to tripping of all Transformers
Bhandaria |  | 0:03 | 92 | 4.6
Faridpur |  | 1:11 | 40 | 47.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Bagerhat |  | 0:08 | 6 | 0.8 | Due to tripping of 132/33 kV Transformer T2
Patuakhali |  | 1:00 | 24 | 24 | Due to tripping of 132/33 kV Transformer T1
Bagerhat |  | 2:03 | 35 | 71.75 | Due to red-hot maintenance of 33 kV Bus
|  | 0:10 | 55 | 9.1667 | Due to tripping of 132/33 kV Transformer T1
Barisal |  | 4:38 | 15 | 69.5 | Due to S/D 132/33 kV Transformers-T1 & T2
Magura |  | 1:41 | 18 | 30.3 | Due to S/D of 33 kV Bus
Barisal |  | 1:32 | 20 | 30.6667 | Due to S/D 132/33 kV Transformer-T2
|  | 2:05 | 10 | 20.8333
Noapara |  | 1:14 | 24 | 29.6 | Due to red-hot maintenance of Transformer T4
Barisal(N) |  | 8:34 | 8 | 68.5333 | Due to S/D of 33 kV Bus
Kustia | 1 | 0:48 | 35 | 28 | Due to red-hot maintenance of 132/33 kV Transformer T21
Bottail | 1 | 0:25 | 60 | 25 | Due to tripping of 132/33 kV Transformers T1 & T2
Jhenidah | 1 | 0:35 | 69 | 40.25 | Due to bursting of PT
Bottail | 1 | 0:10 | 64 | 10.6667 | Due Meherpur Feeder fault
Pabna | 1 | 0:04 | 63 | 4.2 | Due to tripping of 132/33 kV Transformer T1
Ishurdi | 1 | 1:13 | 20 | 24.3333 | Due to red-hot maintenance of 33 kV Bus
Pabna |  | 1:08 | 40 | 45.3333 | Due to tripping of 132/33 kV Transformer T3
Bottail |  | 1:20 | 27 | 36 | Due to red-hot maintenance of Transformer T3
Bheramara | 1 | 0:24 | 47 | 18.8 | Due to tripping of Bheramara-Faridpur 132 kV line-1 & 2
| 1 | 5:17 | 50 | 264.1667
Pabna |  | 3:46 | 60 | 226 | Due to S/D of 132 kV Bus
Chuadanga |  | 4:20 | 40 | 260 | Due to S/D of 33 kV Bus
Rajshahi |  | 1:09 | 15 | 17.25 | Due to red-hot maintenance of Transformer T2
Thakurgaon |  | 0:35 | 15 | 8.75 | Due to tripping of 132/33 kV Transformer T1
Rajshahi |  | 4:07 | 10 | 41.1667 | Due to red-hot maintenance of Transformer T2
Bogura(O) |  | 1:21 | 100 | 301.6667 | Due to red-hot maintenance of Transformers T3 &T4
Natore |  | 0:54 | 20 | 18 | Due to red-hot maintenance of Transformer T4
Rajshahi |  | 0:28 | 166 | 77.4667 | Due to bursting of Rajshahi-Natore 132 kV line-1
Thakurgaon |  | 1:23 | 20 | 27.6667 | Due to tripping of Thakurgaon -Panchugar 132 kV line
|  | 1:02 | 20 | 14.4667 | Due to S/D of 132/33 kV Transformer T1
Lalmonirhat |  | 3:51 | 15 | 57.75 | Due to S/D of 132/33 kV Transformer T3
Bogura(N) |  | 2:03 | 35 | 95.0833 | Due to S/D of Bogura(O)-Bogura(N) 132 kV line-2
Bogura(O) |  | 0:34 | 100 | 56.57 | Due to S/D of Bogura(O)-Bogura(N) 132 kV line-2
Bogura(N) |  | 3:45 | 20 | 75 | Due to S/D Bogura(N)-Bogura(O) 132 kV line-1 & 2
|  | 5:00 | 30 | 150 | Due toS/D of Bogura(N)-Bogura(O) 132 kV line-1 &2
| Total unserved energy : |  |  | 6554.7533 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 28 | 2019-04-03 | 19:00
2 | Munsiganj | 126 | 28 | 2019-04-03 | 21:00
3 | Sonargaon | 82 | 27 | 2019-04-03 | 22:00
4 | Shyampur | 200 | 17 | 2019-04-03 | 13:00
5 | Bhulta | 207 | 25 | 2019-04-03 | 21:00
6 | Madanganj | 70 | 30 | 2019-04-03 | 21:00
7 | Shitalakhya | 129 | 25 | 2019-04-03 | 11:00
8 | Rahim steel | 33 | 24 | 2019-04-03 | 10:00
9 | Matuail | 102 | 25 | 2019-04-03 | 10:00
10 | Ghorasal | 97 | 29 | 2019-04-03 | 22:00
11 | Narsingdi | 129 | 25 | 2019-04-03 | 20:00
12 | Haripur (SBU) | 108 | 28 | 2019-04-03 | 19:30
13 | Ullon | 104 | 28 | 2019-04-03 | 19:30
14 | Hasnabad | 233 | 25 | 2019-04-03 | 21:00
15 | Magbazar | 154 | 29 | 2019-04-03 | 16:00
16 | Maniknagar | 124 | 30 | 2019-04-03 | 11:00
17 | Bangabhaban | 38 | 30 | 2019-04-03 | 15:00
18 | Narinda | 104 | 27 | 2019-04-03 | 17:00
19 | Dhanmondi | 179 | 25 | 2019-04-03 | 13:00
20 | Lalbag | 90 | 20 | 2019-04-03 | 19:00
21 | Madartek | 63 | 28 | 2019-04-03 | 23:00
22 | Mirpur | 123 | 29 | 2019-04-03 | 19:00
23 | Kalyanpur | 129 | 27 | 2019-04-03 | 19:00
24 | Gulshan | 182 | 29 | 2019-04-03 | 16:00
25 | Uttara | 75 | 25 | 2019-04-03 | 19:30
26 | Uttara(new) | 19 | 1 | 2019-04-03 | 13:00
27 | Kamrangirchar | 82 | 28 | 2019-04-03 | 19:00
28 | Savar | 157 | 25 | 2019-04-03 | 15:00
29 | Bhasantec | 185 | 29 | 2019-04-03 | 19:00
30 | Agargaon | 68 | 30 | 2019-04-03 | 15:00
31 | Satmosjid | 117 | 28 | 2019-04-03 | 18:00
32 | Tongi | 151 | 30 | 2019-04-03 | 15:00
33 | Kabirpur | 244 | 29 | 2019-04-03 | 16:00
34 | Basundhara | 144 | 24 | 2019-04-03 | 18:30
35 | Manikganj | 108 | 28 | 2019-04-03 | 1:00
36 | Joydevpur | 232 | 24 | 2019-04-03 | 21:00
37 | New Tongi | 117 | 28 | 2019-04-03 | 16:00
38 | Kodda | 265 | 28 | 2019-04-03 | 19:30
39 | Dhamrai | 58 | 25 | 2019-04-03 | 21:00
40 | Valuka | 83 | 30 | 2019-04-03 | 19:00
41 | Tangail | 202 | 28 | 2019-04-03 | 19:00
42 | Mymensing | 246 | 25 | 2019-04-03 | 19:30
43 | Kishorganj | 120 | 25 | 2019-04-03 | 21:00
44 | Netrokona | 101 | 24 | 2019-04-03 | 21:00
45 | Jamalpur | 134 | 29 | 2019-04-03 | 23:00
46 | Sherpur | 100 | 25 | 2019-04-03 | 19:00
47 | Srimongal | 45 | 16 | 2019-04-03 | 20:00
48 | Shahjibazar | 121 | 27 | 2019-04-03 | 22:00
49 | Fenchuganj | 45 | 26 | 2019-04-03 | 22:00
50 | Kulawara | 44 | 25 | 2019-04-03 | 21:00
51 | Sylhet | 142 | 25 | 2019-04-03 | 19:30
52 | Chatak | 33 | 26 | 2019-04-03 | 20:00
53 | Sunamganj | 35 | 25 | 2019-04-03 | 21:00
54 | Bianibazar | 45 | 25 | 2019-04-03 | 19:00
55 | Cumilla (S) | 188 | 28 | 2019-04-03 | 22:00
56 | Cumilla(N) | 121 | 19 | 2019-04-03 | 18:30
57 | Chandpur | 112 | 16 | 2019-04-03 | 19:30
58 | Feni | 142 | 30 | 2019-04-03 | 20:00
59 | Chowmuhani | 184 | 15 | 2019-04-03 | 20:00
60 | Ashuganj | 61 | 24 | 2019-04-03 | 23:00
61 | Daudkandi | 130 | 20 | 2019-04-03 | 19:00
62 | B.Baria | 134 | 30 | 2019-04-03 | 20:00
63 | Ramganj | 80 | 30 | 2019-04-03 | 20:00
64 | Madanhat | 77.5 | 16 | 2019-04-03 | 19:00
65 | Hathazari | 102 | 27 | 2019-04-03 | 17:00
66 | Khulshi | 226 | 23 | 2019-04-03 | 15:00
67 | Halishahar | 164 | 25 | 2019-04-03 | 16:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 192 | 28 | 2019-04-03 | 12:00
69 | Sikalbaha | 42 | 2 | 2019-04-03 | 18:30
70 | Dohazari | 106 | 16 | 2019-04-03 | 20:00
71 | Cox'sbazar | 93 | 26 | 2019-04-03 | 19:30
72 | Chandraghona | 34 | 29 | 2019-04-03 | 22:00
73 | Kaptai | 5 | 2 | 2019-04-03 | 18:30
74 | A. Khaer Stl. | 12 | 22 | 2019-04-03 | 10:00
75 | Bakulia | 116 | 29 | 2019-04-03 | 19:00
76 | Julda | 24 | 25 | 2019-04-03 | 15:00
77 | TK chemical | 6 | 5 | 2019-04-03 | 12:00
78 | Modern Steel | 16 | 1 | 2019-04-03 | 01:00
79 | Shahmirpur | 39 | 24 | 2019-04-03 | 01:00
80 | Khagrachhari | 20 | 20 | 2019-04-03 | 19:00
81 | Matarbari | 29 | 25 | 2019-04-03 | 20:00
82 | Baroiar Hat | 28 | 7 | 2019-04-03 | 8:00
83 | Rangamati | 23 | 24 | 2019-04-03 | 18:00
84 | Abul Khair 230 | 154 | 8 | 2019-04-03 | 8:00
85 | BSRM | 160 | 25 | 2019-04-03 | 5:00
86 | Goalpara | 35 | 16 | 2019-04-03 | 18:30
87 | Central s/s | 105 | 15 | 2019-04-03 | 20:00
88 | Noapara | 97 | 16 | 2019-04-03 | 19:00
89 | Jashore | 160 | 16 | 2019-04-03 | 20:00
90 | Jhenida | 106 | 24 | 2019-04-03 | 20:00
91 | Bottail | 128 | 16 | 2019-04-03 | 18:30
92 | G.K Project | 57 | 29 | 2019-04-03 | 21:00
93 | Faridpur | 170 | 30 | 2019-04-03 | 22:00
94 | Madaripur | 139 | 29 | 2019-04-03 | 21:00
95 | Gopalganj | 92 | 24 | 2019-04-03 | 19:30
96 | Bagerhat | 89 | 30 | 2019-04-03 | 20:00
97 | Mongla | 44 | 5 | 2019-04-03 | 10:00
98 | Satkhira | 104 | 16 | 2019-04-03 | 21:00
99 | Gallamari | 55 | 16 | 2019-04-03 | 13:00
100 | Magura | 59 | 21 | 2019-04-03 | 19:00
101 | Chuadanga | 83 | 16 | 2019-04-03 | 19:30
102 | Barishal | 126 | 29 | 2019-04-03 | 21:00
103 | Patuakhali | 97 | 28 | 2019-04-03 | 22:00
104 | Bhandaria | 64 | 26 | 2019-04-03 | 21:00
105 | Ishurdi | 72 | 29 | 2019-04-03 | 21:00
106 | Ruppur Paromanobik | 2 | 23 | 2019-04-03 | 15:00
107 | Natore | 133 | 27 | 2019-04-03 | 21:00
108 | Bogura | 243 | 24 | 2019-04-03 | 19:30
109 | Noagaon | 133 | 29 | 2019-04-03 | 21:00
110 | Rajshahi | 172 | 29 | 2019-04-03 | 21:00
111 | C.Nawabganj | 77 | 24 | 2019-04-03 | 20:00
112 | Amnura | 41 | 4 | 2019-04-03 | 19:00
113 | Pabna | 113 | 15 | 2019-04-03 | 20:00
114 | Shahjadpur | 112 | 30 | 2019-04-03 | 19:30
115 | Serajganj | 115 | 16 | 2019-04-03 | 20:00
116 | Niyamatpur | 112 | 21 | 2019-04-03 | 19:00
117 | Joypurhat | 54 | 20 | 2019-04-03 | 21:00
118 | Mohastangor | 15 | 23 | 2019-04-03 | 21:00
119 | Rangpur | 135 | 27 | 2019-04-03 | 19:00
120 | Lalmonirhat | 94 | 22 | 2019-04-03 | 23:00
121 | Saidpur | 107 | 24 | 2019-04-03 | 19:00
122 | Purbasadipur | 100 | 30 | 2019-04-03 | 20:00
123 | Thakurgaon | 74 | 20 | 2019-04-03 | 20:00
124 | Palashbari | 114 | 24 | 2019-04-03 | 21:00
125 | Barapukuria | 57 | 25 | 2019-04-03 | 20:00
126 | Panchagar | 40 | 3 | 2019-04-03 | 19:00
127 | Joldhaka | 20 | 25 | 2019-04-03 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4550 | 29.04.19 | 19:00
Chattogram | 1280 | 16.04.19 | 23:00
Khulna | 1386 | 25.04.19 | 21:00
Rajshahi | 1269 | 30.04.19 | 22:00
Cumilla | 1090 | 25.04.19 | 22:00
Mymensingh | 918 | 25.04.19 | 23:00
Sylhet | 475 | 25.04.19 | 20:00
Barisal | 300 | 27.04.19 | 20:00
Rangpur | 693 | 27.04.19 | 19:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 402 | 1 | 2019-04-03 | 05:00 | 367 | 2 | 2019-04-03 | 11:00
2 | Bheramara | 400 | 405 | 1 | 2019-04-03 | 4:00 | 382 | 7 | 2019-04-03 | 19:30
3 | Ashuganj(N) | 400 | 408 | 9 | 2019-04-03 | 4:00 | 379 | 1 | 2019-04-03 | 17:00
4 | Kaliakoir | 400 | 396 | 1 | 2019-04-03 | 05:00 | 356 | 2 | 2019-04-03 | 12:00
5 | Bhulta | 400 | 409 | 9 | 2019-04-03 | 18:30 | 339 | 8 | 2019-04-03 | 6:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 238 | 6 | 2019-04-03 | 23:00 | 224 | 1 | 2019-04-03 | 11:00
2 | Ishurdi | 230 | 245 | 1 | 2019-04-03 | 04:00 | 221 | 8 | 2019-04-03 | 19:00
3 | Ashuganj | 230 | 245 | 19 | 2019-04-03 | 1:00 | 226 | 1 | 2019-04-03 | 12:00
4 | Serajganj | 230 | 240 | 3 | 2019-04-03 | 1:00 | 220 | 14 | 2019-04-03 | 21:00
5 | Baghabari | 230 | 239 | 1 | 2019-04-03 | 4:00 | 219 | 23 | 2019-04-03 | 19:30
6 | Barapukuria | 230 | 237 | 1 | 2019-04-03 | 2:00 | 213 | 28 | 2019-04-03 | 15:00
7 | Bogra | 230 | 239 | 1 | 2019-04-03 | 3:00 | 205 | 23 | 2019-04-03 | 19:00
8 | Khulna South | 230 | 248 | 6 | 2019-04-03 | 21:00 | 209 | 14 | 2019-04-03 | 21:00
9 | Rampura | 230 | 230 | 6 | 2019-04-03 | 22:00 | 216 | 2 | 2019-04-03 | 12:00
10 | Haripur | 230 | 230 | 6 | 2019-04-03 | 23:00 | 215 | 1 | 2019-04-03 | 11:00
11 | Hasnabad | 230 | 234 | 1 | 2019-04-03 | 4:00 | 215 | 1 | 2019-04-03 | 11:00
12 | Aminbazar | 230 | 234 | 9 | 2019-04-03 | 19:00 | 214 | 2 | 2019-04-03 | 12:00
13 | Tongi | 230 | 234 | 6 | 2019-04-03 | 22:00 | 208 | 1 | 2019-04-03 | 11:00
14 | Comilla (N) | 230 | 242 | 6 | 2019-04-03 | 23:00 | 221 | 28 | 2019-04-03 | 11:00
15 | Hathazari | 230 | 224 | 25 | 2019-04-03 | 7:00 | 205 | 9 | 2019-04-03 | 09:00
16 | Megnaghat | 230 | 236 | 9 | 2019-04-03 | 18:30 | 218 | 2 | 2019-04-03 | 12:00
17 | Fenchuganj | 230 | 241 | 1 | 2019-04-03 | 2:00 | 226 | 2 | 2019-04-03 | 11:00
18 | Siddhirganj | 230 | 236 | 9 | 2019-04-03 | 18:30 | 215 | 2 | 2019-04-03 | 11:00
19 | Maniknagar | 230 | 236 | 9 | 2019-04-03 | 19:00 | 213 | 2 | 2019-04-03 | 15:00
20 | Old Airport | 230 | 235 | 9 | 2019-04-03 | 18:30 | 212 | 2 | 2019-04-03 | 11:00
21 | Barisal | 230 | 248 | 1 | 2019-04-03 | 05:00 | 223 | 15 | 2019-04-03 | 12:00
22 | AKSML | 230 | 226 | 1 | 2019-04-03 | 07:00 | 205 | 9 | 2019-04-03 | 15:00
23 | BSRM | 230 | 229 | 1 | 2019-04-03 | 07:00 | 208 | 9 | 2019-04-03 | 10:00
24 | Bibiyana | 230 | 240 | 9 | 2019-04-03 | 04:00 | 215 | 1 | 2019-04-03 | 14:00
25 | Bhulta | 230 | 233 | 6 | 2019-04-03 | 24:00 | 215 | 1 | 2019-04-03 | 11:00
26 | Ashuganj (S) | 230 | 242 | 9 | 2019-04-03 | 18:30 | 227 | 1 | 2019-04-03 | 12:00
27 | Kaliakoir | 230 | 238 | 9 | 2019-04-03 | 18:30 | 215 | 1 | 2019-04-03 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 9 | 2019-04-03 | 18:30 | 123 | 23 | 2019-04-03 | 15:00
2 | Munsiganj | 132 | 139 | 9 | 2019-04-03 | 18:30 | 122 | 17 | 2019-04-03 | 15:00
3 | Megnaghat | 132 | 137 | 9 | 2019-04-03 | 18:30 | 123 | 17 | 2019-04-03 | 14:00
4 | Shyampur | 132 | 138 | 9 | 2019-04-03 | 18:30 | 122 | 16 | 2019-04-03 | 12:00
5 | Bhulta | 132 | 135 | 9 | 2019-04-03 | 18:30 | 117 | 24 | 2019-04-03 | 10:00
6 | Madanganj | 132 | 137 | 9 | 2019-04-03 | 18:30 | 120 | 17 | 2019-04-03 | 12:00
7 | Shitalakhya | 132 | 140 | 26 | 2019-04-03 | 01:00 | 122 | 2 | 2019-04-03 | 10:00
8 | Rahim Steal | 132 | 137 | 9 | 2019-04-03 | 18:30 | 123 | 24 | 2019-04-03 | 10:00
9 | Matuail | 132 | 136 | 9 | 2019-04-03 | 18:30 | 121 | 24 | 2019-04-03 | 10:00
10 | Ghorasal | 132 | 145 | 2 | 2019-04-03 | 20:00 | 130 | 19 | 2019-04-03 | 13:00
11 | Narsinghdi | 132 | 142 | 2 | 2019-04-03 | 19:00 | 114 | 16 | 2019-04-03 | 21:00
12 | Haripur (SBU) | 132 | 138 | 9 | 2019-04-03 | 18:30 | 122 | 13 | 2019-04-03 | 11:00
13 | Ullon | 132 | 141 | 9 | 2019-04-03 | 18:30 | 122 | 17 | 2019-04-03 | 12:00
14 | Hasnabad | 132 | 138 | 9 | 2019-04-03 | 18:30 | 124 | 1 | 2019-04-03 | 11:00
15 | Magbazar | 132 | 141 | 9 | 2019-04-03 | 18:30 | 123 | 1 | 2019-04-03 | 11:00
16 | Maniknagar | 132 | 140 | 9 | 2019-04-03 | 18:30 | 120 | 24 | 2019-04-03 | 12:00
17 | Bangabhaban | 132 | 136 | 1 | 2019-04-03 | 5:00 | 119 | 1 | 2019-04-03 | 12:00
18 | Narinda | 132 | 138 | 8 | 2019-04-03 | 6:00 | 120 | 27 | 2019-04-03 | 12:00
19 | Dhanmondi | 132 | 141 | 9 | 2019-04-03 | 18:30 | 122 | 17 | 2019-04-03 | 12:00
20 | Lalbag | 132 | 136 | 1 | 2019-04-03 | 5:00 | 119 | 1 | 2019-04-03 | 12:00
21 | Madartek | 132 | 138 | 8 | 2019-04-03 | 06:00 | 120 | 27 | 2019-04-03 | 12:00
22 | Mirpur | 132 | 139 | 9 | 2019-04-03 | 18:30 | 122 | 2 | 2019-04-03 | 11:00
23 | Kalyanpur | 132 | 140 | 9 | 2019-04-03 | 18:30 | 125 | 1 | 2019-04-03 | 12:00
24 | Gulshan | 132 | 141 | 9 | 2019-04-03 | 18:30 | 122 | 1 | 2019-04-03 | 11:00
25 | Uttara | 132 | 138 | 9 | 2019-04-03 | 18:30 | 120 | 1 | 2019-04-03 | 12:00
26 | Uttara(New) | 132 | 137 | 1 | 2019-04-03 | 6:00 | 121 | 2 | 2019-04-03 | 12:00
27 | Kamrangirchar | 132 | 139 | 9 | 2019-04-03 | 18:30 | 119 | 18 | 2019-04-03 | 11:00
28 | Savar | 132 | 138 | 9 | 2019-04-03 | 18:30 | 120 | 17 | 2019-04-03 | 17:00
29 | Bhasantec | 132 | 143 | 9 | 2019-04-03 | 18:30 | 123 | 1 | 2019-04-03 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2019
|  | Rated | Maxm | Date |  | 1 | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 142 | 9 | 2019-04-03 | 18:30 | 124 | 1 | 2019-04-03 | 12:00
31 | Satmosjid | 132 | 143 | 9 | 2019-04-03 | 18:30 | 125 | 1 | 2019-04-03 | 12:00
32 | Tongi | 132 | 140 | 6 | 2019-04-03 | 22:00 | 123 | 1 | 2019-04-03 | 11:00
33 | Kabirpur | 132 | 142 | 6 | 2019-04-03 | 22:00 | 120 | 30 | 2019-04-03 | 11:00
34 | Basundhara | 132 | 138 | 9 | 2019-04-03 | 18:30 | 119 | 28 | 2019-04-03 | 10:00
35 | Manikganj | 132 | 142 | 6 | 2019-04-03 | 22:00 | 125 | 1 | 2019-04-03 | 13:00
36 | Joydevpur | 132 | 143 | 1 | 2019-04-03 | 07:00 | 128 | 1 | 2019-04-03 | 11:00
37 | New Tongi | 132 | 140 | 21 | 2019-04-03 | 22:00 | 121 | 4 | 2019-04-03 | 12:00
38 | Kodda | 132 | 145 | 9 | 2019-04-03 | 18:30 | 121 | 18 | 2019-04-03 | 08:00
39 | Dhamrai | 132 | 143 | 6 | 2019-04-03 | 22:00 | 124 | 1 | 2019-04-03 | 12:00
40 | Valuka | 133 | 140 | 2 | 2019-04-03 | 18:00 | 118 | 16 | 2019-04-03 | 21:00
41 | Tangail | 132 | 145 | 2 | 2019-04-03 | 18:00 | 122 | 25 | 2019-04-03 | 21:00
42 | Mymensing | 132 | 141 | 9 | 2019-04-03 | 18:00 | 112 | 17 | 2019-04-03 | 20:00
43 | Kishorganj | 132 | 140 | 1 | 2019-04-03 | 07:00 | 118 | 18 | 2019-04-03 | 19:00
44 | Netrokona | 132 | 145 | 1 | 2019-04-03 | 03:00 | 111 | 18 | 2019-04-03 | 19:00
45 | Jamalpur | 132 | 140 | 9 | 2019-04-03 | 18:00 | 111 | 17 | 2019-04-03 | 20:00
46 | Sherpur | 132 | 140 | 9 | 2019-04-03 | 18:00 | 108 | 17 | 2019-04-03 | 20:00
47 | Srimongal | 132 | 141 | 7 | 2019-04-03 | 02:00 | 130 | 16 | 2019-04-03 | 18:30
48 | Shahjibazar | 132 | 141 | 7 | 2019-04-03 | 02:00 | 127 | 18 | 2019-04-03 | 18:30
49 | Fenchuganj | 132 | 138 | 1 | 2019-04-03 | 02:00 | 130 | 25 | 2019-04-03 | 18:30
50 | Khulawara | 132 | 138 | 29 | 2019-04-03 | 03:00 | 130 | 15 | 2019-04-03 | 1:00
51 | Sylhet | 132 | 138 | 29 | 2019-04-03 | 6:00 | 126 | 25 | 2019-04-03 | 18:30
52 | Chattak | 132 | 139 | 29 | 2019-04-03 | 03:00 | 125 | 25 | 2019-04-03 | 18:00
53 | Sunamganj | 132 | 139 | 29 | 2019-04-03 | 06:00 | 123 | 25 | 2019-04-03 | 18:30
54 | Biani Bazar | 132 | 139 | 29 | 2019-04-03 | 03:00 | 125 | 25 | 2019-04-03 | 18:30
55 | Comilla(South) | 132 | 136 | 1 | 2019-04-03 | 5:00 | 118 | 27 | 2019-04-03 | 21:00
56 | Comilla (North) | 132 | 144 | 9 | 2019-04-03 | 19:00 | 129 | 2 | 2019-04-03 | 12:00
57 | Chandpur | 132 | 142 | 1 | 2019-04-03 | 07:00 | 112 | 27 | 2019-04-03 | 22:00
58 | Feni | 132 | 140 | 1 | 2019-04-03 | 7:00 | 116 | 27 | 2019-04-03 | 22:00
59 | Chowmuhani | 132 | 136 | 1 | 2019-04-03 | 07:00 | 108 | 27 | 2019-04-03 | 22:00
60 | Ashuganj | 132 | 144 | 1 | 2019-04-03 | 7:00 | 120 | 25 | 2019-04-03 | 21:00
61 | Daudkandi | 132 | 139 | 9 | 2019-04-03 | 20:00 | 122 | 17 | 2019-04-03 | 15:00
62 | Brahminbaria | 132 | 142 | 9 | 2019-04-03 | 18:30 | 120 | 16 | 2019-04-03 | 19:00
63 | Ramganj | 132 | 139 | 6 | 2019-04-03 | 23:00 | 107 | 27 | 2019-04-03 | 19:00
64 | Madanhat | 132 | 138 | 1 | 2019-04-03 | 06:00 | 121 | 29 | 2019-04-03 | 21:00
65 | Hathazari | 132 | 136 | 10 | 2019-04-03 | 04:00 | 123 | 28 | 2019-04-03 | 11:00
66 | Khulshi | 132 | 136 | 8 | 2019-04-03 | 13:00 | 120 | 19 | 2019-04-03 | 21:00
67 | Halishahar | 132 | 138 | 1 | 2019-04-03 | 07:00 | 122 | 19 | 2019-04-03 | 21:00
68 | Baraulia | 132 | 134 | 1 | 2019-04-03 | 7:00 | 120 | 8 | 2019-04-03 | 19:00
69 | Sikalbaha | 132 | 136 | 8 | 2019-04-03 | 13:00 | 122 | 19 | 2019-04-03 | 21:00
70 | Dohazari | 132 | 137 | 1 | 2019-04-03 | 7:00 | 120 | 19 | 2019-04-03 | 21:00
71 | Cox'sbazar | 132 | 136 | 1 | 2019-04-03 | 7:00 | 110 | 19 | 2019-04-03 | 21:00
72 | Chandraghona | 132 | 136 | 21 | 2019-04-03 | 7:00 | 121 | 30 | 2019-04-03 | 8:00
73 | Kaptai | 132 | 135 | 2 | 2019-04-03 | 21:00 | 124 | 4 | 2019-04-03 | 16:00
74 | A. Khaer Stl. | 132 | 134 | 9 | 2019-04-03 | 21:00 | 122 | 17 | 2019-04-03 | 15:00
75 | Bakulia | 132 | 136 | 1 | 2019-04-03 | 07:00 | 120 | 20 | 2019-04-03 | 12:00
76 | Julda | 132 | 137 | 1 | 2019-04-03 | 07:00 | 121 | 19 | 2019-04-03 | 21:00
77 | TK Chemical | 132 | 137 | 1 | 2019-04-03 | 01:00 | 123 | 25 | 2019-04-03 | 10:00
78 | Modern Steel | 132 | 135 | 8 | 2019-04-03 | 13:00 | 121 | 11 | 2019-04-03 | 9:00
79 | Shahmirpur | 132 | 137 | 1 | 2019-04-03 | 07:00 | 121 | 19 | 2019-04-03 | 21:00
80 | Khagrachhari | 132 | 139 | 1 | 2019-04-03 | 07:00 | 115 | 22 | 2019-04-03 | 10:00
81 | Matarbari | 132 | 138 | 1 | 2019-04-03 | 07:00 | 112 | 19 | 2019-04-03 | 21:00
82 | Baroiar Hat | 132 | 136 | 1 | 2019-04-03 | 01:00 | 118 | 13 | 2019-04-03 | 18:30
83 | Rangamati | 133 | 138 | 1 | 2019-04-03 | 07:00 | 119 | 19 | 2019-04-03 | 4:00
84 | Goalpara | 132 | 147 | 6 | 2019-04-03 | 22:00 | 122 | 13 | 2019-04-03 | 13:00
85 | Khulna Central | 132 | 146 | 6 | 2019-04-03 | 22:00 | 122 | 13 | 2019-04-03 | 13:00
86 | Noapara | 132 | 147 | 6 | 2019-04-03 | 22:00 | 119 | 8 | 2019-04-03 | 19:00
87 | Jessore | 132 | 140 | 1 | 2019-04-03 | 3:00 | 112 | 14 | 2019-04-03 | 21:00
88 | Jhenida | 132 | 146 | 6 | 2019-04-03 | 22:00 | 108 | 14 | 2019-04-03 | 21:00
89 | Bottail | 132 | 145 | 6 | 2019-04-03 | 20:00 | 112 | 12 | 2019-04-03 | 20:00
90 | G.K.Project | 132 | 145 | 1 | 2019-04-03 | 04:00 | 126 | 14 | 2019-04-03 | 21:00
91 | Faridpur | 132 | 142 | 1 | 2019-04-03 | 4:00 | 116 | 24 | 2019-04-03 | 21:00
92 | Madaripur | 132 | 145 | 1 | 2019-04-03 | 5:00 | 120 | 22 | 2019-04-03 | 15:00
93 | Gopalganj | 132 | 148 | 1 | 2019-04-03 | 5:00 | 118 | 22 | 2019-04-03 | 15:00
94 | Bagerhat | 132 | 150 | 6 | 2019-04-03 | 22:00 | 116 | 22 | 2019-04-03 | 12:00
95 | Mongla | 132 | 146 | 6 | 2019-04-03 | 22:00 | 118 | 29 | 2019-04-03 | 18:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Satkhira | 132 | 148 | 1 | 2019-04-03 | 3:00 | 119 | 14 | 2019-04-03 | 21:00
97 | Gallamari | 132 | 147 | 1 | 2019-04-03 | 5:00 | 123 | 13 | 2019-04-03 | 13:00
98 | Magura | 132 | 147 | 1 | 2019-04-03 | 5:00 | 105 | 14 | 2019-04-03 | 21:00
99 | Chuadanga | 132 | 146 | 6 | 2019-04-03 | 21:00 | 100 | 14 | 2019-04-03 | 21:00
100 | Barisal | 132 | 144 | 1 | 2019-04-03 | 5:00 | 126 | 1 | 2019-04-03 | 15:00
101 | Patuakhali | 132 | 143 | 1 | 2019-04-03 | 5:00 | 124 | 14 | 2019-04-03 | 22:00
102 | Bhandaria | 132 | 145 | 1 | 2019-04-03 | 4:00 | 121 | 12 | 2019-04-03 | 15:00
103 | Ishurdi | 132 | 145 | 1 | 2019-04-03 | 3:00 | 125 | 23 | 2019-04-03 | 19:00
104 | Ruppur paromanobik | 132 | 146 | 6 | 2019-04-03 | 20:00 | 126 | 29 | 2019-04-03 | 19:00
105 | Natore | 132 | 145 | 1 | 2019-04-03 | 3:00 | 120 | 8 | 2019-04-03 | 19:00
106 | Bogra | 132 | 146 | 1 | 2019-04-03 | 3:00 | 115 | 22 | 2019-04-03 | 16:00
107 | Noagaon | 132 | 144 | 1 | 2019-04-03 | 3:00 | 112 | 22 | 2019-04-03 | 16:00
108 | Rajshahi | 132 | 140 | 1 | 2019-04-03 | 3:00 | 114 | 8 | 2019-04-03 | 19:00
109 | C.Nawabganj | 132 | 135 | 6 | 2019-04-03 | 18:00 | 105 | 8 | 2019-04-03 | 19:00
110 | Amnura | 132 | 139 | 6 | 2019-04-03 | 19:00 | 108 | 8 | 2019-04-03 | 19:00
111 | Pabna | 132 | 140 | 1 | 2019-04-03 | 4:00 | 120 | 28 | 2019-04-03 | 20:00
112 | Shahjadpur | 132 | 148 | 1 | 2019-04-03 | 3:00 | 130 | 25 | 2019-04-03 | 20:00
113 | Serajganj | 132 | 144 | 1 | 2019-04-03 | 3:00 | 122 | 23 | 2019-04-03 | 19:30
114 | Niyamatpur | 132 | 145 | 1 | 2019-04-03 | 3:00 | 103 | 25 | 2019-04-03 | 2:00
115 | Joypurhat | 132 | 146 | 1 | 2019-04-03 | 3:00 | 105 | 25 | 2019-04-03 | 2:00
116 | Mohastangor | 132 | 145 | 1 | 2019-04-03 | 3:00 | 109 | 12 | 2019-04-03 | 15:00
117 | Rangpur | 132 | 137 | 1 | 2019-04-03 | 1:00 | 105 | 25 | 2019-04-03 | 13:00
118 | Lalmonirhat | 132 | 141 | 1 | 2019-04-03 | 1:00 | 98 | 25 | 2019-04-03 | 2:00
119 | Saidpur | 132 | 139 | 1 | 2019-04-03 | 1:00 | 102 | 25 | 2019-04-03 | 13:00
120 | Purbasadipur | 132 | 138 | 1 | 2019-04-03 | 2:00 | 105 | 24 | 2019-04-03 | 19:30
121 | Thakurgaon | 132 | 137 | 1 | 2019-04-03 | 3:00 | 95 | 12 | 2019-04-03 | 19:00
122 | Palashbari | 132 | 143 | 1 | 2019-04-03 | 2:00 | 102 | 25 | 2019-04-03 | 8:00
123 | Barapukuria | 132 | 137 | 1 | 2019-04-03 | 2:00 | 115 | 8 | 2019-04-03 | 19:00
124 | Panchagar | 132 | 142 | 1 | 2019-04-03 | 1:00 | 88 | 25 | 2019-04-03 | 22:00
125 | Joldhaka | 132 | 140 | 1 | 2019-04-03 | 1:00 | 98 | 24 | 2019-04-03 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:April' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 115 | 350
IP-299421 | Hasnabad | TR2 | 225 | 110 | 350 | 18.04.19 | 12:00
|  | TR3 | 225 | 110 | 330
|  | TR1 | 225 | 150 | 460
IP-299866 | Tongi | TR2 | 225 | 150 | 460 | 16.04.19 | 20:00
|  | TR3 | 225 | 150 | 460
|  | TR1 | 225 | 128 | 425
IP-299427 | Haripur | TR2 | 225 |  |  | 19.04.19 | 01:00 | S/D
|  | TR3 | 225 | 128 | 425
|  | TR1 | 225 | 170 | 565
IP-299728 | Rampura | TR2 | 225 | 170 | 565 | 29.04.19 | 16:00
|  | TR3 | 225 | 170 | 565
|  | TR1 | 225 | 146 | 406
IP-299264 | Aminbazar | TR2 | 225 | 146 | 406 | 15.04.19 | 09:00
|  | TR3 | 225 | 1150 | 415
| Maniknagar | TR1 | 300 | 125 | 400 | 29.04.19 | 16:00
|  | TR2 | 300 | 125 | 400
IP-399266 | Cumilla (N) | TR1 | 225 | 185 | 550 | 20.04.19 | 18:30
|  | TR2 | 225 | 186 | 548
| Fenchuganj | TR1 | 300 | 212 | 558 | 02.04.19 | 11:00
|  | TR1 | 150 | 122 | 340
IP-399428 | Hathazari | TR3 | 150 | 122 | 340 | 13.04.19 | 18:30
|  | TR4 | 150 | 122 | 340
|  | TR1 | 225 | 160 | 460
| Ishurdi | TR2 | 225 | 160 | 460 | 14.04.19 | 20:00
IP-499474 |  | TR3 | 225 | 160 | 460
| Khulna(S) | TR1 | 225 | 118 | 328
IP-58001/58002 |  | TR2 | 225 | 118 | 328 | 23.04.19 | 02:00
|  | TR3 | 300 | 154 | 422
| Bogra | TR1 | 225 | 146 | 440 | 22.04.19 | 20:00
|  | TR2 | 225 | 146 | 440
IP-43002/499264 |  | TR3 | 225 | 196 | 573
IP-499224 | Baghabari | TR1 | 225 | 186 | 560 | 29.04.19 | 20:00
| Barapukuria | TR1 | 225 | 200 | 1000 | 22.04.19 | 17:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 150 | 740 | 23.04.20 | 8:00 | 132 kV current is being provided
|  | TR6 | 225 | 194 | 967
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 350.1 | 630 | 13.04.19 | 10:30
|  | TR1(400/132 kV) | 325 | 240.4 | 414 | 27.04.19 | 20:00
|  | TR2(400/132 kV) | 325 | 240.4 | 414
| Bibiyana | ICT1(400/230 kV) | 520 | 140 | 240 | 02.04.19 | 11:00
|  | ICT2(400/230kV) | 520 | 140 | 240
| Bhulta | ATR1(400/230 kV) | 520 | 209 | 341 | 06.04.19 | 16:45
|  | ATR2(400/230kV) | 520 | 209 | 341
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:April' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:April' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-04-19 | 9015 | 9015 | - | - | - | - | - | - | - | - | - | - | - | - | 01-04-19 | 6561.4 | 6561.4 | - | - | - | - | - | - | - | - | - | - | - | -
02-04-19 | 7099 | 7099 | - | - | - | - | - | - | - | - | - | - | - | - | 02-04-19 | 8703.6 | 8703.6 | - | - | - | - | - | - | - | - | - | - | - | -
03-04-19 | 9252 | 9252 | - | - | - | - | - | - | - | - | - | - | - | - | 03-04-19 | 7659 | 7659 | - | - | - | - | - | - | - | - | - | - | - | -
04-04-19 | 10407 | 10407 | - | - | - | - | - | - | - | - | - | - | - | - | 04-04-19 | 8440.3 | 8440.3 | - | - | - | - | - | - | - | - | - | - | - | -
05-04-19 | 9752 | 9752 | - | - | - | - | - | - | - | - | - | - | - | - | 05-04-19 | 6737.3 | 6737.3 | - | - | - | - | - | - | - | - | - | - | - | -
06-04-19 | 9197 | 9197 | - | - | - | - | - | - | - | - | - | - | - | - | 06-04-19 | 7735.6 | 7735.6 | - | - | - | - | - | - | - | - | - | - | - | -
07-04-19 | 9529 | 9529 | - | - | - | - | - | - | - | - | - | - | - | - | 07-04-19 | 7306.6 | 7306.6 | - | - | - | - | - | - | - | - | - | - | - | -
08-04-19 | 9105 | 9105 | - | - | - | - | - | - | - | - | - | - | - | - | 08-04-19 | 7812.2 | 7812.2 | - | - | - | - | - | - | - | - | - | - | - | -
09-04-19 | 6024 | 6024 | - | - | - | - | - | - | - | - | - | - | - | - | 09-04-19 | 6544 | 6544 | - | - | - | - | - | - | - | - | - | - | - | -
10-04-19 | 9389 | 9389 | - | - | - | - | - | - | - | - | - | - | - | - | 10-04-19 | 6931.1 | 6931.1 | - | - | - | - | - | - | - | - | - | - | - | -
11-04-19 | 9894 | 9894 | - | - | - | - | - | - | - | - | - | - | - | - | 11-04-19 | 8566.2 | 8566.2 | - | - | - | - | - | - | - | - | - | - | - | -
12-04-19 | 10181 | 10181 | - | - | - | - | - | - | - | - | - | - | - | - | 12-04-19 | 7580.2 | 7580.2 | - | - | - | - | - | - | - | - | - | - | - | -
13-04-19 | 9962 | 9962 | - | - | - | - | - | - | - | - | - | - | - | - | 13-04-19 | 7462.5 | 7462.5 | - | - | - | - | - | - | - | - | - | - | - | -
14-04-19 | 9962 | 9962 | - | - | - | - | - | - | - | - | - | - | - | - | 14-04-19 | 7462.5 | 7462.5 | - | - | - | - | - | - | - | - | - | - | - | -
15-04-19 | 11190 | 11190 | - | - | - | - | - | - | - | - | - | - | - | - | 15-04-19 | 8775.7 | 8775.7 | - | - | - | - | - | - | - | - | - | - | - | -
16-04-19 | 11440 | 11440 | - | - | - | - | - | - | - | - | - | - | - | - | 16-04-19 | 9511.3 | 9511.3 | - | - | - | - | - | - | - | - | - | - | - | -
17-04-19 | 10871 | 10871 | - | - | - | - | - | - | - | - | - | - | - | - | 17-04-19 | 8936.2 | 8936.2 | - | - | - | - | - | - | - | - | - | - | - | -
18-04-19 | 11242 | 11242 | - | - | - | - | - | - | - | - | - | - | - | - | 18-04-19 | 8841.8 | 8841.8 | - | - | - | - | - | - | - | - | - | - | - | -
19-04-19 | 10858 | 10858 | - | - | - | - | - | - | - | - | - | - | - | - | 19-04-19 | 7787.1 | 7787.1 | - | - | - | - | - | - | - | - | - | - | - | -
20-04-19 | 11300 | 11300 | - | - | - | - | - | - | - | - | - | - | - | - | 20-04-19 | 9196.7 | 9136.7 | - | - | - | - | - | - | - | - | - | - | - | -
21-04-19 | 10184 | 10184 | - | - | - | - | - | - | - | - | - | - | - | - | 21-04-19 | 9943.2 | 9943.2 | - | - | - | - | - | - | - | - | - | - | - | -
22-04-19 | 10755 | 10755 | - | - | - | - | - | - | - | - | - | - | - | - | 22-04-19 | 7385.4 | 7385.4 | - | - | - | - | - | - | - | - | - | - | - | -
23-04-19 | 11581 | 11581 | - | - | - | - | - | - | - | - | - | - | - | - | 23-04-19 | 9663.9 | 9663.9 | - | - | - | - | - | - | - | - | - | - | - | -
24-04-19 | 12057 | 12057 | - | - | - | - | - | - | - | - | - | - | - | - | 24-04-19 | 10057 | 10057 | - | - | - | - | - | - | - | - | - | - | - | -
25-04-19 | 12067 | 12067 | - | - | - | - | - | - | - | - | - | - | - | - | 25-04-19 | 9856.6 | 9856.6 | - | - | - | - | - | - | - | - | - | - | - | -
26-04-19 | 10891 | 10891 | - | - | - | - | - | - | - | - | - | - | - | - | 26-04-19 | 8529.2 | 8529.2 | - | - | - | - | - | - | - | - | - | - | - | -
27-04-19 | 12052 | 12052 | - | - | - | - | - | - | - | - | - | - | - | - | 27-04-19 | 9758.2 | 9758.2 | - | - | - | - | - | - | - | - | - | - | - | -
28-04-19 | 11902 | 11902 | - | - | - | - | - | - | - | - | - | - | - | - | 28-04-19 | 9840.1 | 9840.1 | - | - | - | - | - | - | - | - | - | - | - | -
29-04-20 | 12200 | 12200 | - | - | - | - | - | - | - | - | - | - | - | - | 29-04-20 | 10002.6 | 10002.6 | - | - | - | - | - | - | - | - | - | - | - | -
30-04-19 | 12022 | 12022 | - | - | - | - | - | - | - | - | - | - | - | - | 30-04-19 | 9928 | 9928 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:April' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12200 | 29/04/19 | 19:30
2 | Maximum day peak Genaration | MW | 10057 | 24/04/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 12200 | 29/04/19 | 19:30
4 | Minimum Generation | MW | 2605 | 01/04/19 | 5:00
5 | Average of the daily evening peak Genaration | MW | 10379.3333
6 | Average of the daily day peak Genaration | MW | 8450.5167
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW | -
11 | Total Generation | MKWH | 6218.602
12 | Total Generation by IPP | MKWH | 1827.0218 | % of total Gen. | 29.38%
13 | Total Generation by BPDB | MKWH | 3100.9672 | " | 49.87%
14 | A) Total Generation by RPCL | MKWH | 108.3794 | '' | 1.743%
| B) Total Generation by REB | MKWH | 128.616 | " | 2.068%
| C) Total Generation by RENTAL | MKWH | 427.5001 | " | 6.875%
| D) Total Imported from India (HVDC) | MKWH | 542.4913 | " | 8.724%
| E) Total Imported from Tripura, India (A.C) | MKWH | 83.6262 | " | 1.345%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4100.9893 | % of total Gen. | 65.95%
| B) Oil | MKWH | 1266.4537 | '' | 20.37%
| C) Hydro | MKWH | 51.4805 | '' | 0.8278%
| D) Solar | MKWH | 4.0002 | '' | 0.06433%
| E) Coal | MKWH | 169.5608 | '' | 2.727%
| F) HVDC (Import from India) | MKWH | 542.4913 | '' | 8.724%
| G) A.C (Import from Tripura, India) | MKWH | 83.6262 | '' | 1.345%
16 | Maximun of the daily total Generation . | MKWH | 256.8131 | 29/04/19
17 | Monthly Load factor | % | 70.7946
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 1089.0066
| A) Gas | M.Taka | 466.2744
| B) Liquid fuel | M.Taka | 595.665
| C) Coal | M.Taka | 27.0672
| D) HVDC (Import from India) | M.Taka | 2766.7055
| E) Tripura(Import from India) | M.Taka | 572.0035
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1123.9438 | 06/04/19
| A) Gas | M.Taka | 890.1158 | 06/04/19
| B) Liquid fuel | M.Taka | 764.8952 | 25/04/19
| C) Coal | M.Taka | 309.3641 | 21/04/19
| D) HVDC (Import from India) | M.Taka | 104.3441 | 29-04-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.1846
| B) Excluding Hydro & Solar | Taka/KWHR | 3.2133
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.2 | 30/04/19 | 06:00
b) | Actual | FT (MSL) | 76.64 | 30/04/19 | 06:00
22 | Peak Genaration of April 2018 | MW | 10137 | 24/04/18 | 19:30
23 | Peak Demand of April 2018 | MW | 10137 | 24/04/18 | 19:30
24 | Maximum peak Generation recorded upto 30/04/19 | MW | 12200 | 29/04/19 | 19:30
25 | Maximum peak Demand recorded upto 30/04/19 | MW | 12200 | 29/04/19 | 19:30
26 | Maximum load shed recorded upto 30/04/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.