## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | March 2019 |  | February 2019 |  | March 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10933 | 30/03/19 | 9403 | 24/02/19 | 10084 | 19/03/18 | 11623 | 19/09/18
|  |  | 20:00 |  | 19:00 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 4710 | 02/03/19 | 3497 | 26/02/19 | 1774 | 31/03/18 | - | -
|  |  | 5:00 |  | 5:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10933 | 30/03/19 | 9403 | 24/02/19 | 10084 | 19/03/18 | 11623 | 19/09/18
|  |  | 20:00 |  | 19:00 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 9132.3 | 31/03/19 | 7765.8 | 23/02/19 | 8476.9 | 22/03/18 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10933 | 30/03/19 | 9403 | 24/02/19 | 10084 | 19/03/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 9524.1613 |  | 8652.54 |  | 9296.54 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 7899.1097 |  | 7016.69 |  | 7779.98 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 864 | 12/02/19 | 864 | 12/02/19 | 488 | 03/03/18 | 864 | 2019-12-02
|  |  | 21:00 |  | 21:00 |  | 10:00 |  | 21:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 25'/03/19 | 152 | 23/02/19 | 174 | 27/03/18 | 188 | 29/05/18
|  |  | 19:00 |  | 18:30 |  | 18:30 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3315.9631 |  | 2632.18 |  | 2868.69 |  | 3315.96 | March-19
21 | Station Use of BPDB (MKWH) | 120.7397 |  | 88.69 |  | 94.27
22 | Net Generation of BPDB (MKWH) | 3195.2234 |  | 2543.49 |  | 2774.42
23 | Net Generation of IPP & RPCL (MKWH) | 1441.9411 |  | 1086.61 |  | 1603.06
24 | Net Generation of REB (MKWH) | 138.6817 |  | 118.64 |  | 143.12
24 | Net Generation of Rental Power Plant (MKWH) | 370.9007 |  | 299.97 |  | 700.15
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5146.7469 |  | 4048.72 |  | 5220.75 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 4289.7961 |  | 3514.59 |  | 3545 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 118.3913 |  | 35.64 |  | 298.94 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 676.8041 |  | 435.52 |  | 1180.53 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 52.3268 |  | 44.77 |  | 53.53 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 3.9096 |  | 3.52 |  | 0.38 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 126.2587 |  | 103.37 |  | 236.64 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 611.4663 |  | 486.49 |  | 423.51 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 72.2749 |  | 73.18 |  | 76.49 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10933 | 30/03/19 | 20:00
Generation Period
| Dhaka | MW | 3816
| Chattogram | MW | 1145
| Cumilla | MW | 945
| Mymensingh | MW | 790
| Sylhet | MW | 423
a) | Total supply in East zone | MW | 7119
| Khulna | MW | 1161
| Barisal | MW | 242
| Rajshahi | MW | 1116
| Rangpur | MW | 627
b) | Total supply in West zone | MW | 3146
c) | Total supply in both zone ( a+b) | MW | 10265
Ref: | 27.21.2604.603.16.086.18.142 | Date: 18/04/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 340 | 31/03/19 | 18:30
| b) Ishurdi end | MW | 260 | 25/03/19 | 9:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 320 | 25/03/19 | 9:00
| b) Ishurdi end | MW | 300 | 31/03/19 | 18:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 15.4306
| b) Ishurdi end | MKWH | 33.8393
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 32.8241
| b) Ishurdi end | MKWH | 14.9812
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 350 | 13/03/19 | 19:00
| b)Serajganj end | MW | 200 | 02/03/19 | 11:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 190 | 02/03/19 | 11:00
| b)Sirajganj end | MW | 320 | 13/03/19 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 5.822 | 17/03/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 5.778 | 17/03/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 57.148
| b)Sirajganj end | MKWH | 16.558
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 16.404
| b)Sirajganj end | MKWH | 56.716
30 | Transmission loss of EWI /NO-2 | % | 0.795
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF_LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV Transformer-T-3 | 2019-03-11 18:32 | 2019-03-11 18:40 | 0:08 | E/O | Due to Fulbaria feeder faultsulator clamp | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2019-03-11 19:53 | 2019-03-11 21:10 | 1:17 | E/O | Due to Gas filling | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T-1 | 2019-03-14 20:15 | 2019-03-15 00:44 | 4:29 | E/O | Due to bursting of CT | 8 | 35.8667 | Power interruption
Kishoreganj | 132/33 kV Transformer-T-2 | 2019-03-25 18:36 | 2019-03-25 18:40 | 0:04 | T | Tripped showing E/F 33 kV side relay | 90 | 6 | Power interruption
Tongi | 132/33 kV Transformer-T3 | 2019-03-28 11:05 | 2019-03-29 22:23 | 35:18 | E/O | Due to bursting of 33 kV bushing | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformers-T-1 & T-2 | 2019-03-28 18:19 | 2019-03-28 18:25 | 0:06 | T | Tripped showing E/F 33 kV side relay | 124 | 12.4 | Power interruption
|  |  | Total : | 41:22 |  | Unserved Energy: |  | 54.2667
Dhaka (South) Grid Circle :
Munshiganj | 132/33 kV Transformer-T2 | 2019-03-03 16:00 | 2019-03-03 20:04 | 4:04 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 with 33 kV Bus | 2019-03-05 06:04 | 2019-03-05 06:42 | 0:38 | T | Tripped showing dir.& O/C relay at 33 kV dohar feeder fault | 45 | 28.5 | Power interruption
| 33 kV full Bus | 2019-03-07 02:26 | 2019-03-07 02:54 | 0:28 | E/O | Due to Postagola feeder fault | 110 | 51.3333 | Power interruption
| 132/33 kV Transformer-T-5 | 2019-03-07 09:28 | 2019-03-07 13:16 | 3:48 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T-1, T2 & T-5 | 2019-03-09 03:49 | 2019-03-09 04:42 | 0:53 | E/O | Due to 33 kV bushing burst | 100 | 88.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-03-09 09:48 | 2019-03-09 12:19 | 2:31 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T-2, & T-5 | 2019-03-10 04:58 | 2019-03-10 05:35 | 0:37 | E/O | Due to 33 kV B-phase CB burst | 80 | 49.3333 | Power interruption
Lalbagh | 132/33 kV Transformer-T1 | 2019-03-22 08:22 | 2019-03-22 15:44 | 4:04 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ghorasal | 230/132 kV Transformer AT12 | 2019-03-30 11:00 | 2019-03-30 11:45 | 0:45 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T-1 & T2 | 2019-03-31 16:38 | 2019-03-31 16:55 | 0:35 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T-1 & T2 | 2019-03-31 18:13 | 2019-03-31 18:55 | 1:35 | T |  | 0 | 0 | No interruption
|  |  | Total : | 4:04 |  | Unserved Energy: |  | 217.5
Chittagong Grid Circle :
Barohat | 132/33 kV Transformer-T1 | 2019-03-05 10:20 | 2019-03-05 13:10 | 2:50 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Sikalbaha | 132/33 kV Transformer T3 | 2019-03-05 15:23 | 2019-03-05 15:46 | 0:23 | E/O | Due to re hot maintenance | 17 | 6.5167 | Power interruption
| 230/132 kV Transformer T02 | 2019-03-20 14:09 | 2019-03-25 21:39 | 127:30 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2019-03-24 11:17 | 2019-03-24 12:09 | 0:52 | E/O | Due to re hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 131:35 |  | Unserved Energy: |  | 6.5167
Cumilla Grid Circle :
Cumilla(N) | 230/132 kV Transformer T02 | 2019-03-14 11:07 | 2019-03-14 14:34 | 3:27 | T | Tripped showing lock out relay | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2019-03-16 08:19 | 2019-03-16 08:53 | 0:34 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformers-T1 & T2 | 2019-03-18 07:04 | 2019-03-18 18:06 | 11:02 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer T02 | 2019-03-19 17:12 | 2019-03-19 17:23 | 0:11 | T | Tripped showing DTT-1 signal | 0 | 0 | No interruption
| 230/132 kV Transformer T02 | 2019-03-23 10:00 | 2019-03-23 16:58 | 6:58 | T | Tripped showing DTT-1 signal | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer TR1 | 2019-03-31 17:53 | 2019-03-31 20:50 | 2:57 | T | Tripped without showing any relay | 195 | 575.25 | Power interruption
|  |  | Total : | 25:09 |  | Unserved Energy: |  | 575.25
Khulna Grid Circle :
Faridpur | 132/33 kV Transformers-T1 & T2 | 2019-03-02 17:18 | 2019-03-02 17:22 | 0:04 | T | Tripped showing O/C relay at 33 kV side | 60 | 4 | Power interruption
Goalpara | 132/33 kV Transformer-T6 | 2019-03-04 07:45 | 2019-03-04 09:11 | 1:26 | E/O | Due to re hot maintenance at 33 kV Breaker | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-03-09 14:17 | 2019-03-09 15:09 | 0:52 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T6 | 2019-03-17 07:35 | 2019-03-17 10:47 | 3:12 | E/O | Due to re hot maintenance at 33 kV Breaker | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-03-17 13:42 | 2019-03-17 14:08 | 0:26 | T | Tripped showing O/V relay 33 kV side | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-03-17 22:03 | 2019-03-18 00:25 | 2:22 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-03-17 23:07 | 2019-03-18 01:07 | 2:00 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-03-17 23:07 | 2019-03-17 23:54 | 0:47 | T | Due to bad weather | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-03-17 23:10 | 2019-03-18 00:15 | 1:05 | T | Due to bad weather | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformers-T1 & T2 | 2019-03-21 02:59 | 2019-03-21 03:13 | 0:14 | T | Due to 33 kV Jhalkathi 33 kV feeder fault | 52 | 12.1333 | Power interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-03-22 15:30 | 2019-03-22 15:40 | 0:10 | T | Tripped showing O/C relay at 33 kV side | 11 | 1.8333 | Power interruption
Gopalganj | 132/33 kV Transformers-T1 & T2 | 2019-03-23 12:18 | 2019-03-23 12:26 | 0:08 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Khulna | 132/33 kV Transformer-T3 | 2019-03-27 16:33 | 2019-03-27 18:46 | 2:13 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-03-28 07:09 | 2019-03-28 07:50 | 0:41 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2019-03-30 16:15 | 2019-03-30 16:28 | 0:13 | E/O | Due to Oil leakage | 60 | 13 | Power interruption
|  |  | Total : | 15:53 |  | Unserved Energy: |  | 30.9667
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Shahjadpur | 132/33 kV Transformer1-T1 | 2019-03-06 18:25 | 2019-03-06 19:12 | 0:47 | E/O | Due to red hot maintenance at 33 kV R-phase bushing | 10 | 7.8333 | Power interruption
Bottail | 132/33 kV Transformer-T1 | 2019-03-12 14:48 | 2019-03-12 16:02 | 1:14 | E/O | Due to re hot maintenance | 28 | 34.5333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-03-12 14:56 | 2019-03-12 15:01 | 0:05 | T | Tripped showing O/C relay | 31 | 2.5833 | Power interruption
| 132/33 kV Transformer-T1 | 2019-03-17 08:08 | 2019-03-17 08:32 | 0:24 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T3 | 2019-03-17 22:02 | 2019-03-18 09:39 | 11:37 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Bheramara HVDC | 33/0.4 kV auxiliary Transformer | 2019-03-21 11:19 | 2019-03-21 16:58 | 5:39 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformers-T1 & T2 | 2019-03-23 08:53 | 2019-03-23 09:12 | 0:19 | T | Tripped showing O/C relay at 33 side | 0 | 0 | No interruption
|  |  | Total : | 20:05 |  |  |  | 44.95
Bogra Grid Circle:
Rangpur | 132/33 kV Transformer-T3 | 2019-03-05 09:40 | 2019-03-05 10:10 | 0:30 | E/O | Due to red hot maintenance at 33 kV B-phase CT bushing | 7 | 3.5 | Power interruption
Amnura | 132/33 kV Transformer-T3 | 2019-03-11 22:58 | 2019-03-12 01:05 | 2:07 | E/O | Due to R-phase CT burst | 32 | 67.7333 | Power interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-03-21 13:30 | 2019-03-21 16:15 | 2:45 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T3 | 2019-03-24 04:50 | 2019-03-24 05:22 | 0:32 | E/O | Due to R-phase CT burst | 100 | 53.3333 | Power interruption
N.nawabganj | 132/33 kV Transformer-T3 | 2019-03-25 10:17 | 2019-03-25 13:19 | 3:02 | E/O | Due to oil leakage of bushing | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2019-03-25 09:39 | 2019-03-25 11:03 | 1:24 | T | Tripped showing differential relay | 14 | 33.6 | Power interruption
Pabna | 132/33 kV Transformers-T1 & T2 | 2019-03-26 17:56 | 2019-03-26 18:10 | 0:14 | E/O | Due to 33 kV Poilanpur feeder fault | 50 | 11.6667 | Power interruption
Thakurgaon | 33 kV Bus | 2019-03-30 06:43 | 2019-03-30 07:30 | 0:47 | E/O | Due to re hot maintenance | 60 | 47 | Power interruption
Saidpur | 132/33 kV Transformer-T3 | 2019-03-31 11:45 | 2019-03-31 12:11 | 0:30 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 11:51 |  | Unserved Energy: |  | 216.8333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 249:59 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF_LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-New Tongi 132 kV line-1 | 2019-03-05 19:58 | 2019-03-05 21:55 | 1:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2019-03-08 13:30 | 2019-03-08 14:58 | 1:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-03-08 23:33 | 2019-03-08 23:37 | 0:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2019-03-11 10:06 | 2019-03-11 10:12 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-1 | 2019-03-14 11:50 | 2019-03-14 12:25 | 0:35 | T | Tripped showing PTAW,PTA5,PTD3,DSTW signal | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2019-03-17 23:06 | 2019-03-17 23:20 | 0:14 | T | Tripped showing CAD,CE Zone1 & Z1 VT fail | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-1 | 2019-03-19 16:29 | 2019-03-19 16:52 | 0:23 | T | Tripped showing BN signal | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2019-03-19 16:29 | 2019-03-19 16:44 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2019-03-23 11:04 | 2019-03-24 00:36 | 13:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2019-03-30 09:23 | 2019-03-30 13:48 | 4:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2019-03-30 10:11 | 2019-03-30 13:15 | 3:04 | T | Tripped showing dist. relay | 85 | 260.6667 | Power interruption
| Aminbazar-Mirpur 132 kV line-1 | 2019-03-31 18:16 | 2019-03-31 19:01 | 0:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-1 | 2019-03-31 19:34 | 2019-03-31 19:55 | 0:21 | T |  | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2019-03-31 18:16 | 2019-03-31 19:34 | 1:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-2 | 2019-03-31 18:11 | 2019-03-31 23:05 | 4:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 kV line-2 | 2019-03-31 18:11 | 2019-03-31 23:09 | 4:58 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2019-03-31 18:08 | 2019-04-01 15:40 | 21:32 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2019-03-31 19:34 | 2019-03-31 19:50 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-1 | 2019-03-31 19:34 | 2019-03-31 19:57 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-2 | 2019-03-31 19:34 | 2019-03-31 19:52 | 0:18 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2019-03-31 17:59 | 2019-03-31 20:44 | 2:45 | T | Tripped showing dist. relay | 5 | 13.75 | Power interruption
| Tongi-Kabirpur 132 kV line-2 | 2019-03-31 17:51 | 2019-03-31 19:44 | 1:53 | T | Tripped showing CSW,CAT,CD,& CE signal | 0 | 0 | No interruption
|  |  | Total : | 65:26 |  | Unserved Energy: |  | 274.4167
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-03-03 06:20 | 2019-03-03 06:31 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line-2 | 2019-03-05 06:45 | 2019-03-05 06:53 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur(New) 132 kV line-2 | 2019-03-08 22:00 | 2019-03-09 01:00 | 3:00 | T | Tripped showing neutral voltage displacement | 0 | 0 | No interruption
| Shyampur(Old)-Shyampur(New) 132 kV line-2 | 2019-03-09 03:34 | 2019-03-10 01:47 | 22:13 | T |  | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line-2 | 2019-03-09 08:12 | 2019-03-09 13:30 | 5:18 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur(New) 132 kV line-2 | 2019-03-10 02:23 | 2019-03-10 02:37 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2019-03-11 02:28 | 2019-03-11 22:55 | 20:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-03-16 10:25 | 2019-03-16 10:59 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line-2 | 2019-03-16 10:25 | 2019-03-16 10:54 | 0:29 | T | Tripped showing dist. relay | 100 | 48.3333 | Power interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2019-03-16 11:27 | 2019-03-16 11:58 | 0:31 | T | Tripped showing dist.(R-phase)relay | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-2 | 2019-03-17 23:07 | 2019-03-18 00:43 | 1:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2019-03-18 00:44 | 2019-03-18 00:54 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj(S) 230 kV line-2 | 2019-03-20 10:25 | 2019-03-21 00:34 | 14:09 | T | Tripped showing Breaker fail | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV line-2 | 2019-03-22 08:50 | 2019-03-22 12:58 | 4:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj(S) 230 kV line-2 | 2019-03-22 15:00 | 2019-03-22 17:55 | 2:55 | T |  | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-2 | 2019-03-23 15:55 | 2019-03-23 17:25 | 1:30 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2019-03-23 21:22 | 2019-03-23 23:15 | 1:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-1 | 2019-03-25 10:43 | 2019-03-25 11:20 | 0:37 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Tongi-Ghorashal 230 kV line-1 | 2019-03-25 11:58 | 2019-03-25 15:08 | 3:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-03-31 18:22 | 2019-03-31 19:56 | 1:34 | T | Tripped showing mai protection relay | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line-2 | 2019-03-31 18:23 | 2019-03-31 18:47 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-03-31 18:18 | 2019-03-31 19:58 | 1:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2019-03-31 18:30 | 2019-03-31 20:52 | 2:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Haripur-Shyampur 132 kV line | 2019-03-31 18:21 | 2019-03-31 20:18 | 1:57 | T | Tripped showing dist.(Z1) relay | 18 | 35.1 | Power interruption
| Haripur-Ullon 132 kV line | 2019-03-31 18:24 | 2019-03-31 18:54 | 0:30 | T | Tripped showing dist.(Z2) relay | 31 | 15.5 | Power interruption
| Haripur-Madanganj 132 kV line | 2019-03-31 18:21 | 2019-03-31 19:21 | 1:00 | T | Tripped showing dist.(Z1) relay | 30 | 30 | Power interruption
Ghorasal | Ghorasal-Joydevpur 132 kV line-2 | 2019-03-31 17:35 | 2019-03-31 20:40 | 3:05 | T | Tripped showing remote protection relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-03-31 18:21 | 2019-03-31 19:06 | 0:45 | T | Tripped showing dist.R-phase relay | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV line | 2019-03-31 18:21 | 2019-04-01 17:10 | 22:49 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-03-31 21:26 | 2019-04-01 10:15 | 12:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-1 | 2019-03-31 11:50 | 2019-04-01 12:24 | 24:34 | T |  | 0 | 0 | No interruption
|  |  | Total : | 156:42 |  | Unserved Energy: |  | 128.9333
Chittagong Grid Circle :
Madunaghat | Madunaghat-TK.chemical 132 kV line | 2019-03-11 20:48 | 2019-03-12 09:25 | 12:37 | E/O | Due to sparking of CT terminal at TK chemical | 0 | 0 | No interruption
| Madunaghat-TK.chemical 132 kV line | 2019-03-12 08:10 | 2019-03-12 09:25 | 1:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line | 2019-03-14 08:28 | 2019-03-14 10:10 | 1:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2019-03-16 17:16 | 2019-03-16 17:34 | 0:18 | T | Tripped showing O/C relay | 121 | 34.2833 | Power interruption 17:16 to 17:33
| Khulshi-Halishahar 132 kV line-1 | 2019-03-16 17:16 | 2019-03-16 17:33 | 0:17 | T | Tripped showing dist. relay
Bakulia | Bakulia-Madern steel 132 kV line | 2019-03-16 17:17 | 2019-03-16 17:52 | 0:35 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Bakulia-Khulshi 132 kV line | 2019-03-16 17:12 | 2019-03-16 17:52 | 0:40 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV line-1 | 2019-03-16 17:17 | 2019-03-16 17:54 | 0:37 | T |  | 0 | 0 | No interruption
Sikalbaha(N) | Sikalbaha(N)-Madunaghat 132 kV line | 2019-03-16 17:39 | 2019-03-16 17:54 | 0:15 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-TK.chemical 132 kV line | 2019-03-16 17:40 | 2019-03-16 18:05 | 0:25 | T | Tripped showing O/C relay | 200 | 83.3333 | Power interruption
Bakulia | Bakulia-Khulshi 132 kV line | 2019-03-20 07:21 | 2019-03-20 08:02 | 0:41 | T | Tripped showing dist. relay | 10 | 6.8333 | Power interruption
T.K. chemical | T.K. chemical -Sikalbaha (New) 132 kV line | 2019-03-21 10:16 | 2019-03-21 12:10 | 1:54 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| T.K. chemical -Madunaghat 132 kV line & Bus | 2019-03-21 10:28 | 2019-03-21 12:25 | 1:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| T.K. chemical -Madunaghat 132 kV line -2 | 2019-03-25 12:53 | 2019-03-25 14:01 | 1:08 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 268:45 |  | Unserved Energy: |  | 124.45
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj with Biyanibazar S/S | 2019-03-07 01:00 | 2019-03-07 01:23 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sylhet-Fenchuganj 132 kV line | 2019-03-10 02:39 | 2019-03-10 03:02 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Sylhet 132 kV line | 2019-03-12 04:25 | 2019-03-12 04:56 | 0:31 | T | Tripped showing dist. relay | 14 | 7.2333 | Power interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-03-14 15:43 | 2019-03-17 18:45 | 75:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuagnj | Ashuagnj-Ghorashal 132 kV line-1 | 2019-03-17 22:04 | 2019-03-17 23:28 | 1:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line | 2019-03-17 23:34 | 2019-03-18 01:40 | 2:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuagnj | Ashuagnj-Ghorashal 230 kV line-2 | 2019-03-19 23:05 | 2019-03-20 10:57 | 11:52 | T | Tripped showing voltage fail | 0 | 0 | No interruption
Sylhet S/S | Sylhet S/S-Sylhet 50 MW P/S 132 kV line | 2019-03-21 10:22 | 2019-03-21 10:53 | 0:31 | E/O | Due to SF6 gas pressure low | 0 | 0 | No interruption
Ashuagnj | Ashuagnj-Ghorashal 230 kV line-2 | 2019-03-21 14:32 | 2019-03-21 15:35 | 1:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuagnj-Ghorashal 230 kV line-2 | 2019-03-21 15:35 | 2019-03-21 17:49 | 2:14 | T |  | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Sylhet 132 kV line | 2019-03-22 00:43 | 2019-03-22 00:59 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2019-03-22 01:15 | 2019-03-22 01:50 | 0:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj(S)-Ghorashal 230 kV line-2 | 2019-03-22 05:00 | 2019-03-22 07:00 | 2:00 | T |  | 0 | 0 | No interruption
Sylhet | Sylhet -Fenchuganj 132 kV line | 2019-03-22 06:18 | 2019-03-22 06:28 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Sylhet 132 kV line | 2019-03-29 22:08 | 2019-03-29 22:23 | 0:15 | T | Tripped showing dist. relay | 30 | 7.5 | Power interruption
Sylhet S/S | Sylhet S/S-Sylhet 50 MW P/S 132 kV Ckt | 2019-03-29 22:08 | 2019-03-30 02:15 | 4:07 | E/O | Due to MCB of PT got burned. | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-1 | 2019-03-31 17:53 | 2019-03-31 18:24 | 0:31 | T | Tripped showing dist.protection & E/F relay | 59 | 148.4833 | Power interruption 17:53 to 20:24
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-2 | 2019-03-31 17:53 | 2019-03-31 18:25 | 0:32 | T | Tripped showing dist.protection & E/F relay | 0 | 0 | No interruption
Sylhet S/S | Sylhet S/S-Fenchuganj P/S 132 kV line | 2019-03-31 17:53 | 2019-03-31 19:19 | 1:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-3 | 2019-03-31 17:53 | 2019-03-31 20:50 | 2:57 | T | Tripped showing dist.protection relay | 0 | 0 | No interruption
|  |  | Total : | 108:18 |  | Unserved Energy: |  | 163.2167
Khulna Grid Circle :
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-03-11 17:11 | 2019-03-11 17:32 | 0:21 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barisal(S) 132 kV line | 2019-03-13 07:01 | 2019-03-13 07:38 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-03-13 07:24 | 2019-03-13 07:38 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2019-03-14 21:52 | 2019-03-15 00:38 | 2:46 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Khulna(C) | Khulna©-Goalpara 132 kV line-1 | 2019-03-16 10:34 | 2019-03-16 13:29 | 2:55 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2019-03-17 20:53 | 2019-03-17 21:47 | 0:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-2 | 2019-03-17 21:57 | 2019-03-17 22:53 | 0:21 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Bhandaria 132 kV line | 2019-03-17 22:14 | 2019-03-17 22:47 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2019-03-17 21:59 | 2019-03-17 22:13 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2019-03-22 20:14 | 2019-03-22 20:32 | 0:18 | T | Tripped showing inst.E/F relay | 12 | 3.6 | Power interruption
|  |  | Total : | 9:13 |  | Unserved Energy: |  | 3.6
HVDC Grid Circle :
HVDC Bheramara | HVDC Bheramara block-1 | 2019-03-10 06:18 | 2019-03-10 09:39 | 3:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2019-03-15 07:51 | 2019-03-15 09:57 | 2:06 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Bheramara HVDC-Bahrampur 400 kV line-1 | 2019-03-31 15:50 | 2019-03-31 16:37 | 0:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bheramara HVDC-Bahrampur 400 kV line-2 | 2019-03-31 15:50 | 2019-03-31 16:19 | 0:29 | T |  | 0 | 0 | No interruption
| Bheramara-Ishurdi 132 kV line-1 | 2019-03-31 16:33 | 2019-03-31 16:57 | 0:24 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
|  |  | Total : | 7:07 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura (Old) | Bogura (Old)-Bogra(new) 132 kV line-2 | 2019-03-09 07:44 | 2019-03-09 09:44 | 2:00 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2019-03-10 12:58 | 2019-03-10 16:02 | 3:04 | T | Tripped showing CB air pressure low | 60 | 184 | Power interruption
Amnura | Amnura-C.nawabganj -Rajshahi 132 kV line | 2019-03-11 22:58 | 2019-03-12 01:05 | 2:07 | E/O | Due to bursting o R-phase CT | 0 | 0 | No interruption
Bogura(New) | Bogura(New)-Bogura 132 kV line-2 | 2019-03-17 10:33 | 2019-03-17 12:45 | 2:12 | E/O | Due to red hot maintenance | 60 | 132 | Power interruption
Natore | Natore-Bogura 132 kV line-2 | 2019-03-27 00:32 | 2019-03-27 00:57 | 0:25 | T | Tripped showing dist.CE,CAT,CD signal | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2019-03-31 09:23 | 2019-03-31 11:58 | 2:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Palshbari | Palshbari-Rangpur 132 kV line-1 | 2019-03-31 15:32 | 2019-03-31 15:45 | 0:13 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
| Palshbari-Rangpur 132 kV line-1 | 2019-03-31 15:45 | 2019-03-31 17:14 | 1:29 | T |  | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2019-03-31 17:01 | 2019-03-31 17:20 | 0:19 | T | Tripped showing dist. relay | 27 | 8.55 | Power interruption
|  |  | Total : | 14:24 |  | Unserved Energy: |  | 324.55
Others :
Maniknagar | Maniknagar-Bangabhban 132 kV line-1 | 2019-03-06 08:25 | 2019-03-06 17:37 | 9:12 | T | Tripped showing mian protection relay | 0 | 0 | No interruption
|  |  | Total : | 9:12 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 639:07 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF_LDC-25
Page: 1/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400/230 kV Transformer-T2 | 2019-03-02 09:19 | 2019-03-02 17:02 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T2 | 2019-03-02 09:07 | 2019-03-02 13:28 | 4:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-2 | 2019-03-02 09:45 | 2019-03-02 18:10 | 8:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2019-03-02 11:10 | 2019-03-02 14:34 | 3:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2019-03-03 09:02 | 2019-03-03 13:34 | 4:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2019-03-04 07:12 | 2019-03-04 17:30 | 10:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T3 | 2019-03-04 06:56 | 2019-03-04 11:10 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT1 | 2019-03-04 09:32 | 2019-03-04 11:18 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-GT2 | 2019-03-04 11:22 | 2019-03-04 12:02 | 0:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-GT3 | 2019-03-04 12:04 | 2019-03-04 14:13 | 2:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-GT1 | 2019-03-06 09:27 | 2019-03-06 14:17 | 4:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132 kV Bus-A & 132/33 kV Transformer GT4 | 2019-03-06 08:07 | 2019-03-06 18:53 | 10:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | 132/33 kV Bus-1 | 2019-03-06 08:40 | 2019-03-06 17:40 | 9:00 | S/O | Due to D/W work | 10 | 1.6667 | Power interruption 8:40 to 8:50
Uttara | 132/33 kV Transformer-GT2 | 2019-03-07 10:16 | 2019-03-07 15:54 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-03-09 08:46 | 2019-03-09 10:54 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2019-03-10 11:04 | 2019-03-10 16:20 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2019-03-11 10:00 | 2019-03-11 15:10 | 5:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2019-03-11 10:01 | 2019-03-11 18:09 | 8:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-03-12 10:20 | 2019-03-12 11:45 | 1:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-03-12 13:14 | 2019-03-12 13:20 | 0:06 | S/O | Due to relay test | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2019-03-14 07:04 | 2019-03-14 09:12 | 2:08 | S/O | Due to 33 kV feeder maintenance | 50 | 106.6667 | Power interruption
Bhulta | 132/33 kV Transformer-T1 | 2019-03-15 09:50 | 2019-03-15 15:12 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2019-03-15 20:15 | 2019-03-16 00:44 | 4:29 | S/O | Due to differential signal | 8 | 35.8667 | Power interruption
Kabirpur | 132/33 kV Transformer-T-3 | 2019-03-17 10:34 | 2019-03-17 11:58 | 1:24 | S/O | Due to 33 kV feeder maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T2 & T3 & 33 kV Bus | 2019-03-19 06:40 | 2019-03-19 08:55 | 2:15 | S/O | Due to maintenance work | 50 | 112.5 | Power interruption
Joydevpur | 132/33 kV Transformer-T1 | 2019-03-19 19:31 | 2019-03-19 19:57 | 0:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 with 33 kV Bus | 2019-03-22 06:45 | 2019-03-22 09:30 | 2:45 | S/O | Due to D/W work | 30 | 82.5 | Power interruption
Jamalpur | 132/33 kV Transformer-T2 | 2019-03-22 06:30 | 2019-03-22 10:45 | 4:15 | S/O | Due to C/M work | 20 | 60 | Power interruption
| 33 kV Bus | 2019-03-22 06:30 | 2019-03-22 09:30 | 3:00 | S/O
Mymensingh | 132/33 kV Transformer-T2 with 33 kV Bus | 2019-03-24 07:15 | 2019-03-24 07:48 | 0:33 | S/O | Due to maintenance work | 24 | 13.2 | Power interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-03-24 10:28 | 2019-03-24 13:10 | 2:42 | S/O | Due to 33 kV CT maintenance
Joydevpur | 132/33 kV Transformers-T-4 | 2019-03-25 06:18 | 2019-03-25 09:31 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformers- T-5 | 2019-03-25 06:18 | 2019-03-25 09:56 | 3:38 | S/O |  | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2019-03-25 08:35 | 2019-03-25 20:58 | 12:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-TR-2 | 2019-03-28 07:38 | 2019-03-28 17:23 | 9:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kaliakoir 400/132 kV T2 | 2019-03-29 08:37 | 2019-03-29 16:51 | 8:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kaliakoir 400/132 kV T2 | 2019-03-30 08:19 | 2019-03-30 16:47 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 122:37 |  | Unserved Energy: |  | 412.4
Page: 2/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Munshiganj | 132/33 kV Transformer-T1 | 2019-03-01 08:00 | 2019-03-03 15:57 | 55:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | 132/33 kV Transformer-T3 | 2019-03-02 19:10 | 2019-03-04 18:30 | 47:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 | 2019-03-04 07:42 | 2019-03-04 18:05 | 10:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2019-03-04 08:11 | 2019-03-04 10:54 | 2:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T02 | 2019-02-26 14:35 | 2019-03-06 16:53 | 194:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2019-03-09 07:11 | 2019-03-09 09:43 | 2:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-03-09 10:54 | 2019-03-09 17:49 | 6:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Dhanmondi | 132/33 kV Transformer-T1(New) |  | 2019-03-09 12:55 |  | S/O
Hasnabad | 132/33 kV Transformer-T2 | 2019-03-09 17:26 | 2019-03-09 22:24 | 4:58 | S/O | Due to smoke was coming out from 33 kV Y-phase CT | 0 | 0 | No interruption
Shyampur(Old) | 132/33 kV Transformer-T4 | 2019-03-09 03:40 | 2019-03-10 02:02 | 22:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T1 | 2019-03-12 08:14 | 2019-03-12 16:53 | 8:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnagat | 230 kV Bus-1 | 2019-03-13 09:50 | 2019-03-13 13:35 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T1 | 2019-03-14 10:02 | 2019-03-14 20:41 | 10:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | 132 kV Bus-2 | 2019-03-15 07:24 | 2019-03-15 09:34 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2019-03-15 07:40 | 2019-03-15 14:32 | 6:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | 132 kV Bus-2 | 2019-03-15 07:24 | 2019-03-15 09:34 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2019-03-15 07:40 | 2019-03-15 14:32 | 6:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 | 2019-03-19 08:04 | 2019-03-19 17:24 | 9:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2019-03-20 08:54 | 2019-03-20 14:07 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2019-03-23 08:27 | 2019-03-23 13:05 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T2 | 2019-03-23 08:02 | 2019-03-24 13:40 | 29:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T1 | 2019-03-25 06:13 | 2019-03-25 23:05 | 16:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T3 | 2019-03-25 08:35 | 2019-03-25 14:50 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T1 | 2019-03-27 07:10 | 2019-03-27 15:10 | 8:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T1 | 2019-03-27 07:55 | 2019-03-27 10:22 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | 230/132 kV Transformer-T02 | 2019-03-30 10:15 | 2019-03-30 11:15 | 1:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2019-03-30 08:30 | 2019-03-30 15:50 | 7:20 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 479:18 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV Transformer-T1 | 2019-03-12 10:11 | 2019-03-12 12:01 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-03-12 12:08 | 2019-03-12 13:30 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2019-03-14 06:41 | 2019-03-14 08:06 | 1:25 | S/O | Due to C/M work | 15 | 21.25 | Power interruption
| 132 kV Bus-A | 2019-03-15 07:11 | 2019-03-15 09:35 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2019-03-15 07:54 | 2019-03-15 10:13 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-03-15 07:53 | 2019-03-15 10:13 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T3 & 33 kV Bus | 2019-03-21 15:09 | 2019-03-21 16:08 | 0:59 | S/O | Due to maintenance work | 25 | 24.5833 | Power interruption
Shahmirpur | 132/33 kV Transformers-T1 | 2019-03-22 10:19 | 2019-03-23 18:28 | 32:09 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-03-22 10:19 | 2019-03-23 18:30 | 32:11 | S/O |  | 0 | 0 | No interruption
Page: 3/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Halishahar | 132 kV Bus | 2019-03-23 07:01 | 2019-03-23 12:27 | 5:26 | S/O | Due to C/M work | 60 | 326 | Power interruption
Sikalbaha | 230/132 kV Transformer T02 | 2019-03-20 14:09 | 2019-03-26 10:56 | 140:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
Juldah | 132 kV Bus | 2019-03-30 08:22 | 2019-03-30 17:42 | 9:20 | S/O | Due to D/W work | 15 | 140 | Power interruption
|  |  | Total : | 232:32 |  | Unserved Energy: |  | 511.8333
Cumilla Grid Circle :
Bibiyana | 400/230 kV Transformer-ICT2 | 2019-03-02 08:52 | 2019-03-02 12:13 | 3:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T2 | 2019-03-02 12:45 | 2019-03-02 17:38 | 4:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T2 | 2019-03-03 11:11 | 2019-03-03 12:53 | 1:42 | S/O | Due to Delta test | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2019-03-03 07:56 | 2019-03-03 11:09 | 3:13 | S/O |  | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformers-T1 | 2019-03-04 09:15 | 2019-03-04 12:05 | 2:50 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-ICT2 | 2019-03-05 08:57 | 2019-03-05 16:11 | 7:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T2 | 2019-03-06 09:40 | 2019-03-06 11:40 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-03-07 11:08 | 2019-03-07 14:53 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2019-03-07 15:33 | 2019-03-07 17:25 | 1:52 | S/O | Due to delta test | 0 | 0 | No interruption
Ramganj | 33 kV full Bus | 2019-03-08 08:22 | 2019-03-08 16:06 | 7:44 | S/O | Due to C/M work | 10 | 77.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2019-03-08 15:05 | 2019-03-08 18:12 | 3:07 | S/O | Due to PBS work | 0 | 0 | No interruption
Chandpur | 33 kV Bus | 2019-03-09 06:05 | 2019-03-09 09:10 | 3:05 | S/O | Due to maintenance work | 42 | 129.5 | Power interruption
Bibiyana | 230 kV Bus-2 with Bus-2 | 2019-03-09 09:09 | 2019-03-09 17:12 | 8:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2019-03-10 09:58 | 2019-03-10 12:54 | 2:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformers-T3 | 2019-03-10 09:23 | 2019-03-10 11:43 | 2:20 | S/O | Due to Delta test | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2019-03-10 12:55 | 2019-03-10 18:57 | 6:02 | S/O | Due to D/W work | 20 | 120 | Power interruption
Kulaura | 132/33 kV Transformer-T1 | 2019-03-11 10:23 | 2019-03-11 14:13 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400 kV Bus-1 | 2019-03-11 10:16 | 2019-03-11 21:51 | 11:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-03-13 12:28 | 2019-03-13 14:58 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2019-03-14 06:42 | 2019-03-14 07:53 | 1:11 | S/O | Due to 33 kV feeder maintenance | 36 | 42.6 | Power interruption
Cumilla(N) | 230/132 kV Transformer-T01 | 2019-03-16 08:35 | 2019-03-19 17:30 | 80:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2019-03-20 12:02 | 2019-03-20 13:43 | 1:41 | S/O | Due to protection test | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T2 & T3 | 2019-03-24 09:42 | 2019-03-24 16:22 | 6:40 | S/O | Due to tan delta test | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2019-03-24 11:37 | 2019-03-24 12:25 | 0:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-03-25 09:40 | 2019-03-25 12:05 | 2:25 | S/O | Due to replacement work at 33 kV side | 15 | 31.25 | Power interruption
Bibiyana | 400/230 kV Transformer-T1 | 2019-03-27 08:12 | 2019-03-27 16:52 | 8:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| 400/230 kV Transformer-ICT-2 | 2019-03-28 06:59 | 2019-03-28 13:17 | 6:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2019-03-28 14:38 | 2019-03-28 17:30 | 2:52 | S/O | Due to tan delta test | 0 | 0 | No interruption
Bibiyana | 400 kV Bus-1 | 2019-03-30 09:02 | 2019-03-30 17:08 | 8:06 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 159:57 |  | Unserved Energy : |  | 400.6833
Page: 4/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformer-T1 | 2019-03-01 09:04 | 2019-03-01 12:12 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-03-02 08:31 | 2019-03-02 11:41 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T6 | 2019-03-02 09:00 | 2019-03-03 16:33 | 31:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna | 230 kV Bus-1 | 2019-03-04 08:10 | 2019-03-04 16:34 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2019-03-05 08:37 | 2019-03-05 17:05 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T4 | 2019-03-05 10:30 | 2019-03-05 17:58 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2019-03-06 09:30 | 2019-03-06 17:58 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-03-08 08:40 | 2019-03-08 18:08 | 9:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-03-09 08:47 | 2019-03-09 14:12 | 5:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2019-03-10 09:07 | 2019-03-10 13:18 | 4:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | 132 kV main Bus | 2019-03-15 07:57 | 2019-03-15 16:46 | 8:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T3(New) |  | 2019-03-21 23:00 | [5 empty] | Comissioning works
Madaripur | 132/33 kV Transformers-T1 & T3 | 2019-03-22 07:56 | 2019-03-22 11:01 | 3:05 | S/O | Due to C/M work | 30 | 92.5 | Power interruption
| 132/33 kV Transformer-T3 | 2019-03-25 07:21 | 2019-03-25 19:09 | 11:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main Bus-A | 2019-03-25 07:22 | 2019-03-25 14:30 | 7:08 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-B | 2019-03-25 14:45 | 2019-03-25 18:30 | 3:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2019-03-27 07:30 | 2019-03-27 17:20 | 9:50 | S/O | Due to C/M work at 33 kV side | 20 | 196.6667 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2019-03-28 07:46 | 2019-03-28 07:54 | 0:08 | S/O | Due to reconductoring work | 60 | 8 | Power interruption
Madaripur | 132 kV Bus-A | 2019-03-28 07:36 | 2019-03-28 10:55 | 3:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132 kV Bus-B | 2019-03-28 11:05 | 2019-03-28 16:55 | 5:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2019-03-30 07:10 | 2019-03-30 18:30 | 11:20 | S/O | Due to C/M work at 33 kV side | 20 | 226.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2019-03-30 12:57 | 2019-03-30 15:20 | 2:23 | S/O | Due to D/W work | 65 | 154.9167 | Power interruption
| 33 kV Bus | 2019-03-31 07:27 | 2019-03-31 10:25 | 2:58 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 480:00 |  | Unserved Energy : |  | 678.75
HVDC Grid Circle :
Bottail | 33 kV Bus | 2019-03-15 08:08 | 2019-03-15 09:37 | 1:29 | S/O | Due to maintenance work | 30 | 44.5 | Power interruption
Gallamari | 132/33 kV Transformers-T2 | 2019-03-18 10:34 | 2019-03-18 12:48 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-03-18 12:53 | 2019-03-18 13:48 | 0:55 | S/O |  | 0 | 0 | No interruption
Ishurdi | 33 kV Bus-1 | 2019-03-20 06:17 | 2019-03-20 08:05 | 1:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Bottail | 33 kV Bus-A & B | 2019-03-22 08:45 | 2019-03-22 12:24 | 3:39 | S/O | Due to D/W work | 60 | 219 | Power interruption
Chuadanga | 132/33 kV Transformer-T1 | 2019-03-29 08:13 | 2019-03-30 11:54 | 27:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-03-30 11:58 | 2019-03-30 15:43 | 3:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 33 kV Bus section--2 | 2019-03-30 15:15 | 2019-03-30 16:38 | 1:23 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 42:54 |  | Unserved Energy : |  | 263.5
Page: 5/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Purbasadipur | 132/33 kV Transformer T3 & 33 kV Bus | 2019-03-01 08:14 | 2019-03-01 16:56 | 8:42 | S/O | Due to C/M work | 20 | 174 | Power interruption
Saidpur | 132/33 kV Transformer-T4 | 2019-03-02 10:30 | 2019-03-02 17:10 | 6:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T1 | 2019-03-03 08:58 | 2019-03-03 08:58 | 0:00 | S/O | Due to reconductoring work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T1 | 2019-03-04 10:05 | 2019-03-05 15:20 | 29:15 | S/O | Due to CB change | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-03-05 15:40 | 2019-03-05 15:44 | 0:04 | S/O | Due to replacement work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2(New) |  | 2019-03-05 15:36 |  |  |  | 0 | 0 | Comissioning works
Sirajganj | 132/33 kV Transformer-T4 | 2019-03-08 07:52 | 2019-03-28 17:56 | 490:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 33 kV full Bus | 2019-03-09 08:00 | 2019-03-09 18:35 | 10:35 | S/O | Due to C/M work | 25 | 264.5833 | Power interruption
Amnura | 132/33 kV Transformer-T2 | 2019-03-11 23:08 | 2019-03-12 01:08 | 2:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 33 Bus-2 | 2019-03-15 06:12 | 2019-03-15 08:25 | 2:13 | S/O | Due to C/M work | 30 | 66.5 | Power interruption
Rajshahi | 132/33 kV Transformer-T2 | 2019-03-21 17:07 | 2019-03-21 18:27 | 1:20 | S/O | Due to replacement work | 0 | 0 | No interruption
Sirajganj | 132 kV main Bus | 2019-03-22 06:11 | 2019-03-22 13:53 | 7:42 | S/O | Due to D/W work | 60 | 462 | Power interruption
Barapukuria | 132/33 kV Transformer-IBT2 & IBT6 | 2019-03-23 06:41 | 2019-03-23 18:40 | 11:59 | S/O | Due to C/M work | 200 | 2396.6667 | Power interruption
Thakurgaon | 33 kV full Bus | 2019-03-29 06:05 | 2019-03-29 19:25 | 13:20 | S/O | Due to C/M work | 60 | 800 | Power interruption
Satkhira | 132/33 kV Transformer-T2 | 2019-03-30 08:03 | 2019-03-30 17:55 | 9:52 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 593:46 |  | Unserved Energy : |  | 4163.75
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 2111:04 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF_LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | Savar-Aminbazar 132 kV line-1 | 2019-03-02 09:36 | 2019-03-02 16:30 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-03-02 09:49 | 2019-03-02 18:10 | 8:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-1 | 2019-03-03 09:22 | 2019-03-03 16:36 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV line-1 | 2019-03-03 13:51 | 2019-03-03 15:11 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Agargaon-Cantonment 132 kV line-2 | 2019-03-03 15:14 | 2019-03-03 15:33 | 0:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kalyanpur 132 kV line-2 | 2019-03-04 09:27 | 2019-03-04 09:42 | 0:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 & 2 | 2019-03-05 12:54 | 2019-03-05 16:10 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kallyanpur-Aminbazar 132 kV line-1 | 2019-03-05 13:41 | 2019-03-05 16:09 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kalyanpur 132 kV line-1 | 2019-03-07 10:18 | 2019-03-07 16:30 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2019-03-11 09:58 | 2019-03-11 16:26 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | Netrakona-Mymensingh 132 kV line-2 | 2019-03-12 09:56 | 2019-03-12 13:10 | 3:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Netrakona-Mymensingh 132 kV line-1 | 2019-03-13 08:40 | 2019-03-13 13:20 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-03-19 09:28 | 2019-03-19 16:51 | 7:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2019-03-21 08:20 | 2019-03-21 14:10 | 5:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2019-03-24 08:35 | 2019-03-24 17:05 | 8:30 | S/O | Due to replacement work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-03-25 10:46 | 2019-03-28 13:28 | 74:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 & Bus-A | 2019-03-25 09:56 | 2019-03-25 16:56 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 154:06 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Cumilla(N) 132 kV line-1 | 2019-03-02 09:00 | 2019-03-02 14:53 | 5:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghnaghat-Cumilla(N) 230 kV line-2 | 2019-03-03 09:55 | 2019-03-03 14:00 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-1 | 2019-03-04 10:21 | 2019-03-04 21:45 | 11:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur 230 S/S-Haripur AES 360 MW P/S 132 kV line-1 | 2019-03-04 10:15 | 2019-03-16 07:07 | 284:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur 230 S/S-Haripur AES 360 MW P/S 132 kV line-2 | 2019-03-05 09:20 | 2019-03-11 12:44 | 147:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2019-02-27 10:28 | 2019-03-06 13:52 | 171:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-03-05 08:14 | 2019-03-05 13:18 | 5:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-2 | 2019-03-09 09:02 | 2019-03-09 15:14 | 6:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (New) 132 kV line-1 | 2019-03-10 10:43 | 2019-03-10 20:14 | 9:31 | S/O | Due to PT replacement | 60 | 571 | Power interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2019-03-13 09:01 | 2019-03-13 16:50 | 7:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line | 2019-03-14 12:18 | 2019-03-14 16:02 | 3:44 | S/O | Due to protection test | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-03-15 12:21 | 2019-03-15 16:13 | 3:52 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-2 | 2019-03-15 16:24 | 2019-03-15 17:40 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 230 kV line | 2019-03-18 10:46 | 2019-03-18 15:09 | 4:23 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shyampur-APR 230 kV line | 2019-03-18 08:08 | 2019-03-18 10:35 | 2:27 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shyampur(N)-Shyampur (Old) 132 kV line-2 | 2019-03-19 09:21 | 2019-03-19 12:07 | 2:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-2 | 2019-03-19 07:15 | 2019-03-19 09:11 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur(Old) 132 kV line-1 | 2019-03-20 09:40 | 2019-03-20 12:04 | 2:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-1 | 2019-03-31 19:35 | 2019-04-01 00:58 | 5:23 | S/O | Due to post insulator broken at Siddhirganj S/S | 0 | 0 | No interruption
|  |  | Total : | 681:49 |  | Unserved Energy: |  | 571
Chattogram Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-03-13 12:05 | 2019-03-13 15:59 | 3:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV line | 2018-04-10 10:42 | 2019-03-20 17:41 | 8262:59 | S/O |  | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV line-1 | 2018-03-27 09:42 | 2018-03-27 14:54 | 5:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2018-03-29 07:37 | 2018-03-29 15:48 | 8:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV line-1 | 2018-03-30 07:30 | 2018-03-30 16:15 | 8:45 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 8285:07 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-2 | 2019-03-01 09:52 | 2019-03-02 14:36 | 28:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2019-03-02 18:10 | 2019-03-02 23:16 | 5:06 | S/O | Due to CT problem | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV line-1 | 2019-03-03 11:30 | 2019-03-03 12:10 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV line | 2019-03-04 08:29 | 2019-03-04 11:02 | 2:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2019-03-04 10:44 | 2019-03-04 14:15 | 3:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| Feni-Chowmuhani 132 kV line-2 | 2019-03-05 11:35 | 2019-03-05 14:19 | 2:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2019-03-05 08:59 | 2019-03-05 16:09 | 7:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-2 | 2019-03-05 10:06 | 2019-03-05 14:19 | 4:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2019-03-05 10:55 | 2019-03-06 15:06 | 28:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2019-03-06 12:15 | 2019-03-06 13:53 | 1:38 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria S/S | B.Baria S/S-B.Baria P/S 132 kV line | 2019-03-04 12:00 | 2019-03-06 15:01 | 51:01 | S/O | Due to restoring auxiliary supply | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-1 | 2019-03-06 14:20 | 2019-03-06 15:19 | 0:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj P/S | Fenchuganj P/S-Sylhet 132 kV line | 2019-03-08 07:08 | 2019-03-08 17:46 | 10:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-2 | 2019-03-09 07:09 | 2019-03-09 17:58 | 10:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana S/S-Bibiyana 400 kV line | 2019-03-12 12:14 | 2019-03-12 16:06 | 3:52 | S/O | Due to project work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 & 2 | 2019-03-13 09:01 | 2019-03-13 14:08 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 132 kV line-1 | 2019-03-13 12:07 | 2019-03-13 12:47 | 0:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shahjibazar-Bibiyana 132 kV line-1 | 2019-03-13 12:37 | 2019-03-13 14:57 | 2:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana S/S-Bibiyana 400 kV line | 2019-03-13 15:56 | 2019-03-14 10:49 | 18:53 | S/O | Due to project work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 132 kV line-2 | 2019-03-13 14:59 | 2019-03-13 15:05 | 0:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2019-03-23 08:54 | 2019-03-23 17:08 | 8:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-2 | 2019-03-24 09:01 | 2019-03-24 17:11 | 8:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2019-03-24 08:06 | 2019-03-24 15:21 | 7:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2019-01-10 14:50 | 2019-03-24 20:40 | 1757:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | Chandpur-Cumilla(N) 132 kV line-1 | 2019-03-26 09:04 | 2019-03-26 09:04 | 0:00 | S/O | Due to reconducting work | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-1 | 2019-03-28 10:00 | 2019-03-28 16:22 | 6:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1809:50 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | Barisal-Madaripur 132 kV line-1 | 2019-03-01 08:55 | 2019-03-01 17:56 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal-Madaripur 132 kV line-1 | 2019-03-02 13:11 | 2019-03-02 17:30 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Madaripur 132 kV line-1 | 2019-03-03 13:15 | 2019-03-03 17:47 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal(N)-Madaripur 132 kV line-2 | 2019-03-04 08:13 | 2019-03-04 14:19 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal(N)-Madaripur 132 kV line-2 | 2019-03-05 07:59 | 2019-03-05 08:58 | 0:59 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barisal(N)-Madaripur 132 kV line-2 | 2019-03-06 07:41 | 2019-03-06 16:08 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Modhumoti P/S 132 kV line | 2019-03-08 10:55 | 2019-03-09 18:10 | 31:15 | S/O | Due to project work | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV line | 2019-03-08 09:23 | 2019-03-08 17:57 | 8:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-03-08 15:20 | 2019-03-08 16:20 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV line | 2019-03-09 09:03 | 2019-03-09 17:53 | 8:50 | S/O | Due to C/M work | 30 | 265 | Power interruption
| Mongla-Bagerhat 132 kV line | 2019-03-11 07:01 | 2019-03-11 17:03 | 10:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2019-03-12 16:38 | 2019-03-12 17:58 | 1:20 | S/O | Due to loop test | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2019-03-13 09:05 | 2019-03-13 17:47 | 8:42 | S/O | Due to C/M work | 30 | 180 | Power interruption 09:05 to 15:05
Mongla | Mongla-Bagerhat 132 kV line | 2019-03-15 08:57 | 2019-03-15 17:25 | 8:28 | S/O | Due to C/M work | 32 | 270.9333 | Power interruption 09:05 to 15:05
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2019-03-15 10:28 | 2019-04-10 15:49 | 629:21 | S/O | Due to reconducting work | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Mongla | Mongla-Bagerhat 132 kV line | 2019-03-16 09:00 | 2019-03-16 15:21 | 6:21 | S/O | Due to C/M work | 32 | 203.2 | Power interruption 09:05 to 15:05
Baghabari | Baghabari-Ishurdi 132 kV line | 2019-03-16 08:38 | 2019-03-16 19:27 | 10:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2019-03-24 09:03 | 2019-03-25 09:28 | 24:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-03-27 07:05 | 2019-03-27 10:32 | 3:27 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 785:58 |  | Unserved Energy: |  | 919.1333
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV line-1 & 2 | 2019-03-08 06:58 | 2019-03-08 16:54 | 9:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2019-03-12 11:38 | 2019-03-12 20:08 | 8:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2019-03-13 11:28 | 2019-03-13 16:34 | 5:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | Bottail-Jhenidah 132 kV line-2 | 2019-02-22 17:30 | 2019-03-24 17:13 | 719:43 | S/O | Due to reconducting work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Chuadanga 132 kV line | 2019-03-29 08:44 | 2019-03-29 09:52 | 1:08 | S/O | Due to C/M work | 40 | 45.3333 | Power interruption
|  |  | Total : | 734:27 |  | Unserved Energy: |  | 45.3333
Bogura Grid Circle :
Amnura | Amnura S/S-Amnura P/S 132 kV line | 2019-03-01 08:40 | 2019-03-01 12:39 | 3:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line | 2019-03-01 09:12 | 2019-03-01 12:08 | 2:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Palashbari 132 kV line-1 | 2019-03-02 07:05 | 2019-03-02 16:28 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 232 kV line | 2019-03-15 06:30 | 2019-03-15 17:52 | 11:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line | 2019-03-15 06:29 | 2019-03-15 17:50 | 11:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2019-03-23 09:32 | 2019-03-23 15:15 | 5:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV Ckt-2 | 2019-03-29 08:05 | 2019-03-29 19:10 | 11:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2019-03-29 10:25 | 2019-03-29 17:06 | 1:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2019-03-30 08:20 | 2019-03-30 17:30 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 66:33 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2019-03-06 14:38 | 2019-03-06 16:12 | 1:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Maniknagar-Haripur 132 kV line | 2019-03-08 09:25 | 2019-03-08 20:26 | 11:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2019-03-12 09:19 | 2019-03-12 17:34 | 8:15 | S/O | Due to replacement work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2019-03-16 10:10 | 2019-03-16 14:29 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 1:34 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 12519:24 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March' 2019
| Area | Previous Month (February 2019) |  |  |  | Current Month (March 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 8 | 7 | 23 | 38 | 22 | 6 | 54 | 82
2 | Dhaka (South) Grid Circle. | 28 | 4 | 39 | 71 | 32 | 10 | 46 | 88
3 | Chattogram Grid Circle. | 12 | 11 | 23 | 46 | 9 | 9 | 17 | 35
4 | Cumilla Grid Circle. | 8 | 4 | 44 | 56 | 22 | 4 | 55 | 81
5 | Khulna Grid Circle. | 23 | 3 | 35 | 61 | 17 | 8 | 41 | 66
6 | Bheramara HVDC Grid Circle | 7 | 4 | 13 | 24 | 6 | 6 | 13 | 25
7 | Bogura Grid Circle. | 8 | 5 | 23 | 36 | 7 | 11 | 25 | 43
8 | Others | 3 | - | 1 | 4 | 1 |  | 4 | 5
9 | Total | 97 | 38 | 201 | 336 | 116 | 54 | 255 | 425
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March' 2019
| Area | Previous Month (February 2019) |  |  |  | Current Month (March 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | - | 100.47 | 59.33 | 159.8 | 292.82 | 35.87 | 412.4 | 741.09
2 | Dhaka (South) Grid Circle. | 75.89 | 36.76 | 1150 | 1262.65 | 157.43 | 188.99 | 571 | 917.42
3 | Chattogram Grid Circle. | 551.25 | 129.2 | 210.33 | 890.78 | 525 | 21.19 | 511.83 | 1058.02
4 | Cumilla Grid Circle. | 6 | 68.75 | 171.33 | 246.08 | 738.46 |  | 400.68 | 1139.14
5 | Khulna Grid Circle. | 116.25 | - | 127.87 | 244.12 | 20.46 | 13 | 1589.89 | 1623.35
6 | Bheramara HVDC Grid Circle | 13.6 | 14.5 | 136 | 164.1 | 2.58 | 42.37 | 308.83 | 353.78
7 | Bogura Grid Circle. | 104.7 | 211.28 | 933.24 | 1249.22 | 226.15 | 315.23 | 4163.75 | 4705.13
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 867.69 | 560.96 | 2788.1 | 4216.75 | 1962.9 | 616.65 | 7958.38 | 10537.93
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 2 | 7 | 9 | 2 | 1 | 6 | 466.67
2 | Dhaka (South) | 5031.6 | 4 | - | 4 | 1 | 1 | 2 | 217.5
3 | Chattogram | 2042 | 1 | 4 | 5 | 1 | 1 | 3 | 518.35
4 | Khulna | 2434 | 5 | 4 | 9 | 4 | 1 | 4 | 756.71
5 | Bheramara (HVDC) | 2423.3 | 3 | 2 | 5 | 1 | 1 | 3 | 308.45
6 | Bogura | 3145.6 | 5 | 6 | 11 | 2 | 1 | 8 | 4333.58
7 | Cumilla | 2981 | 1 | 5 | 6 | - | - | 6 | 975.93
| Total | 23365.5 | [6 empty] | 7577.19
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.92%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.65%
4 | Khulna | 99.95%
5 | Bheramara (HVDC) | 99.96% | [6 empty] | Executive Engineer
6 | Bogura | 99.96% | [6 empty] | Information Management Division
7 | Cumilla | 99.78% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 | - | 2 | - | - | 2 | 274.42
2 | Dhaka (South) | 990.29 |  | 4 | 1 | 5 | 2 | 1 | 2 | 699.93
3 | Chattogram | 917 | 20+9(Partial) | 3 | - | 3 | 2 | 1 | - | 124.45
4 | Khulna | 1238.4 | 21 | 1 | 4 | 5 | 1 | - | 4 | 922.73
5 | Bheramara (HVDC) | 598.7 |  | - | 1 | 1 | - | - | 1 | 45.33
6 | Bogura | 1803.3 | 38 | 3 |  | 3 | 1 | - | 2 | 324.55
7 | Cumilla | 1648.16 | 17 | 3 |  | 3 | 1 | 1 | 1 | 163.22
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 2554.63
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.91%
2 | Dhaka (South) | 98.82%
3 | Chattogram | 99.97%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.95% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 100% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-03-18 | 16 |  | 6 | 08hr58 min | 1 | 02hr12 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:March' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Sherpur | 1 | 4:29 | 8 | 35.8667 | Due to bursting of 132/33 klV Transformer T1
Kishoreganj | 1 | 0:04 | 90 | 6 | Due to tripping of 132/33 kV Transformer T2
Mymensingh | 1 | 0:06 | 124 | 12.4 | Due to tripping of 132/33 kV Transformers T1 & T2
Aminbazar | 1 | 3:04 | 85 | 260.6667 | Due to tripping of Aminbazar-Mirpur 132 kV line-2
Tongi | 1 | 2:45 | 5 | 13.75 | Due to tripping of Tongi-Kabirpur 132 kV line-1
Kadda | 1 | 0:10 | 10 | 1.6667 | Due to S/D of 132 kV Bus-1
Mymensingh | 1 | 2:08 | 50 | 106.6667 | Due to S/D of 132/33 kV Transformer T2
Sherpur | 1 | 0:10 | 8 | 35.8667 | Due to S/D of 132/33 kV Transformer T1
Kishoreganj | 2 | 2:15 | 50 | 112.5 | Due to S/D of 132/33 kV Transformers T2 & T3
|  | 2:45 | 30 | 82.5 | Due to S/D of 132/33 kV Transformer T3
Jamalpur | 1 | 4:15 | 20 | 60 | Due to S/D of 132/33 kV Transformer T2
Mymensingh | 1 | 0:33 | 24 | 13.2 | Due to S/D of 132/33 kV Transformer T2
Hasnabad | 4 | 0:38 | 45 | 28.5 | Due to tripping of 132/33 kV Transformer T2
|  | 0:28 | 110 | 51.3333 | Due to tripping of 33 kV Bus
|  | 0:53 | 100 | 88.3333 | Due to 33 kV bushing burst
|  | 0:37 | 80 | 49.3333 | Due to bursting of 33 kV CB
Rampura | 1 | 0:29 | 100 | 48.3333 | Due to tripping of Rampura-Bashundhara 132 kV line
Haripur | 3 | 1:57 | 18 | 35.1 | Due to tripping of Haripur-Shyampur 132 kV line
|  | 0:30 | 31 | 15.5 | Due to tripping of Haripur-Ullon 132 kV line
|  | 0:01 | 30 | 30 | Due to tripping of Haripur-Madanganj 132 kV line
Shyampur(Old) |  | 9:31 | 60 | 571 | Due to S/D of Shyampur-Shyampur (new) 132 132 kV line
Sikalbaha | 1 | 0:23 | 17 | 6.5167 | Due to red-hot maintenance of 132/33 kV Transformer T3
Cox'sbazar | 1 | 1:28 | 10 | 14.6667 | Due to tripping of Cox'sbazar-Dohazari 132 kV line-1
Hathazari | 1 | 0:42 | 750 | 525 | Due to tripping of Hathazari-Baroitihat 132 kV line-1 & 2
Bakulia | 1 | 1:25 | 15 | 21.25 | Due to S/D of 132/33 kV Transformer T2
Dohazari | 1 | 0:59 | 25 | 24.5833 | Due to S/D of 132/33 kV Transformer T3
Halishahar |  | 5:26 | 60 | 326 | Due to S/D of 132 kV Bus
Juldah | 1 | 9:20 | 15 | 140 | Due to S/D of 132 kV Bus
Fenchuganj | 4 | 2:57 | 195 | 575.25 | Due to tripping of 230/132 kV Transformer T2
|  | 0:31 | 14 | 7.2333 | Due to tripping of Fenchuganj S/S-Sylhet 132 kV line
|  | 0:15 | 30 | 7.5 | Due to tripping of Fenchuganj S/S-Sylhet 132 kV line
|  | 0:31 | 59 | 148.4833 | Due to tripping of Fenchuganj S/S-Sylhet 132 kV line
Ramganj | 1 | 7:44 | 10 | 77.3333 | Due to S/D of 33 kV Full Bus
Chandpur | 1 | 3:05 | 42 | 129.5 | Due to S/D of 33 kV Full Bus
Ramganj | 1 | 6:02 | 20 | 120 | Due to S/D of 132/33 kV Transformer T2
Chowmuhani | 1 | 1:11 | 36 | 42.6 | Due to S/D of 132/33 kV Transformer T1
Cumilla(N) | 1 | 2:25 | 15 | 31.25 | Due to S/D of 132/33 kV Transformer T4
Faridpur | 1 | 0:04 | 60 | 4 | Due to tripping of 230/132 kV Transformers T1 & T2
Barisal(S) | 1 | 0:14 | 52 | 12.1333 | Due to tripping of 132/33 kV Transformers T1 & T2
Madaripur | 1 | 0:04 | 11 | 0.73333 | Due to tripping of 132/33 kV Transformer T3
Barisal(S) | 2 | 0:13 | 60 | 13 | Due to Oil leakge of 132/33 kV Transformer T2
| 1 | 0:18 | 12 | 3.6 | Due to tripping of Barisal-Patuakhali 132 kV line
Madaripur | 1 | 3:05 | 30 | 92.5 | Due to S/D of 132/33 kV Transformers T1 & T3
Barisal | 3 | 9:50 | 20 | 196.6667 | Due to S/D 132/33 kV Transformer-T2
|  | 11:20 | 20 | 226.6667 | Due to S/D 132/33 kV Transformer-T1
|  | 2:23 | 65 | 154.9167 | Due to S/D 132/33 kV Transformer-T2
Mongla | 1 | 8:50 | 30 | 265 | Due to S/D of Mongla-Bagerhat 132 kV line
Bagerhat | 1 | 8:42 | 30 | 180 | Due to S/D of Bagerhat-Mongla 132 kV line
Mongla | 2 | 8:28 | 32 | 270.9333 | Due to S/D of Mongla-Bagerhat 132 kV line
|  | 6:21 | 32 | 203.2 | Due to S/D of Mongla-Bagerhat 132 kV line
Shahjadpur | 1 | 0:47 | 10 | 7.8333 | Due to re hot maintenance of 132/33 kV Transformer T1
Bottail | 2 | 1:14 | 28 | 34.5333 | Due to re hot maintenance of 132/33 kV Transformer T1
|  | 0:05 | 31 | 2.5833 | Due to tripping of 132/33 kV Transformer T2
Bottail | 2 | 1:29 | 30 | 44.5 | Due to S/D of 33 kV Bus
|  | 3:39 | 60 | 219 | Due to S/D of 33 kV Bus-A & B
Jhenidah | 1 | 1:08 | 40 | 45.3333 | Due to S/D of Jhenidah-Chuadanga 132 kV line
Rangpur | 1 | 0:30 | 7 | 3.5 | Due to re hot maintenance of 132/33 kV Transformer T3
Amnura | 2 | 2:07 | 32 | 67.7333 | Due to bursting of 132/33 kV Transformer T3
| 1 | 0:32 | 100 | 53.3333 | Due to bursting of 132/33 kV Transformer T3
Natore | 1 | 1:24 | 14 | 33.6 | Due to tripping of 132/33 kV Transformer T3
Pabna |  | 0:14 | 50 | 11.6667 | Due to tripping of 132/33 kV Transformers T1 & T2
Thakurgaon | 1 | 0:47 | 60 | 47 | Due to red-hot maintenance of 33 kV Bus
Rangpur | 1 | 3:04 | 60 | 184 | Due to tripping of Rangpur-Lalmonirhat 132 kV line
Bogura(New) | 1 | 2:12 | 60 | 132 | Due to tripping of Bogura(New)-Bogura (Old) 132 kV line-2
Rajshahi | 1 | 0:19 | 27 | 8.55 | Due to tripping of Rajshahi-Natore 132 kV line-1
Purbasadipur | 1 | 8:42 | 20 | 174 | Due to S/D 132/33 kV Transformer-T3
Ishurdi | 1 | 10:35 | 25 | 264.5833 | Due to S/D of 33 kV Full Bus
Naogaon | 1 | 2:13 | 30 | 66.5 | Due to S/D of 33 kV Bus-2
Sirajganj | 1 | 7:42 | 60 | 462 | Due to S/D of 132 kV main bus
Barapukuria | 1 | 11:59 | 200 | 2396.6667 | Due to S/D 132/33 kV Transformer-IBT2 & IBT6
Thakurgaon | 1 | 13:20 | 60 | 800 | Due to S/D of 33 kV Full Bus
| Total unserved energy : |  |  | 10537.95 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 122 | 25 | 2019-03-03 | 18:30
2 | Munsiganj | 112 | 30 | 2019-03-03 | 20:00
3 | Sonargaon | 71 | 12 | 2019-03-03 | 19:00
4 | Shyampur | 187 | 14 | 2019-03-03 | 24:00
5 | Bhulta | 188 | 30 | 2019-03-03 | 19:30
6 | Madanganj | 64 | 21 | 2019-03-03 | 19:00
7 | Shitalakhya | 119 | 16 | 2019-03-03 | 15:00
8 | Rahim steel | 30 | 30 | 2019-03-03 | 15:00
9 | Matuail | 95 | 19 | 2019-03-03 | 10:00
10 | Ghorasal | 87 | 25 | 2019-03-03 | 1:00
11 | Narsingdi | 119 | 14 | 2019-03-03 | 20:00
12 | Haripur (SBU) | 98 | 21 | 2019-03-03 | 12:00
13 | Ullon | 83 | 17 | 2019-03-03 | 19:30
14 | Hasnabad | 195 | 23 | 2019-03-03 | 19:00
15 | Magbazar | 146 | 31 | 2019-03-03 | 15:00
16 | Maniknagar | 126 | 31 | 2019-03-03 | 1300:00
17 | Bangabhaban | 30 | 31 | 2019-03-03 | 11:00
18 | Narinda | 98 | 13 | 2019-03-03 | 13:00
19 | Dhanmondi | 134 | 31 | 2019-03-03 | 13:00
20 | Lalbag | 88 | 19 | 2019-03-03 | 19:00
21 | Madartek | 55 | 22 | 2019-03-03 | 19:00
22 | Mirpur | 101 | 30 | 2019-03-03 | 18:30
23 | Kalyanpur | 102 | 13 | 2019-03-03 | 18:30
24 | Gulshan | 136 | 31 | 2019-03-03 | 12:00
25 | Uttara | 64 | 28 | 2019-03-03 | 17:00
26 | Uttara(new) | 14 | 25 | 2019-03-03 | 18:30
27 | Kamrangirchar | 88 | 13 | 2019-03-03 | 19:00
28 | Savar | 140 | 31 | 2019-03-03 | 15:00
29 | Bhasantec | 164 | 31 | 2019-03-03 | 17:00
30 | Agargaon | 52 | 31 | 2019-03-03 | 12:00
31 | Satmosjid | 93 | 30 | 2019-03-03 | 19:00
32 | Tongi | 145 | 25 | 2019-03-03 | 18:00
33 | Kabirpur | 211 | 28 | 2019-03-03 | 19:00
34 | Basundhara | 136 | 31 | 2019-03-03 | 13:00
35 | Manikganj | 87 | 17 | 2019-03-03 | 19:00
36 | Joydevpur | 217 | 30 | 2019-03-03 | 19:00
37 | New Tongi | 119 | 31 | 2019-03-03 | 12:00
38 | Kodda | 248 | 17 | 2019-03-03 | 10:00
39 | Dhamrai | 52 | 17 | 2019-03-03 | 19:00
40 | Valuka | 76 | 17 | 2019-03-03 | 16:00
41 | Tangail | 198 | 30 | 2019-03-03 | 14:00
42 | Mymensing | 214 | 16 | 2019-03-03 | 19:00
43 | Kishorganj | 106 | 25 | 2019-03-03 | 19:00
44 | Netrokona | 97 | 25 | 2019-03-03 | 18:30
45 | Jamalpur | 125 | 29 | 2019-03-03 | 19:00
46 | Sherpur | 104 | 28 | 2019-03-03 | 20:00
47 | Srimongal | 32 | 30 | 2019-03-03 | 19:00
48 | Shahjibazar | 105 | 30 | 2019-03-03 | 19:30
49 | Fenchuganj | 39 | 30 | 2019-03-03 | 19:30
50 | Kulawara | 34 | 17 | 2019-03-03 | 18:30
51 | Sylhet | 123 | 16 | 2019-03-03 | 19:00
52 | Chatak | 29 | 30 | 2019-03-03 | 19:00
53 | Sunamganj | 30 | 30 | 2019-03-03 | 20:00
54 | Bianibazar | 39 | 30 | 2019-03-03 | 20:00
55 | Cumilla (S) | 172 | 25 | 2019-03-03 | 19:00
56 | Cumilla(N) | 125 | 30 | 2019-03-03 | 19:30
57 | Chandpur | 101 | 21 | 2019-03-03 | 19:00
58 | Feni | 122 | 30 | 2019-03-03 | 19:00
59 | Chowmuhani | 162 | 13 | 2019-03-03 | 19:00
60 | Ashuganj | 55 | 21 | 2019-03-03 | 20:00
61 | Daudkandi | 124 | 30 | 2019-03-03 | 19:00
62 | B.Baria | 129 | 17 | 2019-03-03 | 19:30
63 | Ramganj | 54 | 15 | 2019-03-03 | 19:00
64 | Madanhat | 61 | 30 | 2019-03-03 | 18:30
65 | Hathazari | 99 | 31 | 2019-03-03 | 19:00
66 | Khulshi | 214 | 24 | 2019-03-03 | 16:00
67 | Halishahar | 136 | 23 | 2019-03-03 | 16:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 165 | 5 | 2019-03-03 | 06:00
69 | Sikalbaha | 42 | 23 | 2019-03-03 | 18:30
70 | Dohazari | 92 | 14 | 2019-03-03 | 18:30
71 | Cox'sbazar | 90 | 31 | 2019-03-03 | 21:00
72 | Chandraghona | 31 | 22 | 2019-03-03 | 18:30
73 | Kaptai | 23 | 3 | 2019-03-03 | 8:00
74 | A. Khaer Stl. | 0 | 1 | 2019-03-03 | 10:00
75 | Bakulia | 107 | 31 | 2019-03-03 | 19:00
76 | Julda | 23 | 16 | 2019-03-03 | 15:00
77 | TK chemical | 6 | 28 | 2019-03-03 | 14:00
78 | Modern Steel | 18 | 28 | 2019-03-03 | 24:00
79 | Shahmirpur | 31 | 21 | 2019-03-03 | 11:00
80 | Khagrachhari | 19 | 29 | 2019-03-03 | 18:30
81 | Matarbari | 28 | 31 | 2019-03-03 | 21:00
82 | Baroiar Hat | 40 | 20 | 2019-03-03 | 18:30
83 | Rangamati | 12 | 15 | 2019-03-03 | 19:00
84 | Abul Khair 230 | 157 | 13 | 2019-03-03 | 17:00
85 | BSRM | 154 | 24 | 2019-03-03 | 5:00
86 | Goalpara | 31 | 27 | 2019-03-03 | 19:00
87 | Central s/s | 84 | 17 | 2019-03-03 | 18:30
88 | Noapara | 95 | 23 | 2019-03-03 | 19:00
89 | Jashore | 148 | 30 | 2019-03-03 | 19:00
90 | Jhenida | 98 | 30 | 2019-03-03 | 19:00
91 | Bottail | 106 | 13 | 2019-03-03 | 19:00
92 | G.K Project | 45 | 21 | 2019-03-03 | 19:00
93 | Faridpur | 138 | 17 | 2019-03-03 | 19:00
94 | Madaripur | 122 | 15 | 2019-03-03 | 21:00
95 | Gopalganj | 81 | 30 | 2019-03-03 | 19:00
96 | Bagerhat | 78 | 17 | 2019-03-03 | 20:00
97 | Mongla | 40 | 7 | 2019-03-03 | 11:00
98 | Satkhira | 94 | 30 | 2019-03-03 | 19:00
99 | Gallamari | 45 | 31 | 2019-03-03 | 13:00
100 | Magura | 54 | 30 | 2019-03-03 | 19:00
101 | Chuadanga | 78 | 28 | 2019-03-03 | 19:30
102 | Barishal | 120 | 31 | 2019-03-03 | 19:00
103 | Patuakhali | 82 | 30 | 2019-03-03 | 21:00
104 | Bhandaria | 48 | 17 | 2019-03-03 | 19:30
105 | Ishurdi | 55 | 28 | 2019-03-03 | 19:00
106 | Ruppur Paromanobik | 1 | 1 | 2019-03-03 | 1:00
107 | Natore | 114 | 29 | 2019-03-03 | 20:00
108 | Bogura | 231 | 28 | 2019-03-03 | 20:00
109 | Noagaon | 126 | 20 | 2019-03-03 | 19:30
110 | Rajshahi | 140 | 28 | 2019-03-03 | 20:00
111 | C.Nawabganj | 76 | 29 | 2019-03-03 | 19:00
112 | Amnura | 46 | 23 | 2019-03-03 | 19:00
113 | Pabna | 104 | 25 | 2019-03-03 | 19:30
114 | Shahjadpur | 91 | 17 | 2019-03-03 | 19:00
115 | Serajganj | 88 | 24 | 2019-03-03 | 20:00
116 | Niyamatpur | 103 | 29 | 2019-03-03 | 19:00
117 | Joypurhat | 50 | 25 | 2019-03-03 | 06:00
118 | Mohastangor | 12 | 25 | 2019-03-03 | 19:30
119 | Rangpur | 125 | 30 | 2019-03-03 | 19:00
120 | Lalmonirhat | 91 | 25 | 2019-03-03 | 18:30
121 | Saidpur | 110 | 18 | 2019-03-03 | 20:00
122 | Purbasadipur | 98 | 30 | 2019-03-03 | 20:00
123 | Thakurgaon | 77 | 29 | 2019-03-03 | 19:30
124 | Palashbari | 107 | 24 | 2019-03-03 | 18:30
125 | Barapukuria | 59 | 27 | 2019-03-03 | 19:30
126 | Panchagar | 44 | 29 | 2019-03-03 | 19:00
127 | Joldhaka | 19 | 18 | 2019-03-03 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 3886 | 30.03.19 | 19:00
Chattogram | 1190 | 30.03.19 | 23:00
Khulna | 1217 | 28.03.19 | 21:00
Rajshahi | 1169 | 28.03.19 | 20:00
Cumilla | 969 | 17.03.19 | 19:30
Mymensingh | 813 | 21.03.19 | 19:30
Sylhet | 423 | 30.03.19 | 20:00
Barisal | 261 | 31.03.19 | 19:00
Rangpur | 672 | 25.03.19 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 411 | 2 | 2019-03-03 | 01:00 | 289 | 24 | 2019-03-03 | 16:00
2 | Bheramara | 400 | 409 | 2 | 2019-03-03 | 1:00 | 383 | 18 | 2019-03-03 | 18:30
3 | Ashuganj(N) | 400 | 411 | 7 | 2019-03-03 | 2:00 | 379 | 23 | 2019-03-03 | 16:00
4 | Kaliakoir | 400 | 403 | 5 | 2019-03-03 | 06:00 | 363 | 31 | 2019-03-03 | 12:00
5 | Bhulta | 400 | 408 | 9 | 2019-03-03 | 2:00 | 378 | 23 | 2019-03-03 | 16:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 3 | 2019-03-03 | 01:00 | 224 | 24 | 2019-03-03 | 11:00
2 | Ishurdi | 230 | 240 | 1 | 2019-03-03 | 05:00 | 225 | 13 | 2019-03-03 | 11:00
3 | Ashuganj | 230 | 244 | 9 | 2019-03-03 | 1:00 | 230 | 23 | 2019-03-03 | 15:00
4 | Serajganj | 230 | 233 | 5 | 2019-03-03 | 5:00 | 220 | 11 | 2019-03-03 | 13:00
5 | Baghabari | 230 | 234 | 1 | 2019-03-03 | 4:00 | 220 | 17 | 2019-03-03 | 18:30
6 | Barapukuria | 230 | 237 | 31 | 2019-03-03 | 23:00 | 213 | 23 | 2019-03-03 | 20:00
7 | Bogra | 230 | 232 | 4 | 2019-03-03 | 16:00 | 205 | 19 | 2019-03-03 | 18:30
8 | Khulna South | 230 | 244 | 17 | 2019-03-03 | 22:00 | 213 | 12 | 2019-03-03 | 7:00
9 | Rampura | 230 | 232 | 8 | 2019-03-03 | 04:00 | 217 | 25 | 2019-03-03 | 12:00
10 | Haripur | 230 | 233 | 5 | 2019-03-03 | 5:00 | 215 | 25 | 2019-03-03 | 12:00
11 | Hasnabad | 230 | 235 | 8 | 2019-03-03 | 5:00 | 212 | 25 | 2019-03-03 | 13:00
12 | Aminbazar | 230 | 239 | 31 | 2019-03-03 | 18:30 | 214 | 24 | 2019-03-03 | 12:00
13 | Tongi | 230 | 233 | 2 | 2019-03-03 | 04:00 | 210 | 24 | 2019-03-03 | 15:00
14 | Comilla (N) | 230 | 242 | 18 | 2019-03-03 | 1:00 | 224 | 31 | 2019-03-03 | 11:00
15 | Hathazari | 230 | 225 | 31 | 2019-03-03 | 23:00 | 210 | 11 | 2019-03-03 | 15:00
16 | Megnaghat | 230 | 238 | 5 | 2019-03-03 | 5:00 | 208 | 31 | 2019-03-03 | 12:00
17 | Fenchuganj | 230 | 243 | 3 | 2019-03-03 | 4:00 | 231 | 31 | 2019-03-03 | 13:00
18 | Siddhirganj | 230 | 248 | 31 | 2019-03-03 | 19:00 | 215 | 25 | 2019-03-03 | 12:00
19 | Maniknagar | 230 | 250 | 31 | 2019-03-03 | 19:00 | 212 | 25 | 2019-03-03 | 15:00
20 | Old Airport | 230 | 238 | 31 | 2019-03-03 | 18:30 | 212 | 25 | 2019-03-03 | 12:00
21 | Barisal | 230 | 244 | 25 | 2019-03-03 | 18:00 | 223 | 3 | 2019-03-03 | 22:00
22 | AKSML | 230 | 227 | 31 | 2019-03-03 | 21:00 | 209 | 31 | 2019-03-03 | 14:00
23 | BSRM | 230 | 228 | 2 | 2019-03-03 | 19:00 | 211 | 30 | 2019-03-03 | 16:00
24 | Bibiyana | 230 | 243 | 1 | 2019-03-03 | 05:00 | 226 | 31 | 2019-03-03 | 12:00
25 | Bhulta | 230 | 236 | 9 | 2019-03-03 | 1:00 | 215 | 25 | 2019-03-03 | 12:00
26 | Ashuganj (S) | 230 | 242 | 7 | 2019-03-03 | 2:00 | 228 | 25 | 2019-03-03 | 13:00
27 | Kaliakoir | 230 | 240 | 31 | 2019-03-03 | 18:30 | 214 | 30 | 2019-03-03 | 15:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 31 | 2019-03-03 | 18:30 | 125 | 25 | 2019-03-03 | 12:00
2 | Munsiganj | 132 | 140 | 31 | 2019-03-03 | 20:00 | 124 | 25 | 2019-03-03 | 11:00
3 | Megnaghat | 132 | 140 | 31 | 2019-03-03 | 20:00 | 125 | 25 | 2019-03-03 | 11:00
4 | Shyampur | 132 | 140 | 31 | 2019-03-03 | 18:30 | 124 | 25 | 2019-03-03 | 12:00
5 | Bhulta | 132 | 136 | 31 | 2019-03-03 | 19:30 | 119 | 31 | 2019-03-03 | 12:00
6 | Madanganj | 132 | 138 | 2 | 2019-03-03 | 1:00 | 119 | 14 | 2019-03-03 | 14:00
7 | Shitalakhya | 132 | 149 | 31 | 2019-03-03 | 19:00 | 123 | 23 | 2019-03-03 | 12:00
8 | Rahim Steal | 132 | 143 | 31 | 2019-03-03 | 19:00 | 125 | 25 | 2019-03-03 | 16:00
9 | Matuail | 132 | 140 | 31 | 2019-03-03 | 18:30 | 124 | 23 | 2019-03-03 | 12:00
10 | Ghorasal | 132 | 148 | 31 | 2019-03-03 | 18:00 | 132 | 25 | 2019-03-03 | 12:00
11 | Narsinghdi | 132 | 145 | 31 | 2019-03-03 | 18:30 | 122 | 17 | 2019-03-03 | 19:00
12 | Haripur (SBU) | 132 | 140 | 31 | 2019-03-03 | 20:00 | 124 | 25 | 2019-03-03 | 12:00
13 | Ullon | 132 | 142 | 31 | 2019-03-03 | 18:30 | 124 | 12 | 2019-03-03 | 12:00
14 | Hasnabad | 132 | 139 | 2 | 2019-03-03 | 03:00 | 124 | 23 | 2019-03-03 | 16:00
15 | Magbazar | 132 | 139 | 18 | 2019-03-03 | 5:00 | 123 | 12 | 2019-03-03 | 12:00
16 | Maniknagar | 132 | 145 | 31 | 2019-03-03 | 19:00 | 122 | 25 | 2019-03-03 | 12:00
17 | Bangabhaban | 132 | 143 | 31 | 2019-03-03 | 20:00 | 121 | 23 | 2019-03-03 | 17:00
18 | Narinda | 132 | 142 | 31 | 2019-03-03 | 18:30 | 125 | 11 | 2019-03-03 | 12:00
19 | Dhanmondi | 132 | 145 | 31 | 2019-03-03 | 19:00 | 124 | 12 | 2019-03-03 | 12:00
20 | Lalbag | 132 | 143 | 31 | 2019-03-03 | 20:00 | 121 | 23 | 2019-03-03 | 17:00
21 | Madartek | 132 | 142 | 31 | 2019-03-03 | 18:30 | 125 | 11 | 2019-03-03 | 12:00
22 | Mirpur | 132 | 137 | 2 | 2019-03-03 | 4:00 | 123 | 23 | 2019-03-03 | 12:00
23 | Kalyanpur | 132 | 142 | 31 | 2019-03-03 | 18:00 | 121 | 19 | 2019-03-03 | 12:00
24 | Gulshan | 132 | 140 | 31 | 2019-03-03 | 18:00 | 120 | 22 | 2019-03-03 | 12:00
25 | Uttara | 132 | 139 | 31 | 2019-03-03 | 18:30 | 120 | 25 | 2019-03-03 | 13:00
26 | Uttara(New) | 132 | 137 | 31 | 2019-03-03 | 3:00 | 121 | 23 | 2019-03-03 | 12:00
27 | Kamrangirchar | 132 | 142 | 31 | 2019-03-03 | 18:30 | 121 | 23 | 2019-03-03 | 12:00
28 | Savar | 132 | 139 | 31 | 2019-03-03 | 18:00 | 121 | 25 | 2019-03-03 | 11:00
29 | Bhasantec | 132 | 143 | 31 | 2019-03-03 | 18:00 | 121 | 23 | 2019-03-03 | 11:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March '2019
|  | Rated | Maxm | Date |  | 1 | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 142 | 31 | 2019-03-03 | 18:30 | 122 | 23 | 2019-03-03 | 11:00
31 | Satmosjid | 132 | 141 | 31 | 2019-03-03 | 18:30 | 122 | 21 | 2019-03-03 | 11:00
32 | Tongi | 132 | 140 | 31 | 2019-03-03 | 18:30 | 117 | 25 | 2019-03-03 | 18:00
33 | Kabirpur | 132 | 137 | 5 | 2019-03-03 | 4:00 | 118 | 14 | 2019-03-03 | 19:00
34 | Basundhara | 132 | 132 | 13 | 2019-03-03 | 4:00 | 120 | 11 | 2019-03-03 | 13:00
35 | Manikganj | 132 | 142 | 5 | 2019-03-03 | 4:00 | 122 | 30 | 2019-03-03 | 15:00
36 | Joydevpur | 132 | 144 | 31 | 2019-03-03 | 19:00 | 128 | 31 | 2019-03-03 | 16:00
37 | New Tongi | 132 | 139 | 31 | 2019-03-03 | 19:00 | 122 | 23 | 2019-03-03 | 16:00
38 | Kodda | 132 | 143 | 31 | 2019-03-03 | 20:00 | 125 | 22 | 2019-03-03 | 14:00
39 | Dhamrai | 132 | 144 | 31 | 2019-03-03 | 18:30 | 125 | 13 | 2019-03-03 | 11:00
40 | Valuka | 133 | 137 | 17 | 2019-03-03 | 01:00 | 108 | 15 | 2019-03-03 | 08:00
41 | Tangail | 132 | 140 | 31 | 2019-03-03 | 17:00 | 122 | 16 | 2019-03-03 | 18:30
42 | Mymensing | 132 | 138 | 31 | 2019-03-03 | 17:00 | 117 | 15 | 2019-03-03 | 8:00
43 | Kishorganj | 132 | 142 | 31 | 2019-03-03 | 18:00 | 120 | 23 | 2019-03-03 | 12:00
44 | Netrokona | 132 | 139 | 31 | 2019-03-03 | 17:00 | 115 | 16 | 2019-03-03 | 7:00
45 | Jamalpur | 132 | 140 | 31 | 2019-03-03 | 17:00 | 113 | 10 | 2019-03-03 | 8:00
46 | Sherpur | 132 | 140 | 31 | 2019-03-03 | 17:00 | 111 | 16 | 2019-03-03 | 7:00
47 | Srimongal | 132 | 146 | 31 | 2019-03-03 | 18:00 | 133 | 30 | 2019-03-03 | 19:00
48 | Shahjibazar | 132 | 144 | 31 | 2019-03-03 | 18:30 | 130 | 24 | 2019-03-03 | 19:00
49 | Fenchuganj | 132 | 139 | 1 | 2019-03-03 | 09:00 | 131 | 13 | 2019-03-03 | 18:00
50 | Khulawara | 132 | 143 | 31 | 2019-03-03 | 18:00 | 132 | 12 | 2019-03-03 | 21:00
51 | Sylhet | 132 | 141 | 31 | 2019-03-03 | 18:00 | 128 | 13 | 2019-03-03 | 18:30
52 | Chattak | 132 | 143 | 31 | 2019-03-03 | 18:30 | 127 | 13 | 2019-03-03 | 18:30
53 | Sunamganj | 132 | 143 | 31 | 2019-03-03 | 18:30 | 127 | 13 | 2019-03-03 | 18:30
54 | Biani Bazar | 132 | 143 | 31 | 2019-03-03 | 18:00 | 127 | 13 | 2019-03-03 | 18:30
55 | Comilla(South) | 132 | 137 | 31 | 2019-03-03 | 21:00 | 120 | 19 | 2019-03-03 | 19:00
56 | Comilla (North) | 132 | 140 | 1 | 2019-03-03 | 18:00 | 128 | 24 | 2019-03-03 | 15:00
57 | Chandpur | 132 | 145 | 31 | 2019-03-03 | 19:30 | 123 | 15 | 2019-03-03 | 13:00
58 | Feni | 132 | 140 | 31 | 2019-03-03 | 21:00 | 122 | 26 | 2019-03-03 | 16:00
59 | Chowmuhani | 132 | 136 | 31 | 2019-03-03 | 22:00 | 119 | 26 | 2019-03-03 | 12:00
60 | Ashuganj | 132 | 145 | 31 | 2019-03-03 | 18:00 | 132 | 24 | 2019-03-03 | 19:00
61 | Daudkandi | 132 | 141 | 31 | 2019-03-03 | 19:00 | 121 | 13 | 2019-03-03 | 12:00
62 | Brahminbaria | 132 | 143 | 31 | 2019-03-03 | 18:30 | 126 | 24 | 2019-03-03 | 19:00
63 | Ramganj | 132 | 136 | 13 | 2019-03-03 | 8:00 | 119 | 21 | 2019-03-03 | 23:00
64 | Madanhat | 132 | 140 | 31 | 2019-03-03 | 23:00 | 126 | 12 | 2019-03-03 | 17:00
65 | Hathazari | 132 | 140 | 31 | 2019-03-03 | 21:00 | 126 | 7 | 2019-03-03 | 15:00
66 | Khulshi | 132 | 138 | 31 | 2019-03-03 | 21:00 | 121 | 30 | 2019-03-03 | 15:00
67 | Halishahar | 132 | 141 | 31 | 2019-03-03 | 02:00 | 122 | 7 | 2019-03-03 | 17:00
68 | Baraulia | 132 | 137 | 31 | 2019-03-03 | 21:00 | 124 | 11 | 2019-03-03 | 11:00
69 | Sikalbaha | 132 | 140 | 31 | 2019-03-03 | 21:00 | 123 | 16 | 2019-03-03 | 18:00
70 | Dohazari | 132 | 140 | 31 | 2019-03-03 | 23:00 | 123 | 30 | 2019-03-03 | 18:30
71 | Cox'sbazar | 132 | 137 | 31 | 2019-03-03 | 23:00 | 115 | 16 | 2019-03-03 | 18:00
72 | Chandraghona | 132 | 140 | 31 | 2019-03-03 | 21:00 | 123 | 18 | 2019-03-03 | 11:00
73 | Kaptai | 132 | 140 | 31 | 2019-03-03 | 21:00 | 126 | 1 | 2019-03-03 | 13:00
74 | A. Khaer Stl. | 132 | 136 | 31 | 2019-03-03 | 22:00 | 124 | 11 | 2019-03-03 | 15:00
75 | Bakulia | 132 | 139 | 31 | 2019-03-03 | 21:00 | 118 | 21 | 2019-03-03 | 19:30
76 | Julda | 132 | 140 | 31 | 2019-03-03 | 21:00 | 124 | 16 | 2019-03-03 | 18:00
77 | TK Chemical | 132 | 143 | 31 | 2019-03-03 | 21:00 | 125 | 30 | 2019-03-03 | 15:00
78 | Modern Steel | 132 | 140 | 31 | 2019-03-03 | 21:00 | 122 | 12 | 2019-03-03 | 17:00
79 | Shahmirpur | 132 | 140 | 31 | 2019-03-03 | 21:00 | 123 | 16 | 2019-03-03 | 18:00
80 | Khagrachhari | 132 | 141 | 31 | 2019-03-03 | 21:00 | 125 | 12 | 2019-03-03 | 17:00
81 | Matarbari | 132 | 138 | 31 | 2019-03-03 | 23:00 | 118 | 16 | 2019-03-03 | 18:00
82 | Baroiar Hat | 132 | 140 | 31 | 2019-03-03 | 21:00 | 113 | 4 | 2019-03-03 | 19:30
83 | Rangamati | 133 | 140 | 31 | 2019-03-03 | 21:00 | 125 | 11 | 2019-03-03 | 15:00
84 | Goalpara | 132 | 140 | 8 | 2019-03-03 | 18:00 | 119 | 12 | 2019-03-03 | 7:00
85 | Khulna Central | 132 | 140 | 17 | 2019-03-03 | 22:00 | 118 | 12 | 2019-03-03 | 7:00
86 | Noapara | 132 | 138 | 1 | 2019-03-03 | 3:00 | 115 | 12 | 2019-03-03 | 07:00
87 | Jessore | 132 | 138 | 1 | 2019-03-03 | 5:00 | 112 | 22 | 2019-03-03 | 11:00
88 | Jhenida | 132 | 136 | 1 | 2019-03-03 | 2:00 | 105 | 23 | 2019-03-03 | 19:00
89 | Bottail | 132 | 140 | 2 | 2019-03-03 | 13:00 | 123 | 13 | 2019-03-03 | 18:30
90 | G.K.Project | 132 | 143 | 1 | 2019-03-03 | 16:00 | 131 | 13 | 2019-03-03 | 18:00
91 | Faridpur | 132 | 140 | 31 | 2019-03-03 | 19:30 | 108 | 15 | 2019-03-03 | 20:00
92 | Madaripur | 132 | 140 | 18 | 2019-03-03 | 11:00 | 120 | 5 | 2019-03-03 | 14:00
93 | Gopalganj | 132 | 142 | 18 | 2019-03-03 | 11:00 | 120 | 27 | 2019-03-03 | 13:00
94 | Bagerhat | 132 | 141 | 17 | 2019-03-03 | 23:00 | 120 | 5 | 2019-03-03 | 18:30
95 | Mongla | 132 | 138 | 2 | 2019-03-03 | 21:00 | 118 | 12 | 2019-03-03 | 7:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Satkhira | 132 | 139 | 1 | 2019-03-03 | 4:00 | 118 | 12 | 2019-03-03 | 7:00
97 | Gallamari | 132 | 142 | 1 | 2019-03-03 | 5:00 | 120 | 12 | 2019-03-03 | 7:00
98 | Magura | 132 | 139 | 1 | 2019-03-03 | 3:00 | 105 | 22 | 2019-03-03 | 10:00
99 | Chuadanga | 132 | 142 | 26 | 2019-03-03 | 16:00 | 98 | 19 | 2019-03-03 | 18:30
100 | Barisal | 132 | 144 | 17 | 2019-03-03 | 23:00 | 130 | 23 | 2019-03-03 | 14:00
101 | Patuakhali | 132 | 144 | 17 | 2019-03-03 | 23:00 | 126 | 23 | 2019-03-03 | 12:00
102 | Bhandaria | 132 | 140 | 17 | 2019-03-03 | 23:00 | 116 | 17 | 2019-03-03 | 18:30
103 | Ishurdi | 132 | 142 | 1 | 2019-03-03 | 4:00 | 130 | 13 | 2019-03-03 | 12:00
104 | Ruppur paromanobik | 132 | 142 | 1 | 2019-03-03 | 4:00 | 132 | 13 | 2019-03-03 | 9:00
105 | Natore | 132 | 140 | 5 | 2019-03-03 | 4:00 | 124 | 26 | 2019-03-03 | 7:00
106 | Bogra | 132 | 141 | 1 | 2019-03-03 | 5:00 | 121 | 19 | 2019-03-03 | 19:00
107 | Noagaon | 132 | 137 | 1 | 2019-03-03 | 3:00 | 115 | 17 | 2019-03-03 | 9:00
108 | Rajshahi | 132 | 136 | 1 | 2019-03-03 | 5:00 | 121 | 23 | 2019-03-03 | 7:00
109 | C.Nawabganj | 132 | 135 | 6 | 2019-03-03 | 19:00 | 115 | 23 | 2019-03-03 | 7:00
110 | Amnura | 132 | 140 | 12 | 2019-03-03 | 18:00 | 117 | 12 | 2019-03-03 | 7:00
111 | Pabna | 132 | 137 | 3 | 2019-03-03 | 4:00 | 125 | 13 | 2019-03-03 | 18:30
112 | Shahjadpur | 132 | 145 | 5 | 2019-03-03 | 4:00 | 132 | 17 | 2019-03-03 | 18:30
113 | Serajganj | 132 | 140 | 1 | 2019-03-03 | 2:00 | 125 | 13 | 2019-03-03 | 8:00
114 | Niyamatpur | 132 | 137 | 1 | 2019-03-03 | 3:00 | 105 | 22 | 2019-03-03 | 19:00
115 | Joypurhat | 132 | 139 | 3 | 2019-03-03 | 2:00 | 110 | 26 | 2019-03-03 | 7:00
116 | Mohastangor | 132 | 138 | 1 | 2019-03-03 | 3:00 | 119 | 13 | 2019-03-03 | 19:30
117 | Rangpur | 132 | 135 | 1 | 2019-03-03 | 11:00 | 108 | 23 | 2019-03-03 | 20:00
118 | Lalmonirhat | 132 | 135 | 26 | 2019-03-03 | 5:00 | 100 | 23 | 2019-03-03 | 20:00
119 | Saidpur | 132 | 135 | 1 | 2019-03-03 | 1:00 | 106 | 23 | 2019-03-03 | 20:00
120 | Purbasadipur | 132 | 135 | 2 | 2019-03-03 | 10:00 | 106 | 23 | 2019-03-03 | 20:00
121 | Thakurgaon | 132 | 132 | 26 | 2019-03-03 | 3:00 | 98 | 23 | 2019-03-03 | 18:30
122 | Palashbari | 132 | 136 | 1 | 2019-03-03 | 2:00 | 112 | 16 | 2019-03-03 | 20:00
123 | Barapukuria | 132 | 136 | 1 | 2019-03-03 | 4:00 | 113 | 23 | 2019-03-03 | 20:00
124 | Panchagar | 132 | 131 | 27 | 2019-03-03 | 7:00 | 89 | 23 | 2019-03-03 | 20:00
125 | Joldhaka | 132 | 134 | 1 | 2019-03-03 | 7:00 | 106 | 23 | 2019-03-03 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:March' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 120 | 375
IP-299421 | Hasnabad | TR2 | 225 | 105 | 375 | 30.03.19 | 12:00
|  | TR3 | 225 | 105 | 365
|  | TR1 | 225 | 140 | 410
IP-299866 | Tongi | TR2 | 225 | 140 | 410 | 31.03.19 | 10:00
|  | TR3 | 225 | 140 | 410
|  | TR1 | 225 | 89 | 320
IP-299427 | Haripur | TR2 | 225 |  |  | 02.03.19 | 12:00 | S/D
|  | TR3 | 225 | 89 | 320
|  | TR1 | 225 | 160 | 470
IP-299728 | Rampura | TR2 | 225 | 160 | 470 | 25.04.19 | 16:00
|  | TR3 | 225 | 160 | 470
|  | TR1 | 225 | 113 | 312
IP-299264 | Aminbazar | TR2 | 225 | 113 | 312 | 23.03.19 | 12:00
|  | TR3 | 225 | 118 | 326
| Maniknagar | TR1 | 300 | 119 | 390 | 31.03.19 | 16:00
|  | TR2 | 300 | 119 | 390
IP-399266 | Cumilla (N) | TR1 | 225 | 160 | 480 | 26.03.19 | 16:00
|  | TR2 | 225 | 157 | 462
| Fenchuganj | TR1 | 300 | 208 | 520 | 31.03.19 | 10:00
|  | TR1 | 150 | 102 | 310
IP-399428 | Hathazari | TR3 | 150 | 102 | 310 | 27.03.19 | 9:00
|  | TR4 | 150 | 102 | 310
|  | TR1 | 225 | 134 | 360
| Ishurdi | TR2 | 225 | 134 | 360 | 13.03.19 | 19:00
IP-499474 |  | TR3 | 225 | 134 | 360
| Khulna(S) | TR1 | 225 | 114 | 310
IP-58001/58002 |  | TR2 | 225 | 114 | 310 | 23.03.19 | 24:00
|  | TR3 | 300 | 150 | 399
| Bogra | TR1 | 225 | 130 | 401 | 20.03.19 | 20:00
|  | TR2 | 225 | 130 | 401
IP-43002/499264 |  | TR3 | 225 | 177 | 530
IP-499224 | Baghabari | TR1 | 225 | 160 | 480 | 13.03.19 | 20:00
| Barapukuria | TR1 | 225 | 201 | 1000 | 21.03.19 | 19:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 153 | 700 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 184 | 936
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 281.2 | 508.1 | 23.03.19 | 9:30
|  | TR1(400/132 kV) | 325 | 224.8 | 373.4 | 20.03.19 | 19:00
|  | TR2(400/132 kV) | 325 | 224.8 | 373.4
| Bibiyana | ICT1(400/230 kV) | 520 | 167 | 281 | 31.03.19 | 10:00
|  | ICT2(400/230kV) | 520 | 167 | 281
| Bhulta | ATR1(400/230 kV) | 520 | 183 | 300 | 20.03.19 | 12:45
|  | ATR2(400/230kV) | 520 | 183 | 300
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:March' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-03-19 | 7459 | 7459 | - | - | - | - | - | - | - | - | - | - | - | - | 01-03-19 | 5492.6 | 5492.6 | - | - | - | - | - | - | - | - | - | - | - | -
02-03-19 | 8509 | 8509 | - | - | - | - | - | - | - | - | - | - | - | - | 02-03-19 | 6749.7 | 6749.7 | - | - | - | - | - | - | - | - | - | - | - | -
03-03-19 | 8493 | 8493 | - | - | - | - | - | - | - | - | - | - | - | - | 03-03-19 | 6881.4 | 6881.4 | - | - | - | - | - | - | - | - | - | - | - | -
04-03-19 | 8736 | 8736 | - | - | - | - | - | - | - | - | - | - | - | - | 04-03-19 | 7188.7 | 7188.7 | - | - | - | - | - | - | - | - | - | - | - | -
05-03-19 | 8611 | 8611 | - | - | - | - | - | - | - | - | - | - | - | - | 05-03-19 | 6909.7 | 6909.7 | - | - | - | - | - | - | - | - | - | - | - | -
06-03-19 | 8900 | 8900 | - | - | - | - | - | - | - | - | - | - | - | - | 06-03-19 | 7071.5 | 7071.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-03-19 | 8721 | 8721 | - | - | - | - | - | - | - | - | - | - | - | - | 07-03-19 | 7303.4 | 7303.4 | - | - | - | - | - | - | - | - | - | - | - | -
08-03-19 | 8075 | 8075 | - | - | - | - | - | - | - | - | - | - | - | - | 08-03-19 | 6131.7 | 6131.7 | - | - | - | - | - | - | - | - | - | - | - | -
09-03-19 | 8941 | 8941 | - | - | - | - | - | - | - | - | - | - | - | - | 09-03-19 | 6789.4 | 6789.4 | - | - | - | - | - | - | - | - | - | - | - | -
10-03-19 | 9369 | 9369 | - | - | - | - | - | - | - | - | - | - | - | - | 10-03-19 | 7006.3 | 7006.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-03-19 | 9965 | 9965 | - | - | - | - | - | - | - | - | - | - | - | - | 11-03-19 | 8076.6 | 8076.6 | - | - | - | - | - | - | - | - | - | - | - | -
12-03-19 | 10071 | 10071 | - | - | - | - | - | - | - | - | - | - | - | - | 12-03-19 | 8373.4 | 8373.4 | - | - | - | - | - | - | - | - | - | - | - | -
13-03-19 | 10500 | 10500 | - | - | - | - | - | - | - | - | - | - | - | - | 13-03-19 | 8517.5 | 8517.5 | - | - | - | - | - | - | - | - | - | - | - | -
14-03-19 | 10441 | 10441 | - | - | - | - | - | - | - | - | - | - | - | - | 14-03-19 | 8670.3 | 8670.3 | - | - | - | - | - | - | - | - | - | - | - | -
15-03-19 | 9644 | 9644 | - | - | - | - | - | - | - | - | - | - | - | - | 15-03-19 | 7432.6 | 7432.6 | - | - | - | - | - | - | - | - | - | - | - | -
16-03-19 | 10796 | 10796 | - | - | - | - | - | - | - | - | - | - | - | - | 16-03-19 | 8474.4 | 8474.4 | - | - | - | - | - | - | - | - | - | - | - | -
17-03-19 | 10499 | 10499 | - | - | - | - | - | - | - | - | - | - | - | - | 17-03-19 | 8792.5 | 8792.5 | - | - | - | - | - | - | - | - | - | - | - | -
18-03-19 | 10034 | 10034 | - | - | - | - | - | - | - | - | - | - | - | - | 18-03-19 | 8347.3 | 8347.3 | - | - | - | - | - | - | - | - | - | - | - | -
19-03-19 | 10115 | 10115 | - | - | - | - | - | - | - | - | - | - | - | - | 19-03-19 | 8296.8 | 8296.8 | - | - | - | - | - | - | - | - | - | - | - | -
20-03-19 | 10340 | 10340 | - | - | - | - | - | - | - | - | - | - | - | - | 20-03-19 | 8984.2 | 8984.2 | - | - | - | - | - | - | - | - | - | - | - | -
21-03-19 | 10626 | 10626 | - | - | - | - | - | - | - | - | - | - | - | - | 21-03-19 | 9097.3 | 9097.3 | - | - | - | - | - | - | - | - | - | - | - | -
22-03-19 | 9490 | 9490 | - | - | - | - | - | - | - | - | - | - | - | - | 22-03-19 | 7718.8 | 7718.8 | - | - | - | - | - | - | - | - | - | - | - | -
23-03-19 | 10744 | 10744 | - | - | - | - | - | - | - | - | - | - | - | - | 23-03-19 | 8224.6 | 8224.6 | - | - | - | - | - | - | - | - | - | - | - | -
24-03-19 | 10540 | 10540 | - | - | - | - | - | - | - | - | - | - | - | - | 24-03-19 | 8731.4 | 8731.4 | - | - | - | - | - | - | - | - | - | - | - | -
25-03-19 | 10707 | 10707 | - | - | - | - | - | - | - | - | - | - | - | - | 25-03-19 | 8909.2 | 8909.2 | - | - | - | - | - | - | - | - | - | - | - | -
26-03-19 | 8334 | 8334 | - | - | - | - | - | - | - | - | - | - | - | - | 26-03-19 | 7743 | 7743 | - | - | - | - | - | - | - | - | - | - | - | -
27-03-19 | 10182 | 10182 | - | - | - | - | - | - | - | - | - | - | - | - | 27-03-19 | 8110.2 | 8110.2 | - | - | - | - | - | - | - | - | - | - | - | -
28-03-19 | 10613 | 10613 | - | - | - | - | - | - | - | - | - | - | - | - | 28-03-19 | 8855.7 | 8855.7 | - | - | - | - | - | - | - | - | - | - | - | -
29-03-20 | 10006 | 10006 | - | - | - | - | - | - | - | - | - | - | - | - | 29-03-20 | 8108 | 8108 | - | - | - | - | - | - | - | - | - | - | - | -
30-03-21 | 10933 | 10933 | - | - | - | - | - | - | - | - | - | - | - | - | 30-03-21 | 8751.9 | 8751.9 | - | - | - | - | - | - | - | - | - | - | - | -
31-03-22 | 4855 | 4855 | - | - | - | - | - | - | - | - | - | - | - | - | 31-03-22 | 9132.3 | 9132.3 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10933 | 30/03/19 | 20:00
2 | Maximum day peak Genaration | MW | 9132.3 | 31/03/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 10933 | 30/03/19 | 19:00
4 | Minimum Generation | MW | 4710 | 02/03/19 | 5:00
5 | Average of the daily evening peak Genaration | MW | 9524.1613
6 | Average of the daily day peak Genaration | MW | 7899.1097
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5878.9529
12 | Total Generation by IPP | MKWH | 1320.6751 | % of total Gen. | 22.46%
13 | Total Generation by BPDB | MKWH | 3315.9631 | " | 56.4%
14 | A) Total Generation by RPCL | MKWH | 121.266 | '' | 2.063%
| B) Total Generation by REB | MKWH | 138.6817 | " | 2.359%
| C) Total Generation by RENTAL | MKWH | 370.9007 | " | 6.309%
| D) Total Imported from India (HVDC) | MKWH | 527.9674 | " | 8.981%
| E) Total Imported from Tripura, India (A.C) | MKWH | 83.4989 | " | 1.42%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4289.7961 | % of total Gen. | 72.97%
| B) Oil | MKWH | 795.1953 | '' | 13.53%
| C) Hydro | MKWH | 52.3268 | '' | 0.8901%
| D) Solar | MKWH | 3.9096 | '' | 0.0665%
| E) Coal | MKWH | 126.2587 | '' | 2.148%
| F) HVDC (Import from India) | MKWH | 527.9674 | '' | 8.981%
| G) A.C (Import from Tripura, India) | MKWH | 83.4989 | '' | 1.42%
16 | Maximun of the daily total Generation . | MKWH | 217.1334 | 10/03/19
17 | Monthly Load factor | % | 72.2749
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 9304.3773
| A) Gas | M.Taka | 3050.7202
| B) Liquid fuel | M.Taka | 5740.7044
| C) Coal | M.Taka | 512.9526
| D) HVDC (Import from India) | M.Taka | 2692.6337
| E) Tripura(Import from India) | M.Taka | 571.1326
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 431.7265 | 21/03/19
| A) Gas | M.Taka | 128.1436 | 10/03/19
| B) Liquid fuel | M.Taka | 310.8135 | 21/03/19
| C) Coal | M.Taka | 25.1327 | 20/03/19
| D) HVDC (Import from India) | M.Taka | 102.905 | 25-03-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.6007
| B) Excluding Hydro & Solar | Taka/KWHR | 2.6258
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.17 | 31/03/19 | 06:00
b) | Actual | FT (MSL) | 86 | 31/03/19 | 06:00
22 | Peak Genaration of March 2018 | MW | 10084 | 19/03/18 | 19:30
23 | Peak Demand of March 2018 | MW | 10084 | 19/03/18 | 19:30
24 | Maximum peak Generation recorded upto 31/03/19 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 31/03/19 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 31/03/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.