## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:February' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | February 2019 |  | January 2019 |  | February 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9403 | 24/02/19 | 8893 | 30/01/19 | 8848 | 24/02/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 3497 | 26/02/19 | 4350 | 01/01/19 | 2515 | 26/02/18 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9403 | 24/02/19 | 8893 | 30/01/19 | 8848 | 24/02/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 7765.8 | 23/02/19 | 7189.5 | 27/01/19 | 7547.8 | 25/02/18 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9403 | 24/02/19 | 8893 | 30/01/19 | 8848 | 24/02/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 8652.5357 |  | 8425.06 |  | 8183.61 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 7016.6929 |  | 6485.91 |  | 6720.43 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 864 | 12/02/19 | 710 | 12/01/19 | 485 | 05/02/18 | 864 | 2019-12-02
|  |  | 21:00 |  | 20:00 |  | 19:30 |  | 21:00
9 | Maximum Power Import from Tripura, India (MW) | 152 | 23'/02/19 | 136 | 22/01/19 | 152 | 28/02/18 | 188 | 29/05/18
|  |  | 18:30 |  | 19:30 |  | 18:30 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2632.179 |  | 2531.59 |  | 2291.72
21 | Station Use of BPDB (MKWH) | 88.6901 |  | 197.11 |  | 77.21
22 | Net Generation of BPDB (MKWH) | 2543.4889 |  | 2334.48 |  | 2214.52
23 | Net Generation of IPP & RPCL (MKWH) | 1086.612 |  | 1416.26 |  | 1131.29
24 | Net Generation of REB (MKWH) | 118.6409 |  | 137.09 |  | 129.42
24 | Net Generation of Rental Power Plant (MKWH) | 299.974 |  | 350.99 |  | 494.98
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4048.7158 |  | 4238.82 |  | 3970.21 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 3514.5943 |  | 3703.98 |  | 3002.47 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 35.6407 |  | 28.79 |  | 15.65 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 435.5161 |  | 547.71 |  | 754.47 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 44.7686 |  | 35.25 |  | 52.44 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 3.5208 |  | 5.45 |  | 0.28 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 103.3654 |  | 114.75 |  | 222.1 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 486.4898 |  | 423.75 |  | 329.45 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 73.1766 |  | 73.45 |  | 73.61 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:February' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9403 | 24/02/19 | 19:00
Generation Period
| Dhaka | MW | 3175
| Chattogram | MW | 1016
| Cumilla | MW | 788
| Mymensingh | MW | 710
| Sylhet | MW | 324
a) | Total supply in East zone | MW | 6013
| Khulna | MW | 1088
| Barisal | MW | 217
| Rajshahi | MW | 1007
| Rangpur | MW | 621
b) | Total supply in West zone | MW | 2933
c) | Total supply in both zone ( a+b) | MW | 8946
Ref: | 27.21.2604.603.16.086.18.132 | Date: 20/03/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:February' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 700 | 01/02/19 | 1:00
| b) Ishurdi end | MW | 240 | 27/02/19 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 420 | 27/02/19 | 16:00
| b) Ishurdi end | MW | 300 | 01/02/19 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.3287 | 01/02/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 3.1845 | 01/02/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 26.6287
| b) Ishurdi end | MKWH | 28.2858
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 27.4372
| b) Ishurdi end | MKWH | 25.8531
23 | Transmission loss of EWI/ NO-1 | % | 2.912
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 440 | 03/02/19 | 18:30
| b)Serajganj end | MW | 240 | 27/02/19 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 180 | 27/02/19 | 16:00
| b)Sirajganj end | MW | 400 | 03/02/19 | 18:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 8.802 | 05/02/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 8.646 | 05/02/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 80.608
| b)Sirajganj end | MKWH | 13.48
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 13.37
| b)Sirajganj end | MKWH | 79.602
30 | Transmission loss of EWI /NO-2 | % | 1.186
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## DF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bibiyana | 400 kV bus-2 | 2019-02-03 00:27 | 2019-02-03 09:52 | 9:25 | E/O | Due to sparking at B-phase post insulator clamp | 0 | 0 | No interruption
Joydevpur | 230/132 kV Transformer-GT-4 | 2019-02-16 11:51 | 2019-02-16 13:41 | 1:50 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T-1 | 2019-02-23 09:43 | 2019-02-23 10:02 | 0:19 | E/O | Due to Oil leakage | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T-1 | 2019-02-23 13:42 | 2019-02-23 15:49 | 2:07 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Kabirpur | 33 kV Bus with 132/33 kV Transformer T2 | 2019-02-23 15:29 | 2019-02-23 16:33 | 1:04 | E/O | Due to re hot maintenance | 27 | 28.8 | Power interruption
| 132/33 kV all Transformers | 2019-02-24 10:34 | 2019-02-24 11:02 | 0:28 | E/O | Due to bursting of PT | 105 | 49 | Power interruption
| 132/33 kV Transformers-T-1 & T2 | 2019-02-28 14:05 | 2019-02-28 14:39 | 0:34 | E/O | Due to 33 kV feeder fault | 40 | 22.6667 | Power interruption
|  |  | Total : | 15:47 |  | Unserved Energy: |  | 100.4667
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformer-T2 | 2019-02-05 17:35 | 2019-02-05 17:49 | 0:14 | E/O | Due to CT burst. | 58 | 13.5333 | Power interruption
Mniknagar | 230/132 kV Transformer-T02 | 2019-02-13 14:26 | 2019-02-13 14:48 | 0:22 | T | Tripped showing protection relay | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformers-T1 & T2 | 2019-02-15 18:35 | 2019-02-15 18:52 | 0:17 | E/O | Due to L/A burst of 33 kV REB | 82 | 23.2333 | Power interruption
Mniknagar | 230/132 kV Transformer-T02 | 2019-02-17 07:37 | 2019-02-17 08:07 | 0:30 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformers-T1 & T2 | 2019-02-17 07:29 | 2019-02-17 07:59 | 0:30 | T | Due to of 33 kV feeder fault | 50 | 25 | Power interruption
| 33 kV reserve Bus | 2019-02-25 07:05 | 2019-02-25 07:20 | 0:15 | T | Due to 33 kV Lalbagh feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer T5 | 2019-02-28 06:32 | 2019-02-28 07:49 | 1:17 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Sitalakyha | 132/33 kV Transformer-T1 | 2019-02-28 16:55 | 2019-02-28 20:18 | 3:23 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
|  |  | Total : | 0:14 |  | Unserved Energy: |  | 61.7667
Chittagong Grid Circle :
Sikalbaha | 132/33 kV Transformer-T3 | 2019-02-05 15:02 | 2019-02-05 16:06 | 1:04 | E/O | Due to red hot maintenance | 21 | 22.4 | Power interruption
Dohazari | 132/33 kV Transformer-T2 | 2019-02-11 13:30 | 2019-02-11 15:40 | 2:10 | E/O | Due to red hot maintenance | 20 | 43.3333 | Power interruption
G.K.project | 132/33 kV Transformers-T1 | 2019-02-22 23:43 | 2019-02-23 01:45 | 2:02 | E/O | Due to 33 kV Y-phase PT burst | 24 | 48.8 | Power interruption 23:43 to 01:45
| 132/33 kV Transformers-T2 | 2019-02-22 23:43 | 2019-02-23 01:46 | 2:03 | E/O
Hathazari | 230/132 kV Transformer-MT1 & MT4 | 2019-02-24 22:00 | 2019-02-24 22:36 | 0:36 | E/O | Due to Y-phase CVT burst at Juldah S/S | 0 | 0 | No interruption
| 230/132 kV Transformer-MT3 | 2019-02-24 22:00 | 2019-02-24 22:14 | 0:14 | E/O |  | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformers T1 | 2019-02-26 03:50 | 2019-02-26 07:05 | 0:01 | T | Tripped showing O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformers T2 | 2019-02-26 03:50 | 2019-02-26 05:24 | 1:01 | T |  | 0 | 0 | No interruption
Halishahar | 132/33 kV TransformersT1 & T3 | 2019-02-28 12:40 | 2019-02-28 13:15 | 0:35 | T | Tripped showing O/C & E/F relay | 45 | 26.25 | Power interruption
|  |  | Total : | 9:46 |  | Unserved Energy: |  | 140.7833
Comilla Grid Circle :
Sreemongal | 132/33 kV TransformersT2 & T3 | 2019-02-01 08:07 | 2019-02-01 08:08 | 0:01 | T | Tripped showing E/F relay at 33 kV side | 9 | 0.15 | Power interruption
Biyanibazar | 132/33 kV Transformer-T2 | 2019-02-05 17:09 | 2019-02-05 21:04 | 3:55 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2019-02-10 10:04 | 2019-02-10 16:53 | 6:49 | E/O | Due to Oil leakage of 33 kV bushing | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2019-02-19 07:00 | 2019-02-19 09:45 | 2:45 | E/O | Due to re hot maintenance | 25 | 68.75 | Power interruption
Comilla (S) | 132/33 kV Transformer-T1 | 2019-02-19 15:05 | 2019-02-19 15:37 | 0:32 | T | Tripped showing E/F & O/C relay | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-T1 | 2019-02-23 07:04 | 2019-02-23 07:59 | 0:55 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 14:57 |  | Unserved Energy: |  | 68.9
Khulna Grid Circle :
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-02-17 05:43 | 2019-02-17 05:56 | 0:13 | T | Due to bird fallen on 33 kV Bus | 26 | 5.6333 | Power interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-02-24 23:46 | 2019-02-25 13:14 | 13:28 | E/O | Due to re hot maintenance | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-02-25 06:16 | 2019-02-25 08:22 | 2:06 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T1 | 2019-02-25 06:27 | 2019-02-25 08:26 | 1:59 | T | Tripped showing O/V relay | 32 | 62.9333 | Power interruption 06:47 to 08:26
| 132/33 kV Transformers-T2 | 2019-02-25 06:47 | 2019-02-25 08:45 | 1:58 | T
Gallamari | 132/33 kV Transformers-T1 | 2019-02-25 06:11 | 2019-02-25 06:30 | 0:19 | T | Tripped showing inst.O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-02-25 06:11 | 2019-02-25 07:37 | 1:26 | T |  | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-02-26 04:15 | 2019-02-26 06:10 | 1:55 | T | Tripped showing O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-02-26 04:18 | 2019-02-26 06:24 | 2:06 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformers-T1 & T2 | 2019-02-26 19:05 | 2019-02-26 19:15 | 0:10 | T | Tripped showing inst.O/C relay | 60 | 10 | Power interruption
|  |  | Total : | 25:40 |  | Unserved Energy: |  | 78.5667
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bottail | 132/33 kV Transformer1-T1 | 2019-02-03 14:22 | 2019-02-04 13:08 | 22:46 | E/O | Due to cable burst | 0 | 0 | No interruption
Bheramara.GK | 132/33 kV Transformers-T1 & T2 | 2019-02-15 21:10 | 2019-02-15 21:39 | 0:29 | E/O | Due to red hot maintenance | 30 | 14.5 | Power interruption
Bottail | 132/33 kV Transformers-T1 & T2 | 2019-02-17 06:06 | 2019-02-17 06:40 | 0:34 | T | Due to bad weather | 24 | 13.6 | Power interruption
Bottail | 33 kV Bus | 2019-02-17 15:56 | 2019-02-17 17:16 | 1:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Jeshore | 132/33 kV Transformer-T3 | 2019-02-25 07:11 | 2019-02-25 13:30 | 6:19 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Bheramara. | 230/132 kV Transformer-T1 | 2019-02-26 03:32 | 2019-02-26 06:16 | 2:44 | T | Due to O/V relay | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2019-02-26 03:46 | 2019-02-26 06:24 | 2:38 | T |  | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2019-02-26 03:50 | 2019-02-26 05:42 | 1:52 | T | Due to O/V relay | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2019-02-26 12:54 | 2019-03-05 15:36 | 170:42 | T | Due to 132/33 kV Y-phase Bushing burst | 0 | 0 | No interruption
|  |  | Total : | 209:24 |  |  |  | 28.1
Bogra Grid Circle:
Niyamatpur | 132/33 kV Transformer-T2 | 2019-02-02 20:09 | 2019-02-02 21:28 | 1:19 | E/O | Due to red hot maintenance | 35 | 61.25 | Power interruption 20:09 to 21:28
Sirajganj | 132/33 kV Transformer-T1 | 2019-02-05 10:14 | 2019-02-05 11:14 | 1:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2019-02-10 20:46 | 2019-02-10 21:14 | 0:28 | E/O | Due to red hot maintenance | 18 | 8.4 | Power interruption
Rajshahi | 132/33 kV Transformers-T1 & T2 | 2019-02-14 13:06 | 2019-02-14 13:13 | 0:07 | T | Tripped showing E/F relay at 33 kV side | 64 | 7.4667 | Power interruption
Naogaon | 132/33 kV Transformer-T1 | 2019-02-20 08:25 | 2019-02-20 09:08 | 0:43 | E/O | Due to red hot maintenance | 20 | 14.3333 | Power interruption
Ruppur | 132/33 kV Transformer-T1 | 2019-02-26 03:02 | 2019-02-26 07:04 | 4:02 | T | Due to O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-02-26 03:07 | 2019-02-26 07:04 | 3:57 | T |  | 0 | 0 | No interruption
|  |  | Total : | 11:36 |  | Unserved Energy: |  | 91.45
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2019-02-17 07:38 | 2019-02-17 16:16 | 8:38 | T | Tripped showing pilot wire protcetion relay | 0 | 0 | No interruption
|  |  | Total : | 8:38 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 296:02 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## DF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 | 2019-02-03 16:14 | 2019-02-03 16:34 | 0:20 | T | Tripped showing Gen.trip. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2019-02-03 17:02 | 2019-02-03 17:15 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-1 | 2019-02-15 12:12 | 2019-02-15 12:27 | 3:02 | T | Tripped showing directional & O/C relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-1 | 2019-02-17 05:07 | 2019-02-17 05:36 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2019-02-17 07:21 | 2019-02-17 08:06 | 0:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2019-02-17 08:03 | 2019-02-17 08:20 | 0:17 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-02-18 17:28 | 2019-02-18 17:38 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line | 2019-02-27 18:04 | 2019-02-27 18:12 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 5:24 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 | 2019-02-01 09:32 | 2019-02-01 12:34 | 3:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj S/S-Siddhirganj P/S 132 kV line | 2019-02-01 09:32 | 2019-02-01 10:57 | 1:25 | T | Tripped showing master trip relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2019-02-08 08:34 | 2019-02-08 09:14 | 0:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Rampura-Moghbazar 132 kV line-2 | 2019-02-08 09:16 | 2019-02-08 18:24 | 9:08 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Rampura-Moghbazar 132 kV line-2 | 2019-02-13 14:50 | 2019-02-13 15:09 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV line | 2019-02-14 09:32 | 2019-02-14 10:10 | 0:38 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shitalakyha 132 kV line-1 | 2019-02-14 15:41 | 2019-02-14 15:51 | 0:10 | T | Tripped showing dist. relay | 88 | 14.6667 | Power interruption
| Hasnabad-Kamrangirchar 132 kV line-1 | 2019-02-14 15:40 | 2019-02-14 15:56 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj P/S 132 kV line | 2019-02-16 21:43 | 2019-02-17 03:37 | 5:54 | T | Tripped showing master trip relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-2 | 2019-02-17 02:44 | 2019-02-17 03:30 | 0:46 | T | Tripped showing diff. relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line | 2019-02-17 08:25 | 2019-02-17 08:32 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2019-02-17 09:59 | 2019-02-17 10:13 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Bashundhara paper 132 kV line-2 | 2019-02-17 07:38 | 2019-02-17 13:40 | 6:02 | T | Tripped showing dist.high voltage | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2019-02-21 00:38 | 2019-02-21 02:21 | 1:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-2 | 2019-02-21 00:38 | 2019-02-21 01:09 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV line | 2019-02-21 00:42 | 2019-02-21 00:57 | 0:15 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
| Shyampur-APR 230 kV line | 2019-02-21 01:13 | 2019-02-21 02:02 | 0:49 | T |  | 0 | 0 | No interruption
| Shyampur-United Mymensingh 132 kV line | 2019-02-21 02:47 | 2019-02-21 03:28 | 0:41 | T | Tripped showing dist. relay | 53 | 36.2167 | Power interruption
Meghnnaghat | Meghnnaghat-Shyampur 230 kV line | 2019-02-21 02:42 | 2019-02-22 11:33 | 32:51 | T | Tripped showing auto reclose relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2019-02-23 09:30 | 2019-02-23 10:58 | 1:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line | 2019-02-26 02:52 | 2019-02-26 03:13 | 0:21 | T | Tripped showing dist. B-phase relay | 0 | 0 | No interruption
| Ullon-Haripur 132 kV line | 2019-02-26 03:33 | 2019-02-26 05:58 | 2:25 | T |  | 0 | 0 | No interruption
Ghorashal | Ghorashal-joydevpur 1321 kV line-2 | 2019-02-26 06:45 | 2019-02-26 10:11 | 3:26 | T | Tripped showing remote protection relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line | 2019-02-27 16:20 | 2019-02-27 16:49 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2019-02-27 17:35 | 2019-02-27 17:48 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 73:53 |  | Unserved Energy: |  | 50.8833
Chittagong Grid Circle :
Shahmirpur | Shahmirpur-Juldah 132 kV line-2 | 2019-02-05 12:42 | 2019-02-05 14:13 | 2:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2019-02-05 14:44 | 2019-02-05 15:40 | 0:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Sikalbaha-Sikalbaha RPP 132 kV line | 2019-02-07 08:55 | 2019-02-07 10:36 | 1:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-AKSM 230 kV line | 2019-02-13 10:37 | 2019-02-13 10:52 | 0:15 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Chandraghona | Chandraghona-Kaptai 132 kV line-2 | 2019-02-13 11:37 | 2019-02-13 11:51 | 0:14 | T | Tripped showing genreal trip relay | 0 | 0 | No interruption
| Chandraghona-Kaptai 132 kV line-1 | 2019-02-13 11:44 | 2019-02-13 11:56 | 0:12 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line | 2019-02-17 14:32 | 2019-02-17 14:41 | 0:09 | T | Tripped showing SE value -D3p | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar -Dohazari 132 kV line-1 | 2019-02-23 13:25 | 2019-02-23 14:53 | 1:28 | E/O | Due to sparking at PT connector | 10 | 14.6667 | Power interruption
Rangamati | Rangamati-Chandraghona 132 kV line-1 | 2019-02-23 20:28 | 2019-02-24 11:28 | 15:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Hathazari | Hathazari-Baroitihat 132 kV line-1 & 2 | 2019-02-24 22:00 | 2019-02-24 22:42 | 0:42 | T | Tripped showing dist.(R-B)-phase Z1 relay | 750 | 525 | Power interruption
Cox'sbazar | Cox'sbazar -Dohazari 132 kV line-2 | 2019-02-25 09:01 | 2019-02-25 10:10 | 1:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 | 2019-02-25 08:48 | 2019-02-25 13:50 | 5:02 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Khulshi-Halishahar 132 kV line-2 | 2019-02-26 06:29 | 2019-02-26 06:58 | 0:29 | T |  | 0 | 0 | No interruption
|  |  | Total : | 29:22 |  | Unserved Energy: |  | 539.6667
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj S/S 132 kV line | 2019-02-14 21:18 | 2019-02-14 21:31 | 0:13 | T | Tripped showing dist.A-phase relay | 27 | 5.85 | Power interruption
Feni | Feni-Baroihat 132 kV line-2 | 2019-02-18 13:42 | 2019-02-18 14:02 | 0:20 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2019-02-23 19:42 | 2019-02-23 20:31 | 0:49 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Feni | Feni-Baroihat 132 kV line-1 | 2019-02-24 22:00 | 2019-02-24 22:26 | 0:26 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-2 | 2019-02-26 08:48 | 2019-02-26 09:13 | 0:25 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2019-02-27 16:20 | 2019-02-27 17:23 | 1:03 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
|  |  | Total : | 3:16 |  | Unserved Energy: |  | 5.85
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-02-01 08:38 | 2019-02-01 08:41 | 0:03 | T | Tripped showing O/C. relay | 116 | 5.8 | Power interruption
Barishal | Barishal-Patuakhali 132 kV line | 2019-02-01 09:28 | 2019-02-01 14:20 | 4:52 | E/O | Due to snapping of Y-phase conductor | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2019-02-01 14:57 | 2019-02-01 15:34 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna© 132 kV line-2 | 2019-02-12 18:44 | 2019-02-12 18:52 | 0:08 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Mongla | Mongla-Bagerhat 132 kV line | 2019-02-13 10:05 | 2019-02-13 10:44 | 0:39 | T | Tripped showing dist. relay | 38 | 24.7 | Power interruption
Barishal | Barishal-Madaripur 132 kV line-1 | 2019-02-14 07:19 | 2019-02-14 17:56 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2019-02-20 04:05 | 2019-02-20 12:49 | 0:06 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
| Khulna(S)-Satkhira 132 kV line-1 | 2019-02-21 05:07 | 2019-02-21 10:15 | 5:08 | E/O | Due to snapping of loop | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line | 2019-02-25 06:50 | 2019-02-25 08:19 | 0:06 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2019-02-25 05:48 | 2019-02-25 08:07 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line | 2019-02-25 06:59 | 2019-02-25 07:59 | 0:08 | T | Tripped showing O/C. relay | 20 | 2.6667 | Power interruption
| Barishal-Barisal(N) 132 kV line-1 | 2019-02-25 10:51 | 2019-02-25 11:13 | 0:06 | T | Tripped showing B-phase relay | 43 | 4.3 | Power interruption
| Barishal-Bhandaria 132 kV line | 2019-02-25 10:51 | 2019-02-25 11:38 | 0:06 | T |  | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kv line | 2019-02-25 11:23 | 2019-02-25 11:36 | 0:13 | T | Tripped showing dist. relay | 1 | 0.21667 | Power interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2019-02-27 17:44 | 2019-02-27 17:50 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Faridpur-Madaripur 132 kV line-2 | 2019-02-27 17:56 | 2019-02-27 18:14 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 12:48 |  | Unserved Energy: |  | 37.6833
HVDC Grid Circle :
Jhenidah | Jhenidah-Bottail 132 kV line-2 | 2019-02-02 11:39 | 2019-02-02 11:45 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2019-02-26 12:54 | 2019-02-26 13:21 | 0:06 | T | Due to breaking out of fire on 132/33 kV Transformer T2 CT bushing | 0 | 0 | No interruption
|  |  | Total : | 0:12 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura | Bogura -Naogaon 132 kV line-1 | 2019-02-10 20:03 | 2019-02-10 20:26 | 0:23 | T | Tripped showing inst.O/C . relay | 183 | 70.15 | Power interruption
| Bogura -Naogaon 132 kV line-2 | 2019-02-11 21:15 | 2019-02-12 00:20 | 3:05 | E/O | Due to red hot maintenance | 201 | 127.3 | Power interruption 21:15 to 21:53
Ishurdi | Ishurdi-HVDC 230 kV line-4 | 2019-02-26 12:54 | 2019-02-26 14:28 | 1:34 | T | Tripped showing dist. relay | 25 | 27.0833 | Power interruption 12:54 to 13:59
Rangpur | Rangpur-Palashbari 132 kv line-1 | 2019-02-27 13:04 | 2019-02-27 13:10 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2019-02-27 16:20 | 2019-02-27 17:21 | 1:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sirajganj-Ashuganj 230 kV line-2 | 2019-02-27 16:20 | 2019-02-27 16:44 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:33 |  | Unserved Energy: |  | 224.5333
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2019-02-04 23:06 | 2019-02-05 22:33 | 23:27 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Maniknagar-Bangabhaban 132 kV line-2 | 2019-02-05 23:06
| Maniknagar-Bangabhaban 132 kV line-3 | 2019-02-06 23:06
| Maniknagar-Bangabhaban 132 kV line-4 | 2019-02-07 23:06
| Maniknagar-Bangabhaban 132 kV line-5 | 2019-02-08 23:06
| Maniknagar-Bangabhaban 132 kV line-6 | 2019-02-09 23:06
| Maniknagar-Bangabhaban 132 kV line-7 | 2019-02-10 23:06
| Maniknagar-Bangabhaban 132 kV line-2 | 2019-02-25 11:33 | 2019-02-25 13:50 | 2:17 | T |  | 0 | 0 | No interruption
|  |  | Total : | 25:44 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 157:12 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## DF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 33 kV Bus-A with 132/33 kV Transformer T-1 | 2019-02-02 07:24 | 2019-02-02 11:44 | 4:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T1 |  | 2019-02-02 20:27 |  | S/O | Due to new Transformer connection | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2019-02-03 09:13 | 2019-02-03 16:55 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A | 2019-02-03 10:10 | 2019-02-03 16:54 | 6:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbagh | 132/33 kV Transformer-T1 | 2019-02-05 13:33 | 2019-02-05 19:20 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2019-02-05 13:21 | 2019-02-05 14:47 | 1:26 | S/O | Due to metering work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2019-02-06 09:28 | 2019-02-06 14:17 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-02-06 14:18 | 2019-02-06 15:39 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-02-07 09:45 | 2019-02-07 13:06 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2019-02-09 07:20 | 2019-02-09 15:47 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2019-02-09 09:35 | 2019-02-09 15:47 | 6:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2019-02-09 08:26 | 2019-02-09 16:30 | 8:04 | S/O | Due to test purpose | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A | 2019-02-10 08:55 | 2019-02-10 17:28 | 8:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-02-10 08:11 | 2019-02-14 14:07 | 101:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-02-10 20:32 | 2019-02-10 21:55 | 1:23 | S/O | Due to 33 kV PBS feeder maintenance | 10 | 13.8333 | Power interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2019-02-14 09:07 | 2019-02-14 16:57 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2019-02-15 09:57 | 2019-02-15 20:12 | 10:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 with 33 kV bus | 2019-02-17 09:40 | 2019-02-17 14:01 | 4:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer(New)-T1 |  | 2019-02-20 17:00 |  | S/O | Due to new Transformer connection | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2019-02-24 15:52 | 2019-02-24 17:23 | 1:31 | S/O | Due to replacing work | 30 | 45.5 | Power interruption
Kadda | 132 kV Bus-2 | 2019-02-27 12:50 | 2019-02-27 16:46 | 3:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-02-28 08:10 | 2019-02-28 08:32 | 0:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-02-28 09:39 | 2019-03-01 11:18 | 25:39 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 173:50 |  | Unserved Energy: |  | 59.3333
Dhaka (South) Grid Circle :
Lalbagh | 132/33 kV Transformer-T2 | 2019-02-06 08:36 | 2019-02-06 16:54 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T3 | 2019-02-07 10:26 | 2019-02-07 15:29 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T2 | 2019-02-09 09:15 | 2019-02-09 15:37 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-02-10 09:16 | 2019-02-10 16:40 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 132 kV main Bus | 2019-02-12 09:50 | 2019-02-12 15:55 | 6:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-T01 | 2019-02-16 09:57 | 2019-02-16 16:55 | 6:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnahat | 230 kV Bus-2 | 2019-02-18 10:35 | 2019-02-18 14:45 | 4:10 | S/O | Due to MPL work | 0 | 0 | No interruption
Haripur | 230 kV Bus-2 | 2019-02-20 09:43 | 2019-02-20 15:06 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | 230/132 kV Transformer-TR-1 | 2019-02-22 07:44 | 2019-02-22 16:47 | 9:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | 132/33 kV Transformer-T1 | 2019-02-22 09:33 | 2019-02-22 17:45 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara(Old) | 132/33 kV Transformer-T2 | 2019-02-26 06:58 | 2019-02-26 17:20 | 10:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-2 | 2019-02-26 14:35 | 2019-03-06 16:53 | 194:18 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 271:38 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV Transformer-T2 | 2019-02-08 05:45 | 2019-02-08 15:27 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
G.K.project | 33 kV Bus | 2019-02-08 07:12 | 2019-02-08 16:43 | 9:31 | S/O | Due to A/M work | 20 | 190.3333 | Power interruption
Hathazari | 230/132 kV Transformer-MT1 | 2019-02-08 09:45 | 2019-02-08 10:41 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2019-02-10 09:46 | 2019-02-10 12:47 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T1 | 2019-02-10 11:39 | 2019-02-10 12:09 | 0:30 | S/O | Due to earthing connection | 40 | 20 | Power interruption
Dohazari | 132/33 kV Transformer-T1 | 2019-02-19 10:01 | 2019-02-19 14:43 | 4:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-02-20 08:52 | 2019-02-20 14:30 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV Transformer-T1 | 2019-02-20 11:20 | 2019-02-20 14:05 | 2:45 | S/O | Due to replacement work | 0 | 0 | No interruption
Baraulia | 132 kV mian Bus | 2019-02-22 06:43 | 2019-02-22 11:55 | 5:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(Old) | 132 kV mian Bus-B | 2019-02-22 08:28 | 2019-02-22 10:16 | 1:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2019-02-23 20:38 | 2019-02-23 22:34 | 1:56 | S/O | Due to high temperature at 33 kV breaker terminal | 0 | 0 | No interruption
|  |  | Total : | 45:41 |  | Unserved Energy: |  | 210.3333
Cumilla Grid Circle :
Cumilla(N) | 230/132 kV Transformer-T02 | 2019-02-04 09:12 | 2019-02-04 15:46 | 6:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2019-02-05 08:35 | 2019-02-05 15:24 | 6:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T1 | 2019-02-05 12:30 | 2019-02-05 16:48 | 4:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2019-02-07 10:47 | 2019-02-07 14:08 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2019-02-10 08:05 | 2019-02-10 11:54 | 3:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-02-10 11:55 | 2019-02-10 14:46 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 230 kV Bus-1 | 2019-02-11 09:24 | 2019-02-11 12:14 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2019-02-11 12:17 | 2019-02-11 15:09 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2019-02-12 08:42 | 2019-02-12 19:31 | 10:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T2 | 2019-02-12 15:05 | 2019-02-12 19:42 | 4:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2019-02-13 06:59 | 2019-02-13 18:06 | 11:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2019-02-13 08:29 | 2019-02-13 12:13 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2019-02-14 07:11 | 2019-02-15 07:50 | 24:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T1 | 2019-02-15 08:27 | 2019-02-15 09:28 | 1:01 | S/O | Due to protection test | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2019-02-18 12:10 | 2019-02-18 12:44 | 0:34 | S/O | Due to 33 kV L/A burst at PDB feeder | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2019-02-22 08:15 | 2019-02-22 12:30 | 4:15 | S/O | Due to 33 kV Nabinagar feeder isolator change | 25 | 170 | Power interruption
Bibiyana | 400 kv Bus-1 | 2019-02-27 10:47 | 2019-02-28 15:01 | 28:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2019-02-27 12:12 | 2019-02-27 14:07 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-ICT2 | 2019-02-28 09:16 | 2019-02-28 17:50 | 8:34 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 72:56 |  | Unserved Energy : |  | 170
Khulna Grid Circle :
Khulna(C) | 132 kV Bus-1 | 2019-02-02 07:10 | 2019-02-02 10:06 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-02-02 06:54 | 2019-02-02 19:52 | 12:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2019-02-02 13:51 | 2019-02-02 17:25 | 3:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-02-04 05:39 | 2019-02-07 17:53 | 84:14 | S/O | Due to buchholz alarm activated | 0 | 0 | No interruption
Noapara | 33 kV Bus | 2019-02-08 07:31 | 2019-02-08 17:15 | 9:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 33 kV buso 132/33 kV Transformer T-2 | 2019-02-08 08:12 | 2019-02-08 11:40 | 3:28 | S/O | Due to C/M work | 12 | 41.6 | Power interruption
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Mongla | 132/33 kV Transformer-T1 | 2019-02-08 08:57 | 2019-02-08 13:09 | 4:12 | S/O | Due to A/M work | 20 | 84 | Power interruption
Barisal | 230/132 kV Transformer-T1 | 2019-02-11 09:18 | 2019-02-11 13:56 | 4:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2019-02-11 14:08 | 2019-02-11 15:35 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2019-02-14 09:14 | 2019-02-14 11:47 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | 132/33 kV Transformer-T2 | 2019-02-19 09:33 | 2019-02-19 17:09 | 7:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2019-02-19 10:17 | 2019-02-19 10:34 | 0:17 | S/O | Due to C/M work | 8 | 2.2667 | Power interruption
Patuakhali | 132/33 kV Transformer-T1 | 2019-02-26 14:04 | 2019-02-27 09:47 | 19:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 157:20 |  | Unserved Energy : |  | 127.8667
HVDC Grid Circle :
Bheramara HVDC | 230 kV Bus-2 | 2019-02-11 10:35 | 2019-02-11 16:30 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T02 | 2019-02-15 08:04 | 2019-02-15 17:43 | 9:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | 132 kV Bus-A & B | 2019-02-15 08:19 | 2019-02-15 12:34 | 4:15 | S/O | Due to D/W work | 32 | 136 | Power interruption
Baghabari | 230/132 kV Transformer-T02 | 2019-02-16 08:27 | 2019-02-16 18:15 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2019-02-18 15:29 | 2019-02-19 17:25 | 25:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | 132 kV Bus-A | 2019-02-21 01:18 | 2019-02-21 14:25 | 13:07 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 68:40 |  | Unserved Energy : |  | 136
Bogura Grid Circle:
Natore | 33 kV Bus of 132/33 kV Transformers T2 & T2 | 2019-02-08 07:04 | 2019-02-08 14:29 | 7:25 | S/O | Due to project work | 50 | 370.8333 | Power interruption
Joldhaka | 132/33 kV Transformer-T1 | 2019-02-08 11:15 | 2019-02-08 17:40 | 6:25 | S/O | Due to SAS work | 0 | 0 | No interruption
Bogra (old) | 132 kV auxiliary bus | 2019-02-08 10:01 | 2019-02-08 14:45 | 4:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main bus | 2019-02-08 15:30 | 2019-02-08 22:37 | 7:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T01 | 2019-02-15 08:52 | 2019-02-15 12:57 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T1 | 2019-02-18 12:15 | 2019-02-18 12:43 | 0:28 | S/O | Due to SCADA work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T1 | 2019-02-22 08:07 | 2019-02-22 11:57 | 3:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T1 with 33 kV Bus | 2019-02-27 07:20 | 2019-02-27 10:10 | 2:50 | S/O | Due to C/M work | 40 | 113.3333 | Power interruption
Amnura | 132/33 kV Transformer-T2 | 2019-02-28 09:10 | 2019-02-28 20:47 | 11:37 | S/O | Due to 33 kV loop changing | 0 | 0 | No interruption
|  |  | Total : | 48:31 |  | Unserved Energy : |  | 484.1667
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 838:36 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## DF-LDC-26
Page: 1/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Bhaluka(new) 132 kV line-1 & 2 | 2019-02-02 20:16 | 2019-02-02 20:16 | 0:00 | S/O | Newly commissioned | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-2 | 2019-03-02 07:30 | 2019-03-02 16:10 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2019-03-03 10:01 | 2019-03-03 17:02 | 7:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-02-04 08:36 | 2019-02-04 17:37 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-2 | 2019-02-05 08:50 | 2019-02-05 17:26 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2019-02-05 10:32 | 2019-02-05 14:49 | 4:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2019-02-06 13:28 | 2019-02-06 16:42 | 3:14 | S/O | Due to relay test | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-02-07 09:24 | 2019-02-07 17:24 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2019-02-07 13:56 | 2019-02-07 17:22 | 3:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2019-02-07 13:47 | 2019-02-07 14:21 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2019-02-09 09:21 | 2019-02-09 15:15 | 5:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-02-09 08:47 | 2019-02-09 10:01 | 1:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-1 | 2019-02-09 12:02 | 2019-02-09 17:11 | 5:09 | S/O |  | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2019-02-10 08:46 | 2019-02-10 17:31 | 8:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Baluka 132 kV line-2 | 2019-02-13 09:18 | 2019-02-13 14:28 | 5:10 | S/O | Due to project work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2019-02-16 07:06 | 2019-02-16 09:18 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur -Aminbazar132 kV line-1 | 2019-02-18 07:27 | 2019-02-18 12:18 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kallyanpur -Aminbazar132 kV line-2 | 2019-02-18 12:20 | 2019-02-18 16:50 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2019-02-20 09:02 | 2019-02-20 15:26 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kv line-2 | 2019-02-25 11:14 | 2019-02-25 14:29 | 3:15 | S/O | Due to armoring work | 0 | 0 | No interruption
|  |  | Total : | 100:13 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Maniknagar | Maniknagar-Siddhirganj 230 kV line-2 | 2019-02-04 06:42 | 2019-02-05 12:18 | 29:36 | S/O | Due to Y-phase isolator displacement. | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-02-05 07:16 | 2019-02-05 10:33 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorasal-Joydevpur 132 kV line-2 | 2019-02-05 09:54 | 2019-02-05 10:56 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorasal-Joydevpur 132 kV line-1 | 2019-02-05 10:57 | 2019-02-05 13:56 | 2:59 | S/O |  | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-2 | 2019-02-05 08:20 | 2019-02-05 16:55 | 8:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (new) 132 kV line | 2019-02-06 07:06 | 2019-02-06 14:01 | 6:55 | S/O | Due to project work | 140 | 968.3333 | Power interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-02-06 08:21 | 2019-02-06 17:50 | 9:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-1 & 2 | 2019-02-06 08:42 | 2019-02-06 16:20 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV line-1 & 2 | 2019-02-07 09:33 | 2019-02-07 15:54 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV line | 2019-02-07 14:56 | 2019-02-07 17:20 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur 132 kV line-1 & 2 | 2019-02-08 07:42 | 2019-02-08 11:20 | 3:38 | S/O | Due to D/W work | 120 | 181.6667 | Power interruption
Haripur | Haripur-Ullon 132 kV line-2(Siddhirganj-Maniknagar) | 2019-02-08 08:24 | 2019-02-08 17:12 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-02-09 08:48 | 2019-02-09 16:41 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Rahin steel 132 kV line | 2019-02-12 13:12 | 2019-02-12 19:02 | 5:50 | S/O | Due totesting works | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line | 2019-02-16 06:48 | 2019-02-16 14:04 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-APR Energy 230 kV line | 2019-02-18 07:52 | 2019-02-18 11:00 | 3:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbagh | Lalbagh -Kallyanpur 132 kV line-1 | 2019-02-18 09:58 | 2019-02-18 13:35 | 3:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Lalbagh -Kallyanpur 132 kV line-1 | 2019-02-19 07:22 | 2019-02-19 20:27 | 13:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Katpotti P.P 132 kV line | 2019-02-20 10:32 | 2019-02-20 15:30 | 4:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | Moghbazar-Rampura 132 kV line-1 | 2019-02-22 09:16 | 2019-02-22 17:55 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnnaghat | Meghnnaghat-Haripur 230 kV line-1 | 2019-02-23 09:30 | 2019-02-23 13:17 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Meghnaghat | Meghnnaghat-Haripur 230 kV line-1 | 2019-02-24 09:23 | 2019-02-24 20:34 | 11:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2019-02-24 10:04 | 2019-03-04 21:46 | 203:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnnaghat | Meghnnaghat-Haripur 230 kV line-1 | 2019-02-24 09:23 | 2019-02-24 20:34 | 11:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundahara | Bashundahara-Rampura 132 kV line-1 | 2019-02-27 10:38 | 2019-02-27 13:52 | 3:14 | S/O | Due to project work | 0 | 0 | No interruption
Meghnnaghat | Meghnnaghat-Haripur 230 kV line-2 | 2019-02-27 11:06 | 2019-02-27 16:16 | 5:10 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 383:23 |  | Unserved Energy: |  | 1150
Chattogram Grid Circle :
BSRM | BSRM-AKSTM 230 kV line | 2019-02-01 08:22 | 2019-02-01 11:40 | 3:18 | S/O | Due to CT ratio change | 0 | 0 | No interruption
Hathazari | Hathazari-AKSTM 230 kV line | 2019-02-01 12:01 | 2019-02-01 14:34 | 2:33 | S/O |  | 0 | 0 | No interruption
Baroihat | Baroihat-132 kV line-2 | 2019-02-04 06:46 | 2019-02-04 10:04 | 3:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV line-2 | 2019-02-07 09:05 | 2019-02-07 11:56 | 2:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-AKSTM 132 kV line | 2019-02-07 12:00 | 2019-02-07 14:45 | 2:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2019-02-07 13:39 | 2019-02-07 17:20 | 3:41 | S/O | Due to D/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbha 132 kV line-1 | 2019-02-08 18:05 | 2019-02-08 18:34 | 0:29 | S/O | Due to capacity test | 0 | 0 | No interruption
| Dohazari-Sikalbha 132 kV line-2 | 2019-02-08 18:35 | 2019-02-08 19:12 | 0:37 | S/O |  | 0 | 0 | No interruption
Hathazari | Hathazari-Borihat 132 kV line-2 | 2019-02-13 08:49 | 2019-02-13 12:12 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Borihat 132 kV line-2 | 2019-02-14 09:13 | 2019-02-14 16:24 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-BSRM 230 KV line | 2019-02-15 06:26 | 2019-02-16 18:00 | 35:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Borihat 132 kV line-2 | 2019-02-25 11:25 | 2019-02-25 14:05 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 65:02 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2019-02-02 07:20 | 2019-02-02 18:01 | 10:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-1 | 2019-02-02 08:30 | 2019-02-02 15:55 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Baria 132 kV line-2 | 2019-02-02 08:33 | 2019-02-02 17:16 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-1 | 2019-02-03 08:24 | 2019-02-03 16:33 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Baria 132 kV line-2 | 2019-02-03 08:52 | 2019-02-03 17:58 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-1 | 2019-02-04 09:18 | 2019-02-04 14:14 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-1 | 2019-02-04 09:49 | 2019-02-04 13:07 | 3:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-01-31 10:06 | 2019-02-04 20:38 | 106:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2019-02-06 14:42 | 2019-03-07 20:38 | 701:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-2 | 2019-02-07 10:30 | 2019-02-07 17:32 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Feni 132 kV line-1 | 2019-02-08 07:11 | 2019-02-08 17:15 | 10:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV line-1 & 2 | 2019-02-08 07:03 | 2019-02-08 07:05 | 0:02 | S/O | Due to D/W work | 40 | 1.3333 | Power interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2019-02-09 09:13 | 2019-02-09 15:54 | 6:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2019-02-18 06:50 | 2019-02-18 20:20 | 13:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line-1 | 2019-02-18 15:12 | 2019-02-18 20:17 | 5:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-1 | 2019-02-20 11:25 | 2019-02-20 13:26 | 2:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Feni-Hathazari 132 kV line-2 | 2019-02-20 13:28 | 2019-02-20 14:25 | 0:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-2 | 2019-02-22 06:52 | 2019-02-22 17:36 | 10:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV line | 2019-02-23 07:04 | 2019-02-23 09:38 | 2:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroihat 132 kV line-2 | 2019-02-23 09:21 | 2019-02-23 16:21 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-2 | 2019-02-23 13:38 | 2019-02-23 15:50 | 2:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2019-02-25 06:46 | 2019-02-25 16:33 | 9:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Fenchuganj S/S | Fenchuganj S/S-Fenchuagnj P/S 132 kV line-1 | 2019-02-26 07:37 | 2019-02-28 22:50 | 63:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2019-02-27 10:44 | 2019-02-27 16:55 | 6:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2019-02-27 19:40 | 2019-03-15 22:38 | 386:58 | S/O | Due to torn of wave trap conductor at Ashuganj | 0 | 0 | No interruption
|  |  | Total : | 1394:47 |  | Unserved Energy: |  | 1.3333
Khulna Grid Circle :
Khulna© | Khulna©-Khulna(S) 132 kV line-1 & 2 | 2019-02-02 06:48 | 2019-02-02 10:09 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-Noapara 132 kV line- 1& 2 | 2019-02-02 06:47 | 2019-02-02 10:07 | 3:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-North west 132 kV line- 1& 2 | 2019-02-02 06:52 | 2019-02-02 17:42 | 10:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-KPCL -2 132 kV line | 2019-02-02 06:50 | 2019-02-02 12:01 | 5:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2019-02-05 07:09 | 2019-02-05 17:55 | 10:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-07 06:55 | 2019-02-07 17:13 | 10:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-08 07:22 | 2019-02-08 16:57 | 9:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line-1 | 2019-02-09 07:47 | 2019-02-09 17:35 | 9:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line-1 | 2019-02-10 07:43 | 2019-02-10 18:54 | 11:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-11 07:49 | 2019-02-11 17:39 | 9:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-12 07:03 | 2019-02-12 17:17 | 10:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Noapara | Noapara-Khulna© 132 kV line-2 | 2019-02-12 10:01 | 2019-02-12 12:04 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Noapara-Jessore 132 kV line-1 | 2019-02-12 13:12 | 2019-02-12 16:03 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2019-02-13 09:13 | 2019-02-13 16:51 | 7:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-14 07:35 | 2019-02-14 14:40 | 7:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line- 1 | 2019-02-14 13:42 | 2019-02-14 15:36 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2019-02-15 07:14 | 2019-02-15 17:56 | 10:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-17 07:53 | 2019-02-17 17:33 | 9:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-18 07:20 | 2019-02-18 17:50 | 10:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhandaria 132 kV line | 2019-02-19 08:13 | 2019-02-19 11:08 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-02-24 08:46 | 2019-02-24 14:47 | 6:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-1 | 2019-02-25 14:52 | 2019-02-25 14:58 | 0:06 | S/O | Due to protection test | 0 | 0 | No interruption
|  |  | Total : | 155:49 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2019-02-03 07:37 | 2019-02-03 17:14 | 19:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Kustia 132 kV line-2 | 2019-02-03 13:30 | 2019-02-03 15:40 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2019-02-03 13:10 | 2019-02-03 13:56 | 0:46 | S/O | Due to carrying nuclear furnace by road | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV line | 2019-02-03 13:48 | 2019-02-03 13:52 | 0:04 | S/O |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2019-02-04 08:24 | 2019-02-04 17:19 | 8:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Rupsha 132 kV line | 2019-02-13 10:44 | 2019-02-13 17:53 | 7:09 | S/O | Due to Oil centrifuging M/C safty purpose | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-2 | 2019-02-22 17:30 | 2019-02-22 17:30 | 0:00 | S/O | Due to re-conductoring | 0 | 0 | No interruption
|  |  | Total : | 19:04 |  | Unserved Energy: |  | 0
Page: 4/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2019-02-04 10:41 | 2019-02-04 13:18 | 2:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Joldhaka | Joldhaka-Saidpur 132 kV line-1 | 2019-02-04 14:25 | 2019-02-04 18:10 | 3:45 | S/O | Due to automation testing | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-1 | 2019-02-06 13:50 | 2019-02-20 13:57 | 336:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogra 132 kV line-1 | 2019-02-07 13:28 | 2019-02-07 18:35 | 5:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2019-02-08 07:18 | 2019-02-08 22:37 | 15:19 | S/O | Due to D/W work | 15 | 229.75 | Power interruption
| Bogura-Natore 132 kV line-1 | 2019-02-08 10:10 | 2019-02-08 16:18 | 6:08 | S/O | Due to safety work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogura 132 kV line-2 | 2019-02-09 13:06 | 2019-02-09 20:28 | 7:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| Naogaon-Joypurhat 132 kV line | 2019-02-10 06:05 | 2019-02-10 07:43 | 1:38 | S/O | Due to maintenance work | 23 | 37.5667 | Power interruption
| Naogaon-Bogura 132 kV line-2 | 2019-02-10 08:24 | 2019-02-10 20:31 | 12:07 | S/O | Due to D/W work | 15 | 181.75 | Power interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2019-02-11 13:12 | 2019-02-11 21:53 | 8:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niamatpur 132 kV line | 2019-02-18 08:50 | 2019-02-18 09:00 | 0:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogura(Old) | Bogura(Old)-Bogura(N) 132 kV line-2 | 2019-02-20 15:01 | 2019-02-20 16:12 | 1:11 | S/O | Due to high temperature | 0 | 0 | No interruption
| Bogura(Old)-Bogura(N) 132 kV line-1 | 2019-02-20 16:13 | 2019-02-20 17:59 | 1:46 | S/O | Due to high temperature | 0 | 0 | No interruption
Rangpur | Rangpur-Palashbari 132 kV line-2 | 2019-02-28 10:40 | 2019-02-28 18:35 | 7:55 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 409:53 |  | Unserved Energy: |  | 449.0667
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2019-02-01 08:39 | 2019-02-01 19:25 | 10:46 | S/O | Due to manintenance work | 0 | 0 | No interruption
|  |  | Total : | 10:46 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 2538:57 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:February' 2019
| Area | Previous Month (January 2019) |  |  |  | Current Month (February 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 9 | 4 | 138 | 151 | 8 | 7 | 23 | 38
2 | Dhaka (South) Grid Circle. | 12 | 3 | 96 | 111 | 28 | 4 | 39 | 71
3 | Chattogram Grid Circle. | 6 | 2 | 51 | 59 | 12 | 11 | 23 | 46
4 | Cumilla Grid Circle. | 5 | 2 | 94 | 101 | 8 | 4 | 44 | 56
5 | Khulna Grid Circle. | 7 | 7 | 54 | 68 | 23 | 3 | 35 | 61
6 | Bheramara HVDC Grid Circle | 3 | 2 | 29 | 34 | 7 | 4 | 13 | 24
7 | Bogura Grid Circle. | 6 | 4 | 71 | 81 | 8 | 5 | 23 | 36
8 | Others | 1 | - | 9 | 10 | 3 | - | 1 | 4
9 | Total | 49 | 24 | 542 | 615 | 97 | 38 | 201 | 336
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:February' 2019
| Area | Previous Month (January 2019) |  |  |  | Current Month (February 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 109.92 |  | 808.5 | 918.42 | - | 100.47 | 59.33 | 159.8
2 | Dhaka (South) Grid Circle. | 279.86 | 145 | 1775.67 | 2200.53 | 75.89 | 36.76 | 1150 | 1262.65
3 | Chattogram Grid Circle. | 160.17 | 22.67 | 188 | 370.84 | 551.25 | 129.2 | 210.33 | 890.78
4 | Cumilla Grid Circle. | 13.27 | 66 | 78.75 | 158.02 | 6 | 68.75 | 171.33 | 246.08
5 | Khulna Grid Circle. | 19.54 | 102.03 | 1508 | 1629.57 | 116.25 | - | 127.87 | 244.12
6 | Bheramara HVDC Grid Circle | - | - | 490.67 | 490.67 | 13.6 | 14.5 | 136 | 164.1
7 | Bogura Grid Circle. | 13.75 | 178.83 | 2728.85 | 2921.43 | 104.7 | 211.28 | 933.24 | 1249.22
8 | Others | 23.2 | - | - | 23.2 | - | - | - | 0
9 | Total | 619.71 | 514.53 | 7578.44 | 8712.68 | 867.69 | 560.96 | 2788.1 | 4216.75
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:February' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 3 | 2 | 5 | 1 | 1 | 3 | 159.8
2 | Dhaka (South) | 5031.6 | 3 | - | 3 | 3 | - | - | 61.77
3 | Chattogram | 2042 | 4 | 2 | 6 | 1 | 1 | 4 | 351.11
4 | Khulna | 2434 | 3 | 3 | 6 | 3 |  | 3 | 206.44
5 | Bheramara (HVDC) | 2423.3 | 2 | 1 | 3 | 1 | 1 | 2 | 164.1
6 | Bogura | 3145.6 | 3 | 2 | 5 | 1 | 1 | 3 | 575.62
7 | Cumilla | 2981 | 2 | 1 | 3 | 1 |  | 2 | 238.9
| Total | 23365.5 | [6 empty] | 1757.74
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 100%
3 | Chattogram | 100%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.71% | [6 empty] | Executive Engineer
6 | Bogura | 99.99% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:February' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | - | - | - | - | - | - | -
2 | Dhaka (South) | 990.29 |  | 2 | 2 | 4 | 1 | 1 | 2 | 1200.88
3 | Chattogram | 917 | 20+9(Partial) | 2 | - | 2 | 1 | 1 | - | 539.67
4 | Khulna | 1238.4 | 21 | 5 | - | 4 | 3 | 1 |  | 37.68
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 3 | 3 | 6 | 1 | - | 5 | 673.6
7 | Cumilla | 1648.16 | 17 | 1 | 1 | 2 | 2 | - | - | 7.18
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 2459.01
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.94%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 99.98% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:February' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-02-18 | 12 |  | 3 | 02hr52 min | 2 | 04hr33 min | - | - | 1 | 00hr52 min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:February' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 3 | 1:04 | 27 | 28.8 | Due to tripping of 132/33 kV Transformer T2
|  | 0:28 | 105 | 49 | Due to bursting of PT
|  | 0:34 | 40 | 22.6667 | Due to tripping of 132/33 kV Transformers T1 & T2
Jamalpur | 1 | 1:23 | 10 | 13.8333 | Due to S/D of 132/33 kV Transformer T4
Kabirpur | 1 | 1:31 | 30 | 45.5 | Due to S/D of 132 /33 kV Transformer T2
Hasnabad | 1 | 0:14 | 58 | 13.5333 | Due to CT burst 132/33 kV Transformer T2
Netrakona | 1 | 0:17 | 82 | 23.2333 | Due to L/A bursting of 132/33 kV Transformers T1 & T2
Hasnabad | 2 | 0:30 | 50 | 25 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:10 | 88 | 14.6667 | Due to tripping of Hasnabad-Shitalalkhya 132 kV line-1
Shyampur | 1 | 0:41 | 53 | 36.2167 | Due to tripping of Shyampur-United Mymensingh 132 kV line
| 3 | 6:55 | 140 | 968.3333 | Due to S/D of Shyampur (new)-Shyampur (old) 132 kV line
|  | 3:38 | 120 | 181.6667 | Due to S/D of Shyampur (new)-Shyampur (old) 132 kV line-1 & 2
Sikalbaha | 1 | 1:04 | 21 | 22.4 | Due to red-hot maintenance of 132/33 kV Transformer T3
Dohazari | 1 | 2:10 | 20 | 43.33 | Due to red-hot maintenance of 132/33 kV Transformer T2
G.K project | 1 | 2:02 | 24 | 48.8 | Due to PT burst of 132/33 kV Transfoemers T1 & T2
Halishahar | 1 | 0:35 | 45 | 26.25 | Due to tripping of 132/33 kV Transformers T1 & T3
Cox'sbazar | 1 | 1:28 | 10 | 14.6667 | Due to sparking at Cox'sbazar-Dohazari 132 kV line-1
Hathazari | 1 | 0:42 | 750 | 525 | Due to tripping of Hathazari-Bariohat 132 kV line-1 & 2
G.K project | 1 | 9:31 | 20 | 190.3333 | Due to S/D of 33 kV Bus
Bakulia | 1 | 0:30 | 40 | 20 | Due to S/D of 132/33 kV Transformer T2
Sreemongal | 1 | 0:01 | 9 | 0.15 | Due to tripping of 132/33 kV Transformers T2 & T3
B.Baria | 1 | 1:55 | 25 | 68.75 | Due to tripping of 132/33 kV Transformer T1
Sylhet | 1 | 0:13 | 27 | 5.85 | Due to tripping of Sylhet-Fenchuganj 132 kV line
B.Baria | 1 | 4:15 | 25 | 170 | Due to tripping of 132/33 kV Transformer T2
Cumilla(S) | 1 | 0:02 | 40 | 1.3333 | Due to S/D of Cumilla(s)-Surjamoninagar 132 kV line-1 & 2
Mongla | 1 | 0:13 | 26 | 5.6333 | Due to tripping of 132/33 kV Transformers T1 & T2
Gopalganj | 1 | 1:59 | 32 | 62.9333 | Due to tripping of 132/33 kV Transformers T1 & T2
Bagerhat |  | 0:03 | 116 | 5.8 | Due to tripping of Bagerhat-Bhandaria 132 kV line
Mongla | 1 | 0:39 | 38 | 24.7 | Due to tripping of Mongla-Bagerhat 132 kV line
Barishal | 2 | 1:00 | 20 | 0.33333 | Due to tripping of Barishal-Patuakhali 132 kV line
|  | 0:22 | 43 | 15.7667 | Due to tripping of Barishal-Barishal(N) 132 kV line
Bagerhat | 1 | 0:13 | 1 | 0.21667 | Due to tripping of Bagerhat-Bhandaria 132 kV line
Madaripur | 1 | 3:28 | 12 | 41.6 | Due to S/D of 132/33 kV Transformer T2
Mongla | 1 | 4:12 | 20 | 84 | Due to S/D of 132/33 kV Transformer T1
Bhandaria | 1 | 0:17 | 8 | 2.2667 | Due to S/D of 132/33 kV Transformer T2
Bheramara.GK | 1 | 0:29 | 30 | 14.5 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
Bottail | 1 | 0:34 | 24 | 13.6 | Due to tripping of 132/33 kV Transformers T1 & T2
Kustia | 1 | 4:15 | 32 | 136 | Due to S/D of 132 kV Bus-A & B
Niyamatpur | 1 | 1:19 | 35 | 61.25 | Due to red-hot maintenance of 132/33 kV Transformer T2
Natore | 1 | 0:28 | 18 | 8.4 | Due to red-hot maintenance of 132/33 kV Transformer T3
Rajshahi | 1 | 0:07 | 64 | 7.4667 | Due to tripping of 132/33 kV Transformers T1 & T2
Naogaon | 1 | 0:43 | 20 | 14.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bogura | 3 | 0:23 | 183 | 70.15 | Due to tripping of Bogura-Naogaon 132 kV line-1
|  | 0:38 | 201 | 127.3 | Due to tripping of Bogura-Naogaon 132 kV line-2
|  | 1:05 | 25 | 27.0833 | Due to tripping of Ishurdi-HVDC 230 kV line-4
Natore | 1 | 7:25 | 50 | 370.8333 | Due to S/D of 132/33 kV Transformers T1 & T2
Bogura | 2 | 2:50 | 40 | 113.3333 | Due to S/D of 132/33 kV Transformers T1 & T2
|  | 15:19 | 15 | 229.75 | Due to S/D of Bogura-Naogaon 132 kv line-1
Naogaon | 2 | 1:38 | 23 | 37.5667 | Due to S/D of Naogaon-Joypurhat 132 kV line
|  | 12:07 | 15 | 181.75 | Due to S/D of Naogaon-Bogura 132 kV line-1
| Total unserved energy : |  |  | 4215.88 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:February'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 100 | 19 | 2019-02-01 | 15:00
2 | Munsiganj | 82 | 1 | 2019-02-01 | 19:30
3 | Sonargaon | 54 | 26 | 2019-02-01 | 16:00
4 | Shyampur | 170 | 12 | 2019-02-01 | 12:00
5 | Bhulta | 165 | 3 | 2019-02-01 | 19:00
6 | Madanganj | 56 | 17 | 2019-02-01 | 21:00
7 | Shitalakhya | 99 | 24 | 2019-02-01 | 12:00
8 | Rahim steel | 20 | 26 | 2019-02-01 | 11:00
9 | Matuail | 86 | 6 | 2019-02-01 | 11:00
10 | Ghorasal | 71 | 6 | 2019-02-01 | 19:30
11 | Narsingdi | 108 | 23 | 2019-02-01 | 19:00
12 | Haripur (SBU) | 102 | 13 | 2019-02-01 | 16:00
13 | Ullon | 60 | 13 | 2019-02-01 | 18:30
14 | Hasnabad | 164 | 19 | 2019-02-01 | 20:00
15 | Magbazar | 100 | 7 | 2019-02-01 | 13:00
16 | Maniknagar | 97 | 6 | 2019-02-01 | 15:00
17 | Bangabhaban | 20 | 13 | 2019-02-01 | 13:00
18 | Narinda | 86 | 23 | 2019-02-01 | 16:00
19 | Dhanmondi | 90 | 24 | 2019-02-01 | 13:00
20 | Lalbag | 68 | 20 | 2019-02-01 | 13:00
21 | Madartek | 42 | 23 | 2019-02-01 | 19:00
22 | Mirpur | 84 | 23 | 2019-02-01 | 18:30
23 | Kalyanpur | 84 | 23 | 2019-02-01 | 18:30
24 | Gulshan | 92 | 24 | 2019-02-01 | 13:00
25 | Uttara | 42 | 23 | 2019-02-01 | 19:00
26 | Uttara(new) | 14 | 26 | 2019-02-01 | 10:00
27 | Kamrangirchar | 66 | 23 | 2019-02-01 | 18:00
28 | Savar | 113 | 23 | 2019-02-01 | 18:30
29 | Bhasantec | 124 | 23 | 2019-02-01 | 18:30
30 | Agargaon | 40 | 2 | 2019-02-01 | 18:30
31 | Satmosjid | 72 | 23 | 2019-02-01 | 19:30
32 | Tongi | 132 | 23 | 2019-02-01 | 15:00
33 | Kabirpur | 193 | 16 | 2019-02-01 | 19:00
34 | Basundhara | 98 | 24 | 2019-02-01 | 18:30
35 | Manikganj | 76 | 16 | 2019-02-01 | 19:30
36 | Joydevpur | 197 | 3 | 2019-02-01 | 19:00
37 | New Tongi | 99 | 9 | 2019-02-01 | 15:00
38 | Kodda | 225 | 24 | 2019-02-01 | 15:00
39 | Dhamrai | 48 | 16 | 2019-02-01 | 18:30
40 | Valuka | 67 | 9 | 2019-02-01 | 20:00
41 | Tangail | 162 | 24 | 2019-02-01 | 18:30
42 | Mymensing | 220 | 2 | 2019-02-01 | 18:30
43 | Kishorganj | 86 | 9 | 2019-02-01 | 18:30
44 | Netrokona | 93 | 5 | 2019-02-01 | 18:30
45 | Jamalpur | 108 | 3 | 2019-02-01 | 18:30
46 | Sherpur | 100 | 1 | 2019-02-01 | 19:00
47 | Srimongal | 24 | 6 | 2019-02-01 | 19:00
48 | Shahjibazar | 89 | 23 | 2019-02-01 | 19:00
49 | Fenchuganj | 31 | 28 | 2019-02-01 | 19:00
50 | Kulawara | 28 | 11 | 2019-02-01 | 18:30
51 | Sylhet | 99 | 26 | 2019-02-01 | 19:30
52 | Chatak | 24 | 26 | 2019-02-01 | 19:30
53 | Sunamganj | 25 | 7 | 2019-02-01 | 19:30
54 | Bianibazar | 30 | 16 | 2019-02-01 | 18:30
55 | Cumilla (S) | 152 | 23 | 2019-02-01 | 18:30
56 | Cumilla(N) | 96 | 22 | 2019-02-01 | 20:00
57 | Chandpur | 85 | 3 | 2019-02-01 | 18:30
58 | Feni | 105 | 24 | 2019-02-01 | 19:00
59 | Chowmuhani | 152 | 23 | 2019-02-01 | 18:30
60 | Ashuganj | 46 | 23 | 2019-02-01 | 19:00
61 | Daudkandi | 94 | 20 | 2019-02-01 | 18:30
62 | B.Baria | 106 | 23 | 2019-02-01 | 18:30
63 | Ramganj | 28 | 23 | 2019-02-01 | 18:30
64 | Madanhat | 68 | 24 | 2019-02-01 | 18:30
65 | Hathazari | 74 | 20 | 2019-02-01 | 13:00
66 | Khulshi | 196 | 24 | 2019-02-01 | 18:30
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:February'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Halishahar | 137 | 18 | 2019-02-01 | 23:00
68 | Baraulia | 154 | 3 | 2019-02-01 | 19:00
69 | Sikalbaha | 32 | 24 | 2019-02-01 | 18:30
70 | Dohazari | 80 | 19 | 2019-02-01 | 20:00
71 | Cox'sbazar | 78 | 27 | 2019-02-01 | 18:30
72 | Chandraghona | 23 | 3 | 2019-02-01 | 18:30
73 | Kaptai | 4 | 1 | 2019-02-01 | 3:00
74 | A. Khaer Stl. | 8 | 6 | 2019-02-01 | 18:30
75 | Bakulia | 86 | 23 | 2019-02-01 | 18:30
76 | Julda | 22 | 11 | 2019-02-01 | 11:00
77 | TK chemical | 6 | 7 | 2019-02-01 | 10:00
78 | Modern Steel | 18 | 13 | 2019-02-01 | 18:30
79 | Shahmirpur | 25.5 | 2 | 2019-02-01 | 18:30
80 | Khagrachhari | 17 | 8 | 2019-02-01 | 19:30
81 | Matarbari | 25.5 | 3 | 2019-02-01 | 18:00
82 | Baroiar Hat | 24 | 5 | 2019-02-01 | 18:30
83 | Rangamati | 10 | 3 | 2019-02-01 | 3:00
84 | Abul Khair 230 | 162 | 4 | 2019-02-01 | 21:00
85 | BSRM | 110 | 1 | 2019-02-01 | 19:00
86 | Goalpara | 31.8 | 7 | 2019-02-01 | 19:00
87 | Central s/s | 66 | 28 | 2019-02-01 | 18:30
88 | Noapara | 79 | 7 | 2019-02-01 | 19:30
89 | Jashore | 174 | 3 | 2019-02-01 | 19:00
90 | Jhenida | 81 | 6 | 2019-02-01 | 19:00
91 | Bottail | 96 | 19 | 2019-02-01 | 18:30
92 | G.K Project | 38 | 5 | 2019-02-01 | 18:30
93 | Faridpur | 124 | 4 | 2019-02-01 | 19:30
94 | Madaripur | 97 | 22 | 2019-02-01 | 19:30
95 | Gopalganj | 66 | 4 | 2019-02-01 | 19:30
96 | Bagerhat | 68 | 16 | 2019-02-01 | 16:00
97 | Mongla | 40 | 16 | 2019-02-01 | 20:00
98 | Satkhira | 75 | 22 | 2019-02-01 | 14:00
99 | Gallamari | 42 | 27 | 2019-02-01 | 18:30
100 | Magura | 43 | 4 | 2019-02-01 | 18:30
101 | Chuadanga | 59 | 11 | 2019-02-01 | 19:30
102 | Barishal | 88 | 6 | 2019-02-01 | 19:30
103 | Patuakhali | 66 | 1 | 2019-02-01 | 19:30
104 | Bhandaria | 42 | 1 | 2019-02-01 | 18:30
105 | Ishurdi | 43 | 9 | 2019-02-01 | 1:00
106 | Ruppur Paromanobik | 1 | 1 | 2019-02-01 | 18:30
107 | Natore | 99 | 14 | 2019-02-01 | 19:00
108 | Bogura | 202 | 4 | 2019-02-01 | 20:00
109 | Noagaon | 116 | 5 | 2019-02-01 | 19:30
110 | Rajshahi | 109 | 18 | 2019-02-01 | 19:00
111 | C.Nawabganj | 64 | 5 | 2019-02-01 | 18:30
112 | Amnura | 41 | 9 | 2019-02-01 | 19:00
113 | Pabna | 87 | 12 | 2019-02-01 | 19:00
114 | Shahjadpur | 80 | 20 | 2019-02-01 | 08:00
115 | Serajganj | 79 | 5 | 2019-02-01 | 18:30
116 | Niyamatpur | 95 | 1 | 2019-02-01 | 10:00
117 | Joypurhat | 51 | 26 | 2019-02-01 | 19:30
118 | Mohastangor | 10 | 12 | 2019-02-01 | 19:00
119 | Rangpur | 112 | 13 | 2019-02-01 | 18:30
120 | Lalmonirhat | 83 | 1 | 2019-02-01 | 18:30
121 | Saidpur | 103 | 3 | 2019-02-01 | 19:30
122 | Purbasadipur | 95 | 6 | 2019-02-01 | 18:30
123 | Thakurgaon | 70 | 5 | 2019-02-01 | 19:00
124 | Palashbari | 100 | 9 | 2019-02-01 | 8:00
125 | Barapukuria | 53 | 1 | 2019-02-01 | 18:30
126 | Panchagar | 40 | 12 | 2019-02-01 | 18:30
127 | Joldhaka | 18 | 1 | 2019-02-01 | 19:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 412 | 26 | 2019-02-01 | 05:00 | 390 | 19 | 2019-02-01 | 11:00
2 | Bheramara | 400 | 407 | 4 | 2019-02-01 | 04:00 | 383 | 23 | 2019-02-01 | 19:00
3 | Ashuganj(N) | 400 | 414 | 26 | 2019-02-01 | 5:00 | 385 | 14 | 2019-02-01 | 11:00
4 | Kaliakoir | 400 | 405 | 26 | 2019-02-01 | 04:00 | 371 | 27 | 2019-02-01 | 12:00
5 | Bhulta | 400 | 412 | 2 | 2019-02-01 | 4:00 | 383 | 14 | 2019-02-01 | 12:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 242 | 12 | 2019-02-01 | 04:00 | 220 | 5 | 2019-02-01 | 13:00
2 | Ishurdi | 230 | 243 | 26 | 2019-02-01 | 05:00 | 223 | 4 | 2019-02-01 | 07:00
3 | Ashuganj | 230 | 246 | 26 | 2019-02-01 | 4:00 | 229 | 23 | 2019-02-01 | 16:00
4 | Serajganj | 230 | 234 | 26 | 2019-02-01 | 5:00 | 216 | 4 | 2019-02-01 | 8:00
5 | Baghabari | 230 | 237 | 14 | 2019-02-01 | 2:00 | 219 | 3 | 2019-02-01 | 12:00
6 | Barapukuria | 230 | 240 | 27 | 2019-02-01 | 14:00 | 203 | 6 | 2019-02-01 | 22:00
7 | Bogra | 230 | 232 | 27 | 2019-02-01 | 14:00 | 205 | 4 | 2019-02-01 | 8:00
8 | Khulna South | 230 | 245 | 25 | 2019-02-01 | 7:00 | 217 | 24 | 2019-02-01 | 7:00
9 | Rampura | 230 | 232 | 17 | 2019-02-01 | 08:00 | 220 | 14 | 2019-02-01 | 12:00
10 | Haripur | 230 | 237 | 17 | 2019-02-01 | 8:00 | 219 | 14 | 2019-02-01 | 12:00
11 | Hasnabad | 230 | 235 | 1 | 2019-02-01 | 7:00 | 215 | 12 | 2019-02-01 | 11:00
12 | Aminbazar | 230 | 238 | 17 | 2019-02-01 | 08:00 | 218 | 14 | 2019-02-01 | 11:00
13 | Tongi | 230 | 235 | 26 | 2019-02-01 | 03:00 | 215 | 14 | 2019-02-01 | 12:00
14 | Comilla (N) | 230 | 243 | 26 | 2019-02-01 | 6:00 | 230 | 3 | 2019-02-01 | 12:00
15 | Hathazari | 230 | 231 | 6 | 2019-02-01 | 19:00 | 208 | 27 | 2019-02-01 | 10:00
16 | Megnaghat | 230 | 240 | 17 | 2019-02-01 | 8:00 | 222 | 14 | 2019-02-01 | 11:00
17 | Fenchuganj | 230 | 245 | 26 | 2019-02-01 | 4:00 | 229 | 12 | 2019-02-01 | 18:00
18 | Siddhirganj | 230 | 236 | 2 | 2019-02-01 | 04:00 | 220 | 14 | 2019-02-01 | 12:00
19 | Maniknagar | 230 | 238 | 17 | 2019-02-01 | 8:00 | 218 | 14 | 2019-02-01 | 15:00
20 | Old Airport | 230 | 239 | 26 | 2019-02-01 | 05:00 | 215 | 12 | 2019-02-01 | 12:00
21 | Barisal | 230 | 244 | 25 | 2019-02-01 | 07:00 | 223 | 13 | 2019-02-01 | 13:00
22 | AKSML | 230 | 231 | 1 | 2019-02-01 | 18:30 | 211 | 7 | 2019-02-01 | 15:00
23 | BSRM | 230 | 232 | 1 | 2019-02-01 | 18:30 | 212 | 24 | 2019-02-01 | 12:00
24 | Bibiyana | 230 | 245 | 2 | 2019-02-01 | 03:00 | 232 | 18 | 2019-02-01 | 15:00
25 | Bhulta | 230 | 237 | 17 | 2019-02-01 | 8:00 | 221 | 14 | 2019-02-01 | 12:00
26 | Ashuganj (S) | 230 | 244 | 26 | 2019-02-01 | 5:00 | 230 | 20 | 2019-02-01 | 12:00
27 | Kaliakoir | 230 | 242 | 26 | 2019-02-01 | 5:00 | 219 | 14 | 2019-02-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 17 | 2019-02-01 | 08:00 | 129 | 3 | 2019-02-01 | 12:00
2 | Munsiganj | 132 | 140 | 2 | 2019-02-01 | 20:00 | 128 | 4 | 2019-02-01 | 11:00
3 | Megnaghat | 132 | 142 | 7 | 2019-02-01 | 13:00 | 127 | 3 | 2019-02-01 | 13:00
4 | Shyampur | 132 | 144 | 17 | 2019-02-01 | 8:00 | 122 | 11 | 2019-02-01 | 13:00
5 | Bhulta | 132 | 135 | 17 | 2019-02-01 | 8:00 | 121 | 12 | 2019-02-01 | 12:00
6 | Madanganj | 132 | 140 | 17 | 2019-02-01 | 7:00 | 125 | 12 | 2019-02-01 | 11:00
7 | Shitalakhya | 132 | 145 | 17 | 2019-02-01 | 08:00 | 121 | 12 | 2019-02-01 | 12:00
8 | Rahim Steal | 132 | 141 | 17 | 2019-02-01 | 08:00 | 129 | 4 | 2019-02-01 | 11:00
9 | Matuail | 132 | 140 | 17 | 2019-02-01 | 08:00 | 128 | 4 | 2019-02-01 | 10:00
10 | Ghorasal | 132 | 145 | 15 | 2019-02-01 | 18:00 | 135 | 23 | 2019-02-01 | 17:00
11 | Narsinghdi | 132 | 141 | 26 | 2019-02-01 | 4:00 | 129 | 3 | 2019-02-01 | 9:00
12 | Haripur (SBU) | 132 | 140 | 17 | 2019-02-01 | 8:00 | 128 | 11 | 2019-02-01 | 13:00
13 | Ullon | 132 | 137 | 26 | 2019-02-01 | 6:00 | 124 | 14 | 2019-02-01 | 12:00
14 | Hasnabad | 132 | 140 | 1 | 2019-02-01 | 7:00 | 124 | 11 | 2019-02-01 | 12:00
15 | Magbazar | 132 | 138 | 12 | 2019-02-01 | 6:00 | 124 | 14 | 2019-02-01 | 12:00
16 | Maniknagar | 132 | 138 | 17 | 2019-02-01 | 8:00 | 125 | 5 | 2019-02-01 | 12:00
17 | Bangabhaban | 132 | 143 | 26 | 2019-02-01 | 5:00 | 122 | 12 | 2019-02-01 | 12:00
18 | Narinda | 132 | 137 | 26 | 2019-02-01 | 6:00 | 123 | 14 | 2019-02-01 | 12:00
19 | Dhanmondi | 132 | 137 | 26 | 2019-02-01 | 6:00 | 124 | 23 | 2019-02-01 | 18:00
20 | Lalbag | 132 | 143 | 26 | 2019-02-01 | 5:00 | 122 | 12 | 2019-02-01 | 12:00
21 | Madartek | 132 | 137 | 26 | 2019-02-01 | 06:00 | 123 | 14 | 2019-02-01 | 12:00
22 | Mirpur | 132 | 136 | 1 | 2019-02-01 | 2:00 | 123 | 12 | 2019-02-01 | 12:00
23 | Kalyanpur | 132 | 142 | 1 | 2019-02-01 | 7:00 | 103 | 3 | 2019-02-01 | 12:00
24 | Gulshan | 132 | 134 | 16 | 2019-02-01 | 5:00 | 124 | 12 | 2019-02-01 | 12:00
25 | Uttara | 132 | 140 | 26 | 2019-02-01 | 5:00 | 121 | 12 | 2019-02-01 | 12:00
26 | Uttara(New) | 132 | 135 | 28 | 2019-02-01 | 5:00 | 121 | 12 | 2019-02-01 | 12:00
27 | Kamrangirchar | 132 | 142 | 2 | 2019-02-01 | 4:00 | 122 | 12 | 2019-02-01 | 12:00
28 | Savar | 132 | 136 | 26 | 2019-02-01 | 6:00 | 121 | 12 | 2019-02-01 | 12:00
29 | Bhasantec | 132 | 142 | 26 | 2019-02-01 | 5:00 | 124 | 14 | 2019-02-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 142 | 26 | 2019-02-01 | 06:00 | 122 | 11 | 2019-02-01 | 13:00
31 | Satmosjid | 132 | 142 | 26 | 2019-02-01 | 05:00 | 124 | 12 | 2019-02-01 | 12:00
32 | Tongi | 132 | 142 | 26 | 2019-02-01 | 3:00 | 127 | 23 | 2019-02-01 | 15:00
33 | Kabirpur | 132 | 141 | 26 | 2019-02-01 | 4:00 | 125 | 23 | 2019-02-01 | 15:00
34 | Basundhara | 132 | 139 | 11 | 2019-02-01 | 2:00 | 120 | 13 | 2019-02-01 | 16:00
35 | Manikganj | 132 | 144 | 26 | 2019-02-01 | 4:00 | 132 | 3 | 2019-02-01 | 9:00
36 | Joydevpur | 132 | 148 | 26 | 2019-02-01 | 06:00 | 130 | 23 | 2019-02-01 | 18:00
37 | New Tongi | 132 | 140 | 17 | 2019-02-01 | 08:00 | 126 | 5 | 2019-02-01 | 12:00
38 | Kodda | 132 | 147 | 26 | 2019-02-01 | 04:00 | 120 | 27 | 2019-02-01 | 15:00
39 | Dhamrai | 132 | 140 | 26 | 2019-02-01 | 04:00 | 125 | 3 | 2019-02-01 | 09:00
40 | Valuka | 132 | 140 | 9 | 2019-02-01 | 03:00 | 112 | 8 | 2019-02-01 | 7:00
41 | Tangail | 132 | 140 | 26 | 2019-02-01 | 3:00 | 125 | 4 | 2019-02-01 | 7:00
42 | Mymensing | 132 | 140 | 9 | 2019-02-01 | 17:00 | 118 | 13 | 2019-02-01 | 8:00
43 | Kishorganj | 132 | 140 | 27 | 2019-02-01 | 04:00 | 122 | 1 | 2019-02-01 | 8:00
44 | Netrokona | 132 | 141 | 26 | 2019-02-01 | 01:00 | 117 | 1 | 2019-02-01 | 7:00
45 | Jamalpur | 132 | 138 | 17 | 2019-02-01 | 5:00 | 111 | 13 | 2019-02-01 | 7:00
46 | Sherpur | 132 | 140 | 9 | 2019-02-01 | 07:00 | 112 | 13 | 2019-02-01 | 15:00
47 | Srimongal | 132 | 142 | 28 | 2019-02-01 | 08:00 | 136 | 8 | 2019-02-01 | 17:00
48 | Shahjibazar | 132 | 141 | 17 | 2019-02-01 | 07:00 | 134 | 24 | 2019-02-01 | 18:00
49 | Fenchuganj | 132 | 140 | 26 | 2019-02-01 | 24:00 | 133 | 23 | 2019-02-01 | 18:00
50 | Khulawara | 132 | 138 | 2 | 2019-02-01 | 6:00 | 133 | 23 | 2019-02-01 | 18:00
51 | Sylhet | 132 | 139 | 20 | 2019-02-01 | 05:00 | 129 | 23 | 2019-02-01 | 18:30
52 | Chattak | 132 | 138 | 22 | 2019-02-01 | 07:00 | 129 | 23 | 2019-02-01 | 7:00
53 | Sunamganj | 132 | 138 | 17 | 2019-02-01 | 08:00 | 128 | 23 | 2019-02-01 | 18:30
54 | Biani Bazar | 132 | 139 | 17 | 2019-02-01 | 10:00 | 131 | 19 | 2019-02-01 | 21:00
55 | Comilla(South) | 132 | 132 | 17 | 2019-02-01 | 7:00 | 122 | 18 | 2019-02-01 | 12:00
56 | Comilla (North) | 132 | 145 | 26 | 2019-02-01 | 15:00 | 132 | 24 | 2019-02-01 | 24:00
57 | Chandpur | 132 | 141 | 5 | 2019-02-01 | 8:00 | 130 | 23 | 2019-02-01 | 12:00
58 | Feni | 132 | 137 | 25 | 2019-02-01 | 09:00 | 125 | 12 | 2019-02-01 | 19:00
59 | Chowmuhani | 132 | 137 | 25 | 2019-02-01 | 9:00 | 122 | 24 | 2019-02-01 | 7:00
60 | Ashuganj | 132 | 143 | 17 | 2019-02-01 | 8:00 | 129 | 2 | 2019-02-01 | 12:00
61 | Daudkandi | 132 | 141 | 17 | 2019-02-01 | 4:00 | 129 | 12 | 2019-02-01 | 1:00
62 | Brahminbaria | 132 | 143 | 26 | 2019-02-01 | 14:00 | 132 | 15 | 2019-02-01 | 18:00
63 | Ramganj | 132 | 137 | 7 | 2019-02-01 | 18:00 | 126 | 16 | 2019-02-01 | 11:00
64 | Madanhat | 132 | 140 | 1 | 2019-02-01 | 19:00 | 126 | 7 | 2019-02-01 | 10:00
65 | Hathazari | 132 | 137 | 1 | 2019-02-01 | 20:00 | 125 | 27 | 2019-02-01 | 12:00
66 | Khulshi | 132 | 136 | 1 | 2019-02-01 | 18:30 | 122 | 12 | 2019-02-01 | 12:00
67 | Halishahar | 132 | 140 | 1 | 2019-02-01 | 18:00 | 124 | 12 | 2019-02-01 | 12:00
68 | Baraulia | 132 | 137 | 1 | 2019-02-01 | 18:00 | 123 | 12 | 2019-02-01 | 12:00
69 | Sikalbaha | 132 | 138 | 1 | 2019-02-01 | 9:00 | 124 | 12 | 2019-02-01 | 12:00
70 | Dohazari | 132 | 139 | 1 | 2019-02-01 | 21:00 | 124 | 12 | 2019-02-01 | 12:00
71 | Cox'sbazar | 132 | 134 | 21 | 2019-02-01 | 18:30 | 116 | 12 | 2019-02-01 | 11:00
72 | Chandraghona | 132 | 138 | 1 | 2019-02-01 | 10:00 | 126 | 7 | 2019-02-01 | 12:00
73 | Kaptai | 132 | 137 | 1 | 2019-02-01 | 18:00 | 129 | 26 | 2019-02-01 | 12:00
74 | A. Khaer Stl. | 132 | 136 | 1 | 2019-02-01 | 09:00 | 124 | 12 | 2019-02-01 | 12:00
75 | Bakulia | 132 | 136 | 1 | 2019-02-01 | 18:00 | 122 | 12 | 2019-02-01 | 03:00
76 | Julda | 132 | 138 | 1 | 2019-02-01 | 18:00 | 124 | 11 | 2019-02-01 | 11:00
77 | TK Chemical | 132 | 141 | 1 | 2019-02-01 | 18:30 | 126 | 7 | 2019-02-01 | 11:00
78 | Modern Steel | 132 | 138 | 1 | 2019-02-01 | 09:00 | 121 | 7 | 2019-02-01 | 3:00
79 | Shahmirpur | 132 | 137 | 1 | 2019-02-01 | 18:00 | 124 | 10 | 2019-02-01 | 11:00
80 | Khagrachhari | 132 | 138 | 1 | 2019-02-01 | 09:00 | 125 | 7 | 2019-02-01 | 12:00
81 | Matarbari | 132 | 137 | 1 | 2019-02-01 | 12:00 | 118 | 7 | 2019-02-01 | 12:00
82 | Baroiar Hat | 133 | 139 | 13 | 2019-02-01 | 18:00 | 126 | 12 | 2019-02-01 | 11:00
83 | Rangamati | 132 | 138 | 1 | 2019-02-01 | 4:00 | 124 | 7 | 2019-02-01 | 7:00
84 | Goalpara | 132 | 140 | 9 | 2019-02-01 | 14:00 | 125 | 3 | 2019-02-01 | 18:30
85 | Khulna Central | 132 | 139 | 12 | 2019-02-01 | 5:00 | 123 | 12 | 2019-02-01 | 08:00
86 | Noapara | 132 | 137 | 1 | 2019-02-01 | 3:00 | 120 | 4 | 2019-02-01 | 18:30
87 | Jessore | 132 | 135 | 9 | 2019-02-01 | 5:00 | 115 | 12 | 2019-02-01 | 18:30
88 | Jhenida | 132 | 143 | 26 | 2019-02-01 | 6:00 | 112 | 12 | 2019-02-01 | 13:00
89 | Bottail | 132 | 142 | 26 | 2019-02-01 | 03:00 | 129 | 21 | 2019-02-01 | 11:00
90 | G.K.Project | 132 | 145 | 26 | 2019-02-01 | 6:00 | 132 | 2 | 2019-02-01 | 12:00
91 | Faridpur | 132 | 140 | 26 | 2019-02-01 | 6:00 | 127 | 21 | 2019-02-01 | 12:00
92 | Madaripur | 132 | 142 | 26 | 2019-02-01 | 5:00 | 126 | 21 | 2019-02-01 | 21:00
93 | Gopalganj | 132 | 145 | 26 | 2019-02-01 | 10:00 | 123 | 28 | 2019-02-01 | 18:30
94 | Bagerhat | 132 | 140 | 1 | 2019-02-01 | 10:00 | 120 | 12 | 2019-02-01 | 18:30
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
95 | Mongla | 132 | 137 | 1 | 2019-02-01 | 2:00 | 119 | 12 | 2019-02-01 | 18:30
96 | Satkhira | 132 | 140 | 26 | 2019-02-01 | 4:00 | 120 | 12 | 2019-02-01 | 18:30
97 | Gallamari | 132 | 139 | 10 | 2019-02-01 | 18:30 | 124 | 12 | 2019-02-01 | 12:00
98 | Magura | 132 | 142 | 16 | 2019-02-01 | 4:00 | 117 | 28 | 2019-02-01 | 14:00
99 | Chuadanga | 132 | 144 | 26 | 2019-02-01 | 15:00 | 113 | 20 | 2019-02-01 | 14:00
100 | Barisal | 132 | 140 | 5 | 2019-02-01 | 17:00 | 128 | 27 | 2019-02-01 | 18:00
101 | Patuakhali | 132 | 140 | 4 | 2019-02-01 | 10:00 | 125 | 14 | 2019-02-01 | 18:00
102 | Bhandaria | 132 | 138 | 1 | 2019-02-01 | 4:00 | 117 | 12 | 2019-02-01 | 8:00
103 | Ishurdi | 132 | 144 | 26 | 2019-02-01 | 4:00 | 132 | 21 | 2019-02-01 | 18:30
104 | Ruppur paromanobik | 132 | 145 | 26 | 2019-02-01 | 2:00 | 135 | 5 | 2019-02-01 | 8:00
105 | Natore | 132 | 141 | 26 | 2019-02-01 | 4:00 | 126 | 5 | 2019-02-01 | 8:00
106 | Bogra | 132 | 141 | 9 | 2019-02-01 | 13:00 | 120 | 7 | 2019-02-01 | 8:00
107 | Noagaon | 132 | 138 | 27 | 2019-02-01 | 4:00 | 115 | 1 | 2019-02-01 | 8:00
108 | Rajshahi | 132 | 138 | 26 | 2019-02-01 | 18:00 | 123 | 3 | 2019-02-01 | 8:00
109 | C.Nawabganj | 132 | 136 | 7 | 2019-02-01 | 19:00 | 118 | 21 | 2019-02-01 | 8:00
110 | Amnura | 132 | 142 | 8 | 2019-02-01 | 3:00 | 120 | 21 | 2019-02-01 | 8:00
111 | Pabna | 132 | 140 | 26 | 2019-02-01 | 3:00 | 126 | 3 | 2019-02-01 | 12:00
112 | Shahjadpur | 132 | 145 | 28 | 2019-02-01 | 4:00 | 131 | 7 | 2019-02-01 | 8:00
113 | Serajganj | 132 | 141 | 26 | 2019-02-01 | 15:00 | 123 | 4 | 2019-02-01 | 8:00
114 | Niyamatpur | 132 | 140 | 27 | 2019-02-01 | 14:00 | 106 | 2 | 2019-02-01 | 11:00
115 | Joypurhat | 132 | 141 | 27 | 2019-02-01 | 6:00 | 112 | 3 | 2019-02-01 | 9:00
116 | Mohastangor | 132 | 141 | 27 | 2019-02-01 | 6:00 | 118 | 7 | 2019-02-01 | 10:00
117 | Rangpur | 132 | 139 | 9 | 2019-02-01 | 6:00 | 108 | 1 | 2019-02-01 | 8:00
118 | Lalmonirhat | 132 | 137 | 9 | 2019-02-01 | 7:00 | 100 | 1 | 2019-02-01 | 8:00
119 | Saidpur | 132 | 138 | 9 | 2019-02-01 | 6:00 | 106 | 12 | 2019-02-01 | 8:00
120 | Purbasadipur | 132 | 138 | 9 | 2019-02-01 | 12:00 | 100 | 3 | 2019-02-01 | 12:00
121 | Thakurgaon | 132 | 136 | 9 | 2019-02-01 | 5:00 | 92 | 3 | 2019-02-01 | 8:00
122 | Palashbari | 132 | 140 | 27 | 2019-02-01 | 7:00 | 112 | 3 | 2019-02-01 | 9:00
123 | Barapukuria | 132 | 140 | 9 | 2019-02-01 | 6:00 | 117 | 1 | 2019-02-01 | 8:00
124 | Panchagar | 132 | 134 | 9 | 2019-02-01 | 6:00 | 90 | 1 | 2019-02-01 | 8:00
125 | Joldhaka | 132 | 137 | 9 | 2019-02-01 | 6:00 | 106 | 3 | 2019-02-01 | 8:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:February' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 3175 | 24.02.19 | 19:00
Chattogram | 998 | 18.02.19 | 18:30
Khulna | 1097 | 23.02.19 | 19:30
Rajshahi | 1007 | 24.02.19 | 19:00
Cumilla | 788 | 24.02.19 | 19:00
Mymensingh | 785 | 16.02.19 | 18:30
Sylhet | 334 | 06.02.19 | 19:00
Barisal | 235 | 23.02.19 | 20:00
Rangpur | 637 | 04.02.19 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:February' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 110 | 370
IP-299421 | Hasnabad | TR2 | 225 | 100 | 370 | 12.02.19 | 12:00
|  | TR3 | 225 | 100 | 360
|  | TR1 | 225 | 125 | 350
IP-299866 | Tongi | TR2 | 225 | 125 | 350 | 23.02.19 | 18:30
|  | TR3 | 225 | 125 | 350
|  | TR1 | 225 | 105 | 380
IP-299427 | Haripur | TR2 | 225 |  |  | 11.02.19 | 13:00 | S/D
|  | TR3 | 225 | 105 | 380
|  | TR1 | 225 | 125 | 360
IP-299728 | Rampura | TR2 | 225 | 125 | 360 | 09.02.19 | 14:00
|  | TR3 | 225 | 125 | 360
|  | TR1 | 225 | 111 | 295
IP-299264 | Aminbazar | TR2 | 225 | 111 | 295 | 03.02.19 | 12:00
|  | TR3 | 225 | 113 | 299
| Maniknagar | TR1 | 300 | 94 | 300 | 24.02.19 | 19:00
|  | TR2 | 300 | 94 | 300
IP-399266 | Cumilla (N) | TR1 | 225 | 149 | 405 | 23.02.19 | 4:00
|  | TR2 | 225 | 149 | 405
| Fenchuganj | TR1 | 300 | 187 | 470 | 18.02.19 | 12:00
|  | TR1 | 150 | 127 | 380
IP-399428 | Hathazari | TR3 | 150 | 127 | 380 | 27.02.19 | 10:00
|  | TR4 | 150 | 127 | 380
|  | TR1 | 225 | 105 | 480
| Ishurdi | TR2 | 225 | 105 | 480 | 23.02.19 | 20:00
IP-499474 |  | TR3 | 225 | 105 | 480
| Khulna(S) | TR1 | 225 | 187 | 502
IP-58001/58002 |  | TR2 | 225 | 187 | 502 | 12.02.19 | 18:30
| Bogra | TR1 | 225 | 120 | 375 | 24.02.19 | 7:00
|  | TR2 | 225 | 120 | 375
IP-43002/499264 |  | TR3 | 225 | 164 | 500
IP-499224 | Baghabari | TR1 | 225 | 150 | 450 | 03.02.19 | 12:00
| Barapukuria | TR1 | 225 | 195 | 920 | 27.02.19 | 14:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 117 | 940 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 144 | 692
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 348.6 | 584 | 11.02.19 | 13:00
|  | TR1(400/132 kV) | 325 | 188.3 | 305 | 16.02.19 | 7:00
|  | TR2(400/132 kV) | 325 | 188.3 | 305
| Bibiyana | ICT1(400/230 kV) | 520 | 155 | 238 | 18.02.19 | 20:00
|  | ICT2(400/230kV) | 520 | 154 | 235
| Bhulta | ATR1(400/230 kV) | 520 | 196 | 311 | 26.02.19 | 13:30
|  | ATR2(400/230kV) | 520 | 196 | 311
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:February' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:February' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-02-19 | 8038 | 8038 | - | - | - | - | - | - | - | - | - | - | - | - | 01-02-19 | 6056.3 | 6056.3 | - | - | - | - | - | - | - | - | - | - | - | -
02-02-19 | 8744 | 8744 | - | - | - | - | - | - | - | - | - | - | - | - | 02-02-19 | 7387.2 | 7387.2 | - | - | - | - | - | - | - | - | - | - | - | -
03-02-19 | 8763 | 8763 | - | - | - | - | - | - | - | - | - | - | - | - | 03-02-19 | 7483 | 7483 | - | - | - | - | - | - | - | - | - | - | - | -
04-02-19 | 8919 | 8919 | - | - | - | - | - | - | - | - | - | - | - | - | 04-02-19 | 7275.5 | 7275 | - | - | - | - | - | - | - | - | - | - | - | -
05-02-19 | 8867 | 8867 | - | - | - | - | - | - | - | - | - | - | - | - | 05-02-19 | 7453 | 7453 | - | - | - | - | - | - | - | - | - | - | - | -
06-02-19 | 9063 | 9063 | - | - | - | - | - | - | - | - | - | - | - | - | 06-02-19 | 7028.1 | 7028.1 | - | - | - | - | - | - | - | - | - | - | - | -
07-02-19 | 8880 | 8880 | - | - | - | - | - | - | - | - | - | - | - | - | 07-02-19 | 7482.9 | 7482.9 | - | - | - | - | - | - | - | - | - | - | - | -
08-02-19 | 7853 | 7853 | - | - | - | - | - | - | - | - | - | - | - | - | 08-02-19 | 5952.9 | 5952.9 | - | - | - | - | - | - | - | - | - | - | - | -
09-02-19 | 8806 | 8806 | - | - | - | - | - | - | - | - | - | - | - | - | 09-02-19 | 6996.2 | 6996.2 | - | - | - | - | - | - | - | - | - | - | - | -
10-02-19 | 8733 | 8733 | - | - | - | - | - | - | - | - | - | - | - | - | 10-02-19 | 7006.3 | 7006.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-02-19 | 8863 | 8863 | - | - | - | - | - | - | - | - | - | - | - | - | 11-02-19 | 7348.7 | 7348.7 | - | - | - | - | - | - | - | - | - | - | - | -
12-02-19 | 8884 | 8884 | - | - | - | - | - | - | - | - | - | - | - | - | 12-02-19 | 7403.3 | 7403.3 | - | - | - | - | - | - | - | - | - | - | - | -
13-02-19 | 9030 | 9030 | - | - | - | - | - | - | - | - | - | - | - | - | 13-02-19 | 7467.3 | 7467.3 | - | - | - | - | - | - | - | - | - | - | - | -
14-02-19 | 9061 | 9061 | - | - | - | - | - | - | - | - | - | - | - | - | 14-02-19 | 7605.9 | 7605.9 | - | - | - | - | - | - | - | - | - | - | - | -
15-02-19 | 8243 | 8243 | - | - | - | - | - | - | - | - | - | - | - | - | 15-02-19 | 6250 | 6250 | - | - | - | - | - | - | - | - | - | - | - | -
16-02-19 | 8838 | 8838 | - | - | - | - | - | - | - | - | - | - | - | - | 16-02-19 | 7006.8 | 7006.8 | - | - | - | - | - | - | - | - | - | - | - | -
17-02-19 | 8824 | 8824 | - | - | - | - | - | - | - | - | - | - | - | - | 17-02-19 | 6667.2 | 6667.2 | - | - | - | - | - | - | - | - | - | - | - | -
18-02-19 | 8891 | 8891 | - | - | - | - | - | - | - | - | - | - | - | - | 18-02-19 | 7444.4 | 7444.4 | - | - | - | - | - | - | - | - | - | - | - | -
19-02-19 | 9066 | 9066 | - | - | - | - | - | - | - | - | - | - | - | - | 19-02-19 | 7377 | 7377 | - | - | - | - | - | - | - | - | - | - | - | -
20-02-19 | 9159 | 9159 | - | - | - | - | - | - | - | - | - | - | - | - | 20-02-19 | 7539.1 | 7539.1 | - | - | - | - | - | - | - | - | - | - | - | -
21-02-19 | 8096 | 8096 | - | - | - | - | - | - | - | - | - | - | - | - | 21-02-19 | 6527 | 6527 | - | - | - | - | - | - | - | - | - | - | - | -
22-02-19 | 8345 | 8345 | - | - | - | - | - | - | - | - | - | - | - | - | 22-02-19 | 6022.3 | 6022.3 | - | - | - | - | - | - | - | - | - | - | - | -
23-02-19 | 9397 | 9397 | - | - | - | - | - | - | - | - | - | - | - | - | 23-02-19 | 7765.8 | 7765.8 | - | - | - | - | - | - | - | - | - | - | - | -
24-02-19 | 9403 | 9403 | - | - | - | - | - | - | - | - | - | - | - | - | 24-02-19 | 7680 | 7680 | - | - | - | - | - | - | - | - | - | - | - | -
25-02-19 | 8684 | 8684 | - | - | - | - | - | - | - | - | - | - | - | - | 25-02-19 | 6734 | 6734 | - | - | - | - | - | - | - | - | - | - | - | -
26-02-19 | 8480 | 8480 | - | - | - | - | - | - | - | - | - | - | - | - | 26-02-19 | 6723 | 6723 | - | - | - | - | - | - | - | - | - | - | - | -
27-02-19 | 6346 | 6346 | - | - | - | - | - | - | - | - | - | - | - | - | 27-02-19 | 6518.2 | 6518.2 | - | - | - | - | - | - | - | - | - | - | - | -
28-02-19 | 7995 | 7995 | - | - | - | - | - | - | - | - | - | - | - | - | 28-02-19 | 6266 | 6266 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:February' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9403 | 24/02/19 | 19:00
2 | Maximum day peak Genaration | MW | 7765.8 | 23/02/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 9403 | 24/02/19 | 19:00
4 | Minimum Generation | MW | 3497 | 26/02/19 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8652.5357
6 | Average of the daily day peak Genaration | MW | 7016.6929
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 28 days in the month) | MW | -
11 | Total Generation | MKWH | 4623.8958
12 | Total Generation by IPP | MKWH | 988.9579 | % of total Gen. | 21.39%
13 | Total Generation by BPDB | MKWH | 2632.179 | " | 56.93%
14 | A) Total Generation by RPCL | MKWH | 97.6541 | '' | 2.112%
| B) Total Generation by REB | MKWH | 118.6409 | " | 2.566%
| C) Total Generation by RENTAL | MKWH | 299.974 | " | 6.487%
| D) Total Imported from India (HVDC) | MKWH | 421.5629 | " | 9.117%
| E) Total Imported from Tripura, India (A.C) | MKWH | 64.9269 | " | 1.404%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3514.5943 | % of total Gen. | 76.01%
| B) Oil | MKWH | 471.1569 | '' | 10.19%
| C) Hydro | MKWH | 44.7686 | '' | 0.9682%
| D) Solar | MKWH | 3.5208 | '' | 0.07614%
| E) Coal | MKWH | 103.3654 | '' | 2.235%
| F) HVDC (Import from India) | MKWH | 421.5629 | '' | 9.117%
| G) A.C (Import from Tripura, India) | MKWH | 64.9269 | '' | 1.404%
16 | Maximun of the daily total Generation . | MKWH | 179.5634 | 23/02/19
17 | Monthly Load factor | % | 73.1766
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 6677.7057
| A) Gas | M.Taka | 3242.4387
| B) Liquid fuel | M.Taka | 3036.2662
| C) Coal | M.Taka | 399.0009
| D) HVDC (Import from India) | M.Taka | 2149.9708
| E) Tripura(Import from India) | M.Taka | 444.1002
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 881.2608 | 28/02/19
| A) Gas | M.Taka | 842.471 | 28/02/19
| B) Liquid fuel | M.Taka | 208.9259 | 07/02/19
| C) Coal | M.Taka | 17.9266 | 20/02/19
| D) HVDC (Import from India) | M.Taka | 87.5716 | 19-02-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.2964
| B) Excluding Hydro & Solar | Taka/KWHR | 2.3206
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93.45 | 28/02/19 | 06:00
b) | Actual | FT (MSL) | 91.98 | 28/02/19 | 06:00
22 | Peak Genaration of February 2018 | MW | 8848 | 24/02/18 | 19:30
23 | Peak Demand of February 2018 | MW | 8028 | 24/02/18 | 19:30
24 | Maximum peak Generation recorded upto 28/02/19 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 28/02/19 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 28/02/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.