## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | January 2019 |  | December 2018 |  | January 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 8893 | 30/01/19 | 8534 | 04/12/18 | 8251 | 29/01/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 4350 | 01/01/19 | 3366 | 31/12/18 | 4098 | 06/01/18 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 8893 | 30/01/19 | 8534 | 04/12/18 | 8251 | 29/01/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 7189.5 | 27/01/19 | 6723.8 | 13/12/18 | 6766.4 | 02/01/18 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 9:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 8893 | 30/01/19 | 8534 | 04/12/18 | 8251 | 29/01/18 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 8425.0645 |  | 8032.26 |  | 7796.06 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 6485.9097 |  | 6134.52 |  | 6055.18 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 710 | 12/01/19 | 694 | 28/12/18 | 497 | 22/01/18 | 788 | 11/09/18
|  |  | 20:00 |  | 20:00 |  | 10:00 |  | 22:00
9 | Maximum Power Import from Tripura, India (MW) | 136 | 22'/01/19 | 134 | 23/12/18 | 132 | 25/01/18 | 188 | 29/05/18
|  |  | 19:30 |  | 18:00 |  | 18:30 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2531.5904 |  | 2648.26 |  | 2096.37
21 | Station Use of BPDB (MKWH) | 197.1123 |  | 104.02 |  | 74.33
22 | Net Generation of BPDB (MKWH) | 2334.4781 |  | 2544.23 |  | 2022.03
23 | Net Generation of IPP & RPCL (MKWH) | 1416.2616 |  | 1084.36 |  | 1343.21
24 | Net Generation of REB (MKWH) | 137.089 |  | 129.67 |  | 144.18
24 | Net Generation of Rental Power Plant (MKWH) | 350.9928 |  | 263.21 |  | 459.37
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4238.8214 |  | 4021.48 |  | 3968.79 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 3703.9793 |  | 3591.19 |  | 3085.21 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 28.7918 |  | 17.94 |  | 11 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 547.7089 |  | 354.68 |  | 744.01 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 35.2467 |  | 31.52 |  | 44.1 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 5.4525 |  | 4.72 |  | 0.17 |  | 5.45 | 2019-01-16
31 | Energy Generation by Coal (MKWH) | 114.7545 |  | 125.45 |  | 158.65 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 423.7544 |  | 412.4 |  | 339.25 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 73.4492 |  | 71.47 |  | 71.39 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:January' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 8893 | 30/01/19 | 19:00
Generation Period
| Dhaka | MW | 2931
| Chattogram | MW | 932
| Cumilla | MW | 681
| Mymensingh | MW | 704
| Sylhet | MW | 319
a) | Total supply in East zone | MW | 5567
| Khulna | MW | 1022
| Barisal | MW | 208
| Rajshahi | MW | 950
| Rangpur | MW | 599
b) | Total supply in West zone | MW | 2779
c) | Total supply in both zone ( a+b) | MW | 8346
Ref: | 27.21.2604.603.16.086.18.127 | Date: 14/02/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:January' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 920 | 29/01/19 | 1:00
| b) Ishurdi end | MW | 180 | 12/01/19 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 340 | 12/01/19 | 17:00
| b) Ishurdi end | MW | 400 | 29/01/19 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.0855 | 28/01/19
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 3.0276 | 28/01/19
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 82.7838
| b) Ishurdi end | MKWH | 4.1316
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 4.0077
| b) Ishurdi end | MKWH | 80.3726
23 | Transmission loss of EWI/ NO-1 | % | 2.912
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 29/01/19 | 1:00
| b)Serajganj end | MW | 80 | 09/01/19 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 50 | 09/01/19 | 10:00
| b)Sirajganj end | MW | 430 | 29/01/19 | 1:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 7.914 | 24/01/19
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 7.842 | 24/01/19
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 145.87
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 144.56
30 | Transmission loss of EWI /NO-2 | % | 0.899
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
New Tongi | 132/33 kV Transformers-T1 & T2 | 2019-01-15 03:55 | 2019-01-15 04:56 | 1:01 | T | Tripped showing U/G cable fault | 45 | 45.75 | Power interruption
Aminbazar | 230/132 kV Transformer-T1 | 2019-01-27 14:57 | 2019-01-27 20:09 | 5:12 | T | Tripped showing WTA relay 230 kV side & OLA at 132 kV side | 0 | 0 | No interruption
Hasnabad | 230 kV bus-2 | 2019-01-28 07:12 | 2019-01-28 12:24 | 1:45 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 7:58 |  | Unserved Energy: |  | 45.75
Dhaka (South) Grid Circle :
Shyampur | 132/33 kV Transformer-GT4 | 2019-01-15 11:44 | 2019-01-15 17:18 | 5:34 | T | Tripped showing Dir. & O/C relay | 0 | 0 | No interruption
|  |  | Total : | 5:34 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Sikalbaha | 132/33 kV Transformer-T1 | 2019-01-04 09:30 | 2019-01-04 10:50 | 1:20 | E/O | Due to re hot maintenance at 33 kV CT B-phase | 17 | 22.6667 | Power interruption
|  |  | Total : | 1:20 |  | Unserved Energy: |  | 22.6667
Cumilla Grid Circle :
Fenchuganj | 132/33 kV Transformer-T2 | 2019-01-10 16:30 | 2019-01-10 16:34 | 0:04 | T | Tripped showing O/C relay | 10 | 0.66667 | Power interruption
Chowmuhani | 132/33 kV Transformer-T2 | 2019-01-24 16:49 | 2019-01-24 18:05 | 1:16 | E/O | Due to re hot maintenance | 35 | 44.3333 | Power interruption
| 132/33 kV Transformers-T2 & T3 | 2019-01-24 18:20 | 2019-01-24 18:26 | 0:06 | T | Tripped showing O/C relay | 125 | 12.6 | Power interruption
| 132/33 kV Transformer-T2 | 2019-01-25 11:10 | 2019-01-25 13:05 | 1:55 | E/O | Due to re hot maintenance | 10 | 21.6667 | Power interruption 11:10 to 13:20
|  |  | Total : | 3:21 |  | Unserved Energy: |  | 79.2667
Khulna Grid Circle :
Mongla | 132/33 kV Transformers-T1 & T2 | 2019-01-01 09:28 | 2019-01-01 09:36 | 0:08 | T | Tripped showing O/C relay at 33 kV side | 20 | 2.6667 | Power interruption
Noapara | 132/33 kV Transformer-T1 | 2019-01-14 10:30 | 2019-01-14 12:02 | 1:32 | T | Due to 33 kV REB feeder fault | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2019-01-02 12:24 | 2019-01-02 12:27 | 0:03 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Noapara | 132/33 kV Transformers-T1 & T2 | 2019-01-15 10:30 | 2019-01-15 12:02 | 1:32 | T | Tripped showing no signal | 11 | 16.8667 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 | 2019-01-19 09:21 | 2019-01-19 16:36 | 7:15 | E/O | Due to re hot maintenance | 28 | 51.3333 | Power interruption 09:21to 11:11
| 132/33 kV Transformers-T2 | 2019-01-19 09:21 | 2019-01-19 11:11 | 1:50 | E/O
Nopapara | 132/33 kV Transformers-T1 & T2 | 2019-01-20 15:15 | 2019-01-20 16:15 | 1:00 | E/O | Due to red hot maintenance at 33 kV REB feeder | 22 | 22 | Power interruption
Bhandaria | 132/33 kV Transformer-T1 | 2019-01-22 14:14 | 2019-01-22 14:20 | 0:06 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-01-26 21:03 | 2019-01-26 21:44 | 0:41 | E/O | Due to bursting of L/A at 33 kV side | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2019-01-28 15:54 | 2019-01-28 16:10 | 0:16 | T | Tripped showing 33 kV REB feeder fault | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-01-29 20:43 | 2019-01-29 21:41 | 0:58 | E/O | Due to red hot maintenance | 9 | 8.7 | Power interruption
|  |  | Total : | 15:21 |  | Unserved Energy: |  | 101.5667
HVDC Grid Circle :
Ishurdi | 230/132 kV Transformer-T03 | 2019-01-16 10:06 | 2019-01-16 17:45 | 7:39 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T3 | 2019-01-21 16:15 | 2019-01-21 08:31 | 1:45 | E/O | Due to cable fault of 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 9:24 |  |  |  | 0
Bogura Grid Circle:
Rajshahi | 132/33 kV Transformer-T1 | 2019-01-13 19:42 | 2019-01-13 21:03 | 1:21 | E/O | Due to red hot maintenance | 10 | 13.5 | Power interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-01-15 07:03 | 2019-01-15 07:07 | 0:04 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2019-01-29 18:31 | 2019-01-29 18:36 | 0:05 | T | Due to 33 kV feeder fault | 41 | 3.4167 | Power interruption
|  |  | Total : | 1:30 |  | Unserved Energy: |  | 16.9167
Others :
Bashundhara | 132 kV main Bus | 2019-01-11 09:20 | 2019-01-11 09:44 | 0:24 | T | Tripped showing Diff. relay | 58 | 23.2 | Power interruption
|  |  | Total : | 0:24 |  | Unserved Energy: |  | 23.2
Total outage period of Sub-station Equipment : |  |  |  | 44:52 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-01-03 10:34 | 2019-01-03 10:53 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakor 230 kV line-1 | 2019-01-07 23:20 | 2019-01-07 23:53 | 0:33 | E/O | Due to bursting at L/A. | 0 | 0 | No interruption
| Aminbazar-Kaliakor 230 kV line-2 | 2019-01-07 23:20 | 2019-01-10 15:18 | 63:58 | E/O |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2019-01-10 13:28 | 2019-01-10 13:34 | 0:06 | T | Tripped showing dist.& E/F relay | 45 | 4.5 | Power interruption
| Tongi-Kabirpur 132 kV line-2 | 2019-01-10 13:28 | 2019-01-10 20:20 | 6:52 | T |  | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2019-01-19 09:58 | 2019-01-19 11:58 | 2:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-2 | 2019-01-22 10:17 | 2019-01-22 20:24 | 10:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Uttara | Uttara 3rd phase -Mirpur 132 kV line | 2019-01-25 10:46 | 2019-01-25 11:13 | 0:27 | T | Tripped showing directional & O/C relay | 65 | 4.3333 | Power interruption 10:46 to 10:50
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 & 2 | 2019-01-26 07:02 | 2019-01-26 07:13 | 0:11 | T | Tripped showing O/C relay | 415 | 55.3333 | Power interruption 07:02 to 07:10
Lalbagh | Lalbagh-Kallyanpur 132 kV line-2 | 2019-01-30 07:08 | 2019-01-30 07:20 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 84:45 |  | Unserved Energy: |  | 64.1667
Dhaka (South) Grid Circle :
Haripur | Haripur-Ullon 132 kV line | 2018-01-10 16:55 | 2018-01-10 17:20 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuial 132 kV line | 2018-01-11 02:01 | 2018-01-11 02:12 | 0:11 | T | Tripped showing dist.& O/C relay | 54 | 9.9 | Power interruption
Shyampur | Shyampur-B.Gaon 132 kV line | 2018-01-13 06:57 | 2018-01-13 10:26 | 3:29 | T | Tripped showing dist. relay | 40 | 139.3333 | Power interruption
Rampura | Rampura-Ullon 132 kV line | 2018-01-14 21:06 | 2018-01-14 21:28 | 0:22 | T | Tripped showing dist.& O/C relay | 59 | 21.6333 | Power interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2019-01-16 12:08 | 2019-01-16 12:39 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Siddhirganj-Matuial 132 kV line | 2019-01-16 21:23 | 2019-01-16 21:43 | 0:20 | T | Tripped showing dist. relay | 54 | 18 | Power interruption
Haripur | Haripur-Shyampur 132 kV line | 2019-01-17 14:54 | 2019-01-17 16:12 | 1:18 | T | Due to DC Supply failure | 70 | 91 | Power interruption
| Haripur-Ullon 132 kV line | 2019-01-18 14:38 | 2019-01-18 14:46 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dutch Bangla | Dutch Bangla-Siddhirganj S/S 132 kV line | 2019-01-20 10:19 | 2019-01-21 14:52 | 28:33 | E/O | Due to Y-phase torn out at Siddhirganj S/S | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-3 | 2019-01-20 13:44 | 2019-01-20 15:59 | 2:15 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-1 | 2019-01-21 22:11 | 2019-01-22 00:48 | 2:37 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Shyampur | Shyampur 230 kV S/S-Bramomgaon 132 kV line | 2019-01-26 16:02 | 2019-01-26 18:56 | 2:54 | E/O | Due to Oil leakage | 50 | 145 | Power interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2019-01-28 10:19 | 2019-01-28 12:51 | 2:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2019-01-31 14:37 | 2019-01-31 15:15 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 46:13 |  | Unserved Energy: |  | 424.8667
Chattogram Grid Circle :
Madunaghat | Madunaghat-Sikalbaha 132 kV line-1 | 2019-01-04 16:24 | 2019-01-04 16:39 | 0:15 | T | Tripped showing dist.B-phase &.E/F. relay | 0 | 0 | No interruption
Abul Khair | Abul Khair-BSRM 230 kV line | 2019-01-08 10:54 | 2019-01-08 11:04 | 0:10 | T | Tripped showing O/C relay | 886 | 147.6667 | Power interruption 10:54 to 11:04
Hathazari | Hathazari-Baraulia 132 kV line-1 & 2 | 2019-01-08 10:54 | 2019-01-08 11:10 | 0:16 | T |  | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-1 | 2019-01-16 08:44 | 2019-01-16 08:48 | 0:04 | T | Tripped showing O/C relay | 250 | 12.5 | Power interruption 08:44 to 08:47
| Hathazari-Madunaghat 132 kV line-2 | 2019-01-16 08:44 | 2019-01-16 08:49 | 0:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 | 2019-01-21 08:36 | 2019-01-21 09:45 | 2:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Baroihat 132 kV line-1 | 2019-01-27 13:27 | 2019-01-27 13:56 | 0:29 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
|  |  | Total : | 3:24 |  | Unserved Energy: |  | 160.1667
Cumilla Grid Circle :
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2019-01-10 14:55 | 2019-01-10 15:29 | 0:34 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2019-01-26 07:02 | 2019-01-26 07:13 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2019-01-26 11:13 | 2019-01-26 11:26 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:56 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 V line | 2019-01-05 22:59 | 2019-01-05 23:24 | 0:25 | E/O | Due to bursting of B-phase PT at Gopalganj S/S | 48 | 20 | Power interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2019-01-07 17:56 | 2019-01-08 15:20 | 21:24 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Gopalpara | Gopalpara-Khulna© 132 kV line-1 | 2019-01-14 03:44 | 2019-01-14 09:35 | 5:51 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Noapara | Noapara-Bangla track P/S 132 kV line | 2019-01-14 03:44 | 2019-01-14 04:03 | 0:19 | T |  | 0 | 0 | No interruption
|  |  | Total : | 27:59 |  | Unserved Energy: |  | 20
HVDC Grid Circle :
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2019-01-08 10:29 | 2019-01-08 12:13 | 1:44 | T | Tripped showing CAT,CE,CSW,dist.Z1-phase relay | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-2 | 2019-01-18 15:42 | 2019-01-18 16:22 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV line | 2019-01-30 09:02 | 2019-01-30 10:15 | 1:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 2:24 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Natore | Natore-Ishurdi 132 kV line-1 & 2 | 2019-01-02 20:38 | 2019-01-03 01:09 | 4:31 | E/O | Due to bursting of breake at Natore S/S | 248 | 165.3333 | Power interruption 20:38 to 21:18
Bogura | Bogura -Natore 132 kV line-1 | 2019-01-02 20:38 | 2019-01-02 21:18 | 0:40 | E/O
| Bogura -Natore 132 kV line-2 | 2019-01-02 20:38 | 2019-01-02 22:22 | 1:44 | E/O
Rangpur | Rangpur-Palashbari 132 132 kV line-1 | 2019-01-15 07:03 | 2019-01-15 13:03 | 6:00 | T | Tripped showing no relay | 0 | 0 | No interruption
| Rangpur-Palashbari 132 132 kV line-2 | 2019-01-15 07:03 | 2019-01-15 07:26 | 0:23 | T |  | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-1&2 | 2019-01-15 08:22 | 2019-01-15 08:27 | 0:05 | T | Tripped showing O/C . relay | 124 | 10.3333 | Power interruption
|  |  | Total : | 13:23 |  | Unserved Energy: |  | 175.6667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 178:08 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 230/132 kV Transformer-TR-3 | 2019-01-01 08:45 | 2019-01-01 15:07 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-01-02 08:30 | 2019-01-02 16:25 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-ICT-1 | 2019-01-02 08:59 | 2019-01-02 16:50 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-TR-3 | 2019-01-03 08:40 | 2019-01-03 15:12 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-01-03 08:15 | 2019-01-03 17:26 | 9:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2019-01-05 09:20 | 2019-01-05 17:36 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2019-01-05 09:03 | 2019-01-05 13:15 | 4:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T3 | 2019-01-06 09:12 | 2019-01-06 16:15 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A | 2019-01-06 09:42 | 2019-01-06 15:43 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132 kV Bus | 2019-01-07 10:59 | 2019-01-07 14:30 | 3:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T3 | 2019-01-07 09:22 | 2019-01-07 16:07 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-01-08 12:34 | 2019-01-08 13:54 | 1:20 | S/O | Due to Delta test | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T3 | 2019-01-08 09:13 | 2019-01-15 15:57 | 174:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T1 | 2019-01-09 09:17 | 2019-01-09 16:58 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T2 | 2019-01-09 08:14 | 2019-01-09 14:34 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A & 132/33 kV Transformer T2 | 2019-01-09 09:50 | 2019-01-09 14:58 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T1 | 2019-01-10 09:17 | 2019-01-10 16:45 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A | 2019-01-10 09:45 | 2019-01-10 14:52 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2019-01-10 09:44 | 2019-01-10 17:52 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T2 | 2019-01-10 09:12 | 2019-01-10 13:45 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132 kV mian Bus | 2019-01-11 08:25 | 2019-01-11 12:08 | 3:43 | S/O | Due to A/M work | 105 | 390.25 | Power interruption
| 33 kV Bus | 2019-01-12 08:31 | 2019-01-12 12:20 | 3:49 | S/O | Due to A/M work | 105 | 400.75 | Power interruption
Satmosjid | 132/33 kV Transformer-T2 | 2019-01-12 08:33 | 2019-01-12 15:27 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-01-12 10:11 | 2019-01-12 15:25 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 | 2019-01-13 09:35 | 2019-01-13 17:38 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2019-01-13 08:45 | 2019-01-13 15:19 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 33 kV Bus | 2019-01-13 09:24 | 2019-01-13 11:55 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 | 2019-01-14 09:05 | 2019-01-14 17:45 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2019-01-14 09:56 | 2019-01-14 20:15 | 10:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2019-01-14 09:20 | 2019-01-14 15:36 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-01-15 09:48 | 2019-01-15 11:43 | 1:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-2 | 2019-01-15 08:48 | 2019-01-15 14:38 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-01-16 09:42 | 2019-01-16 12:01 | 2:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T1 | 2019-01-18 08:50 | 2019-01-18 10:20 | 1:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-01-18 08:57 | 2019-01-24 14:46 | 149:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 2/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132 kV Bus & 132/33 kV Transformer T-2 | 2019-01-19 08:41 | 2019-01-19 10:13 | 1:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132 kV Bus-B | 2019-01-20 12:03 | 2019-01-20 15:35 | 3:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2019-01-20 11:12 | 2019-01-20 15:55 | 4:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T2 | 2019-01-20 09:34 | 2019-01-20 13:41 | 4:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(new) | 132 kV Bus section -2 | 2019-01-21 08:55 | 2019-01-21 13:11 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2019-01-21 13:45 | 2019-01-21 14:05 | 0:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2019-01-22 08:50 | 2019-01-22 15:33 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2019-01-23 08:52 | 2019-01-23 12:05 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2019-01-23 09:50 | 2019-01-23 16:17 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2019-01-23 12:15 | 2019-01-23 13:45 | 1:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2019-01-24 09:27 | 2019-01-24 16:23 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 with 33 kV Bus-A | 2019-01-25 07:01 | 2019-01-25 17:34 | 10:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-2 | 2019-01-25 15:10 | 2019-01-25 16:25 | 1:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2019-01-26 08:20 | 2019-01-26 12:18 | 3:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-2 | 2019-01-27 09:22 | 2019-01-27 17:13 | 7:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2019-01-28 09:36 | 2019-01-28 16:35 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2019-01-28 11:55 | 2019-01-28 12:55 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-2 | 2019-01-28 07:20 | 2019-01-28 16:56 | 9:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-01-29 09:25 | 2019-01-29 11:32 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-01-29 11:47 | 2019-01-29 13:32 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2019-01-29 11:14 | 2019-01-29 13:37 | 2:23 | S/O | Due to maintenance work | 0 | 0 | No interruption
Savar | 33 kV Bus-A | 2019-01-30 08:07 | 2019-01-30 10:17 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2019-01-30 08:16 | 2019-01-30 09:00 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-01-31 11:32 | 2019-01-31 12:42 | 1:10 | S/O | Due to C/M work | 15 | 17.5 | Power interruption
|  |  | Total : | 612:24 |  | Unserved Energy: |  | 808.5
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-TR2 | 2019-01-03 00:16 | 2019-01-03 10:04 | 9:48 | S/O | Due to high voltage | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer T2 | 2019-01-03 10:37 | 2019-01-03 11:58 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T03 | 2019-01-03 08:46 | 2019-01-03 16:52 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2019-01-04 09:22 | 2019-01-04 14:04 | 4:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T5 | 2019-01-05 09:20 | 2019-01-05 19:56 | 10:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2019-01-06 02:51 | 2019-01-11 17:32 | 134:41 | S/O | Due to high voltage | 0 | 0 | No interruption
| 230/132 kV Transformer-T03 | 2019-01-07 07:35 | 2019-01-07 14:44 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Ullon | 132/33 kV Transformer-T2 | 2019-01-09 10:21 | 2019-01-09 14:18 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-1 | 2019-01-12 08:36 | 2019-01-12 17:07 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-1 | 2019-01-12 09:51 | 2019-01-12 16:19 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer ATR-1 | 2019-01-15 12:02 | 2019-01-15 20:14 | 8:12 | S/O | Due to fire tightning system testing work | 0 | 0 | No interruption
| 400/230 kV Transformer ATR-1 | 2019-01-15 12:02 | 2019-01-15 20:14 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-GT2 | 2019-01-16 07:09 | 2019-01-16 17:25 | 10:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2019-01-19 09:01 | 2019-01-19 15:15 | 6:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-01-20 08:08 | 2019-01-20 13:54 | 5:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T3 | 2019-01-21 09:52 | 2019-01-23 20:50 | 58:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-GT2 | 2019-01-23 10:45 | 2019-01-23 15:35 | 4:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-2 | 2019-01-25 07:06 | 2019-01-25 17:09 | 10:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | 230 kV Bus-2 | 2019-01-25 08:30 | 2019-01-25 11:49 | 3:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | 230/132 kV Transformer-AT2 | 2019-01-26 08:40 | 2019-01-26 16:29 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T1 | 2019-01-26 09:14 | 2019-01-26 13:31 | 4:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-GT1 | 2019-01-26 11:02 | 2019-01-26 15:59 | 4:57 | S/O | Due to maintenanace by DPDC | 0 | 0 | No interruption
Ghorasal | 230/132 kV Transformer-AT2 | 2019-01-26 08:40 | 2019-01-26 16:29 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230 kV Bus | 2019-01-29 09:11 | 2019-01-29 11:31 | 2:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230 kV Bus-1 | 2019-01-30 09:15 | 2019-01-30 15:12 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230 kV Bus-2 | 2019-01-30 09:12 | 2019-01-30 13:18 | 4:06 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 348:24 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Halishahar | 132/33 kV Transformer-T2 | 2019-01-04 09:30 | 2019-01-04 17:06 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | 132 kV main Bus | 2019-01-05 08:50 | 2019-01-05 12:52 | 4:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2019-01-10 08:42 | 2019-01-10 15:20 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T1 | 2019-01-11 07:03 | 2019-01-11 10:48 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132 kV main Bus | 2019-01-12 07:14 | 2019-01-12 13:30 | 6:16 | S/O | Due to A/M work | 30 | 188 | Power interruption
Dohazari | 132 kV main Bus | 2019-01-12 08:16 | 2019-01-12 15:16 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T3 | 2019-01-21 08:15 | 2019-01-21 13:24 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-01-22 08:25 | 2019-01-22 15:04 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-A | 2019-01-23 08:07 | 2019-01-23 12:47 | 4:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T2 | 2019-01-25 06:55 | 2019-01-25 12:07 | 5:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T1 | 2019-01-24 22:02 | 2019-01-26 13:55 | 39:53 | S/O | Due to Oil centrifuging | 0 | 0 | No interruption
Dohazari | 132 kV main Bus | 2019-01-26 08:30 | 2019-01-26 13:59 | 5:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 4/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Hathazari | 230/132 kV Transformer-MT4 | 2019-01-28 08:54 | 2019-01-28 16:35 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T3 | 2019-01-29 09:00 | 2019-01-29 15:18 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-MT1 | 2019-01-30 09:26 | 2019-01-30 17:12 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 124:04 |  | Unserved Energy: |  | 188
Cumilla Grid Circle :
Bibiyana | 400/230 kV Transformer-T1 | 2019-01-01 09:51 | 2019-01-01 14:15 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400/230 kV Transformer-ICT-1 | 2019-01-03 08:38 | 2019-01-03 17:01 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2019-01-04 08:12 | 2019-01-04 13:20 | 5:08 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-01-04 14:10 | 2019-01-04 17:25 | 3:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer-T01 | 2019-01-06 09:11 | 2019-01-06 15:23 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T4 | 2019-01-06 09:04 | 2019-01-07 17:22 | 32:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2019-01-07 05:48 | 2019-01-09 23:44 | 65:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer-T01 | 2019-01-07 10:20 | 2019-01-07 17:27 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-1 | 2019-01-10 10:41 | 2019-01-10 15:36 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2019-01-10 11:27 | 2019-01-10 20:00 | 8:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-01-11 12:12 | 2019-01-11 15:37 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2019-01-13 07:42 | 2019-01-13 23:53 | 16:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-AT02 | 2019-01-15 08:40 | 2019-01-15 19:32 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2019-01-15 09:10 | 2019-01-15 11:45 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-01-16 11:22 | 2019-01-16 17:25 | 6:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer T-1 | 2019-01-16 08:34 | 2019-01-16 15:35 | 7:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer-T02 | 2019-01-24 08:19 | 2019-01-24 02:05 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2019-01-24 08:52 | 2019-01-24 20:50 | 11:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-01-25 08:50 | 2019-01-25 14:05 | 5:15 | S/O | Due to C/M work | 15 | 78.75 | Power interruption
Ashuganj | 132 kV Bus-2 | 2019-01-25 08:40 | 2019-01-26 07:43 | 23:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T2 & T3 | 2019-01-27 07:29 | 2019-01-27 13:05 | 5:36 | S/O | Due to extension work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-2 | 2019-01-27 08:41 | 2019-01-27 15:00 | 6:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-2 | 2019-01-29 09:58 | 2019-01-29 16:33 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | 230 kV Bas-A | 2019-01-30 10:07 | 2019-01-30 13:41 | 3:34 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 188:34 |  | Unserved Energy : |  | 78.75
Khulna Grid Circle :
Bhola | 132/33 kV Transformer-T2 | 2018-01-02 09:02 | 2018-01-02 16:15 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2018-01-04 08:46 | 2018-01-04 18:11 | 9:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-01-07 10:41 | 2018-01-07 12:30 | 1:49 | S/O | Due to mainteanace work | 0 | 0 | No interruption
Golapganj | 132 kV mian Bus | 2018-01-12 08:19 | 2018-01-12 16:24 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2018-01-12 10:30 | 2018-01-12 13:03 | 2:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132 kV Bus &132/33 kV Transformer T3 | 2019-01-14 08:46 | 2019-01-14 15:38 | 6:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-2 | 2019-01-17 09:28 | 2019-01-17 15:24 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-T2 | 2019-01-18 09:22 | 2019-01-18 16:35 | 7:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2019-01-19 10:23 | 2019-01-19 16:30 | 6:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 5/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Khulna(S) | 132 kV Bus | 2019-01-19 09:01 | 2019-01-19 16:02 | 7:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2019-01-19 10:01 | 2019-01-19 13:26 | 3:25 | S/O | Due to connect of 33 kV PBS feeder | 8 | 27.3333 | Power interruption
| 132/33 kV Transformer-T1 | 2019-01-20 08:43 | 2019-01-20 14:25 | 5:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-1 | 2019-01-24 10:10 | 2019-01-24 17:17 | 7:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 33 kV Bus | 2019-01-24 09:58 | 2019-01-24 14:17 | 4:19 | S/O | Due to maintenance work | 10 | 43.1667 | Power interruption
Khulna(S) | 230/132 kV Transformer-T1 | 2019-01-25 09:09 | 2019-01-25 16:26 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2019-01-25 09:46 | 2019-01-25 15:46 | 6:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2019-01-26 09:20 | 2019-01-26 16:51 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2019-01-26 07:49 | 2019-01-26 17:36 | 9:47 | S/O | Due to D/W work | 20 | 195.6667 | Power interruption
|  |  | Total : | 113:22 |  | Unserved Energy : |  | 266.1667
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T1 | 2019-01-01 08:34 | 2019-01-01 16:40 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2019-01-03 08:27 | 2019-01-03 17:26 | 8:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-01-05 08:58 | 2019-01-05 13:17 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T1 | 2019-01-06 08:53 | 2019-01-06 11:17 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T3 | 2019-01-08 08:44 | 2019-01-08 17:36 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T2 | 2019-01-19 10:31 | 2019-01-19 14:45 | 4:14 | S/O | Due to D/W work | 10 | 42.3333 | Power interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2019-01-19 09:40 | 2019-01-23 20:03 | 106:23 | S/O | Due to Oil centrifuging | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-1 | 2019-01-20 08:25 | 2019-01-20 10:22 | 1:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 133 kV Bus-2 | 2019-01-22 08:10 | 2019-01-22 10:38 | 2:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132 kV main Bus | 2019-01-25 08:07 | 2019-01-25 17:05 | 8:58 | S/O | Due to C/W work | 50 | 448.3333 | Power interruption
Ishurdi | 132/33 kV Transformer-T1 | 2019-01-29 08:40 | 2019-02-11 10:27 | 313:47 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 470:27 |  | Unserved Energy : |  | 490.6667
Bogra Grid Circle:
Rajshahi | 132/33 kV Transformer-T3 | 2019-01-03 10:30 | 2019-01-03 19:12 | 8:42 | S/O | Due to C/W work | 0 | 0 | No interruption
Saidpur | 132 kV Bus-1 & 2 | 2019-01-04 06:33 | 2019-01-04 16:40 | 10:07 | S/O | Due to Bus conductor changing | 150 | 1517.5 | Power interruption
Natore | 132/33 kV Transformer-T4 | 2019-01-05 08:49 | 2019-01-05 13:30 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T1 | 2019-01-05 08:17 | 2019-01-05 19:45 | 11:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-TR-2 | 2019-01-07 12:50 | 2019-01-08 18:04 | 29:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T2 | 2019-01-09 10:06 | 2019-01-09 12:58 | 2:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T01 | 2019-01-09 10:24 | 2019-01-09 17:52 | 7:28 | S/O | Due to re-conductoring | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2019-01-10 08:24 | 2019-01-10 14:00 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T01 | 2019-01-10 09:07 | 2019-01-10 17:35 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 33 kV Bus | 2019-01-11 06:44 | 2019-01-11 11:36 | 4:52 | S/O | Due to D/W work | 22 | 107.0667 | Power interruption
Barapukuria | 230/132 kV Transformer-T02 | 2019-01-11 07:12 | 2019-01-11 18:50 | 11:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2019-01-12 07:23 | 2019-01-12 18:05 | 10:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T1 | 2019-01-12 09:35 | 2019-01-12 12:30 | 2:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T02 | 2019-01-13 07:20 | 2019-01-13 17:41 | 10:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra (new) | 132 kV main Bus | 2019-01-14 07:11 | 2019-01-14 08:46 | 1:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra (old)) | 132 kV main Bus | 2019-01-14 07:21 | 2019-01-14 10:02 | 2:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-TR-1 | 2019-01-14 07:17 | 2019-01-14 17:51 | 10:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra (old)) | 132 kV main Bus | 2019-01-14 09:02 | 2019-01-14 10:02 | 1:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132 kV Reserv Bus | 2019-01-15 07:08 | 2019-01-15 10:09 | 3:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra (N)) | 230/132 kV Transformer-T01 | 2019-01-16 06:56 | 2019-01-16 11:47 | 4:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 & T03 | 2019-01-16 06:56 | 2019-01-16 10:07 | 3:11 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main Bus | 2019-01-16 06:56 | 2019-01-16 10:07 | 3:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 6/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Amnura | 132/33 kV Transformer-T2 | 2019-01-16 12:16 | 2019-01-16 13:50 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2019-01-16 08:06 | 2019-01-16 16:12 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformers-T06 & T2 | 2019-01-16 10:06 | 2019-01-16 17:45 | 7:39 | S/O | Due to D/W work | 30 | 229.5 | Power interruption
| 230/132 kV Transformers-T06 & T2 | 2019-01-17 07:07 | 2019-01-17 18:15 | 11:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-01-17 09:28 | 2019-01-17 15:48 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132 kV main Bus | 2019-01-18 07:57 | 2019-01-18 12:57 | 5:00 | S/O | Due to A/M work | 50 | 250 | Power interruption
Barapukuria | 230/132 kV Transformer-T01 | 2019-01-19 07:46 | 2019-01-19 17:34 | 9:48 | S/O | Due to reconductoring | 0 | 0 | No interruption
| 230/132 kV Transformers-T02 & T06 | 2019-01-21 08:48 | 2019-01-21 17:57 | 9:09 | S/O | Due to reconductoring | 40 | 366 | Power interruption
Ruppur | 132/33 kV Transformer-T2 | 2019-01-21 09:52 | 2019-01-21 13:21 | 3:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-01-21 13:21 | 2019-01-21 20:31 | 7:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 33 kV bus & 132/33 kV Transformer T1 | 2019-01-22 06:30 | 2019-01-22 08:05 | 1:35 | S/O | Due to D/W work | 30 | 47.5 | Power interruption
Barapukuria | 230/132 kV Transformers-T02 & T06 | 2019-01-22 09:20 | 2019-01-22 14:02 | 4:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 33 kV bus-1 | 2019-01-22 06:30 | 2019-01-22 08:05 | 1:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-01-25 08:55 | 2019-01-25 10:30 | 1:35 | S/O | Due to C/M work | 25 | 39.5833 | Power interruption
Natore | 132/33 kV Transformer-T2 | 2019-01-27 10:03 | 2019-01-27 11:31 | 1:28 | S/O | Due to C/M work | 6 | 8.8 | Power interruption
|  |  | Total : | 239:26 |  | Unserved Energy : |  | 2565.95
Others :
Bashundhara | 132/33 kV Transformer-T3 | 2019-01-06 08:55 | 2019-01-06 15:24 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T3 | 2019-01-10 08:12 | 2019-01-10 17:38 | 9:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2019-01-12 06:54 | 2019-01-12 18:06 | 11:12 | S/O | Due to mainteanace by DPDC | 0 | 0 | No interruption
Matuial | 132/33 kV Transformer-T2 | 2019-01-12 09:32 | 2019-01-12 15:11 | 5:39 | S/O | Due to A/M work | 20 | 113 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2019-01-13 07:02 | 2019-01-13 17:35 | 10:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-01-14 07:03 | 2019-01-14 17:33 | 10:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-01-15 07:22 | 2019-01-15 17:26 | 10:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundhara | 132/33 kV Transformer-T3 | 2019-01-21 11:02 | 2019-01-27 16:40 | 149:38 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total | 213:31 |  | Unserved Energy : |  | 113
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 2310:12 | Hours
S/O=Schedule Outage D/W= Development Work A/M= Annual Maintenance C/M= Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | Joydevpur-Kadda 132 kV line-1 | 2019-01-01 10:30 | 2019-01-01 10:42 | 0:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Joydevpur-Kadda 132 kV line-2 | 2019-01-01 10:45 | 2019-01-01 12:45 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2019-01-01 09:20 | 2019-01-01 13:44 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2019-01-02 09:01 | 2019-01-02 16:25 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | Kadda-Kabirpur 132 kV line-1 | 2019-01-02 09:37 | 2019-01-02 12:49 | 3:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2019-01-03 09:04 | 2019-01-03 13:52 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(Old) | Tongi(Old)-Tongi (New) 132 kV line-1 | 2019-01-03 13:17 | 2019-01-03 16:56 | 3:39 | S/O | Due to protection test | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-01-04 10:09 | 2019-01-04 14:59 | 4:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2019-01-06 09:42 | 2019-01-06 15:43 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-01-07 09:45 | 2019-01-07 16:31 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2019-01-07 09:01 | 2019-01-07 13:33 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | Netrakona-Mymensingh132 kV line-1 | 2019-01-08 08:35 | 2019-01-08 15:55 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2019-01-08 10:11 | 2019-01-08 13:15 | 3:04 | S/O | Due to protection test | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-09 09:25 | 2019-01-09 15:42 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2019-01-09 08:28 | 2019-01-09 16:10 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-01-10 10:29 | 2019-01-10 14:52 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2019-01-10 08:30 | 2019-01-10 14:46 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2019-01-12 09:06 | 2019-01-12 16:58 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | Netrakona-Myemnsingh 132 kV line-1 | 2019-01-12 08:45 | 2019-01-12 15:07 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2019-01-12 08:48 | 2019-01-12 15:19 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2019-01-12 09:45 | 2019-01-12 14:44 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-01-14 08:32 | 2019-01-14 15:59 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2019-01-14 09:43 | 2019-01-14 15:50 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-15 06:10 | 2019-01-15 20:04 | 13:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Uttara | Uttara-Tongi 132 kV line | 2019-01-15 06:20 | 2019-01-15 20:02 | 13:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | Netrakona-Myemnsingh 132 kV line-2 | 2019-01-15 08:40 | 2019-01-15 14:20 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Jamalpur 132 kV line-2 | 2019-01-15 13:30 | 2019-01-15 20:09 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-16 06:55 | 2019-01-16 20:14 | 13:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2019-01-16 07:40 | 2019-01-16 20:18 | 12:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2019-01-16 12:13 | 2019-01-16 16:14 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-01-17 06:30 | 2019-01-17 20:05 | 13:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-17 06:31 | 2019-01-17 20:02 | 13:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-01-17 09:44 | 2019-01-17 13:54 | 4:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-01-17 12:14 | 2019-01-17 13:56 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-18 06:21 | 2019-01-18 19:26 | 13:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-01-18 06:42 | 2019-01-18 19:23 | 12:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2019-01-18 08:43 | 2019-01-18 16:39 | 7:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-19 06:12 | 2019-01-19 19:12 | 13:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-01-19 06:30 | 2019-01-19 19:37 | 13:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-01-19 09:40 | 2019-01-19 16:09 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2019-01-19 10:23 | 2019-01-19 16:30 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-20 06:24 | 2019-01-20 07:07 | 0:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-01-20 07:07 | 2019-01-20 20:08 | 13:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-01-20 11:12 | 2019-01-20 15:41 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-01-20 11:12 | 2019-01-20 15:20 | 4:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-21 06:25 | 2019-01-21 20:40 | 14:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-01-21 06:35 | 2019-01-21 20:38 | 14:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-01-21 09:13 | 2019-01-21 20:10 | 10:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2019-01-21 08:48 | 2019-01-21 20:27 | 11:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-22 06:01 | 2019-01-22 16:46 | 10:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase132 kV line | 2019-01-22 06:05 | 2019-01-22 20:36 | 14:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-01-23 06:15 | 2019-01-23 20:03 | 13:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV line | 2019-01-23 06:15 | 2019-01-23 20:10 | 13:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2019-01-23 08:25 | 2019-01-23 17:08 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2019-01-23 08:28 | 2019-01-23 17:13 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Bibiyana 400 kV line-2 | 2019-01-24 09:27 | 2019-01-24 16:23 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2019-01-24 09:26 | 2019-01-24 22:15 | 12:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 & 2 | 2019-01-25 10:17 | 2019-01-25 17:40 | 7:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2019-01-25 08:22 | 2019-01-25 12:45 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Joydevpur-Ghorashal 132 kV line-1 | 2019-01-26 08:34 | 2019-01-26 12:50 | 4:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2019-01-26 09:50 | 2019-01-26 16:31 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2019-01-26 08:18 | 2019-01-26 12:36 | 4:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-2 | 2019-01-26 09:51 | 2019-01-26 16:32 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line- 1 | 2019-01-26 10:16 | 2019-01-26 21:31 | 11:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mirpur-Aminbazar 132 kV line-2 | 2019-01-26 10:16 | 2019-01-26 21:29 | 11:13 | S/O |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-01-27 08:56 | 2019-01-27 17:10 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2019-01-27 09:20 | 2019-01-27 14:14 | 4:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2019-01-27 09:18 | 2019-01-27 17:35 | 8:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2019-01-28 09:37 | 2019-01-28 20:09 | 10:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-2 | 2019-01-28 09:37 | 2019-01-28 17:24 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara 3rd phase | Uttara-Mirpur 132 kV line | 2019-01-28 10:25 | 2019-01-28 20:13 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2019-01-29 07:38 | 2019-01-29 15:59 | 8:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2019-01-29 09:32 | 2019-01-29 17:08 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara 3rd phase | Uttara-Mirpur 132 kV line | 2019-01-29 08:58 | 2019-01-29 17:31 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2019-01-29 11:41 | 2019-01-29 13:10 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-2 | 2019-01-29 09:51 | 2019-01-29 17:05 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2019-01-29 13:12 | 2019-01-29 14:27 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2019-01-29 07:33 | 2019-01-29 11:59 | 4:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara 3rd phase | Uttara-Mirpur 132 kV line | 2019-01-31 08:54 | 2019-01-31 15:52 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 612:25 |  | Unserved Energy: |  | 0
Page: 3/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Haripur | Haripur-Narsingdi-Bhulta 132 kV line | 2019-01-01 10:35 | 2019-01-01 14:03 | 3:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 230 kV line-2 | 2019-01-03 09:50 | 2019-01-03 15:38 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2019-01-05 09:12 | 2019-01-05 15:46 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 | 2019-01-05 09:26 | 2019-01-05 13:59 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-06 08:13 | 2019-01-06 16:52 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2019-01-06 09:49 | 2019-01-06 15:30 | 5:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-07 08:07 | 2019-01-07 20:09 | 12:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2019-01-07 09:09 | 2019-01-07 17:23 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-08 08:58 | 2019-01-08 18:41 | 9:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2019-01-08 08:48 | 2019-01-08 14:14 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2019-01-09 09:16 | 2019-01-09 14:32 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-3 | 2019-01-09 08:29 | 2019-01-09 16:22 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-09 09:38 | 2019-01-09 17:29 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorasal-Ashuganj 132 kV line-1 | 2019-01-09 11:57 | 2019-01-09 18:50 | 6:53 | S/O | Due to re-conductoring | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2019-01-09 14:41 | 2019-01-09 16:58 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 132 kV line-1 | 2019-01-10 07:31 | 2019-02-12 15:40 | 800:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2019-01-10 08:28 | 2019-01-10 15:59 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-10 08:49 | 2019-01-10 17:12 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar & Lalbagh 132 kV line | 2019-01-12 07:33 | 2019-01-12 17:23 | 9:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorasal 230 kV line-1 | 2019-01-11 08:15 | 2019-01-11 20:07 | 11:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2019-01-12 06:44 | 2019-01-12 15:13 | 8:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-12 09:16 | 2019-01-12 16:57 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV line-1 | 2019-01-12 09:18 | 2019-01-12 14:38 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Bhulta 230 kV line-2 | 2019-01-12 08:35 | 2019-01-12 17:36 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur(new) 230 kV line | 2019-01-12 14:18 | 2019-02-12 16:04 | 745:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar-Lalbagh 132 kV line | 2019-01-13 07:09 | 2019-01-13 15:50 | 8:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-13 08:53 | 2019-01-13 17:29 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kVline | 2019-01-14 06:50 | 2019-01-14 15:19 | 8:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar 132 kV line | 2019-01-14 06:51 | 2019-01-14 15:04 | 8:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-01-14 08:24 | 2019-01-14 20:09 | 11:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2019-01-14 09:35 | 2019-01-14 15:56 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Midland P/S | Midland P/S-APSCL S/S 230 kV line | 2019-01-14 11:55 | 2019-01-14 16:55 | 5:00 | S/O | Due to project work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2019-01-15 09:15 | 2019-01-15 17:20 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar,Hasnabad-Lalbagh 132 kV line-5 | 2019-01-15 08:46 | 2019-01-15 17:15 | 8:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar & Lalbagh 132 kV line | 2019-01-16 07:35 | 2019-01-16 16:11 | 8:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-01-16 09:09 | 2019-01-16 17:05 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2019-01-17 07:20 | 2019-01-17 15:48 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-01-17 08:31 | 2019-01-17 16:48 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Narsingdi 132 kV line | 2019-01-17 09:42 | 2019-01-17 14:50 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2019-01-18 06:57 | 2019-01-18 14:51 | 7:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar 132 kV line | 2019-01-18 06:57 | 2019-01-18 14:53 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-01-18 12:15 | 2019-01-18 17:48 | 5:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2019-01-19 10:28 | 2019-01-19 17:34 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 4/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2019-01-19 09:08 | 2019-01-19 17:03 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh -Kallyanpur 132 kV line-1 & 2 | 2019-01-20 07:29 | 2019-01-20 07:30 | 0:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munsiganj 132 kV line-2 | 2019-01-20 10:38 | 2019-01-20 14:06 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-1 | 2018-12-19 07:50 | 2019-01-21 21:15 | 805:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2019-01-22 06:53 | 2019-01-22 20:41 | 13:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat IEL 132 kV line-1 | 2019-01-22 09:26 | 2019-01-22 16:37 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-Ghorashal 132 kV line-1 | 2019-01-22 09:27 | 2019-01-22 17:28 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2019-01-23 06:29 | 2019-01-23 18:37 | 12:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.baria 132 kV line-1 | 2019-01-23 09:42 | 2019-01-23 16:42 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2019-01-24 06:18 | 2019-01-24 21:14 | 14:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.baria 132 kV line-2 | 2019-01-24 09:32 | 2019-01-24 17:27 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(Old)) | Shyampur(Old))-Shyampur(New)) 132 kV line-1 & 2 | 2019-01-26 06:52 | 2019-01-26 14:48 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2019-01-26 09:19 | 2019-01-26 13:46 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(New) | Shyampur(New)-Shyampur(Old) 132 kV line-1 & 2 | 2019-01-27 07:07 | 2019-01-27 14:03 | 6:56 | S/O | Due to D/W work | 140 | 970.6667 | Power interruption
Bashundhara | Bashundhara-Rampura 132 kV line-2 | 2019-01-27 08:18 | 2019-01-27 16:40 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Bramongaon 132 kV line | 2019-01-27 09:25 | 2019-01-27 13:51 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Tongi 230 kV line-1 | 2019-01-28 07:15 | 2019-01-28 17:06 | 9:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1&2 | 2019-01-28 08:13 | 2019-01-28 16:25 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Tongi 230 kV line-1 | 2019-01-29 07:22 | 2019-01-29 13:37 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(New) | Shyampur(New)-Shyampur(Old) 132 kV line-1 & 2 | 2019-01-29 07:29 | 2019-01-29 13:22 | 5:53 | S/O | Due to D/W work | 140 | 805 | Power interruption
Hasnabad | Hasnabad-Bramongaon 132 kV line | 2019-01-29 07:44 | 2019-01-29 14:30 | 6:46 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2019-01-29 08:36 | 2019-01-29 16:16 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV line-2 | 2019-01-29 08:47 | 2019-01-29 14:19 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Tongi 132 kV line-1 | 2019-01-30 08:40 | 2019-01-30 13:46 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(New) | Shyampur(New)-Shyampur(Old) 132 kV line-1 & 2 | 2019-01-31 06:59 | 2019-01-31 13:51 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Bramongaon P/S 132 kV line | 2019-01-31 07:40 | 2019-01-31 12:06 | 4:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-HPL 230 kV line-1 | 2019-01-31 13:02 | 2019-01-31 13:21 | 0:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 2841:40 |  | Unserved Energy: |  | 1775.6667
Chattogram Grid Circle :
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2019-01-02 07:47 | 2019-01-02 17:06 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV bay | 2019-01-03 09:20 | 2019-01-03 17:40 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2019-01-03 08:43 | 2019-01-03 15:41 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2019-01-04 07:43 | 2019-01-04 13:01 | 5:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chanfraghona 132 kV line-2 | 2019-01-04 08:01 | 2019-01-04 12:39 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazari 132 kV line-1 | 2019-01-05 10:15 | 2019-01-05 16:06 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line | 2019-01-06 09:11 | 2019-01-06 20:20 | 11:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2019-01-06 08:42 | 2019-01-06 16:30 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2019-01-06 11:26 | 2019-01-06 12:30 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2019-01-07 09:18 | 2019-01-07 14:45 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-2 | 2019-01-08 07:42 | 2019-01-08 14:00 | 6:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-2 | 2019-01-08 09:27 | 2019-01-08 11:56 | 2:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2019-01-09 09:23 | 2019-01-09 15:21 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-2 | 2019-01-09 09:49 | 2019-01-09 15:13 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dohazari | Dohazari-Sikalbaha 132 kV line-2 | 2019-01-10 07:17 | 2019-01-11 14:18 | 31:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-2 | 2019-01-10 10:37 | 2019-01-10 15:28 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
BSRM | BSRM-Hathazari 230 kV line | 2019-01-11 08:59 | 2019-01-11 11:20 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona-Kagrachari 132 kV line-2 | 2019-01-12 06:58 | 2019-01-14 12:42 | 53:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2019-01-13 08:55 | 2019-01-13 15:16 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line | 2019-01-13 16:33 | 2019-01-13 17:47 | 1:14 | S/O | Due to TSCR work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2019-01-14 09:24 | 2019-01-14 12:42 | 3:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2019-01-16 08:44 | 2019-01-16 08:47 | 0:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-2 | 2019-01-16 09:52 | 2019-01-16 15:39 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj -Munsinganj 132 kV line-1 | 2019-01-16 10:23 | 2019-01-16 17:18 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line-1 | 2019-01-16 09:51 | 2019-01-16 09:51 | 0:00 | S/O | Due to re-conductoring | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2019-01-17 10:32 | 2019-01-17 14:38 | 4:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-01-18 07:57 | 2019-01-18 13:15 | 5:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2019-01-19 08:49 | 2019-01-19 13:45 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barorihat | Barorihat-Feni 132 kV line-1 | 2019-01-21 07:29 | 2019-01-21 12:09 | 4:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barorihat-Hathazari 132 kV line-2 | 2019-01-21 07:18 | 2019-01-21 16:56 | 9:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Barorihat 132 kV line-1 | 2019-01-21 12:13 | 2019-01-21 16:56 | 4:43 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-BSRM 230 kV line-1 | 2019-01-26 08:08 | 2019-01-26 13:50 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2019-01-28 08:22 | 2019-01-28 13:27 | 5:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulshi-Madunaghat 132 kV line-2 | 2019-01-29 08:43 | 2019-01-29 14:46 | 6:03 | S/O | Due to C/M work | 0 | 0 | No interruption
AKSPL | AKSPL-Baraulia 132 kV line | 2019-01-30 08:38 | 2019-01-30 14:34 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-AKSPL 132 kV line | 2019-01-31 08:39 | 2019-01-31 14:30 | 5:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 254:15 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2019-01-01 08:28 | 2019-01-01 17:25 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirmongal | Sirmongal-Fenchuganj 132 kV line-2 | 2019-01-01 09:20 | 2019-01-01 15:30 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 132 kV line-2 | 2019-01-02 09:05 | 2019-01-02 16:35 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirmongal | Sirmongal-Fenchuganj 132 kV line-2 | 2019-01-02 10:26 | 2019-01-02 16:34 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2019-01-03 08:51 | 2019-01-03 15:50 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirmongal | Sirmongal-Fenchuganj 132 kV line-2 | 2019-01-03 09:04 | 2019-01-03 17:07 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2019-01-05 09:03 | 2019-01-05 15:19 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2019-01-05 08:11 | 2019-01-05 16:51 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-2 | 2019-01-06 08:14 | 2019-01-06 17:27 | 9:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirmongal | Sirmongal-Fenchuganj 132 kV line-2 | 2019-01-07 09:48 | 2019-01-07 16:26 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2019-01-07 08:30 | 2019-01-07 16:19 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2019-01-07 08:53 | 2019-01-07 16:28 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2019-01-08 07:47 | 2019-01-08 08:35 | 0:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirmongal | Sirmongal-Fenchuganj 132 kV line-2 | 2019-01-08 10:38 | 2019-01-08 15:41 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2019-01-08 08:54 | 2019-01-08 15:21 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2019-01-09 09:30 | 2019-01-09 16:36 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2019-01-10 10:34 | 2019-01-10 14:55 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2019-01-10 09:08 | 2019-01-10 17:06 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-2 | 2019-01-10 09:47 | 2019-01-10 20:15 | 10:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2019-01-10 09:10 | 2019-01-10 13:15 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-2 | 2019-01-10 14:57 | 2019-01-10 14:57 | 0:00 | S/O | Due to D/W of 45 days | 0 | 0 | No interruption
Feni | Feni-Baroiarhat 132 kV line-1 | 2019-01-12 08:45 | 2019-01-12 11:43 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2019-01-12 09:03 | 2019-01-12 16:52 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2019-01-13 09:13 | 2019-01-13 16:24 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2019-01-13 09:12 | 2019-01-13 17:42 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-2 | 2019-01-13 11:22 | 2019-01-13 15:01 | 3:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2019-01-14 09:21 | 2019-01-14 14:45 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria P/S | B.Baria P/S-B.baria S/S 132 kV line | 2019-01-14 09:30 | 2019-01-14 17:56 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 | 2019-01-14 09:18 | 2019-01-14 16:21 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-01-14 08:32 | 2019-01-14 17:05 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria P/S | B.Baria P/S-B.baria S/S 132 kV line | 2019-01-15 09:59 | 2019-01-15 15:39 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Kulaura 132 kV line | 2019-01-15 09:27 | 2019-01-15 16:36 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Dudkandi 132 kV line-1 | 2019-01-16 08:34 | 2019-01-16 16:20 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-01-16 09:24 | 2019-01-16 14:10 | 4:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Dudkandi 132 kV line-1 | 2019-01-17 08:29 | 2019-01-17 16:13 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2019-01-17 09:05 | 2019-01-17 16:59 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Dudkandi 132 kV line-1 | 2019-01-19 08:56 | 2019-01-19 16:20 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-2 | 2019-01-19 09:42 | 2019-01-19 16:36 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2019-01-20 09:12 | 2019-01-20 16:49 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-2 | 2019-01-20 09:40 | 2019-01-20 16:27 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-1 | 2019-01-20 08:13 | 2019-01-20 16:22 | 8:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2019-01-20 08:47 | 2019-01-20 16:57 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Dudkandi 132 kV line-2 | 2019-01-21 09:25 | 2019-01-21 16:21 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2019-01-21 09:04 | 2019-01-21 14:30 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-01-22 07:35 | 2019-01-26 21:15 | 109:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-2 | 2019-01-22 07:34 | 2019-01-22 15:24 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2019-01-22 09:23 | 2019-01-22 16:41 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 132 kV line-1 | 2019-01-22 08:23 | 2019-01-22 15:21 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2019-01-23 08:50 | 2019-01-23 15:52 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2019-01-23 09:12 | 2019-01-23 16:52 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| B.Baria-Shahjibazar 132 kV line-2 | 2019-01-24 08:55 | 2019-01-24 14:58 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 132 kV line | 2019-01-25 07:28 | 2019-01-25 16:47 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar P/S132 kV line-3 | 2019-01-25 07:59 | 2019-01-26 20:38 | 36:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line-1 | 2019-01-26 08:08 | 2019-01-26 13:50 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 230 kV line-2 | 2019-01-26 09:10 | 2019-01-26 14:42 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Ramganj 132 kV line-2 | 2019-01-26 08:30 | 2019-01-26 13:52 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Ramganj 132 kV line-2 | 2019-01-27 08:42 | 2019-01-27 15:52 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2019-01-27 09:11 | 2019-01-27 21:01 | 11:50 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2019-01-28 07:20 | 2019-01-28 17:40 | 10:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2019-01-28 08:55 | 2019-01-28 15:40 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2019-01-28 09:11 | 2019-01-28 17:25 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2019-01-28 07:14 | 2019-01-28 17:10 | 9:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2019-01-29 09:15 | 2019-01-29 17:09 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 7/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2019-01-29 09:28 | 2019-01-29 15:54 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-01-29 17:16 | 2019-01-29 20:34 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-2 | 2019-01-30 08:58 | 2019-01-30 15:50 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2019-01-30 11:02 | 2019-01-30 13:26 | 2:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2019-01-30 09:45 | 2019-01-30 13:52 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2019-01-31 08:56 | 2019-01-31 14:58 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2019-01-31 10:01 | 2019-02-04 20:38 | 106:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 707:09 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna© | Khulna©-Noapara 132 kV line-1 | 2019-01-01 10:14 | 2019-01-01 11:59 | 1:45 | S/O | Due to mainteanace work | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line-2 | 2019-01-02 08:11 | 2019-01-02 16:10 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Quantum P/S 132 kV line | 2019-01-02 09:24 | 2019-01-02 14:22 | 4:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2019-01-03 08:33 | 2019-01-03 17:23 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2019-01-06 08:04 | 2019-01-06 18:15 | 10:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Orion power | Orion power-Bagerhat 132 kV line-2 | 2019-01-07 08:31 | 2019-01-07 15:27 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhola -Borhanuddin 230 kV line-2 | 2019-01-08 11:09 | 2019-01-08 15:53 | 4:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-2 | 2019-01-08 08:32 | 2019-01-08 15:45 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-1 | 2019-01-09 10:02 | 2019-01-09 15:20 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhanadaria 132 kV line | 2019-01-09 08:26 | 2019-01-09 17:33 | 9:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Bhanadaria 132 kV line | 2019-01-10 08:09 | 2019-01-10 17:12 | 9:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2019-01-10 09:47 | 2019-01-10 14:09 | 4:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhanadaria 132 kV line | 2019-01-11 07:04 | 2019-01-11 16:52 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2019-01-12 09:26 | 2019-01-12 14:51 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhanadaria 132 kV line | 2019-01-13 07:20 | 2019-01-13 17:10 | 9:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2019-01-13 10:01 | 2019-01-13 16:19 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhanadaria 132 kV line | 2019-01-14 07:05 | 2019-01-14 20:14 | 13:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2019-01-15 09:44 | 2019-01-15 15:23 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Satkhira 132 kV line-2 | 2019-01-16 09:07 | 2019-01-16 15:43 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2019-01-17 08:55 | 2019-01-17 16:09 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2019-01-18 07:08 | 2019-01-18 08:49 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madaripur-Faridpur 132 kV line-1 | 2019-01-18 07:18 | 2019-01-18 08:43 | 1:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-FaridpurP/S 132 kV line | 2019-01-20 08:22 | 2019-01-20 15:56 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2019-01-21 10:10 | 2019-01-21 17:03 | 6:53 | S/O | Due to A/M work | 15 | 103.25 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-22 10:17 | 2019-01-22 19:01 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-23 08:28 | 2019-01-23 17:19 | 8:51 | S/O | Due to C/M work | 15 | 132.75 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2019-01-24 07:19 | 2019-01-24 18:20 | 11:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-FaridpurP/S 132 kV line | 2019-01-24 09:21 | 2019-01-24 15:54 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2019-01-25 07:30 | 2019-01-25 17:10 | 9:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-26 07:04 | 2019-01-26 17:37 | 10:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-27 07:09 | 2019-01-27 19:48 | 12:39 | S/O | Due to C/M work | 25 | 316.25 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-28 08:12 | 2019-01-28 17:35 | 9:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-29 07:04 | 2019-01-29 17:23 | 10:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barisal-Barisal P/S 132 kV line | 2019-01-29 08:15 | 2019-01-29 17:00 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-30 07:10 | 2019-01-30 18:31 | 11:21 | S/O | Due to C/M work | 25 | 283.75 | No interruption
| Barisal-Patuakhali 132 kV line | 2019-01-31 06:53 | 2019-01-31 23:07 | 16:14 | S/O | Due to C/M work | 25 | 405.8333 | No interruption
|  |  | Total : | 286:01 |  | Unserved Energy: |  | 1241.8333
Page: 8/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Kustia | Kustia-Jhenidah 12 kV line-1 | 2019-01-02 10:36 | 2019-01-02 10:36 | 0:00 | S/O | Due to re-conductoring | 0 | 0 | No interruption
Bharamara HVDC | Bharamara HVDC-Bheramara S/S 230 kV line-1 | 2019-01-06 08:08 | 2019-01-06 20:25 | 12:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara HVDC-NW 230 kV line-2 | 2019-01-07 08:10 | 2019-01-07 20:16 | 12:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara | Bharamara-Ishurdi 132 kV line-1 | 2019-01-07 01:01 | 2019-01-07 15:33 | 14:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-2 | 2019-01-12 08:14 | 2019-01-12 16:51 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah-Jessore 132 kV line-2 | 2019-01-13 08:07 | 2019-01-13 17:05 | 8:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah-Jessore 132 kV line-2 | 2019-01-14 08:31 | 2019-01-14 16:34 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah-Jessore 132 kV line-1 | 2019-01-15 08:21 | 2019-01-15 16:56 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-1 | 2019-01-15 09:30 | 2019-01-15 11:09 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-1 | 2019-01-16 08:26 | 2019-01-16 16:39 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jhenidah-Jessore 132 kV line-1 | 2019-01-17 08:51 | 2019-01-17 20:08 | 11:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2019-01-20 10:27 | 2019-01-20 20:15 | 9:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-2 | 2019-01-23 09:34 | 2019-01-23 14:44 | 5:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Bharamara | Bharamara-kustia 132 kV line-1 | 2019-01-26 08:32 | 2019-01-26 15:21 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-kustia 132 kV line-1 | 2019-01-28 08:39 | 2019-01-28 17:01 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-kustia 132 kV line-2 | 2019-01-29 08:19 | 2019-01-29 14:56 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-kustia 132 kV line-2 | 2019-01-30 08:28 | 2019-01-30 15:30 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-kustia 132 kV line-2 | 2019-01-31 08:18 | 2019-01-31 12:55 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 142:42 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2019-01-01 09:25 | 2019-01-04 16:42 | 79:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-2 | 2019-01-02 08:33 | 2019-01-02 20:05 | 11:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baghabari-Sirajganj 230 kV line-1 | 2019-01-03 08:23 | 2019-01-06 11:47 | 75:24 | S/O | Due to project work | 0 | 0 | No interruption
Bogra(New) | Bogra(New)-Bogra(Old) 132 kV line-1 | 2019-01-05 09:56 | 2019-01-11 21:05 | 155:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-1 | 2019-01-05 23:01 | 2019-01-05 23:48 | 0:47 | S/O | Due to CT problem | 0 | 0 | No interruption
| Baghabari-Sirajganj 230 kV line-2 | 2019-01-06 12:04 | 2019-01-08 14:33 | 50:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria P/S | Barapukuria P/S-Barapukuria S/S 230 kV line-2 | 2019-01-06 08:50 | 2019-01-06 15:38 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria P/S | Barapukuria P/S-Barapukuria S/S 230 kV line-2 | 2019-01-09 06:53 | 2019-01-09 17:52 | 10:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura(new) | Bogura(new)-Bogura old 132 kV line-2 | 2019-01-10 07:30 | 2019-01-10 08:13 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-2 | 2019-01-11 09:19 | 2019-01-11 11:14 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(new) | Bogura(new)-Bogura old 132 kV line-2 | 2019-01-12 09:43 | 2019-01-17 13:32 | 123:49 | S/O | Due to re-conductoring | 0 | 0 | No interruption
Bogura(old) | Bogura(old)-Bogura (N) 132 kV line-1 | 2019-01-16 07:08 | 2019-01-16 10:09 | 3:01 | S/O | Due to D/W work | 54 | 162.9 | Power interruption
Barapukuria | Barapukuria -Saidpur 132 kV line-1 | 2019-01-16 11:08 | 2019-01-16 11:08 | 0:00 | S/O | Due to re-conductoring | 0 | 0 | No interruption
Barapukuria S/S | Barapukuria S/S-Barapukuria P/S 230 kV line | 2019-01-17 07:07 | 2019-01-17 18:15 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 9/9 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Bogra(New) | Bogra(New)-Bogra(Old) 132 kV line-1 | 2019-01-17 15:33 | 2019-01-19 19:15 | 51:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Palashbari 132 kV line-1 & 2 | 2019-01-18 07:25 | 2019-01-18 18:37 | 11:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-1 & 2 | 2019-01-18 07:50 | 2019-01-18 17:52 | 10:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-1& 2 | 2019-01-18 08:33 | 2019-01-18 17:56 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-1 | 2019-01-19 07:05 | 2019-01-19 15:44 | 8:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-2 | 2019-01-19 07:05 | 2019-01-19 15:45 | 8:40 | S/O |  | 0 | 0 | No interruption
| Bogura-Palashbari 132 kV line-1& 2 | 2019-01-19 05:52 | 2019-01-19 16:11 | 10:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-1 & 2 | 2019-01-19 06:49 | 2019-01-19 15:47 | 8:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria P/S | Barapukuria P/S-Barapukuria 230 kV line-1 | 2019-01-20 07:15 | 2019-01-20 16:05 | 8:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Palashbari 132 kV line-1 | 2019-01-25 06:35 | 2019-01-25 18:06 | 11:31 | S/O | Due to project work | 0 | 0 | No interruption
| Bogura-Palashbari 132 kV line-2 | 2019-01-25 06:35 | 2019-01-25 18:11 | 11:36 | S/O |  | 0 | 0 | No interruption
| Bogura-Bogura(New) 132 kV line-2 | 2019-01-25 07:16 | 2019-01-25 16:47 | 9:31 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-1 & 2 | 2019-01-25 07:16 | 2019-01-25 16:47 | 9:31 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-1& 2 | 2019-01-25 07:16 | 2019-01-25 16:35 | 9:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Mahastangar 132 kV line-1 | 2019-01-25 06:35 | 2019-01-25 17:22 | 10:47 | S/O | Due to D/W work | 0 | 0 | No interruption
| Palashbari-Mahastangar 132 kV line-2 | 2019-01-25 06:37 | 2019-01-25 17:30 | 10:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura(Old) | Bogura(Old)-Natore 132 kV line-1 & 2 | 2019-01-26 07:20 | 2019-01-26 17:14 | 9:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-1 | 2019-01-26 07:37 | 2019-01-26 17:10 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-2 | 2019-01-26 07:37 | 2019-01-26 17:11 | 9:34 | S/O |  | 0 | 0 | No interruption
| Bogura(Old)-Mahastangar 132 kV line-1& 2 | 2019-01-26 07:08 | 2019-01-26 17:35 | 10:27 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 761:45 |  | Unserved Energy: |  | 162.9
Others :
Maniknagar | Maniknagar-Matuail 132 kV line | 2019-01-06 09:05 | 2019-01-06 16:22 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 7:17 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 5613:14 | Hours |  |  | Executive Engineer
S/O=Schedule Outage D/W= Development Work A/M= Annual Maintenance C/M= Corrective Maintenance | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January' 2019
| Area | Previous Month (December 2018) |  |  |  | Current Month (January 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 7 | 1 | 133 | 141 | 9 | 4 | 138 | 151
2 | Dhaka (South) Grid Circle. | 15 | 11 | 68 | 94 | 12 | 3 | 96 | 111
3 | Chattogram Grid Circle. | 6 | 3 | 36 | 45 | 6 | 2 | 51 | 59
4 | Cumilla Grid Circle. | 24 | 7 | 71 | 102 | 5 | 2 | 94 | 101
5 | Khulna Grid Circle. | 4 | 1 | 27 | 32 | 7 | 7 | 54 | 68
6 | Bheramara HVDC Grid Circle | 8 | 1 | 26 | 35 | 3 | 2 | 29 | 34
7 | Bogura Grid Circle. | 7 | 2 | 80 | 89 | 6 | 4 | 71 | 81
8 | Others | 3 | - | 5 | 8 | 1 | - | 9 | 10
9 | Total | 74 | 26 | 446 | 546 | 49 | 24 | 542 | 615
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January' 2019
| Area | Previous Month (December 2018) |  |  |  | Current Month (January 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 711.63 | - | 131.77 | 843.4 | 109.92 |  | 808.5 | 918.42
2 | Dhaka (South) Grid Circle. | 50.1 | 34.66 | - | 84.76 | 279.86 | 145 | 1775.67 | 2200.53
3 | Chattogram Grid Circle. | 16 | - | 40.08 | 56.08 | 160.17 | 22.67 | 188 | 370.84
4 | Cumilla Grid Circle. | 17.53 | 96.67 | 57.67 | 171.87 | 13.27 | 66 | 78.75 | 158.02
5 | Khulna Grid Circle. | 3.5 |  | 62.5 | 66 | 19.54 | 102.03 | 1508 | 1629.57
6 | Bheramara HVDC Grid Circle | - | - | - | 0 | - | - | 490.67 | 490.67
7 | Bogura Grid Circle. | 15.85 | 41.67 | 120.83 | 178.35 | 13.75 | 178.83 | 2728.85 | 2921.43
8 | Others | 45 | - | 129.83 | 174.83 | 23.2 | - | - | 23.2
9 | Total | 859.61 | 173 | 542.68 | 1575.29 | 619.71 | 514.53 | 7578.44 | 8712.68
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 | 2 | 3 |  | - | 3 | 854.25
2 | Dhaka (South) | 5031.6 | - | - | - | - | - | - | -
3 | Chattogram | 2042 | 1 | 1 | 2 |  | - | 2 | 210.67
4 | Khulna | 2434 | 4 | 3 | 7 |  | 3 | 4 | 367.74
5 | Bheramara (HVDC) | 2423.3 | - | 2 | 2 | - | - | 2 | 490.67
6 | Bogura | 3145.6 | 2 | 8 | 10 | 1 |  | 9 | 2582.87
7 | Cumilla | 2981 | 4 | 1 | 5 | 2 |  | 3 | 158.02
| Total | 23365.5 | [6 empty] | 4664.22
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 99.9% | [6 empty] | Executive Engineer
6 | Bogura | 100% | [6 empty] | Information Management Division
7 | Cumilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 3 |  | 3 | 3 | - |  | 64.17
2 | Dhaka (South) | 990.29 |  | 7 | 2 | 8 | 3 |  | 5 | 2200.54
3 | Chattogram | 917 | 20+9(Partial) | 2 | - | 2 | - | - | - | 160.17
4 | Khulna | 1238.4 | 21 | 1 | 5 | 6 | 1 | - | 5 | 1261.83
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 2 | 1 | 3 | 1 | - | 2 | 338.57
7 | Cumilla | 1648.16 | 17 | - | - | - | - | - | - | -
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 4025.28
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.78%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.98%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.94% | [7 empty] | Information Management Division
7 | Cumilla | 100% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-01-18 | 16 | 00hr53min | 8 | 09hr46 min | 3 | 03hr59 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:January' 2019
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi | 1 | 1:01 | 45 | 45.75 | Due to tripping of 132/33 kV Transformers T1 & T2
| 2 | 0:06 | 45 | 4.5 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
Uttara |  | 0:04 | 65 | 4.3333 | Due to tripping of Uttara-Mirpur 132 kV line
Mymensingh RPCL | 1 | 0:08 | 415 | 55.3333 | Due to tripping of Mymensingh RPCL-Mymensingh S/S 132 kV line
Tangail | 2 | 3:43 | 105 | 390.25 | Due to S/D of 132 kV Bus
|  | 3:49 | 105 | 400.75 | Due to S/D of 33 kV Bus
Jamalpur | 1 | 1:10 | 15 | 17.5 | Due to S/D of 132/33 kV Transformer T3
Siddhirganj | 1 | 0:11 | 54 | 9.9 | Due to tripping of Siddhirganj-Matuail 132 kV line
Shyampur | 1 | 3:29 | 40 | 139.3333 | Due to tripping of Shyampur-B.gaon 132 kV line
Rampura | 1 | 0:22 | 59 | 21.6333 | Due to tripping of Rampura-Ullon 132 kV line
Siddhirganj | 1 | 0:20 | 54 | 18 | Due to tripping of Siddhirganj-Matuail 132 kV line
Haripur | 1 | 1:18 | 70 | 91 | Due to tripping of Haripur-Shyampur 132 kV line
Shyampur | 2 | 2:54 | 50 | 145 | Due to Oil leakage of Shyampur-B.gaon 132 kV line
|  | 6:56 | 140 | 970.6667 | Due to S/D of Shyampur (new)-Shyampur (old) 132 kV line-1 & 2
|  | 5:53 | 140 | 805
Sikalbaha | 1 | 1:20 | 17 | 22.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Abulkhair | 1 | 0:10 | 886 | 147.6667 | Due to tripping of Abulkhair -BSRM 230 kV line
Hathazari | 1 | 0:04 | 250 | 12.5 | Due to tripping of Hathazari-Baraulia 132 kV line-1
Halishahar | 1 | 6:16 | 30 | 188 | Due to S/D of 132 kV main Bus
Fenchuganj | 1 | 0:04 | 10 | 0.66667 | Due to tripping of 132/33 kV Transformer T2
Chowmuhani | 4 | 1:16 | 35 | 44.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 0:06 | 125 | 12.6 | Due to tripping of 132/33 kV Transformers T2 & T3
|  | 1:55 | 10 | 21.6667 | Due to tripping of 132/33 kV Transformer T2
|  | 5:15 | 15 | 78.75 | Due to S/D of 132/33 kV Transformer T1
Mongla | 1 | 0:08 | 20 | 2.6667 | Due to tripping of 132/33 kV Transformers T1 & T2
Bagerhat | 1 | 1:50 | 28 | 51.3333 | Due to tripping of 132/33 kV Transformers T2 & T3
Noapara | 1 | 1:00 | 22 | 22 | Due to red-hot maintenance of 132/33 kV Transformers T1 & T2
| 1 | 1:32 | 11 | 16.8667 | Due to tripping of 132/33 kV Transformers T1 & T2
Madaripur | 2 | 0:58 | 9 | 8.7 | Due to red-hot maintenance of 132/33 kV Transformer T3
|  | 0:25 | 48 | 20 | Due to tripping of Madaripur-Gopalganj 132 kV line
Satkhira | 1 | 3:25 | 8 | 27.3333 | Due to S/D of 132/33 kV Transformer T1
Barisal | 1 | 4:19 | 10 | 43.1667 | Due to S/D of 33 kV Bus
Satkhira | 1 | 9:47 | 20 | 195.6667 | Due to S/D of 132/33 kV Transformer T1
Barisal | 5 | 6:53 | 15 | 103.25 | Due to S/D of Barisal-Patuakhali 132 kV line
|  | 8:51 | 15 | 132.75
|  | 12:39 | 25 | 316.25
|  | 11:21 | 25 | 283.75
|  | 16:14 | 25 | 405.8333
Jhenidah | 1 | 4:14 | 10 | 42.3333 | Due to S/D of 132/33 kV Transformer T2
Shahjadpur | 1 | 8:58 | 50 | 448.3333 | Due to S/D of 132 kV Bus
Rajshahi | 1 | 1:21 | 10 | 13.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
Rangpur | 1 | 0:05 | 41 | 3.4167 | Due to tripping of 132/33 kV Transformer T1
Natore | 1 | 4:31 | 248 | 165.3333 | Due to tripping of Natore-Ishurdi 132 kV line-1 & 2
Rangpur | 1 | 0:05 | 124 | 10.3333 | Due to tripping of Rangpur-Saidpur 132 kV line-1 & 2
Saidpur | 1 | 10:07 | 150 | 1517.5 | Due to S/D of 132 kV Bus-1 & 2
Palashbari | 1 | 4:52 | 22 | 107.0667 | Due to S/D of 33 kV Bus
Barapukuria | 7 | 7:39 | 30 | 229.5 | Due to S/D of 132/33 kV TransformersT06 & T02
|  | 5:00 | 50 | 250
|  | 9:09 | 40 | 366
|  | 1:35 | 30 | 47.5
|  | 1:35 | 25 | 39.5833
|  | 1:28 | 6 | 8.8
|  | 3:01 | 54 | 162.9
| Total unserved energy : |  |  | 8689.4667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 94 | 8 | 2019-01-01 | 12:00
2 | Munsiganj | 82 | 28 | 2019-01-01 | 21:00
3 | Sonargaon | 47 | 27 | 2019-01-01 | 18:30
4 | Shyampur | 166 | 28 | 2019-01-01 | 22:00
5 | Bhulta | 170 | 14 | 2019-01-01 | 12:00
6 | Madanganj | 56 | 16 | 2019-01-01 | 21:00
7 | Shitalakhya | 103 | 12 | 2019-01-01 | 11:00
8 | Rahim steel | 12 | 1 | 2019-01-01 | 17:00
9 | Matuail | 89 | 29 | 2019-01-01 | 10:00
10 | Ghorasal | 69 | 23 | 2019-01-01 | 18:30
11 | Narsingdi | 106 | 17 | 2019-01-01 | 20:00
12 | Haripur (SBU) | 100 | 22 | 2019-01-01 | 09:00
13 | Ullon | 66 | 26 | 2019-01-01 | 18:00
14 | Hasnabad | 161 | 20 | 2019-01-01 | 19:00
15 | Magbazar | 106 | 27 | 2019-01-01 | 15:00
16 | Maniknagar | 92 | 27 | 2019-01-01 | 13:00
17 | Bangabhaban | 20 | 2 | 2019-01-01 | 13:00
18 | Narinda | 76 | 10 | 2019-01-01 | 16:00
19 | Dhanmondi | 80 | 9 | 2019-01-01 | 13:00
20 | Lalbag | 80 | 7 | 2019-01-01 | 13:00
21 | Madartek | 37 | 26 | 2019-01-01 | 18:00
22 | Mirpur | 95 | 28 | 2019-01-01 | 12:00
23 | Kalyanpur | 66 | 23 | 2019-01-01 | 18:30
24 | Gulshan | 94 | 23 | 2019-01-01 | 18:00
25 | Uttara | 41 | 17 | 2019-01-01 | 19:00
26 | Uttara(new) | 7 | 22 | 2019-01-01 | 18:00
27 | Kamrangirchar | 61 | 2 | 2019-01-01 | 18:00
28 | Savar | 102 | 6 | 2019-01-01 | 18:00
29 | Bhasantec | 102 | 27 | 2019-01-01 | 18:30
30 | Agargaon | 46 | 26 | 2019-01-01 | 19:00
31 | Satmosjid | 69 | 19 | 2019-01-01 | 18:30
32 | Tongi | 125 | 21 | 2019-01-01 | 11:00
33 | Kabirpur | 152 | 26 | 2019-01-01 | 20:00
34 | Basundhara | 88 | 28 | 2019-01-01 | 15:00
35 | Manikganj | 67 | 22 | 2019-01-01 | 19:00
36 | Joydevpur | 197 | 14 | 2019-01-01 | 18:00
37 | New Tongi | 92 | 23 | 2019-01-01 | 12:00
38 | Kodda | 211 | 31 | 2019-01-01 | 19:00
39 | Dhamrai | 42 | 28 | 2019-01-01 | 18:30
40 | Tangail | 153 | 24 | 2019-01-01 | 19:30
41 | Mymensing | 225 | 26 | 2019-01-01 | 18:30
42 | Kishorganj | 87 | 13 | 2019-01-01 | 19:30
43 | Netrokona | 92 | 30 | 2019-01-01 | 19:00
44 | Jamalpur | 102 | 22 | 2019-01-01 | 20:00
45 | Sherpur | 88 | 30 | 2019-01-01 | 18:00
46 | Srimongal | 28 | 10 | 2019-01-01 | 18:00
47 | Shahjibazar | 96 | 19 | 2019-01-01 | 19:00
48 | Fenchuganj | 30 | 17 | 2019-01-01 | 18:00
49 | Kulawara | 28 | 30 | 2019-01-01 | 18:30
50 | Sylhet | 95 | 26 | 2019-01-01 | 18:00
51 | Chatak | 21 | 29 | 2019-01-01 | 18:30
52 | Sunamganj | 25 | 3 | 2019-01-01 | 18:00
53 | Bianibazar | 32 | 27 | 2019-01-01 | 18:00
54 | Cumilla (S) | 134 | 30 | 2019-01-01 | 18:30
55 | Cumilla(N) | 93 | 21 | 2019-01-01 | 19:30
56 | Chandpur | 83 | 26 | 2019-01-01 | 18:30
57 | Feni | 99 | 31 | 2019-01-01 | 18:30
58 | Chowmuhani | 130 | 12 | 2019-01-01 | 19:00
59 | Ashuganj | 45 | 15 | 2019-01-01 | 20:00
60 | Daudkandi | 92 | 27 | 2019-01-01 | 19:30
61 | B.Baria | 95 | 27 | 2019-01-01 | 19:30
62 | Ramganj | 30 | 14 | 2019-01-01 | 19:30
63 | Madanhat | 56 | 8 | 2019-01-01 | 9:00
64 | Hathazari | 72 | 8 | 2019-01-01 | 20:00
65 | Khulshi | 164 | 10 | 2019-01-01 | 07:00
66 | Halishahar | 101 | 24 | 2019-01-01 | 20:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Baraulia | 160 | 30 | 2019-01-01 | 08:00
68 | Sikalbaha | 36 | 1 | 2019-01-01 | 18:00
69 | Dohazari | 76 | 19 | 2019-01-01 | 18:30
70 | Cox'sbazar | 74 | 26 | 2019-01-01 | 20:00
71 | Chandraghona | 22 | 21 | 2019-01-01 | 18:00
72 | Kaptai | 4 | 5 | 2019-01-01 | 18:00
73 | A. Khaer Stl. | 25 | 9 | 2019-01-01 | 20:00
74 | Bakulia | 82 | 20 | 2019-01-01 | 14:00
75 | Julda | 21 | 27 | 2019-01-01 | 18:00
76 | TK chemical | 7 | 10 | 2019-01-01 | 10:00
77 | Modern Steel | 18 | 30 | 2019-01-01 | 1:00
78 | Shahmirpur | 23 | 13 | 2019-01-01 | 18:00
79 | Khagrachhari | 17 | 30 | 2019-01-01 | 18:30
80 | Matarbari | 24 | 24 | 2019-01-01 | 4:00
81 | Baroiar Hat | 20 | 21 | 2019-01-01 | 18:00
82 | Rangamati | 10 | 22 | 2019-01-01 | 18:30
83 | Abul Khair 230 | 194 | 17 | 2019-01-01 | 7:00
84 | BSRM | 108 | 27 | 2019-01-01 | 19:00
85 | Goalpara | 32 | 9 | 2019-01-01 | 19:00
86 | Central s/s | 69 | 23 | 2019-01-01 | 18:30
87 | Noapara | 79 | 13 | 2019-01-01 | 18:30
88 | Jashore | 120 | 24 | 2019-01-01 | 18:30
89 | Jhenida | 84 | 13 | 2019-01-01 | 18:30
90 | Bottail | 96 | 7 | 2019-01-01 | 18:00
91 | G.K Project | 43 | 9 | 2019-01-01 | 23:00
92 | Faridpur | 124 | 12 | 2019-01-01 | 19:00
93 | Madaripur | 98 | 10 | 2019-01-01 | 19:30
94 | Gopalganj | 68 | 12 | 2019-01-01 | 19:30
95 | Bagerhat | 71 | 21 | 2019-01-01 | 18:30
96 | Mongla | 38 | 24 | 2019-01-01 | 12:00
97 | Satkhira | 79 | 26 | 2019-01-01 | 19:00
98 | Gallamari | 38 | 10 | 2019-01-01 | 13:00
99 | Magura | 42 | 29 | 2019-01-01 | 18:30
100 | Chuadanga | 60 | 10 | 2019-01-01 | 18:30
101 | Barishal | 90 | 15 | 2019-01-01 | 20:00
102 | Patuakhali | 70 | 27 | 2019-01-01 | 21:00
103 | Bhandaria | 42 | 26 | 2019-01-01 | 19:30
104 | Ishurdi | 43 | 7 | 2019-01-01 | 19:30
105 | Ruppur Paromanobik | 1 | 1 | 2019-01-01 | 1:00
106 | Natore | 93 | 13 | 2019-01-01 | 18:30
107 | Bogura | 200 | 28 | 2019-01-01 | 18:30
108 | Noagaon | 118 | 28 | 2019-01-01 | 20:00
109 | Rajshahi | 105 | 31 | 2019-01-01 | 18:30
110 | C.Nawabganj | 69 | 24 | 2019-01-01 | 12:00
111 | Amnura | 36 | 22 | 2019-01-01 | 18:30
112 | Pabna | 79 | 31 | 2019-01-01 | 18:30
113 | Shahjadpur | 74 | 27 | 2019-01-01 | 18:30
114 | Serajganj | 81 | 29 | 2019-01-01 | 19:00
115 | Niyamatpur | 98 | 30 | 2019-01-01 | 20:00
116 | Joypurhat | 50 | 30 | 2019-01-01 | 19:30
117 | Mohastangor | 0 | 29 | 2019-01-01 | 18:30
118 | Rangpur | 108 | 19 | 2019-01-01 | 18:30
119 | Lalmonirhat | 88 | 22 | 2019-01-01 | 19:00
120 | Saidpur | 107 | 16 | 2019-01-01 | 18:30
121 | Purbasadipur | 86 | 30 | 2019-01-01 | 19:30
122 | Thakurgaon | 61 | 31 | 2019-01-01 | 18:30
123 | Palashbari | 104 | 28 | 2019-01-01 | 19:30
124 | Barapukuria | 55 | 26 | 2019-01-01 | 19:00
125 | Panchagar | 36 | 3 | 2019-01-01 | 18:30
126 | Joldhaka | 19 | 26 | 2019-01-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 3027 | 28.01.19 | 18:30
Chattogram | 989 | 28.01.19 | 14:00
Khulna | 1041 | 26.01.19 | 19:00
Rajshahi | 1000 | 29.01.19 | 19:00
Cumilla | 793 | 02.01.19 | 19:00
Mymensingh | 777 | 22.01.19 | 19:00
Sylhet | 331 | 26.01.19 | 18:30
Barisal | 226 | 24.01.19 | 20:00
Rangpur | 622 | 27.01.19 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 419 | 1 | 2019-01-01 | 04:00 | 394 | 24 | 2019-01-01 | 21:00
2 | Bheramara | 400 | 414 | 28 | 2019-01-01 | 24:00 | 391 | 18 | 2019-01-01 | 19:00
3 | Ashuganj(N) | 400 | 408 | 31 | 2019-01-01 | 19:30 | 388 | 9 | 2019-01-01 | 16:00
4 | Kaliakoir | 400 | 414 | 1 | 2019-01-01 | 04:00 | 373 | 23 | 2019-01-01 | 11:00
5 | Bhulta | 400 | 407 | 5 | 2019-01-01 | 4:00 | 388 | 20 | 2019-01-01 | 16:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 1 | 2019-01-01 | 18:00 | 230 | 16 | 2019-01-01 | 12:00
2 | Ishurdi | 230 | 243 | 8 | 2019-01-01 | 22:00 | 225 | 29 | 2019-01-01 | 08:00
3 | Ashuganj | 230 | 245 | 1 | 2019-01-01 | 4:00 | 204 | 15 | 2019-01-01 | 9:00
4 | Serajganj | 230 | 237 | 12 | 2019-01-01 | 5:00 | 219 | 31 | 2019-01-01 | 18:00
5 | Baghabari | 230 | 234 | 11 | 2019-01-01 | 17:00 | 220 | 8 | 2019-01-01 | 13:00
6 | Barapukuria | 230 | 238 | 4 | 2019-01-01 | 7:00 | 216 | 24 | 2019-01-01 | 18:30
7 | Bogra | 230 | 238 | 11 | 2019-01-01 | 7:00 | 207 | 31 | 2019-01-01 | 2:00
8 | Khulna South | 230 | 243 | 1 | 2019-01-01 | 4:00 | 203 | 6 | 2019-01-01 | 19:00
9 | Rampura | 230 | 231 | 1 | 2019-01-01 | 01:00 | 222 | 20 | 2019-01-01 | 16:00
10 | Haripur | 230 | 234 | 2 | 2019-01-01 | 5:00 | 221 | 20 | 2019-01-01 | 17:00
11 | Hasnabad | 230 | 236 | 3 | 2019-01-01 | 1:00 | 218 | 27 | 2019-01-01 | 16:00
12 | Aminbazar | 230 | 238 | 4 | 2019-01-01 | 04:00 | 221 | 27 | 2019-01-01 | 16:00
13 | Tongi | 230 | 236 | 30 | 2019-01-01 | 04:00 | 216 | 12 | 2019-01-01 | 15:00
14 | Comilla (N) | 230 | 243 | 11 | 2019-01-01 | 9:00 | 228 | 11 | 2019-01-01 | 19:30
15 | Hathazari | 230 | 232 | 27 | 2019-01-01 | 19:00 | 210 | 27 | 2019-01-01 | 09:00
16 | Megnaghat | 230 | 238 | 1 | 2019-01-01 | 1:00 | 227 | 22 | 2019-01-01 | 12:00
17 | Fenchuganj | 230 | 247 | 1 | 2019-01-01 | 17:00 | 234 | 27 | 2019-01-01 | 09:00
18 | Siddhirganj | 230 | 238 | 1 | 2019-01-01 | 04:00 | 225 | 20 | 2019-01-01 | 16:00
19 | Maniknagar | 230 | 236 | 5 | 2019-01-01 | 3:00 | 223 | 20 | 2019-01-01 | 15:00
20 | Old Airport | 230 | 239 | 5 | 2019-01-01 | 04:00 | 219 | 27 | 2019-01-01 | 16:00
21 | Barisal | 230 | 243 | 26 | 2019-01-01 | 10:00 | 220 | 8 | 2019-01-01 | 13:00
22 | AKSML | 230 | 230 | 25 | 2019-01-01 | 08:00 | 213 | 12 | 2019-01-01 | 15:00
23 | BSRM | 230 | 233 | 11 | 2019-01-01 | 09:00 | 211 | 28 | 2019-01-01 | 3:00
24 | Bibiyana | 230 | 247 | 3 | 2019-01-01 | 02:00 | 229 | 25 | 2019-01-01 | 21:00
25 | Bhulta | 230 | 236 | 5 | 2019-01-01 | 4:00 | 224 | 20 | 2019-01-01 | 16:00
26 | Ashuganj (S) | 230 | 244 | 5 | 2019-01-01 | 4:00 | 232 | 23 | 2019-01-01 | 11:00
27 | Kaliakoir | 230 | 240 | 4 | 2019-01-01 | 4:00 | 223 | 20 | 2019-01-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 138 | 5 | 2019-01-01 | 02:00 | 129 | 22 | 2019-01-01 | 11:00
2 | Munsiganj | 132 | 140 | 3 | 2019-01-01 | 19:30 | 130 | 7 | 2019-01-01 | 12:00
3 | Megnaghat | 132 | 139 | 5 | 2019-01-01 | 1:00 | 130 | 14 | 2019-01-01 | 18:00
4 | Shyampur | 132 | 138 | 7 | 2019-01-01 | 4:00 | 124 | 23 | 2019-01-01 | 12:00
5 | Bhulta | 132 | 139 | 1 | 2019-01-01 | 3:00 | 121 | 23 | 2019-01-01 | 12:00
6 | Madanganj | 132 | 141 | 20 | 2019-01-01 | 18:30 | 127 | 19 | 2019-01-01 | 11:00
7 | Shitalakhya | 132 | 143 | 1 | 2019-01-01 | 19:00 | 128 | 19 | 2019-01-01 | 11:00
8 | Rahim Steal | 132 | 138 | 1 | 2019-01-01 | 07:00 | 130 | 22 | 2019-01-01 | 11:00
9 | Matuail | 132 | 138 | 1 | 2019-01-01 | 4:00 | 128 | 22 | 2019-01-01 | 12:00
10 | Ghorasal | 132 | 144 | 1 | 2019-01-01 | 7:00 | 134 | 26 | 2019-01-01 | 12:00
11 | Narsinghdi | 132 | 140 | 1 | 2019-01-01 | 13:00 | 125 | 23 | 2019-01-01 | 12:00
12 | Haripur (SBU) | 132 | 138 | 2 | 2019-01-01 | 6:00 | 129 | 22 | 2019-01-01 | 12:00
13 | Ullon | 132 | 135 | 1 | 2019-01-01 | 3:00 | 126 | 10 | 2019-01-01 | 12:00
14 | Hasnabad | 132 | 141 | 11 | 2019-01-01 | 9:00 | 128 | 24 | 2019-01-01 | 12:00
15 | Magbazar | 132 | 137 | 6 | 2019-01-01 | 6:00 | 126 | 22 | 2019-01-01 | 12:00
16 | Maniknagar | 132 | 137 | 1 | 2019-01-01 | 3:00 | 129 | 20 | 2019-01-01 | 16:00
17 | Bangabhaban | 132 | 141 | 1 | 2019-01-01 | 18:30 | 125 | 12 | 2019-01-01 | 15:00
18 | Narinda | 132 | 139 | 25 | 2019-01-01 | 5:00 | 126 | 3 | 2019-01-01 | 12:00
19 | Dhanmondi | 132 | 137 | 5 | 2019-01-01 | 6:00 | 126 | 22 | 2019-01-01 | 12:00
20 | Lalbag | 132 | 141 | 1 | 2019-01-01 | 18:30 | 125 | 12 | 2019-01-01 | 15:00
21 | Madartek | 132 | 139 | 25 | 2019-01-01 | 05:00 | 126 | 3 | 2019-01-01 | 12:00
22 | Mirpur | 132 | 137 | 5 | 2019-01-01 | 6:00 | 123 | 27 | 2019-01-01 | 16:00
23 | Kalyanpur | 132 | 139 | 4 | 2019-01-01 | 4:00 | 127 | 27 | 2019-01-01 | 17:00
24 | Gulshan | 132 | 135 | 5 | 2019-01-01 | 5:00 | 125 | 22 | 2019-01-01 | 12:00
25 | Uttara | 132 | 138 | 2 | 2019-01-01 | 5:00 | 125 | 17 | 2019-01-01 | 12:00
26 | Uttara(New) | 132 | 136 | 19 | 2019-01-01 | 4:00 | 124 | 10 | 2019-01-01 | 12:00
27 | Kamrangirchar | 132 | 140 | 3 | 2019-01-01 | 1:00 | 122 | 10 | 2019-01-01 | 12:00
28 | Savar | 132 | 136 | 13 | 2019-01-01 | 1:00 | 124 | 10 | 2019-01-01 | 12:00
29 | Bhasantec | 132 | 139 | 5 | 2019-01-01 | 4:00 | 126 | 27 | 2019-01-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 139 | 5 | 2019-01-01 | 05:00 | 127 | 27 | 2019-01-01 | 12:00
31 | Satmosjid | 132 | 139 | 5 | 2019-01-01 | 04:00 | 127 | 24 | 2019-01-01 | 12:00
32 | Tongi | 132 | 139 | 1 | 2019-01-01 | 4:00 | 126 | 20 | 2019-01-01 | 15:00
33 | Kabirpur | 132 | 137 | 4 | 2019-01-01 | 5:00 | 127 | 20 | 2019-01-01 | 16:00
34 | Basundhara | 132 | 139 | 28 | 2019-01-01 | 13:00 | 120 | 20 | 2019-01-01 | 16:00
35 | Manikganj | 132 | 142 | 4 | 2019-01-01 | 6:00 | 130 | 10 | 2019-01-01 | 14:00
36 | Joydevpur | 132 | 143 | 11 | 2019-01-01 | 13:00 | 126 | 28 | 2019-01-01 | 09:00
37 | New Tongi | 132 | 139 | 1 | 2019-01-01 | 01:00 | 127 | 17 | 2019-01-01 | 12:00
38 | Kodda | 132 | 144 | 21 | 2019-01-01 | 16:00 | 126 | 7 | 2019-01-01 | 12:00
39 | Dhamrai | 132 | 139 | 5 | 2019-01-01 | 04:00 | 126 | 23 | 2019-01-01 | 16:00
40 | Tangail | 132 | 140 | 4 | 2019-01-01 | 5:00 | 123 | 31 | 2019-01-01 | 12:00
41 | Mymensing | 132 | 139 | 4 | 2019-01-01 | 7:00 | 117 | 24 | 2019-01-01 | 8:00
42 | Kishorganj | 132 | 138 | 1 | 2019-01-01 | 03:00 | 119 | 26 | 2019-01-01 | 13:00
43 | Netrokona | 132 | 139 | 3 | 2019-01-01 | 06:00 | 112 | 31 | 2019-01-01 | 10:00
44 | Jamalpur | 132 | 139 | 3 | 2019-01-01 | 18:30 | 112 | 31 | 2019-01-01 | 14:00
45 | Sherpur | 132 | 138 | 1 | 2019-01-01 | 18:30 | 110 | 26 | 2019-01-01 | 7:00
46 | Srimongal | 132 | 143 | 1 | 2019-01-01 | 05:00 | 134 | 26 | 2019-01-01 | 13:00
47 | Shahjibazar | 132 | 141 | 1 | 2019-01-01 | 15:00 | 132 | 26 | 2019-01-01 | 13:00
48 | Fenchuganj | 132 | 141 | 3 | 2019-01-01 | 02:00 | 132 | 18 | 2019-01-01 | 13:00
49 | Khulawara | 132 | 140 | 2 | 2019-01-01 | 01:00 | 133 | 18 | 2019-01-01 | 10:00
50 | Sylhet | 132 | 139 | 2 | 2019-01-01 | 1:00 | 132 | 22 | 2019-01-01 | 12:00
51 | Chattak | 132 | 139 | 2 | 2019-01-01 | 04:00 | 131 | 22 | 2019-01-01 | 18:00
52 | Sunamganj | 132 | 138 | 1 | 2019-01-01 | 02:00 | 131 | 22 | 2019-01-01 | 18:00
53 | Biani Bazar | 132 | 139 | 1 | 2019-01-01 | 06:00 | 132 | 22 | 2019-01-01 | 18:00
54 | Comilla(South) | 132 | 133 | 13 | 2019-01-01 | 24:00 | 121 | 24 | 2019-01-01 | 18:00
55 | Comilla (North) | 132 | 143 | 1 | 2019-01-01 | 7:00 | 136 | 10 | 2019-01-01 | 10:00
56 | Chandpur | 132 | 145 | 17 | 2019-01-01 | 09:00 | 130 | 17 | 2019-01-01 | 19:30
57 | Feni | 132 | 139 | 17 | 2019-01-01 | 22:00 | 128 | 27 | 2019-01-01 | 20:00
58 | Chowmuhani | 132 | 139 | 22 | 2019-01-01 | 08:00 | 127 | 16 | 2019-01-01 | 9:00
59 | Ashuganj | 132 | 144 | 1 | 2019-01-01 | 23:00 | 128 | 26 | 2019-01-01 | 13:00
60 | Daudkandi | 132 | 141 | 19 | 2019-01-01 | 7:00 | 131 | 21 | 2019-01-01 | 12:00
61 | Brahminbaria | 132 | 142 | 17 | 2019-01-01 | 4:00 | 131 | 25 | 2019-01-01 | 14:00
62 | Ramganj | 132 | 138 | 3 | 2019-01-01 | 18:30 | 125 | 31 | 2019-01-01 | 17:00
63 | Madanhat | 132 | 140 | 22 | 2019-01-01 | 08:00 | 123 | 13 | 2019-01-01 | 5:00
64 | Hathazari | 132 | 139 | 15 | 2019-01-01 | 19:00 | 127 | 27 | 2019-01-01 | 8:00
65 | Khulshi | 132 | 137 | 17 | 2019-01-01 | 20:00 | 121 | 16 | 2019-01-01 | 9:00
66 | Halishahar | 132 | 142 | 22 | 2019-01-01 | 08:00 | 124 | 12 | 2019-01-01 | 15:00
67 | Baraulia | 132 | 138 | 17 | 2019-01-01 | 20:00 | 124 | 12 | 2019-01-01 | 15:00
68 | Sikalbaha | 132 | 140 | 22 | 2019-01-01 | 8:00 | 120 | 14 | 2019-01-01 | 6:00
69 | Dohazari | 132 | 138 | 15 | 2019-01-01 | 19:00 | 124 | 2 | 2019-01-01 | 12:00
70 | Cox'sbazar | 132 | 137 | 20 | 2019-01-01 | 21:00 | 118 | 8 | 2019-01-01 | 18:00
71 | Chandraghona | 132 | 139 | 17 | 2019-01-01 | 20:00 | 126 | 12 | 2019-01-01 | 15:00
72 | Kaptai | 132 | 140 | 16 | 2019-01-01 | 09:00 | 125 | 19 | 2019-01-01 | 17:00
73 | A. Khaer Stl. | 132 | 136 | 4 | 2019-01-01 | 19:30 | 121 | 27 | 2019-01-01 | 10:00
74 | Bakulia | 132 | 138 | 22 | 2019-01-01 | 08:00 | 122 | 12 | 2019-01-01 | 15:00
75 | Julda | 132 | 139 | 17 | 2019-01-01 | 20:00 | 124 | 16 | 2019-01-01 | 09:00
76 | TK Chemical | 132 | 142 | 17 | 2019-01-01 | 20:00 | 125 | 12 | 2019-01-01 | 17:00
77 | Modern Steel | 132 | 138 | 11 | 2019-01-01 | 10:00 | 123 | 10 | 2019-01-01 | 8:00
78 | Shahmirpur | 132 | 138 | 11 | 2019-01-01 | 09:00 | 123 | 12 | 2019-01-01 | 16:00
79 | Khagrachhari | 132 | 139 | 11 | 2019-01-01 | 09:00 | 125 | 10 | 2019-01-01 | 8:00
80 | Matarbari | 132 | 136 | 14 | 2019-01-01 | 21:00 | 120 | 10 | 2019-01-01 | 7:00
81 | Baroiar Hat | 132 | 138 | 11 | 2019-01-01 | 09:00 | 124 | 26 | 2019-01-01 | 3:00
82 | Rangamati | 133 | 139 | 17 | 2019-01-01 | 20:00 | 125 | 10 | 2019-01-01 | 8:00
83 | Goalpara | 132 | 139 | 1 | 2019-01-01 | 2:00 | 122 | 20 | 2019-01-01 | 8:00
84 | Khulna Central | 132 | 139 | 9 | 2019-01-01 | 19:00 | 123 | 14 | 2019-01-01 | 8:00
85 | Noapara | 132 | 137 | 2 | 2019-01-01 | 15:00 | 120 | 2 | 2019-01-01 | 12:00
86 | Jessore | 132 | 136 | 15 | 2019-01-01 | 10:00 | 115 | 13 | 2019-01-01 | 18:00
87 | Jhenida | 132 | 136 | 1 | 2019-01-01 | 2:00 | 112 | 10 | 2019-01-01 | 07:00
88 | Bottail | 132 | 140 | 4 | 2019-01-01 | 6:00 | 129 | 27 | 2019-01-01 | 13:00
89 | G.K.Project | 132 | 143 | 4 | 2019-01-01 | 17:00 | 133 | 17 | 2019-01-01 | 8:00
90 | Faridpur | 132 | 137 | 1 | 2019-01-01 | 5:00 | 125 | 27 | 2019-01-01 | 20:00
91 | Madaripur | 132 | 138 | 1 | 2019-01-01 | 4:00 | 126 | 8 | 2019-01-01 | 18:30
92 | Gopalganj | 132 | 141 | 28 | 2019-01-01 | 19:00 | 120 | 11 | 2019-01-01 | 19:30
93 | Bagerhat | 132 | 139 | 4 | 2019-01-01 | 17:00 | 120 | 14 | 2019-01-01 | 18:00
94 | Mongla | 132 | 136 | 4 | 2019-01-01 | 17:00 | 118 | 2 | 2019-01-01 | 12:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
95 | Satkhira | 132 | 138 | 26 | 2019-01-01 | 9:00 | 121 | 20 | 2019-01-01 | 8:00
96 | Gallamari | 132 | 140 | 4 | 2019-01-01 | 17:00 | 124 | 8 | 2019-01-01 | 13:00
97 | Magura | 132 | 138 | 5 | 2019-01-01 | 3:00 | 119 | 16 | 2019-01-01 | 19:00
98 | Chuadanga | 132 | 136 | 4 | 2019-01-01 | 1:00 | 118 | 16 | 2019-01-01 | 18:30
99 | Barisal | 132 | 140 | 22 | 2019-01-01 | 5:00 | 129 | 6 | 2019-01-01 | 12:00
100 | Patuakhali | 132 | 139 | 18 | 2019-01-01 | 17:00 | 125 | 5 | 2019-01-01 | 18:00
101 | Bhandaria | 132 | 139 | 25 | 2019-01-01 | 17:00 | 121 | 12 | 2019-01-01 | 12:00
102 | Ishurdi | 132 | 142 | 1 | 2019-01-01 | 3:00 | 130 | 17 | 2019-01-01 | 8:00
103 | Ruppur paromanobik | 132 | 142 | 3 | 2019-01-01 | 3:00 | 132 | 17 | 2019-01-01 | 7:00
104 | Natore | 132 | 139 | 1 | 2019-01-01 | 3:00 | 118 | 16 | 2019-01-01 | 18:30
105 | Bogra | 132 | 139 | 4 | 2019-01-01 | 17:00 | 111 | 14 | 2019-01-01 | 8:00
106 | Noagaon | 132 | 136 | 4 | 2019-01-01 | 7:00 | 106 | 17 | 2019-01-01 | 7:00
107 | Rajshahi | 132 | 137 | 14 | 2019-01-01 | 7:00 | 122 | 31 | 2019-01-01 | 7:00
108 | C.Nawabganj | 132 | 135 | 6 | 2019-01-01 | 14:00 | 120 | 26 | 2019-01-01 | 13:00
109 | Amnura | 132 | 140 | 12 | 2019-01-01 | 17:00 | 119 | 30 | 2019-01-01 | 7:00
110 | Pabna | 132 | 138 | 5 | 2019-01-01 | 3:00 | 125 | 17 | 2019-01-01 | 8:00
111 | Shahjadpur | 132 | 144 | 4 | 2019-01-01 | 4:00 | 132 | 20 | 2019-01-01 | 8:00
112 | Serajganj | 132 | 140 | 25 | 2019-01-01 | 14:00 | 122 | 27 | 2019-01-01 | 7:00
113 | Niyamatpur | 132 | 136 | 1 | 2019-01-01 | 3:00 | 96 | 26 | 2019-01-01 | 18:00
114 | Joypurhat | 132 | 139 | 3 | 2019-01-01 | 1:00 | 106 | 26 | 2019-01-01 | 18:00
115 | Rangpur | 132 | 135 | 4 | 2019-01-01 | 7:00 | 107 | 27 | 2019-01-01 | 19:00
116 | Lalmonirhat | 132 | 134 | 4 | 2019-01-01 | 7:00 | 98 | 27 | 2019-01-01 | 19:00
117 | Saidpur | 132 | 135 | 6 | 2019-01-01 | 5:00 | 110 | 23 | 2019-01-01 | 19:30
118 | Purbasadipur | 132 | 135 | 1 | 2019-01-01 | 2:00 | 102 | 31 | 2019-01-01 | 18:30
119 | Thakurgaon | 132 | 130 | 1 | 2019-01-01 | 1:00 | 93 | 28 | 2019-01-01 | 18:30
120 | Palashbari | 132 | 136 | 6 | 2019-01-01 | 4:00 | 110 | 26 | 2019-01-01 | 13:00
121 | Barapukuria | 132 | 138 | 4 | 2019-01-01 | 7:00 | 116 | 24 | 2019-01-01 | 18:30
122 | Panchagar | 132 | 130 | 1 | 2019-01-01 | 4:00 | 89 | 23 | 2019-01-01 | 19:30
123 | Joldhaka | 132 | 126 | 22 | 2019-01-01 | 15:00 | 108 | 23 | 2019-01-01 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:January' 2019
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 135 | 375
IP-299421 | Hasnabad | TR2 | 225 | 125 | 375 | 26.01.19 | 23:00
|  | TR3 | 225 | 120 | 360
|  | TR1 | 225 | 170 | 480
IP-299866 | Tongi | TR2 | 225 | 170 | 480 | 26.01.19 | 18:30
|  | TR3 | 225 | 170 | 480
|  | TR1 | 225 | 64 | 280
IP-299427 | Haripur | TR2 | 225 |  |  | 29.01.19 | 23:00 | S/D
|  | TR3 | 225 | 64 | 280
|  | TR1 | 225 | 115 | 330
IP-299728 | Rampura | TR2 | 225 | 115 | 330 | 24.01.19 | 18:00
|  | TR3 | 225 | 115 | 300
|  | TR1 | 225 | 100 | 275
IP-299264 | Aminbazar | TR2 | 225 | 100 | 275 | 05.01.19 | 12:00
|  | TR3 | 225 | 102 | 263
| Maniknagar | TR1 | 300 | 90 | 270 | 27.01.19 | 14:00
|  | TR2 | 300 | 90 | 270
IP-399266 | Cumilla (N) | TR1 | 225 | 135 | 400 | 14.01.19 | 6:00
|  | TR2 | 225 | 145 | 376
| Fenchuganj | TR1 | 300 | 213 | 525 | 25.01.19 | 6:00
|  | TR1 | 150 | 110 | 360
IP-399428 | Hathazari | TR3 | 150 | 110 | 360 | 12.01.19 | 18:00
|  | TR4 | 150 | 110 | 360
|  | TR1 | 225 | 100 | 440
| Ishurdi | TR2 | 225 | 100 | 440 | 26.01.19 | 18:00
IP-499474 |  | TR3 | 225 | 100 | 440
| Khulna(S) | TR1 | 225 | 176 | 438
IP-58001/58002 |  | TR2 | 225 | 176 | 438 | 08.01.19 | 8:00
| Bogra | TR1 | 225 | 122 | 401 | 27.01.19 | 19:30
|  | TR2 | 225 | 122 | 401
IP-43002/499264 |  | TR3 | 225 | 166 | 526
IP-499224 | Baghabari | TR1 | 225 | 195 | 590 | 25.01.19 | 6:00
| Barapukuria | TR1 | 225 | 115 | 580 | 28.01.19 | 20:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 127 | 660 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 159 | 853
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 290 | 482 | 31.01.19 | 14:15
|  | TR1(400/132 kV) | 325 | 138 | 215
|  | TR2(400/132 kV) | 325 | 138 | 215
| Bibiyana | ICT1(400/230 kV) | 520 | 84 | 207 | 31.01.19 | 4:00
|  | ICT2(400/230kV) | 520 | 84 | 200
| Bhulta | ATR1(400/230 kV) | 520 | 131.88 | 208 | 30.01.19 | 21:45
|  | ATR2(400/230kV) | 520 | 131.88 | 208
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:January' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:January' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-01-19 | 7991 | 7991 | - | - | - | - | - | - | - | - | - | - | - | - | 01-01-19 | 6299.6 | 6299.6 | - | - | - | - | - | - | - | - | - | - | - | -
02-01-19 | 8339 | 8339 | - | - | - | - | - | - | - | - | - | - | - | - | 02-01-19 | 6366.6 | 6366.6 | - | - | - | - | - | - | - | - | - | - | - | -
03-01-19 | 8222 | 8222 | - | - | - | - | - | - | - | - | - | - | - | - | 03-01-19 | 6418.6 | 6418.6 | - | - | - | - | - | - | - | - | - | - | - | -
04-01-19 | 7436 | 7436 | - | - | - | - | - | - | - | - | - | - | - | - | 04-01-19 | 5286.7 | 5286.7 | - | - | - | - | - | - | - | - | - | - | - | -
05-01-19 | 8241 | 8241 | - | - | - | - | - | - | - | - | - | - | - | - | 05-01-19 | 5987.3 | 5987.3 | - | - | - | - | - | - | - | - | - | - | - | -
06-01-19 | 8347 | 8347 | - | - | - | - | - | - | - | - | - | - | - | - | 06-01-19 | 6444.5 | 6444.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-01-19 | 8157 | 8157 | - | - | - | - | - | - | - | - | - | - | - | - | 07-01-19 | 6387.9 | 6387.9 | - | - | - | - | - | - | - | - | - | - | - | -
08-01-19 | 8384 | 8384 | - | - | - | - | - | - | - | - | - | - | - | - | 08-01-19 | 6340.9 | 6340.9 | - | - | - | - | - | - | - | - | - | - | - | -
09-01-19 | 8397 | 8397 | - | - | - | - | - | - | - | - | - | - | - | - | 09-01-19 | 6426.9 | 6426.9 | - | - | - | - | - | - | - | - | - | - | - | -
10-01-19 | 8348 | 8348 | - | - | - | - | - | - | - | - | - | - | - | - | 10-01-19 | 6491 | 6491 | - | - | - | - | - | - | - | - | - | - | - | -
11-01-19 | 7479 | 7479 | - | - | - | - | - | - | - | - | - | - | - | - | 11-01-19 | 5388.4 | 5388.4 | - | - | - | - | - | - | - | - | - | - | - | -
12-01-19 | 8417 | 8417 | - | - | - | - | - | - | - | - | - | - | - | - | 12-01-19 | 5576.3 | 5576.3 | - | - | - | - | - | - | - | - | - | - | - | -
13-01-19 | 8621 | 8621 | - | - | - | - | - | - | - | - | - | - | - | - | 13-01-19 | 6519 | 6519 | - | - | - | - | - | - | - | - | - | - | - | -
14-01-19 | 8563 | 8563 | - | - | - | - | - | - | - | - | - | - | - | - | 14-01-19 | 6689.8 | 6689.8 | - | - | - | - | - | - | - | - | - | - | - | -
15-01-19 | 8540 | 8540 | - | - | - | - | - | - | - | - | - | - | - | - | 15-01-19 | 6577.8 | 6577.8 | - | - | - | - | - | - | - | - | - | - | - | -
16-01-19 | 8544 | 8544 | - | - | - | - | - | - | - | - | - | - | - | - | 16-01-19 | 6760.8 | 6760.8 | - | - | - | - | - | - | - | - | - | - | - | -
17-01-19 | 8515 | 8515 | - | - | - | - | - | - | - | - | - | - | - | - | 17-01-19 | 6813.9 | 6813.9 | - | - | - | - | - | - | - | - | - | - | - | -
18-01-19 | 7682 | 7682 | - | - | - | - | - | - | - | - | - | - | - | - | 18-01-19 | 5780.3 | 5780.3 | - | - | - | - | - | - | - | - | - | - | - | -
19-01-19 | 8564 | 8564 | - | - | - | - | - | - | - | - | - | - | - | - | 19-01-19 | 6160.4 | 6160.4 | - | - | - | - | - | - | - | - | - | - | - | -
20-01-19 | 8651 | 8651 | - | - | - | - | - | - | - | - | - | - | - | - | 20-01-19 | 6833.5 | 6833.5 | - | - | - | - | - | - | - | - | - | - | - | -
21-01-19 | 8748 | 8748 | - | - | - | - | - | - | - | - | - | - | - | - | 21-01-19 | 6883.5 | 6883.5 | - | - | - | - | - | - | - | - | - | - | - | -
22-01-19 | 8599 | 8599 | - | - | - | - | - | - | - | - | - | - | - | - | 22-01-19 | 6942.4 | 6942.4 | - | - | - | - | - | - | - | - | - | - | - | -
23-01-19 | 8846 | 8846 | - | - | - | - | - | - | - | - | - | - | - | - | 23-01-19 | 6991 | 6991 | - | - | - | - | - | - | - | - | - | - | - | -
24-01-19 | 8774 | 8774 | - | - | - | - | - | - | - | - | - | - | - | - | 24-01-19 | 7173.3 | 7173.3 | - | - | - | - | - | - | - | - | - | - | - | -
25-01-19 | 7864 | 7864 | - | - | - | - | - | - | - | - | - | - | - | - | 25-01-19 | 5846.9 | 5846.9 | - | - | - | - | - | - | - | - | - | - | - | -
26-01-19 | 8769 | 8769 | - | - | - | - | - | - | - | - | - | - | - | - | 26-01-19 | 6167.1 | 6167.1 | - | - | - | - | - | - | - | - | - | - | - | -
27-01-19 | 8814 | 8814 | - | - | - | - | - | - | - | - | - | - | - | - | 27-01-19 | 7189.5 | 7189.5 | - | - | - | - | - | - | - | - | - | - | - | -
28-01-19 | 8891 | 8891 | - | - | - | - | - | - | - | - | - | - | - | - | 28-01-19 | 7144 | 7144 | - | - | - | - | - | - | - | - | - | - | - | -
29-01-19 | 8748 | 8748 | - | - | - | - | - | - | - | - | - | - | - | - | 29-01-19 | 7056.9 | 7056.9 | - | - | - | - | - | - | - | - | - | - | - | -
30-01-19 | 8893 | 8893 | - | - | - | - | - | - | - | - | - | - | - | - | 30-01-19 | 7049.4 | 7049.4 | - | - | - | - | - | - | - | - | - | - | - | -
31-01-19 | 8793 | 8793 | [12 empty] | 31-01-19 | 7069 | 7069

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 8893 | 30/01/19 | 19:00
2 | Maximum day peak Genaration | MW | 7189.5 | 27/01/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 8893 | 30/01/19 | 19:00
4 | Minimum Generation | MW | 4350 | 01/01/19 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8425.0645
6 | Average of the daily day peak Genaration | MW | 6485.9097
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 4859.6881
12 | Total Generation by IPP | MKWH | 1310.2317 | % of total Gen. | 26.96%
13 | Total Generation by BPDB | MKWH | 2531.5904 | " | 52.09%
14 | A) Total Generation by RPCL | MKWH | 106.0298 | '' | 2.182%
| B) Total Generation by REB | MKWH | 137.089 | " | 2.821%
| C) Total Generation by RENTAL | MKWH | 350.9928 | " | 7.223%
| D) Total Imported from India (HVDC) | MKWH | 357.1213 | " | 7.349%
| E) Total Imported from Tripura, India (A.C) | MKWH | 66.6331 | " | 1.371%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3703.9793 | % of total Gen. | 76.22%
| B) Oil | MKWH | 576.5007 | '' | 11.86%
| C) Hydro | MKWH | 35.2467 | '' | 0.7253%
| D) Solar | MKWH | 5.4525 | '' | 0.1122%
| E) Coal | MKWH | 114.7545 | '' | 2.361%
| F) HVDC (Import from India) | MKWH | 357.1213 | '' | 7.349%
| G) A.C (Import from Tripura, India) | MKWH | 66.6331 | '' | 1.371%
16 | Maximun of the daily total Generation . | MKWH | 173.129 | 28/01/19
17 | Monthly Load factor | % | 73.4492
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 7261.1095
| A) Gas | M.Taka | 2721.025
| B) Liquid fuel | M.Taka | 4097.2005
| C) Coal | M.Taka | 442.884
| D) HVDC (Import from India) | M.Taka | 1821.3185
| E) Tripura(Import from India) | M.Taka | 455.7705
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 316.4296 | 17/01/19
| A) Gas | M.Taka | 170.9411 | 15/01/19
| B) Liquid fuel | M.Taka | 224.5768 | 17/01/19
| C) Coal | M.Taka | 19.6845 | 21/01/19
| D) HVDC (Import from India) | M.Taka | 67.2903 | 27-01-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.3268
| B) Excluding Hydro & Solar | Taka/KWHR | 2.3464
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97 | 31/01/19 | 06:00
b) | Actual | FT (MSL) | 96.16 | 31/01/19 | 06:00
22 | Peak Genaration of January 2018 | MW | 8251 | 29/01/18 | 19:30
23 | Peak Demand of January 2018 | MW | 8028 | 29/01/18 | 19:30
24 | Maximum peak Generation recorded upto 31/01/19 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 31/01/19 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 31/01/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.