## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:December' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | December 2018 |  | November 2018 |  | December 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 8534 | 04/12/18 | 9900 | 14/11/18 | 8028 | 11/12/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:30
2 | Minimum Generation (MW) | 3366 | 31/12/18 | 4789 | 24/11/18 | 4019 | 09/12/17 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 8534 | 04/12/18 | 9900 | 14/11/18 | 8028 | 11/12/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 6723.8 | 13/12/18 | 8017 | 05/11/18 | 693.1 | 11/12/17 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 8534 | 04/12/18 | 9900 | 04/11/18 | 8028 | 11/12/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 8032.2581 |  | 8671.83 |  | 7644.48 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 6134.5226 |  | 6828.36 |  | 5688.31 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 694 | 28/12/18 | 704 | 21/11/18 | 491 | 28/12/17 | 788 | 11/09/18
|  |  | 20:00 |  | 22:00 |  | 10:00 |  | 22:00
9 | Maximum Power Import from Tripura, India (MW) | 134 | 23'/12/18 | 150 | 04/11/18 | 132 | 19/12/17 | 188 | 29/05/18
|  |  | 18:00 |  | 18:30 |  | 18:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2648.2572 |  | 2521.84 |  | 2383.86
21 | Station Use of BPDB (MKWH) | 104.0244 |  | 62.93 |  | 78.1
22 | Net Generation of BPDB (MKWH) | 2544.2328 |  | 2458.91 |  | 2305.76
23 | Net Generation of IPP & RPCL (MKWH) | 1084.364 |  | 1344.31 |  | 1108.89
24 | Net Generation of REB (MKWH) | 129.6731 |  | 136.77 |  | 133.88
24 | Net Generation of Rental Power Plant (MKWH) | 263.2062 |  | 409 |  | 399.95
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4021.476 |  | 4348.99 |  | 3948.49 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 3591.186 |  | 3478.78 |  | 3141.52 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 17.9446 |  | 79.67 |  | 67.64 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 354.6814 |  | 691.89 |  | 595.86 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 31.5205 |  | 45.69 |  | 60.48 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 4.7165 |  | 4.05 |  | 0.27 |  | 4.72 | 2018-12-16
31 | Energy Generation by Coal (MKWH) | 125.4514 |  | 111.82 |  | 160.82 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 412.397 |  | 478.69 |  | 294.34 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 71.4709 |  | 68.61 |  | 72.34 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:December' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 8534 | 04/12/18 | 19:00
Generation Period
| Dhaka | MW | 3001
| Chattogram | MW | 849
| Cumilla | MW | 676
| Mymensingh | MW | 572
| Sylhet | MW | 303
a) | Total supply in East zone | MW | 5401
| Khulna | MW | 956
| Barisal | MW | 200
| Rajshahi | MW | 819
| Rangpur | MW | 523
b) | Total supply in West zone | MW | 2498
c) | Total supply in both zone ( a+b) | MW | 7899
Ref: | 27.21.2604.603.16.085.18.123 | Date: 20/01/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:December' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 900 | 28/12/18 | 6:00
| b) Ishurdi end | MW | 200 | 04/12/18 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 460 | 04/12/18 | 10:00
| b) Ishurdi end | MW | 480 | 28/12/18 | 6:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.4615 | 15/12/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 5.2356 | 15/12/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 82.7838
| b) Ishurdi end | MKWH | 4.1316
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 4.0077
| b) Ishurdi end | MKWH | 80.3726
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 560 | 19/12/18 | 19:30
| b)Serajganj end | MW | 160 | 4/12/18 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 150 | 4/12/18 | 10:00
| b)Sirajganj end | MW | 540 | 19/12/18 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 8.872 | 15/12/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 8.716 | 15/12/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 170.63
| b)Sirajganj end | MKWH | 1.282
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.266
| b)Sirajganj end | MKWH | 165.852
30 | Transmission loss of EWI /NO-2 | % | 1.238
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: December 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV Transformer-T1 | 2018-12-01 08:26 | 2018-12-01 09:31 | 1:05 | T | Tripped showing O/C relay | 88 | 698.1333 | Power interruption 08:26 to 16:22
| 132/33 kV Transformer-T2 | 2018-12-01 08:26 | 2018-12-04 03:20 | 66:54 | T |  |  |  | No interruption
| 132/33 kV Transformer-T3 | 2018-12-01 08:26 | 2018-12-01 16:22 | 7:56 | T |  |  |  | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-12-13 06:55 | 2018-12-13 07:06 | 0:11 | T | Tripped due to 33 kV dhanbari feeder fault | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T3 | 2018-12-26 10:57 | 2018-12-26 15:37 | 4:40 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 80:46 |  | Unserved Energy: |  | 698.1333
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformer-T2 | 2018-12-01 09:50 | 2018-12-01 11:35 | 1:45 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2018-12-03 10:02 | 2018-12-03 16:24 | 6:22 | E/O | Due to Oil leakage at 33 kV B-phase CT | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T01 | 2018-12-06 01:40 | 2018-12-06 03:18 | 1:38 | T | Tripped showing Res.E/F relay | 0 | 0 | No interruption
| 230/132 kV Transformer-T02 | 2018-12-06 01:40 | 2018-12-06 11:09 | 9:29 | T |  | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2018-12-18 06:00 | 2018-12-18 09:22 | 3:22 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2018-12-18 05:22 | 2018-12-18 06:00 | 0:38 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 | 2018-12-19 23:49 | 2018-12-20 00:12 | 0:23 | E/O | Due to Y-phase insulator bursting | 72 | 33.6 | Power interruption 23:49 to 00:17
| 132/33 kV Transformers-T2 | 2018-12-19 23:49 | 2018-12-20 00:17 | 0:28 | E/O
Sonargaon | 132/33 kV Transformers-T1 | 2018-12-22 11:26 | 2018-12-22 11:59 | 0:33 | E/O | Due to Y-phase insulator of bus coupler burst | 30 | 16.5 | Power interruption 11:26 to 11:59
| 132/33 kV Transformers-T2 | 2018-12-22 11:26 | 2018-12-22 12:00 | 0:34 | E/O
Siddhirganj | 132 kV Bus | 2018-12-24 13:30 | 2018-12-24 15:51 | 1:45 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformers-T1 & T5 | 2018-12-28 20:28 | 2018-12-28 20:45 | 0:17 | T | Tripped showing Dir. & O/C relay at 33 kV Lalbagh Feeder fault | 40 | 11.3333 | Power interruption
|  |  | Total : | 1:45 |  | Unserved Energy: |  | 61.4333
Chittagong Grid Circle :
Khagrachari | 132/33 kV Transformer-T2 | 2018-12-03 11:25 | 2018-12-03 16:25 | 5:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T1 | 2018-12-12 12:11 | 2018-12-12 12:27 | 0:16 | T | Tripped showing O/C relay at 33 kV side | 40 | 10.6667 | Power interruption
Halishahar | 132/33 kV Transformers-T1 & T3 | 2018-12-18 18:20 | 2018-12-18 18:36 | 0:16 | T | Tripped showing E/F relay | 20 | 5.3333 | Power interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2018-12-20 10:41 | 2018-12-20 13:05 | 2:24 | E/O | Due to Oil leakage at 33 kV end
|  |  | Total : | 7:56 |  | Unserved Energy: |  | 16
Comilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T1 | 2018-12-01 06:57 | 2018-12-01 08:22 | 1:25 | E/O | Due to red hot maintenance at 33 kV Bus | 40 | 96.6667 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2018-12-01 11:55 | 2018-12-01 14:11 | 2:16 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2018-12-03 08:15 | 2018-12-03 09:48 | 1:33 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Biyanibazar | 132/33 kV Transformer-T2 | 2018-12-06 06:33 | 2018-12-06 07:00 | 0:27 | E/O | Due to 33 kV Jakiganj feeder fault | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-T1 | 2018-12-17 08:17 | 2018-12-17 13:21 | 5:04 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T6 | 2018-12-20 05:42 | 2018-12-20 05:49 | 0:07 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2018-12-22 00:58 | 2018-12-22 08:40 | 7:42 | T | Tripped showing O/V relay at 33 kV side | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformers-T1 | 2018-12-23 17:05 | 2018-12-23 17:20 | 0:15 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-12-23 17:05 | 2018-12-23 17:25 | 0:20 | T |  | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2018-12-30 05:56 | 2018-12-31 09:43 | 27:47 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Sirmongal | 132/33 kV Transformers-T1 & T2 | 2018-12-30 05:35 | 2018-12-30 05:36 | 0:01 | T | Tripped due to 33 kV feeder fault | 8 | 0.13333 | Power interruption
B.baria | 132/33 kV Transformers-T1 ,T2 & T3 | 2018-12-31 03:21 | 2018-12-31 03:37 | 0:16 | T | Tripped showing high voltage | 30 | 8 | Power interruption
Daudkandi | 132/33 kV Transformer-T1 | 2018-12-31 03:24 | 2018-12-31 04:52 | 1:28 | T | Tripped showing high voltage | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformers-T1 & T2 | 2018-12-31 17:05 | 2018-12-31 17:09 | 0:04 | T | Tripped showing inst.E/F relay at 33 kV feeder fault | 53 | 3.5333 | Power interruption
|  |  | Total : | 48:45 |  | Unserved Energy: |  | 108.3333
Khulna Grid Circle :
Mongla | 132/33 kV Transformers-T1 | 2018-12-10 03:06 | 2018-12-10 03:13 | 0:07 | T | Tripped due to E/F relay at 33 kV side | 30 | 3.5 | Power interruption 03:06 to 03:13
| 132/33 kV Transformers-T2 | 2018-12-10 03:06 | 2018-12-10 03:17 | 0:11 | T
Bagerhat | 132/33 kV Transformer-T1 | 2018-12-18 11:08 | 2018-12-18 11:15 | 0:07 | T | Tripped due to E/F relay at 33 kV feeder | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2018-12-19 12:26 | 2018-12-19 14:20 | 1:54 | E/O | Due to air leakge | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2018-12-21 09:25 | 2018-12-21 09:38 | 0:13 | T | Tripped due to E/F relay at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 2:32 |  | Unserved Energy: |  | 3.5
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: December 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | 230/132 kV Transformer-T03 | 2018-12-20 10:34 | 2018-12-20 11:04 | 0:30 | T | Due to Oil leakage 33 kV side | 0 | 0 | No interruption
Bheramara | 230/132 kV Transformers-T1 | 2018-12-28 05:30 | 2018-12-28 06:39 | 1:09 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
| 230/132 kV Transformers-T1 | 2018-12-28 05:30 | 2018-12-28 06:30 | 1:00 | T |  | 0 | 0 | No interruption
|  |  | Total : | 2:39 |  |  |  | 0
Bogra Grid Circle:
Ruppur | 132/33 kV Transformer-T1 | 2018-12-11 04:15 | 2018-12-11 05:50 | 1:35 | E/O | Tripped showing Oil leakage | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2018-12-20 10:40 | 2018-12-20 12:15 | 1:35 | T | Tripped showing Oil leakage at 33 kV side | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T1 | 2018-12-18 02:44 | 2018-12-18 10:11 | 7:27 | T | Due to Over voltage | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformers-T1 & T2 | 2018-12-29 13:30 | 2018-12-29 13:39 | 0:09 | T | Due to 33 kV feeder fault | 39 | 5.85 | Power interruption
|  |  | Total : | 10:46 |  | Unserved Energy: |  | 5.85
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 155:09 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: December 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Lalbagh | Lalbagh-Kallyanpur 132 kV line-1 | 2018-12-17 06:17 | 2018-12-17 10:15 | 3:58 | T | Tripped showing 67N. relay | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2018-12-19 08:38 | 2018-12-19 11:01 | 2:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-12-19 15:01 | 2018-12-19 15:10 | 0:09 | T | Tripped showing dist. relay | 90 | 13.5 | Power interruption
|  |  | Total : | 6:30 |  | Unserved Energy: |  | 13.5
Dhaka (South) Grid Circle :
Haripur | Haripur-Rahim Steel 132 kV line | 2018-12-06 09:39 | 2018-12-06 11:35 | 1:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2018-12-10 16:20 | 2018-12-10 16:30 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rampura-Moghbazar 132 kV line-1 | 2018-12-11 15:15 | 2018-12-11 15:29 | 0:14 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Haripur | Haripur-Rahim Steel 132 kV line | 2018-12-14 19:50 | 2018-12-18 18:54 | 95:04 | T | Tripped showing O/C& E/F. relay | 0 | 0 | No interruption
| Haripur-Siddhirganj 132 kV line-1 & 2 | 2018-12-14 19:50 | 2018-12-14 20:15 | 0:25 | T | Tripped showing inst.E/F. relay | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line-1 | 2018-12-16 07:35 | 2018-12-16 08:07 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur (New) | Shyampur (New)-Shyampur(Old) 132 kV line-2 | 2018-12-18 05:58 | 2018-12-18 06:19 | 0:21 | T | Tripped showing dist. relay | 40 | 14 | Power interruption
| Shyampur (New)-Shyampur(Old) 132 kV line-2 | 2018-12-18 06:24 | 2018-12-18 06:42 | 0:18 | T |  | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2018-12-18 05:22 | 2018-12-18 05:52 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR 230 kV line-2 | 2018-12-20 14:30 | 2018-12-20 22:25 | 7:55 | E/O | Due to bursting at L/A. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2018-12-23 11:20 | 2018-12-24 21:57 | 34:37 | T | Tripped showing dist. relay | 65 | 9.3333 | Power interruption 11:22 to 11:30
Ghorasal | Ghorasal-Ashuganj 132 kV line-1 | 2018-12-24 11:22 | 2018-12-24 11:22 | 1:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-12-26 08:45 | 2018-12-26 09:00 | 0:15 | T | Tripped showing O/C& E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 144:13 |  | Unserved Energy: |  | 23.3333
Chittagong Grid Circle :
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2018-12-09 09:23 | 2018-12-09 09:56 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-2 | 2018-12-09 10:41 | 2018-12-09 15:42 | 5:01 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-1 | 2018-12-09 09:28 | 2018-12-09 09:36 | 0:08 | T |  | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-1 | 2018-12-09 10:41 | 2018-12-09 10:48 | 0:07 | T |  | 0 | 0 | No interruption
| Hathazari-Raozan 230i kV line-2 | 2018-12-13 09:03 | 2018-12-13 15:18 | 6:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 12:04 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-12-03 11:59 | 2018-12-03 12:29 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line-2 | 2018-12-03 11:59 | 2018-12-03 12:22 | 0:23 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
| Sylhet-Fenchuganj 132 kV line | 2018-12-03 11:58 | 2018-12-03 12:24 | 0:26 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-1 | 2018-12-12 15:09 | 2018-12-12 17:10 | 2:05 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjanagar 132 kV line-1 | 2018-12-14 00:15 | 2018-12-14 16:54 | 16:39 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2018-12-15 05:17 | 2018-12-15 05:49 | 0:32 | T | Tripped showing dist. relay | 11 | 5.8667 | Power interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-3 | 2018-12-17 08:17 | 2018-12-17 15:44 | 7:27 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
| Fenchuganj S/S-Sylhet 132 kV line | 2018-12-17 08:17 | 2018-12-17 08:43 | 0:26 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1 | 2018-12-19 14:01 | 2018-12-19 14:29 | 0:28 | T | Tripped showing auto reclose relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2018-12-20 18:56 | 2018-12-20 20:15 | 2:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-2 | 2018-12-22 08:03 | 2018-12-22 14:44 | 6:41 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-1 | 2018-12-28 06:35 | 2018-12-28 10:06 | 3:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: December 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Feni | Feni-Chowmuhani 132 kV line-2 | 2018-12-29 07:52 | 2018-12-29 16:30 | 8:38 | E/O | Due to air leakage | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur desh 132 kV line-1 | 2018-12-29 23:10 | 2018-12-29 23:50 | 0:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2018-12-30 13:40 | 2018-12-30 14:13 | 0:33 | T | Tripped showing O/C .& E/F relay | 0 | 0 | No interruption
| Cumilla(N)-Chandpur 132 kV line-2 | 2018-12-30 13:40 | 2018-12-30 19:19 | 5:39 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV line-1 | 2018-12-31 03:21 | 2018-12-31 11:37 | 8:16 | T | Tripped showing O/V . relay | 0 | 0 | No interruption
|  |  | Total : | 64:59 |  | Unserved Energy: |  | 5.8667
Khulna Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jessore | Jessore-Jhenidah 132 kV line-2 | 2018-12-17 12:22 | 2018-12-17 20:27 | 8:05 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2018-12-22 13:56 | 2018-12-22 17:03 | 3:07 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV line | 2018-12-28 05:30 | 2018-12-28 06:13 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Baghabari 230 kV line-1 & 2 | 2018-12-28 05:30 | 2018-12-28 06:21 | 0:51 | T |  | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-12-28 05:30 | 2018-12-29 16:07 | 34:37 | T | Tripped showing PTAW,CAT,CD signal | 0 | 0 | No interruption
| Bheramara-Ishurdi 132 kV line-2 | 2018-12-28 05:30 | 2018-12-28 05:48 | 0:18 | T |  | 0 | 0 | No interruption
|  |  | Total : | 47:41 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2018-12-12 07:10 | 2018-12-12 09:15 | 2:05 | E/O | Due to red hot maintenance | 20 | 41.6667 | Power interruption
Bogura | Bogura-Palashbari 132 kV line-2 | 2018-12-12 10:25 | 2018-12-12 10:40 | 0:15 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Nator 132 kV line-1 | 2018-12-18 02:39 | 2018-12-18 02:52 | 0:13 | T | Tripped showing PTAW,CAT,CD signal | 50 | 10 | Power interruption 0239 to 2:52
| Rajshahi-Nator 132 kV line-2 | 2018-12-18 02:40 | 2018-12-18 02:52 | 0:12 | T | Tripped showing dist. relay
Natore | Natore-Rajshahi 132 kV line-1 | 2018-12-28 05:30 | 2018-12-28 05:45 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 3:00 |  | Unserved Energy: |  | 51.6667
Others :
Maniknagar | Maniknagar-Matuail 132 kV line | 2018-12-06 01:40 | 2018-12-06 02:10 | 0:30 | T | Tripped showing main protection relay | 90 | 45 | Power interruption
| Maniknagar-Bangabhaban 132 kV line-1 | 2018-12-06 01:40 | 2018-12-06 02:50 | 1:10 | T
| Maniknagar-Bangabhaban 132 kV line-2 | 2018-12-06 01:40 | 2018-12-06 01:40 | 0:00 | T |  |  |  | under long time maintenance
|  |  | Total : | 1:40 |  | Unserved Energy: |  | 45
Total outage period of Sub-station Equipment : |  |  |  | 280:07 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV Transformer-T3 | 2018-12-01 07:34 | 2018-12-01 09:22 | 1:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-12-01 08:51 | 2018-12-01 14:48 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2018-12-01 14:33 | 2018-12-01 15:13 | 0:40 | S/O | Due to changing og 33 kV CT ratio | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2018-12-01 08:28 | 2018-12-01 16:07 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T01 | 2018-12-01 09:15 | 2018-12-01 15:51 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2018-12-02 09:41 | 2018-12-02 17:04 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargon | 230/132 kV Transformer-T02 | 2018-12-02 08:29 | 2018-12-02 17:55 | 9:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-12-02 08:15 | 2018-12-02 13:35 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2018-12-02 08:33 | 2018-12-02 16:13 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2018-12-02 08:25 | 2018-12-02 16:55 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T01 | 2018-12-03 08:55 | 2018-12-03 16:32 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T2 | 2018-12-03 08:48 | 2018-12-03 16:32 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-12-03 08:25 | 2018-12-03 14:50 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2018-12-03 08:35 | 2018-12-03 16:09 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2018-12-03 08:29 | 2018-12-03 15:50 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T01 | 2018-12-04 09:56 | 2018-12-04 15:59 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T2 | 2018-12-04 09:33 | 2018-12-04 14:14 | 4:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2018-12-05 09:20 | 2018-12-06 16:53 | 31:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2018-12-05 08:20 | 2018-12-05 14:50 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV bus-1 | 2018-12-05 10:20 | 2018-12-05 15:55 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T02 | 2018-12-06 08:51 | 2018-12-06 17:05 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 | 2018-12-06 08:55 | 2018-12-06 15:13 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-12-06 08:25 | 2018-12-06 14:12 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T1 | 2018-12-06 15:38 | 2018-12-06 16:38 | 1:00 | S/O | Due to Isolator maintenance | 0 | 0 | No interruption
| Bus coupler CB | 2018-12-06 09:51 | 2018-12-06 16:36 | 6:45 | S/O | Due to temperature high | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2018-12-07 08:05 | 2018-12-07 11:05 | 3:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2018-12-07 06:09 | 2018-12-07 09:12 | 3:03 | S/O | Due to 33 kV new bus connection | 22 | 67.1 | Power interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2018-12-08 15:19 | 2018-12-08 15:30 | 0:11 | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-08 15:32 | 2018-12-08 15:42 | 0:10 | S/O |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-12-08 14:27 | 2018-12-08 14:43 | 0:16 | S/O |  | 0 | 0 | No interruption
Kallyanpur | 132 kV bus coupler | 2018-12-10 09:32 | 2018-12-10 14:11 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2018-12-10 08:28 | 2018-12-10 16:27 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2018-12-10 08:25 | 2018-12-10 13:33 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T1 | 2018-12-10 08:41 | 2018-12-10 16:18 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV Transformer-T1 | 2018-12-11 08:55 | 2018-12-11 15:17 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T1 | 2018-12-11 08:38 | 2018-12-11 14:50 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV main bus | 2018-12-12 08:58 | 2018-12-13 15:36 | 30:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2018-12-12 09:31 | 2018-12-12 12:55 | 3:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T1 | 2018-12-12 09:43 | 2018-12-12 11:38 | 1:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2018-12-12 09:25 | 2018-12-12 13:25 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2018-12-12 09:52 | 2018-12-12 14:18 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve bus | 2018-12-13 09:50 | 2018-12-13 16:05 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 | 2018-12-13 09:12 | 2018-12-13 18:10 | 8:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T1 | 2018-12-14 07:07 | 2018-12-14 12:05 | 4:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformers-T1 & T2 | 2018-12-15 07:03 | 2018-12-15 08:40 | 1:37 | S/O | Due to 33 kV bus S/D | 86 | 64.6667 | Power interruption
Savar | 132/33 kV Transformer-T2 | 2018-12-15 08:20 | 2018-12-15 13:38 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-12-15 11:01 | 2018-12-15 13:15 | 2:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2018-12-15 08:10 | 2018-12-15 09:50 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T1 | 2018-12-15 08:03 | 2018-12-15 16:29 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2018-12-15 10:31 | 2018-12-15 13:55 | 3:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132 kV main bus | 2018-12-17 10:40 | 2018-12-17 13:48 | 3:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2018-12-17 09:15 | 2018-12-17 13:39 | 4:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-TR2 | 2018-12-17 10:29 | 2018-12-17 11:12 | 0:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishorganj | 132/33 kV Transformer-T1 | 2018-12-17 09:43 | 2018-12-17 13:33 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2018-12-17 08:30 | 2018-12-17 16:02 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2018-12-17 09:59 | 2018-12-17 17:35 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2018-12-18 08:46 | 2018-12-18 12:36 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2018-12-18 08:49 | 2018-12-18 17:28 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-19 07:21 | 2018-12-19 18:18 | 10:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132 kV main bus | 2018-12-19 09:02 | 2018-12-20 17:05 | 32:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T1 | 2018-12-19 08:44 | 2018-12-19 16:46 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2018-12-19 08:26 | 2018-12-19 16:39 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T1 | 2018-12-20 09:09 | 2018-12-20 15:48 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2018-12-20 12:58 | 2018-12-20 15:15 | 2:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T5 | 2018-12-21 09:26 | 2018-12-21 09:41 | 0:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T2 | 2018-12-22 08:50 | 2018-12-22 14:36 | 5:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-12-22 08:15 | 2018-12-22 10:15 | 2:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Shitalakhya | 132/33 kV Transformer-T2 | 2018-12-22 10:44 | 2018-12-22 13:38 | 2:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T02 | 2018-12-23 09:03 | 2018-12-23 13:34 | 4:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T1 & T2 | 2018-12-23 09:35 | 2018-12-23 10:38 | 1:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T1 | 2018-12-23 08:43 | 2018-12-23 17:18 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2018-12-23 09:45 | 2018-12-23 15:57 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(New) | 132/33 kV Transformer-T1 | 2018-12-24 09:26 | 2018-12-24 13:31 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2018-12-24 09:28 | 2018-12-24 16:51 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T3 | 2018-12-26 09:49 | 2018-12-26 20:33 | 10:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2018-12-26 09:58 | 2018-12-26 13:26 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi(New) | 132/33 kV Transformer-T1 | 2018-12-26 12:02 | 2018-12-26 20:21 | 8:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132 kV reserve bus | 2018-12-26 12:50 | 2018-12-26 14:44 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-TR2 | 2018-12-27 09:30 | 2018-12-27 14:32 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2018-12-27 08:23 | 2018-12-27 16:18 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 499:55 |  | Unserved Energy: |  | 131.7667
Dhaka (South) Grid Circle :
Siddhirganj | 230/132 kV Transformer-TR2 | 2018-12-01 08:24 | 2018-12-01 15:28 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T2 | 2018-12-01 09:35 | 2018-12-01 16:30 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T4 | 2018-12-03 10:00 | 2018-12-03 15:25 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV Transformer-TR1 | 2018-12-04 10:00 | 2018-12-04 12:51 | 2:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/230 kV Transformer-TR2 | 2018-12-04 12:37 | 2018-12-04 15:24 | 2:47 | S/O |  | 0 | 0 | No interruption
| 400/230 kV Transformer-TR1 | 2018-12-05 10:17 | 2018-12-05 14:01 | 3:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/230 kV Transformer-TR2 | 2018-12-05 14:37 | 2018-12-05 16:46 | 2:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2018-12-08 08:23 | 2018-12-08 13:28 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Shitalakyha | 132/33 kV Transformer-T1 | 2018-12-08 10:16 | 2018-12-08 14:06 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2018-12-09 09:24 | 2018-12-09 12:51 | 3:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400 kV bus-2 | 2018-12-09 20:09 | 2018-12-09 22:23 | 2:14 | S/O | Due to DFDR commissioning | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-TR1 | 2018-12-14 07:07 | 2018-12-14 12:06 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-TR1 | 2018-12-15 08:03 | 2018-12-15 16:29 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur(new) | 132/33 kV Transformer-GT2 | 2018-12-15 11:07 | 2018-12-15 13:09 | 2:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-GT2 | 2018-12-15 08:17 | 2018-12-15 13:39 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Shitalakyha | 132/33 kV Transformer-T3 | 2018-12-15 11:03 | 2018-12-15 16:35 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T2 | 2018-12-18 08:48 | 2018-12-18 14:35 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230 kV bus-1 | 2018-12-18 12:04 | 2018-12-18 13:44 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 4/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-T02 | 2018-12-19 00:58 | 2018-12-19 07:39 | 6:41 | S/O | Due to low voltage | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2018-12-19 07:21 | 2018-12-19 18:18 | 10:57 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-20 08:01 | 2018-12-20 19:11 | 11:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2018-12-21 07:41 | 2018-12-21 16:58 | 9:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T02 | 2018-12-21 08:24 | 2018-12-21 12:56 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV Transformer-T2 | 2018-12-21 10:05 | 2018-12-21 17:30 | 7:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T02 | 2018-12-22 08:31 | 2018-12-22 14:02 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T2 | 2018-12-22 08:07 | 2018-12-22 13:33 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T1 | 2018-12-23 10:31 | 2018-12-23 12:10 | 1:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T2 | 2018-12-23 08:35 | 2018-12-23 13:01 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T01 | 2018-12-26 07:38 | 2018-12-26 17:11 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 155:56 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Bakulia | 132/33 kV Transformer-T3 | 2018-12-01 09:41 | 2018-12-01 13:34 | 3:53 | S/O | Due to A/M work | 5 | 19.4167 | Power interruption
Sikalbaha(GIS) | 230/132 kV Transformer-T01 |  | 2018-12-01 15:54 |  |  | Due to A/M work | 0 | 0 | Newly commissioned
| 230/132 kV Transformer-T02 | 2018-12-01 16:33 | 2018-12-09 15:33 | 191:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV Transformer-T1 | 2018-12-03 16:30 | 2018-12-03 17:06 | 0:36 | S/O | Due to tightning nut bolts | 0 | 0 | No interruption
Juldah | 132 kV bus | 2018-12-08 07:29 | 2018-12-08 12:54 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2018-12-11 07:48 | 2018-12-11 10:18 | 2:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T2 | 2018-12-12 08:12 | 2018-12-15 13:01 | 76:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T1 | 2018-12-14 09:31 | 2018-12-14 12:50 | 3:19 | S/O | Due to painting work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-14 12:51 | 2018-12-14 16:03 | 3:12 | S/O | Due to painting work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV Transformer-T2 | 2018-12-17 09:25 | 2018-12-17 13:54 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-18 08:48 | 2018-12-18 14:35 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T1 | 2018-12-21 09:10 | 2018-12-21 17:37 | 8:27 | S/O | Due to painting work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T3 | 2018-12-25 06:35 | 2018-12-25 09:10 | 2:35 | S/O | Due to A/M work | 8 | 20.6667 | Power interruption
| 132/33 kV Transformer-T2 | 2018-12-25 09:17 | 2018-12-25 10:50 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2018-12-28 10:35 | 2018-12-28 12:19 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 311:19 |  | Unserved Energy: |  | 40.0833
Comilla Grid Circle :
Sunamganj | 132/33 kV Transformer-T2 | 2018-12-01 10:33 | 2018-12-01 11:30 | 0:57 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-12-01 11:40 | 2018-12-01 16:41 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T4 | 2018-12-02 10:03 | 2018-12-02 16:03 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400 kV bus-1 | 2018-12-03 09:04 | 2018-12-10 20:23 | 179:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 5/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Bianibazar | 132/33 kV Transformer-T2 | 2018-12-04 10:00 | 2018-12-04 13:15 | 3:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Kulaura | 132 kV bus-1 | 2018-12-05 09:31 | 2018-12-05 13:56 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2018-12-11 11:47 | 2018-12-11 16:16 | 4:29 | S/O | Due to 33 kV CB removing work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2018-12-15 07:23 | 2018-12-15 14:07 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2018-12-21 08:49 | 2018-12-21 14:41 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulaura | 132 kV bus-2 | 2018-12-22 09:41 | 2018-12-22 14:48 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2018-12-23 08:33 | 2018-12-23 16:51 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-12-25 08:05 | 2018-12-25 16:35 | 8:30 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 569:22 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Noapara | 132 kV bus-A | 2018-12-01 09:09 | 2018-12-01 15:03 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV bus-2 | 2018-12-02 09:55 | 2018-12-02 13:41 | 3:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2018-12-02 07:17 | 2018-12-02 09:39 | 2:22 | S/O | Due to replacement of 33 kV feeder | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T4 | 2018-12-04 09:02 | 2018-12-04 12:48 | 3:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2018-12-04 08:32 | 2018-12-04 09:12 | 0:40 | S/O | Due to new Transformer connection | 20 | 13.3333 | Power interruption
Khulna© | 132/33 kV Transformer-T3 | 2018-12-04 10:25 | 2018-12-04 14:57 | 4:32 | S/O | Due to relay test | 0 | 0 | No interruption
Khulna(S) | 132 kV capacitor bank | 2018-12-05 09:05 | 2018-12-05 16:45 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2018-12-07 07:05 | 2018-12-07 09:20 | 2:15 | S/O | Due to D/W work | 10 | 22.5 | Power interruption
Madaripur | 132 kV bus-B | 2018-12-14 08:25 | 2018-12-14 17:15 | 8:50 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-12-21 07:10 | 2018-12-21 10:30 | 3:20 | S/O | Due to 33 kV Tekerhat feeder | 8 | 26.6667 | Power interruption
|  |  | Total : | 43:05 |  | Unserved Energy : |  | 62.5
HVDC Grid Circle :
HVDCBheramara | 400 kV bus-2 | 2018-12-01 10:44 | 2018-12-01 15:56 | 5:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV bus-1 | 2018-12-01 09:48 | 2018-12-01 13:42 | 3:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 400 kV bus-2 | 2018-12-02 07:54 | 2018-12-02 17:16 | 9:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV bus-2 | 2018-12-02 10:30 | 2018-12-02 18:12 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2018-12-03 08:10 | 2018-12-03 13:44 | 5:34 | S/O | Due to changing of 33 kV L/A | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T1 | 2018-12-04 08:18 | 2018-12-04 15:37 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T1 | 2018-12-05 09:15 | 2018-12-05 16:41 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T2 | 2018-12-05 08:18 | 2018-12-05 15:44 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-12-06 08:19 | 2018-12-06 16:14 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2018-12-08 09:25 | 2018-12-08 18:40 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Jessore | 132 kV capacitor bank | 2018-12-08 09:33 | 2018-12-08 19:25 | 9:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| 33 kV capacitor bank | 2018-12-09 08:30 | 2018-12-09 16:32 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2018-12-19 10:57 | 2018-12-19 15:48 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDCBheramara | HVDC Bheramara pole -2 | 2018-12-22 07:23 | 2018-12-22 16:33 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 103:00 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Amnura | 132/33 kV Transformer-T2 | 2018-12-02 08:48 | 2018-12-02 14:56 | 6:08 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-03 09:30 | 2018-12-03 16:12 | 6:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T3 | 2018-12-03 08:45 | 2018-12-03 16:10 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogra Grid Circle:
Palashbari | 132/33 kV Transformer-T3 | 2018-12-04 09:14 | 2018-12-04 14:50 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-12-05 09:05 | 2018-12-05 15:07 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-12-06 09:30 | 2018-12-06 14:31 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T1 | 2018-12-09 09:36 | 2018-12-09 14:58 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T1 | 2018-12-11 11:55 | 2018-12-11 13:45 | 1:50 | S/O | Due to replacement work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2018-12-12 10:21 | 2018-12-12 12:05 | 1:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T2 | 2018-12-12 08:15 | 2018-12-12 15:05 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T1 | 2018-12-12 09:06 | 2018-12-27 15:27 | 366:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | 132 kV Bus | 2018-12-14 09:14 | 2018-12-14 12:20 | 3:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T3 | 2018-12-17 08:33 | 2018-12-17 14:35 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132 kV Bus | 2018-12-18 07:12 | 2018-12-18 08:30 | 1:18 | S/O | Due to D/W work | 30 | 39 | Power interruption
Bogura | 230/132 kV Transformer-T1 | 2018-12-20 09:13 | 2018-12-20 14:05 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-12-22 10:42 | 2018-12-22 11:00 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-12-22 11:00 | 2018-12-22 11:23 | 0:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV bus-1 | 2018-12-22 07:40 | 2018-12-22 16:42 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T3 | 2018-12-22 10:25 | 2018-12-22 12:18 | 1:53 | S/O | Due to delta test | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-12-22 11:29 | 2018-12-22 12:28 | 0:59 | S/O |  | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T2 | 2018-12-24 08:57 | 2018-12-24 15:45 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2018-12-24 10:35 | 2018-12-24 13:42 | 3:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T3 | 2018-12-25 09:35 | 2018-12-25 14:35 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2018-12-27 11:35 | 2018-12-27 13:02 | 1:27 | S/O | Due to 33 kV bus maint. | 0 | 0 | No interruption
Palashbari | 132 kV main Bus | 2018-12-28 10:25 | 2018-12-28 12:50 | 2:25 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 465:41 |  | Unserved Energy : |  | 39
Others :
Shyampur | 132/33 kV Transformer-T3 | 2018-12-01 10:36 | 2018-12-01 15:19 | 4:43 | S/O | Due to A/M work by DPDC | 20 | 94.3333 | Power interruption
Barisal | 132/33 kV Transformer-T2 | 2018-12-01 16:20 | 2018-12-01 18:42 | 2:22 | S/O | Due to repacement work by WZPDCO | 15 | 35.5 | Power interruption
Bashundhara | 132/33 kV Transformer-T2 | 2018-12-09 08:30 | 2018-12-09 15:53 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total | 14:28 |  | Unserved Energy : |  | 129.8333
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 2162:46 | Hours
S/O=Schedule Outage,A/M= Annual Maintenance, D/W= Development Work
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 | 2018-12-02 09:27 | 2018-12-02 16:49 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2018-12-02 08:14 | 2018-12-02 15:14 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV line-1 | 2018-12-02 09:43 | 2018-12-02 12:28 | 2:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2018-12-03 13:08 | 2018-12-03 14:20 | 1:12 | S/O | Due to project work | 0 | 0 | No interruption
| Tangail-RPCL 132 kV line-2 | 2018-12-03 14:27 | 2018-12-03 15:54 | 1:27 | S/O | Due to D/W work | 0 | 0 | No interruption
New Tongi | New Tongi-Tongi 132 kV line-2 | 2018-12-04 08:44 | 2018-12-04 14:59 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2018-12-04 08:26 | 2018-12-04 16:35 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2018-12-08 06:13 | 2018-12-09 00:29 | 18:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV line-2 | 2018-12-08 06:13 | 2018-12-09 00:11 | 17:58 | S/O |  | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-12-08 08:07 | 2018-12-08 16:15 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2018-12-09 08:09 | 2018-12-09 16:10 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-12-09 08:07 | 2018-12-09 16:33 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2018-12-10 09:53 | 2018-12-10 16:30 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2018-12-10 08:13 | 2018-12-10 15:50 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2018-12-10 10:37 | 2018-12-10 20:10 | 9:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-12-10 08:32 | 2018-12-10 16:31 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2018-12-10 11:57 | 2018-12-10 13:40 | 1:43 | S/O | Due to protection test | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2018-12-10 08:48 | 2018-12-10 16:44 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2018-12-10 13:18 | 2018-12-10 14:55 | 1:37 | S/O | Due to protection test | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-2 | 2018-12-11 09:39 | 2018-12-11 15:41 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2018-12-11 10:05 | 2018-12-11 13:51 | 3:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-12-11 08:34 | 2018-12-11 16:44 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2018-12-12 09:55 | 2018-12-12 15:54 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2018-12-12 08:03 | 2018-12-12 16:34 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-12-12 08:08 | 2018-12-12 16:58 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2018-12-12 08:48 | 2018-12-12 15:26 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-12-13 09:05 | 2018-12-13 16:11 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2018-12-15 08:07 | 2018-12-15 16:13 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2018-12-17 10:26 | 2018-12-17 16:50 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Jamalpur 132 kV line-1 | 2018-12-17 11:54 | 2018-12-17 16:01 | 4:07 | S/O | Due to CB testing | 0 | 0 | No interruption
| Mymensingh -Jamalpur 132 kV line-2 | 2018-12-17 16:12 | 2018-12-17 19:28 | 3:16 | S/O | Due to protection work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2018-12-18 20:37 | 2018-12-18 20:52 | 0:15 | S/O | Due to clearing birds nest | 0 | 0 | No interruption
| Aminbazar-Hasnabad 230 kV line-1 | 2018-12-19 07:50 | 2018-12-19 07:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | reconductoring on going
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2018-12-19 09:58 | 2018-12-19 15:33 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2018-12-19 09:25 | 2018-12-19 16:38 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2018-12-22 09:22 | 2018-12-22 16:46 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2018-12-22 08:12 | 2018-12-22 16:19 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-Mymensingh RPCL 132 kV line-2 | 2018-12-22 09:46 | 2018-12-22 16:44 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 Kv line | 2018-12-23 11:28 | 2018-12-24 21:57 | 34:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 & 2 | 2018-12-09 12:19 | 2018-12-23 11:30 | 335:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line | 2018-12-23 08:36 | 2018-12-23 18:12 | 9:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2018-12-23 09:04 | 2018-12-23 15:42 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2018-12-23 08:28 | 2018-12-23 17:04 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2018-12-24 08:15 | 2018-12-24 15:41 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2018-12-24 09:35 | 2018-12-24 17:06 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2018-12-26 09:12 | 2018-12-26 20:46 | 11:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2018-12-26 08:25 | 2018-12-26 16:29 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2018-12-26 08:20 | 2018-12-26 16:29 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-Mymensingh RPCL 132 kV line-1 | 2018-12-26 09:19 | 2018-12-26 16:52 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar -Kallyanpur 132 kV line-2 | 2018-12-27 09:28 | 2018-12-27 14:35 | 5:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2018-12-27 09:38 | 2018-12-27 15:22 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2018-12-27 08:47 | 2018-12-27 15:46 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda S/S | Kadda S/S-Kadda P/S 132 kV line | 2018-12-27 09:10 | 2018-12-27 13:25 | 4:15 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 717:20 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Sonargaon | Sonargaon-Meghnaghat IEL 132 kV line-1 | 2018-12-01 08:50 | 2018-12-01 17:14 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2018-12-01 09:20 | 2018-12-01 14:59 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Rampura 132 kV line-2 | 2018-12-01 09:41 | 2018-12-01 16:18 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV line | 2018-12-02 09:31 | 2018-12-02 15:53 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2018-12-02 09:27 | 2018-12-02 16:37 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV line-1 | 2018-12-02 09:16 | 2018-12-02 14:12 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bhulta-Haripur 230 kV line-2 | 2018-12-03 09:18 | 2018-12-03 12:50 | 3:32 | S/O | Due to D/M work | 0 | 0 | No interruption
| Bhulta-Haripur 132 kV line-2 | 2018-12-03 11:07 | 2018-12-03 16:39 | 5:32 | S/O | Due to D/M work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-Haripur 132 kV line | 2018-12-03 11:02 | 2018-12-03 15:56 | 4:54 | S/O | Due to D/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2018-12-03 12:55 | 2018-12-03 16:06 | 3:11 | S/O | Due to DFDR work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta-Rampura 230 kV line-2 | 2018-12-04 08:53 | 2018-12-04 16:13 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV line-3 | 2018-12-04 09:10 | 2018-12-04 13:58 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-2 | 2018-12-04 08:55 | 2018-12-04 16:58 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2018-12-05 09:21 | 2018-12-05 13:59 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Ullon 132 kV line-1 | 2018-12-08 06:50 | 2018-12-10 07:04 | 48:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kamrangirchar 132 kV line | 2018-12-09 00:26 | 2018-12-09 10:50 | 10:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2018-12-09 08:40 | 2018-12-09 16:03 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2018-12-08 08:46 | 2018-12-08 16:03 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 | 2018-12-09 08:40 | 2018-12-09 16:39 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2018-12-11 08:33 | 2018-12-11 15:35 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Meghnaghat 230 kV line-2 | 2018-12-12 09:00 | 2018-12-12 15:52 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-1 | 2018-12-12 09:52 | 2018-12-12 16:00 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2018-12-13 09:40 | 2018-12-13 20:05 | 10:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | Munsiganj-Munshiganj 132 kV line-1 | 2018-12-13 10:09 | 2018-12-13 14:46 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR 230 kV line | 2018-12-14 06:38 | 2018-12-20 13:32 | 150:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 | 2018-12-14 07:44 | 2018-12-14 15:41 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2018-12-17 10:05 | 2018-12-17 16:01 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-1 | 2018-12-17 08:59 | 2018-12-17 13:24 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hasnabad-Aminbazar 230 kV line-2 | 2018-12-17 13:30 | 2018-12-17 17:29 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-1 | 2018-12-18 15:30 | 2018-12-18 17:50 | 2:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.baria 132 kV line-1 | 2018-12-19 09:45 | 2018-12-19 11:34 | 1:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 3/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Narsingdi | Narsingdi-B.baria 132 kV line-2 | 2018-12-19 11:37 | 2018-12-19 13:02 | 1:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-12-20 09:21 | 2018-12-20 15:47 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-1 | 2018-12-22 12:13 | 2018-12-22 16:03 | 3:50 | S/O | Due to protection test | 0 | 0 | No interruption
Bhulta | Bhulta-Ashuganj 400 kV line-1 | 2018-12-22 13:45 | 2018-12-22 16:20 | 2:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV line-2 | 2018-12-22 16:11 | 2018-12-22 16:45 | 0:34 | S/O | Due to protection test | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2018-12-23 07:39 | 2018-12-23 16:59 | 9:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-2 | 2018-12-23 08:16 | 2018-12-23 20:12 | 11:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV line-1 | 2018-12-25 09:10 | 2018-12-25 12:48 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 414:31 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Raozan | Raozan P/S -Hathazari 230 kV line-2 | 2018-12-01 09:12 | 2018-12-01 16:44 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2018-12-02 09:01 | 2018-12-02 16:07 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV line-1 | 2018-12-02 08:48 | 2018-12-02 16:00 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2018-12-03 08:38 | 2018-12-03 15:40 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV line-1 | 2018-12-03 08:30 | 2018-12-03 14:58 | 6:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2018-12-04 08:25 | 2018-12-04 15:34 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV line-2 | 2018-12-04 08:26 | 2018-12-04 20:40 | 12:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2018-12-04 09:26 | 2018-12-26 13:12 | 531:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK chemical 132 kV line | 2018-12-04 09:25 | 2018-12-04 15:15 | 5:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2018-12-05 08:21 | 2018-12-05 15:57 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV line-2 | 2018-12-05 09:03 | 2018-12-05 15:32 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2018-12-08 09:17 | 2018-12-08 15:50 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Raozan 230 kV line-2 | 2018-12-09 09:09 | 2018-12-09 15:40 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Raozan 230i kV line-2 | 2018-12-10 09:10 | 2018-12-10 15:58 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Sikalbaha 132 kV line-2 | 2018-12-10 09:45 | 2018-12-10 17:40 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbha 132 kV line-1 | 2018-12-13 09:11 | 2018-12-13 14:42 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbha-Juldah 132 kV line | 2018-12-13 10:21 | 2018-12-14 14:15 | 27:54 | S/O | Due to project work | 0 | 0 | No interruption
| Sikalbaha-Shahmirpur 132 kV line-1 | 2018-12-18 11:50 | 2018-12-26 15:56 | 196:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Barauila | Barauila-BSRM 132 kV line | 2018-12-21 08:58 | 2018-12-21 17:17 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line-1 | 2018-12-25 08:10 | 2018-12-25 09:28 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2018-12-26 08:09 | 2018-12-26 16:07 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaptai-Chandraghona 132 kV line-2 | 2018-12-27 08:05 | 2018-12-27 16:22 | 8:17 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 882:02 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Cumilla(N) | Cumilla(N)-Meghnaghat 132 kV line-1 | 2018-12-01 08:34 | 2018-12-01 17:14 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2018-12-01 09:20 | 2018-12-01 16:50 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Srimongal | Sirmongal-Fenchuganj 132 kV line-1 | 2018-12-01 08:32 | 2018-12-01 16:16 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-1 | 2018-12-02 11:24 | 2018-12-25 11:18 | 551:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2018-12-02 08:57 | 2018-12-02 17:11 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Srimongal | Sirmongal-Fenchuganj 132 kV line-1 | 2018-12-02 08:42 | 2018-12-02 17:20 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-02 09:25 | 2018-12-02 12:57 | 3:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| B.baria-Shahjibazar 132 kV line-2 | 2018-12-02 13:05 | 2018-12-02 14:33 | 1:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chatak 132 kV line | 2018-12-03 06:22 | 2018-12-03 07:29 | 1:07 | S/O | Due to project work | 15 | 16.75 | Power interruption
Page: 4/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Shahjibazar | Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-03 09:04 | 2018-12-03 11:38 | 2:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-2 | 2018-12-03 08:23 | 2018-12-03 17:10 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2018-12-03 09:14 | 2018-12-03 16:39 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Srimongal 132 kV line-2 | 2018-12-03 09:35 | 2018-12-03 16:31 | 0:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2018-12-04 08:42 | 2018-12-04 14:00 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2018-12-04 08:58 | 2018-12-04 11:59 | 3:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Srimongal | Sirmongal-Fenchuganj 132 kV line-1 | 2018-12-04 09:28 | 2018-12-04 16:30 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj P/S-Fenchuganj 132 kV line-1 | 2018-12-04 12:11 | 2018-12-04 13:15 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj P/S-Fenchuganj 132 kV line-2 | 2018-12-04 13:07 | 2018-12-04 14:16 | 1:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-2 | 2018-12-05 09:05 | 2018-12-05 14:58 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2018-12-05 08:38 | 2018-12-05 16:11 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-12-05 09:54 | 2018-12-05 11:02 | 1:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line-2 | 2018-12-05 11:05 | 2018-12-05 16:26 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Srimongal | Sirmongal-Fenchuganj 132 kV line-1 | 2018-12-05 08:30 | 2018-12-05 16:10 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sirmongal-Fenchuganj 132 kV line-1 | 2018-12-06 08:53 | 2018-12-06 15:53 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2018-12-06 08:34 | 2018-12-06 13:21 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2018-12-06 13:38 | 2018-12-06 15:50 | 2:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bianibazar-Sylhet 132 kV line | 2018-12-07 08:36 | 2018-12-07 16:47 | 8:11 | S/O | Due to D/W work | 5 | 40.9167 | Power interruption
B.baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-08 08:56 | 2018-12-08 16:44 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2018-12-09 09:32 | 2018-12-09 16:43 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-09 08:59 | 2018-12-09 17:11 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2018-12-10 09:20 | 2018-12-10 17:01 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 | 2018-12-10 10:16 | 2018-12-10 13:31 | 3:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV line-2 | 2018-12-10 13:33 | 2018-12-10 16:22 | 2:49 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-11 08:44 | 2018-12-11 15:33 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2018-12-11 09:43 | 2018-12-11 11:55 | 2:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV line-2 | 2018-12-11 11:58 | 2018-12-11 14:15 | 2:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2018-12-11 11:49 | 2018-12-11 16:45 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Ashuganj 230 kV line-1 | 2018-12-12 08:53 | 2018-12-12 15:20 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-12 08:52 | 2018-12-12 16:39 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirmongal | Sirmongal-Fenchuganj 132 kV line-1 | 2018-12-12 09:52 | 2018-12-12 13:03 | 3:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sirmongal-Fenchuganj 132 kV line-2 | 2018-12-12 13:07 | 2018-12-12 17:16 | 4:09 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-13 09:20 | 2018-12-13 15:54 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-13 09:41 | 2018-12-13 11:45 | 2:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjibazar-Sirmongal 132 kV line-2 | 2018-12-13 11:49 | 2018-12-13 12:34 | 0:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-1 | 2018-12-13 10:02 | 2018-12-13 20:33 | 10:31 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.baria-Shahjibazar 132 kV line-1 | 2018-12-15 08:56 | 2018-12-15 17:02 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-17 08:12 | 2018-12-17 16:03 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-18 12:10 | 2018-12-18 16:40 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2018-12-19 09:58 | 2018-12-19 17:15 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Bibiyana 230 kV line-1 | 2018-12-20 09:21 | 2018-12-20 15:01 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-20 09:22 | 2018-12-20 16:34 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line | 2018-12-23 08:21 | 2018-12-23 20:13 | 11:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 5/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Shahjibazar | Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-23 10:01 | 2018-12-23 15:09 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj P/S | Fenchuganj P/S-Fenchuganj S/S 132 kV line-2 | 2018-12-23 10:08 | 2018-12-23 15:32 | 5:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sirmongal 132 kV line-1 | 2018-12-24 09:09 | 2018-12-24 15:05 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-2 | 2018-12-26 10:01 | 2018-12-26 19:29 | 9:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2018-12-26 09:03 | 2018-12-26 14:40 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-2 | 2018-12-27 09:33 | 2018-12-27 14:40 | 5:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2018-12-27 08:57 | 2018-12-27 15:13 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 875:16 |  | Unserved Energy: |  | 57.6667
Khulna Grid Circle :
Barisal | Barisal-Bhola 230 kV line-2 | 2018-12-01 10:50 | 2018-12-01 15:55 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal-Bhola 230 kV line-2 | 2018-12-02 09:38 | 2018-12-02 15:56 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna(S) 132 kV line-1 | 2018-12-03 11:01 | 2018-12-03 11:48 | 0:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-2 | 2018-12-04 08:51 | 2018-12-04 16:31 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal-Bhola 230 kV line-2 | 2018-12-05 08:06 | 2018-12-05 16:12 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-NWPGCL 132 kV line-1 | 2018-12-08 09:20 | 2018-12-08 16:59 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna©-NWPGCL 132 kV line-2 | 2018-12-09 09:13 | 2018-12-09 15:51 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna©-KPCL 132 kV line | 2018-12-09 08:56 | 2018-12-09 15:41 | 6:45 | S/O | Due to isolator mainteanace | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-12-09 13:17 | 2018-12-09 14:59 | 1:42 | S/O | Due to meter connection | 0 | 0 | No interruption
| Khulna(S)-Khulna(C) 132 kV line-1 | 2018-12-11 08:30 | 2018-12-11 15:55 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Khulna(C) 132 kV line-1 | 2018-12-12 09:13 | 2018-12-12 14:30 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Gallamari 132 kV line-1 | 2018-12-13 09:16 | 2018-12-13 15:34 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV line-2 | 2018-12-22 08:14 | 2018-12-22 13:44 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Barisal(N) 132 kV line-1 | 2018-12-22 08:20 | 2018-12-22 16:22 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barisal(Old) 132 kV line-2 | 2018-12-24 07:16 | 2018-12-24 16:40 | 9:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal(Old)-Barisal(N) 132 kV line-2 | 2018-12-25 07:39 | 2018-12-25 13:35 | 5:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Bhandaria 132 kV line | 2018-12-25 07:38 | 2018-12-25 13:35 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 104:29 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
HVDC Bharamara | Bheramara-Bahrampur 400 kV line-1 | 2018-12-01 09:28 | 2018-12-01 16:24 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2018-12-02 08:41 | 2018-12-02 15:45 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Baharampur 400 kV line-1 | 2018-12-07 07:01 | 2018-12-07 17:20 | 10:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Bharamara HVDC | Bharamara-G.K project 132 kV line | 2018-12-07 08:05 | 2018-12-07 13:19 | 5:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bharamara-Bahrampur 400 kV line-2 | 2018-12-08 06:53 | 2018-12-08 16:23 | 9:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Bharamara | Bharamara-Ishurdi 132 kV line-1 | 2018-12-09 08:22 | 2018-12-09 15:43 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-Ishurdi 132 kV line-2 | 2018-12-10 08:36 | 2018-12-10 15:04 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-Faridpur 132 kV line-1 | 2018-12-15 07:31 | 2018-12-15 12:49 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-Faridpur 132 kV line-2 | 2018-12-15 12:52 | 2018-12-15 15:31 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2018-12-19 09:45 | 2018-12-19 09:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | reconductoring on going
Bharamara | Bharamara-Ishurdi 132 kV line-1 | 2018-12-21 07:56 | 2018-12-21 20:32 | 12:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-Ishurdi 132 kV line-2 | 2018-12-21 07:56 | 2018-12-21 16:17 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 74:50 |  | Unserved Energy: |  | 0
Page: 6/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogra Grid Circle :
Natore | Natore-Ishurdi 132 kV line-1 | 2018-12-01 08:17 | 2018-12-01 17:10 | 8:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV line | 2018-12-01 08:25 | 2018-12-01 16:54 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari 132 kV line-1 | 2018-12-02 10:15 | 2018-12-02 17:13 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra S/S | Bogra S/S BograConfidence P/S 132 kV line | 2018-12-02 11:15 | 2018-12-02 17:29 | 6:14 | S/O | Due to project work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-2 | 2018-12-04 08:11 | 2018-12-04 16:25 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Natore-Ishurdi 132 kV line-2 | 2018-12-05 08:16 | 2018-12-05 14:37 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi 132 kV line-1 | 2018-12-06 08:08 | 2018-12-06 15:25 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-2 | 2018-12-06 09:21 | 2018-12-06 15:55 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat kV line | 2018-12-07 08:15 | 2018-12-07 15:46 | 7:31 | S/O | Due to A/M work | 10 | 81.8333 | Power interruption
Saidpur | Saidpur-Joldhaka 132 kV line-1 | 2018-12-07 10:50 | 2018-12-08 15:10 | 28:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| Saidpur-Joldhaka 132 kV line-2 | 2018-12-07 10:50 | 2018-12-08 15:12 | 28:22 | S/O |  | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2018-12-08 09:28 | 2018-12-08 16:15 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2018-12-08 08:10 | 2018-12-08 17:52 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Palashbari 132 kV line-1 | 2018-12-08 08:50 | 2018-12-08 16:05 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Panchagar 132 kV line | 2018-12-08 08:03 | 2018-12-08 15:58 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Palashbari 132 kV line-1 | 2018-12-09 08:16 | 2018-12-09 16:07 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2018-12-09 09:01 | 2018-12-09 16:57 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sirajganj-Ashuganj 230 kV line-2 | 2018-12-10 08:53 | 2018-12-10 16:24 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Palashbari 132 kV line-1 | 2018-12-10 09:45 | 2018-12-10 16:41 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Palashbari 132 kV line-2 | 2018-12-11 08:37 | 2018-12-11 15:48 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-2 | 2018-12-11 09:04 | 2018-12-11 16:53 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV line-1 | 2018-12-12 08:20 | 2018-12-12 16:12 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV line-1 | 2018-12-13 08:17 | 2018-12-13 16:50 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV line-2 | 2018-12-14 07:52 | 2018-12-14 14:49 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 230 kV line-2 | 2018-12-15 08:20 | 2018-12-15 14:31 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-12-17 07:50 | 2018-12-18 16:56 | 33:06 | S/O | Due to project work | 0 | 0 | No interruption
Bogura | Bogura-Palashbari 132 kV line-2 | 2018-12-17 09:01 | 2018-12-17 14:20 | 5:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-1 | 2018-12-18 08:53 | 2018-12-18 13:26 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-12-18 08:12 | 2018-12-18 09:13 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line | 2018-12-19 07:37 | 2018-12-20 14:40 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-1 | 2018-12-19 08:34 | 2018-12-19 16:25 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-1 | 2018-12-19 08:39 | 2018-12-19 16:13 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Sirajganj-Baghabari 230 kV line-1 | 2018-12-20 08:42 | 2018-12-20 16:34 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajlanka 132 kV line-1 | 2018-12-20 08:37 | 2018-12-20 13:39 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 7/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogra Grid Circle :
Bogura | Bogura-Natore 132 kV line-2 | 2018-12-20 08:26 | 2018-12-20 15:49 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-2 | 2018-12-21 08:28 | 2018-12-21 16:43 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line-2 | 2018-12-21 08:29 | 2018-12-21 10:55 | 2:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV line-2 | 2018-12-21 08:45 | 2018-12-21 10:40 | 1:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-1 | 2018-12-21 12:17 | 2018-12-21 12:43 | 0:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV line-1 | 2018-12-21 12:15 | 2018-12-21 12:45 | 0:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura -Palashbari 132 kV line-2 | 2018-12-21 12:51 | 2018-12-21 13:48 | 0:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sirajganj 132 kV line-2 | 2018-12-21 12:56 | 2018-12-21 13:50 | 0:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Bogura 230 kV line-2 | 2018-12-21 11:07 | 2018-12-21 12:08 | 1:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-2 | 2018-12-22 08:29 | 2018-12-22 09:26 | 0:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Natore-Bogura 132 kV line-1 | 2018-12-22 09:27 | 2018-12-22 09:52 | 0:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogra-Sirajganj 132 kV line-1 | 2018-12-22 10:20 | 2018-12-22 10:40 | 0:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 230 kV line-2 | 2018-12-22 08:38 | 2018-12-22 16:32 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(New) | Bogura(New)-Bogura (Old) 132 kV line-2 | 2018-12-22 14:21 | 2018-12-22 15:35 | 1:14 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi 132 kV line | 2018-12-24 07:03 | 2018-12-24 09:40 | 2:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-2 | 2018-12-24 08:08 | 2018-12-24 15:45 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2018-12-25 07:31 | 2018-12-25 09:45 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(Old) | Bogura(Old)-Bogura (New) 132 kV line-1 | 2018-12-25 09:35 | 2018-12-25 12:12 | 2:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura(Old)-Bogura (New) 132 kV line-2 | 2018-12-25 12:16 | 2018-12-25 14:35 | 2:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Palshbari 132 kV line-1 | 2018-12-25 12:23 | 2018-12-25 14:35 | 2:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Bogra 132 kV line-2 | 2018-12-26 09:27 | 2018-12-26 15:54 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 205:45 |  | Unserved Energy: |  | 81.8333
Others :
Ullon | Ullon-Dhandmondi 132 kV line-2 | 2018-12-11 08:37 | 2018-12-11 12:59 | 4:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Narinda | Narinda-Maniknagar 132 kV line-1 | 2018-12-22 09:53 | 2018-12-22 17:35 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 12:04 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 3286:17 | Hours |  |  | Executive Engineer
S/O=Schedule Outage,A/M= Annual Maintenance, D/W= Development Work | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:December' 2018
| Area | Previous Month (November 2018) |  |  |  | Current Month (December 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 2 | - | 106 | 108 | 7 | 1 | 133 | 141
2 | Dhaka (South) Grid Circle. | 9 | 1 | 48 | 58 | 15 | 11 | 68 | 94
3 | Chattogram Grid Circle. | 7 | 1 | 49 | 57 | 6 | 3 | 36 | 45
4 | Cumilla Grid Circle. | 3 | 6 | 43 | 52 | 24 | 7 | 71 | 102
5 | Khulna Grid Circle. | 2 |  | 65 | 67 | 4 | 1 | 27 | 32
6 | Bheramara HVDC Grid Circle | 2 | 2 | 28 | 32 | 8 | 1 | 26 | 35
7 | Bogura Grid Circle. | 1 | 2 | 68 | 71 | 7 | 2 | 80 | 89
8 | Others | - | - | 3 | 3 | 3 | - | 5 | 8
9 | Total | 26 | 12 | 410 | 448 | 74 | 26 | 446 | 546
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:December' 2018
| Area | Previous Month (November 2018) |  |  |  | Current Month (December 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 30.6 | - | 107.6 | 138.2 | 711.63 | - | 131.77 | 843.4
2 | Dhaka (South) Grid Circle. | 143.33 | - | - | 143.33 | 50.1 | 34.66 | - | 84.76
3 | Chattogram Grid Circle. | 102 | - | 282 | 384 | 16 | - | 40.08 | 56.08
4 | Cumilla Grid Circle. | 58.27 | 49.6 | - | 107.87 | 17.53 | 96.67 | 57.67 | 171.87
5 | Khulna Grid Circle. | 9.06 |  | 195.5 | 204.56 | 3.5 |  | 62.5 | 66
6 | Bheramara HVDC Grid Circle | - | 4.33 | - | 4.33 | - | - | - | -
7 | Bogura Grid Circle. | - | 21.67 | 238.33 | 260 | 15.85 | 41.67 | 120.83 | 178.35
8 | Others | - | - | - | 0 | 45 | - | 129.83 | 174.83
9 | Total | 343.26 | 75.6 | 823.43 | 1242.29 | 859.61 | 173 | 542.68 | 1575.29
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:December' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 | 2 | 3 |  | - | 3 | 829.9
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 | 2 | 1 | - | 61.43
3 | Chattogram | 2042 | 2 | 2 | 4 | 2 | - | 2 | 56.08
4 | Khulna | 2434 | 1 | 3 | 4 | 1 | 1 | 2 | 66
5 | Bheramara (HVDC) | 2423.3 | - | - | - | - | - | - | -
6 | Bogura | 3145.6 | 1 | 1 | 2 | 1 |  | 1 | 44.85
7 | Cumilla | 2981 | 3 | 1 | 4 | 3 |  | 1 | 108.33
| Total | 23365.5 | [6 empty] | 1166.59
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.84%
2 | Dhaka (South) | 99.88%
3 | Chattogram | 99.98%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.97% | [6 empty] | Executive Engineer
6 | Bogura | 99.99% | [6 empty] | Information Management Division
7 | Cumilla | 99.79% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:December' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | - | 1 | 1 | 1 | - |  | 13.5
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | 2 | - | - | 23.33
3 | Chattogram | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 2 | 1 | 3 | 1 | - | 2 | 133.5
7 | Cumilla | 1648.16 | 17 | 1 | 2 | 3 | - | 1 | 2 | 63.54
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 233.87
3 | Chattogram | 99.97%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.73% | [7 empty] | Executive Engineer
6 | Bogura | 99.99% | [7 empty] | Information Management Division
7 | Cumilla | 99.74% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:December' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
December | 19 | - | 2 | 01hr01 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:December' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 1 | 7:56 | 88 | 698.13 | Due to tripping of 132/33 kV Transformers T1 ,T2 & T3
Mymensingh | 2 | 0:09 | 90 | 13.5 | Due to tripping of Mymensingh-Jamalpur 132 kV line-1
|  | 1:37 | 86 | 64.6667 | Due to S/D of 132/33 kV Transformer T2
Tangail | 1 | 3:03 | 22 | 67.1 | Due to S/D of 132/33 kV Transformer T2
Siddhirganj | 1 | 0:28 | 72 | 33.6 | Due to tripping of 132/33 kV Transformers T1 & T2
Sonargaon | 1 | 0:33 | 30 | 16.5 | Due to tripping of 132/33 kV Transformers T1 & T2
Hasnabad | 1 | 0:17 | 40 | 11.3333 | Due to tripping of 132/33 kV Transformers T1 & T5
Shyampur(New) | 1 | 0:21 | 40 | 14 | Due to tripping of Shyampur-(new)-Shyampur (Old) 132 kV line
Hasnabad | 1 | 0:08 | 65 | 9.3333 | Due to tripping of Hasnabad-Lalbagh line
Baraulia | 1 | 0:16 | 40 | 10.6667 | Due to tripping of 132/33 kV Transformer T1
Halishahar | 1 | 0:16 | 20 | 5.3333 | Due to tripping of 132/33 kV Transformers T1 & T3
Bakulia | 1 | 3:53 | 5 | 19.4167 | Due to S/D of 132/33 kV Transformer T3
Cox'sbazar | 1 | 2:35 | 8 | 20.6667 | Due to S/D of 132/33 kV Transformer T3
Chowmuhani | 1 | 1:25 | 40 | 96.6667 | Due to red hot maintenance of 132/33 kV Transformer T1
Sirmongal | 1 | 0:01 | 8 | 0.13333 | Due to tripping of 132/33 kV Transformers T1 & T2
B.baria | 1 | 0:16 | 30 | 8 | Due to tripping of 132/33 kV Transformers T1 ,T2 & T3
Shahjibazar | 1 | 0:04 | 53 | 3.5333 | Due to tripping of 132/33 kV Transformers T1 & T2
Sylhet | 1 | 0:32 | 11 | 5.8667 | Due to S/D of Sylhet-Fenchuganj 132 kV line
Sunamganj | 1 | 1:07 | 15 | 16.75 | Due to S/D of Sunamganj-Chatak 132 kV line
Fenchuganj |  | 8:11 | 5 | 40.9167 | Due to S/D of Fencuganj-Bianibazar-Sylhet 132 kV line
Mongla | 1 | 0:07 | 30 | 3.5 | Due to tripping of 132/33 kV Transformers T1 & T2
Barisal | 2 | 0:40 | 20 | 13.33 | Due to S/D of 132/33 kV Transformer T2
|  | 2:15 | 10 | 22.5 | Due to S/D of 132/33 kV Transformer T1
Madaripur | 1 | 3:20 | 8 | 26.67 | Due to S/D of 132/33 kV Transformer T3
Thakurgaon | 1 | 0:09 | 39 | 5.85 | Due to tripping of 132/33 kV Transformers T1 & T2
Rangpur | 1 | 2:05 | 20 | 41.67 | Due to red hot maintenance of Rangpur-Saidpur 132 kV line-2
Rajshahi | 1 | 0:12 | 50 | 10 | Due to tripping of Rajshahi-Natore 132 kV line-1 & 2
Sirajganj | 1 | 1:18 | 30 | 39 | Due to S/D of 132 kV bus
Naogaon | 1 | 7:31 | 10 | 81.8333 | Due to S/D of Naogaon-Joypurhat 132 kV line
Maniknagar | 1 | 0:30 | 90 | 45 | Due to tripping of Maniknagar-Matuail 132 kV line
Shyampur | 1 | 4:43 | 20 | 94.3333 | Due to S/D of 132/33 kV Transformer T3
Bashundhara | 1 | 2:22 | 15 | 35.5 | Due to S/D of 132/33 kV Transformer T2
| Total unserved energy : |  |  | 1575.3 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:December'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 102 | 13 | 2018-12-01 | 12:00
2 | Munsiganj | 82 | 17 | 2018-12-01 | 19:30
3 | Sonargaon | 57 | 18 | 2018-12-01 | 19:00
4 | Shyampur | 155 | 27 | 2018-12-01 | 13:00
5 | Bhulta | 179 | 10 | 2018-12-01 | 19:30
6 | Madanganj | 53 | 2 | 2018-12-01 | 19:00
7 | Shitalakhya | 102 | 20 | 2018-12-01 | 12:00
8 | Rahim steel | 15 | 11 | 2018-12-01 | 9:00
9 | Matuail | 82 | 4 | 2018-12-01 | 10:00
10 | Ghorasal | 67 | 8 | 2018-12-01 | 18:00
11 | Narsingdi | 109 | 20 | 2018-12-01 | 18:30
12 | Haripur (SBU) | 99 | 3 | 2018-12-01 | 19:00
13 | Ullon | 60 | 13 | 2018-12-01 | 17:00
14 | Hasnabad | 161 | 2 | 2018-12-01 | 19:30
15 | Magbazar | 91 | 3 | 2018-12-01 | 12:00
16 | Maniknagar | 94 | 13 | 2018-12-01 | 11:00
17 | Bangabhaban | 32 | 19 | 2018-12-01 | 13:00
18 | Narinda | 70 | 5 | 2018-12-01 | 18:00
19 | Dhanmondi | 91 | 5 | 2018-12-01 | 13:00
20 | Lalbag | 79 | 20 | 2018-12-01 | 13:00
21 | Madartek | 40 | 1 | 2018-12-01 | 20:00
22 | Mirpur | 94 | 10 | 2018-12-01 | 13:00
23 | Kalyanpur | 87 | 11 | 2018-12-01 | 18:00
24 | Gulshan | 88 | 4 | 2018-12-01 | 18:00
25 | Uttara | 60 | 9 | 2018-12-01 | 18:00
26 | Uttara(new) | 7 | 13 | 2018-12-01 | 12:00
27 | Kamrangirchar | 70 | 4 | 2018-12-01 | 13:00
28 | Savar | 107 | 8 | 2018-12-01 | 18:30
29 | Bhasantec | 108 | 2 | 2018-12-01 | 18:00
30 | Agargaon | 40 | 8 | 2018-12-01 | 18:00
31 | Satmosjid | 67 | 1 | 2018-12-01 | 18:00
32 | Tongi | 109 | 23 | 2018-12-01 | 17:00
33 | Kabirpur | 166 | 5 | 2018-12-01 | 17:00
34 | Basundhara | 100 | 2 | 2018-12-01 | 18:30
35 | Manikganj | 69 | 17 | 2018-12-01 | 19:30
36 | Joydevpur | 197 | 18 | 2018-12-01 | 18:00
37 | New Tongi | 106 | 5 | 2018-12-01 | 12:00
38 | Kodda | 236 | 1 | 2018-12-01 | 18:30
39 | Dhamrai | 42 | 1 | 2018-12-01 | 18:30
40 | Tangail | 130 | 1 | 2018-12-01 | 18:30
41 | Mymensing | 186 | 8 | 2018-12-01 | 18:00
42 | Kishorganj | 72 | 6 | 2018-12-01 | 20:00
43 | Netrokona | 62 | 11 | 2018-12-01 | 18:00
44 | Jamalpur | 89 | 1 | 2018-12-01 | 18:00
45 | Sherpur | 68 | 22 | 2018-12-01 | 18:00
46 | Srimongal | 25 | 4 | 2018-12-01 | 18:30
47 | Shahjibazar | 84 | 5 | 2018-12-01 | 18:00
48 | Fenchuganj | 29 | 10 | 2018-12-01 | 18:00
49 | Kulawara | 30 | 22 | 2018-12-01 | 18:30
50 | Sylhet | 99 | 19 | 2018-12-01 | 17:00
51 | Chatak | 20 | 27 | 2018-12-01 | 18:30
52 | Sunamganj | 25 | 8 | 2018-12-01 | 19:00
53 | Bianibazar | 30 | 7 | 2018-12-01 | 19:00
54 | Cumilla (S) | 134 | 23 | 2018-12-01 | 18:00
55 | Cumilla(N) | 97 | 5 | 2018-12-01 | 19:00
56 | Chandpur | 84 | 10 | 2018-12-01 | 19:00
57 | Feni | 88 | 12 | 2018-12-01 | 20:00
58 | Chowmuhani | 134 | 23 | 2018-12-01 | 18:30
59 | Ashuganj | 43 | 8 | 2018-12-01 | 18:00
60 | Daudkandi | 86 | 3 | 2018-12-01 | 18:30
61 | B.Baria | 86 | 1 | 2018-12-01 | 19:00
62 | Ramganj | 28 | 28 | 2018-12-01 | 19:00
63 | Madanhat | 62 | 8 | 2018-12-01 | 18:00
64 | Hathazari | 71 | 9 | 2018-12-01 | 19:00
65 | Khulshi | 172 | 4 | 2018-12-01 | 13:00
66 | Halishahar | 108 | 10 | 2018-12-01 | 21:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:December'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Baraulia | 156 | 22 | 2018-12-01 | 18:30
68 | Sikalbaha | 36 | 12 | 2018-12-01 | 18:30
69 | Dohazari | 74 | 7 | 2018-12-01 | 18:00
70 | Cox'sbazar | 70 | 12 | 2018-12-01 | 19:30
71 | Chandraghona | 31 | 6 | 2018-12-01 | 13:00
72 | Kaptai | 4 | 1 | 2018-12-01 | 18:00
73 | A. Khaer Stl. | 22 | 25 | 2018-12-01 | 10:00
74 | Bakulia | 79 | 18 | 2018-12-01 | 18:00
75 | Julda | 21 | 10 | 2018-12-01 | 09:00
76 | TK chemical | 6 | 11 | 2018-12-01 | 11:00
77 | Modern Steel | 18 | 20 | 2018-12-01 | 8:00
78 | Shahmirpur | 23 | 6 | 2018-12-01 | 21:00
79 | Khagrachhari | 15 | 12 | 2018-12-01 | 18:00
80 | Matarbari | 22.5 | 18 | 2018-12-01 | 21:00
81 | Baroiar Hat | 19 | 4 | 2018-12-01 | 18:00
82 | Rangamati | 10 | 18 | 2018-12-01 | 18:00
83 | Abul Khair 230 | 196 | 1 | 2018-12-01 | 12:00
84 | BSRM | 109 | 11 | 2018-12-01 | 4:00
85 | Goalpara | 32 | 6 | 2018-12-01 | 18:30
86 | Central s/s | 69 | 11 | 2018-12-01 | 18:00
87 | Noapara | 79 | 17 | 2018-12-01 | 18:30
88 | Jashore | 108 | 8 | 2018-12-01 | 18:00
89 | Jhenida | 77 | 31 | 2018-12-01 | 18:30
90 | Bottail | 92 | 27 | 2018-12-01 | 18:30
91 | G.K Project | 37 | 20 | 2018-12-01 | 22:00
92 | Faridpur | 120 | 5 | 2018-12-01 | 18:00
93 | Madaripur | 90 | 2 | 2018-12-01 | 20:00
94 | Gopalganj | 61 | 26 | 2018-12-01 | 19:00
95 | Bagerhat | 66 | 1 | 2018-12-01 | 18:00
96 | Mongla | 38 | 10 | 2018-12-01 | 9:00
97 | Satkhira | 68 | 12 | 2018-12-01 | 18:00
98 | Gallamari | 37 | 27 | 2018-12-01 | 13:00
99 | Magura | 36 | 2 | 2018-12-01 | 18:00
100 | Chuadanga | 68 | 4 | 2018-12-01 | 19:00
101 | Barishal | 88 | 1 | 2018-12-01 | 19:30
102 | Patuakhali | 76 | 12 | 2018-12-01 | 21:00
103 | Bhandaria | 39 | 31 | 2018-12-01 | 19:30
104 | Ishurdi | 42 | 11 | 2018-12-01 | 18:30
105 | Ruppur Paromanobik | 1 | 1 | 2018-12-01 | 20:00
106 | Natore | 89 | 18 | 2018-12-01 | 18:00
107 | Bogura | 180 | 8 | 2018-12-01 | 18:30
108 | Noagaon | 86 | 8 | 2018-12-01 | 19:00
109 | Rajshahi | 101 | 8 | 2018-12-01 | 20:00
110 | C.Nawabganj | 55 | 12 | 2018-12-01 | 11:00
111 | Amnura | 31 | 15 | 2018-12-01 | 18:30
112 | Pabna | 80 | 13 | 2018-12-01 | 18:30
113 | Shahjadpur | 73 | 4 | 2018-12-01 | 18:00
114 | Serajganj | 71 | 11 | 2018-12-01 | 18:30
115 | Niyamatpur | 45 | 8 | 2018-12-01 | 19:00
116 | Joypurhat | 45 | 7 | 2018-12-01 | 18:00
117 | Rangpur | 101 | 4 | 2018-12-01 | 18:30
118 | Lalmonirhat | 74 | 9 | 2018-12-01 | 18:00
119 | Saidpur | 102 | 4 | 2018-12-01 | 18:30
120 | Purbasadipur | 85 | 27 | 2018-12-01 | 18:30
121 | Thakurgaon | 60 | 9 | 2018-12-01 | 18:00
122 | Palashbari | 84 | 11 | 2018-12-01 | 18:00
123 | Barapukuria | 47 | 19 | 2018-12-01 | 19:30
124 | Panchagar | 35 | 19 | 2018-12-01 | 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:December' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 3123 | 02.12.18 | 18:00
Chittagong | 1000 | 17.12.18 | 21:00
Khulna | 993 | 26.12.18 | 19:00
Rajshahi | 838 | 24.12.18 | 18:30
Comilla | 816 | 06.12.18 | 18:30
Mymensingh | 658 | 26.12.18 | 20:00
Sylhet | 327 | 15.12.18 | 18:30
Barisal | 207 | 01.12.18 | 19:30
Rangpur | 554 | 26.12.18 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 423 | 30 | 2018-12-01 | 23:00 | 381 | 3 | 2018-12-01 | 12:00
2 | Bheramara | 400 | 415 | 3 | 2018-12-01 | 4:00 | 389 | 1 | 2018-12-01 | 10:00
3 | Ashuganj(N) | 400 | 410 | 22 | 2018-12-01 | 1:00 | 386 | 1 | 2018-12-01 | 11:00
4 | Kaliakoir | 400 | 420 | 31 | 2018-12-01 | 02:00 | 364 | 4 | 2018-12-01 | 12:00
5 | Bhulta | 400 | 412 | 29 | 2018-12-01 | 19:00 | 384 | 1 | 2018-12-01 | 11:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 25 | 2018-12-01 | 01:00 | 230 | 1 | 2018-12-01 | 10:00
2 | Ishurdi | 230 | 242 | 31 | 2018-12-01 | 01:00 | 223 | 3 | 2018-12-01 | 07:00
3 | Ashuganj | 230 | 245 | 18 | 2018-12-01 | 6:00 | 232 | 4 | 2018-12-01 | 10:00
4 | Serajganj | 230 | 238 | 30 | 2018-12-01 | 6:00 | 214 | 20 | 2018-12-01 | 18:00
5 | Baghabari | 230 | 238 | 31 | 2018-12-01 | 2:00 | 220 | 20 | 2018-12-01 | 18:30
6 | Barapukuria | 230 | 238 | 18 | 2018-12-01 | 5:00 | 220 | 8 | 2018-12-01 | 18:00
7 | Bogra | 230 | 236 | 30 | 2018-12-01 | 5:00 | 203 | 10 | 2018-12-01 | 2:00
8 | Khulna South | 230 | 244 | 31 | 2018-12-01 | 3:00 | 217 | 22 | 2018-12-01 | 12:00
9 | Rampura | 230 | 232 | 28 | 2018-12-01 | 17:00 | 220 | 4 | 2018-12-01 | 11:00
10 | Haripur | 230 | 237 | 30 | 2018-12-01 | 5:00 | 220 | 4 | 2018-12-01 | 10:00
11 | Hasnabad | 230 | 236 | 27 | 2018-12-01 | 2:00 | 218 | 4 | 2018-12-01 | 12:00
12 | Aminbazar | 230 | 240 | 30 | 2018-12-01 | 04:00 | 218 | 4 | 2018-12-01 | 12:00
13 | Tongi | 230 | 236 | 31 | 2018-12-01 | 04:00 | 216 | 6 | 2018-12-01 | 12:00
14 | Comilla (N) | 230 | 245 | 30 | 2018-12-01 | 11:00 | 228 | 6 | 2018-12-01 | 11:00
15 | Hathazari | 230 | 231 | 30 | 2018-12-01 | 18:30 | 210 | 1 | 2018-12-01 | 10:00
16 | Megnaghat | 230 | 240 | 22 | 2018-12-01 | 5:00 | 223 | 4 | 2018-12-01 | 12:00
17 | Fenchuganj | 230 | 252 | 31 | 2018-12-01 | 5:00 | 231 | 10 | 2018-12-01 | 13:00
18 | Siddhirganj | 230 | 239 | 30 | 2018-12-01 | 04:00 | 220 | 4 | 2018-12-01 | 15:00
19 | Maniknagar | 230 | 237 | 30 | 2018-12-01 | 6:00 | 218 | 9 | 2018-12-01 | 15:00
20 | Old Airport | 230 | 240 | 31 | 2018-12-01 | 02:00 | 218 | 4 | 2018-12-01 | 11:00
21 | Barisal | 230 | 240 | 14 | 2018-12-01 | 02:00 | 218 | 21 | 2018-12-01 | 10:00
22 | AKSML | 230 | 229 | 18 | 2018-12-01 | 18:00 | 210 | 1 | 2018-12-01 | 14:00
23 | BSRM | 230 | 232 | 30 | 2018-12-01 | 18:30 | 212 | 1 | 2018-12-01 | 15:00
24 | Bibiyana | 230 | 250 | 31 | 2018-12-01 | 03:00 | 229 | 1 | 2018-12-01 | 12:00
25 | Bhulta | 230 | 238 | 30 | 2018-12-01 | 5:00 | 221 | 4 | 2018-12-01 | 12:00
26 | Ashuganj (S) | 230 | 245 | 25 | 2018-12-01 | 17:00 | 233 | 1 | 2018-12-01 | 12:00
27 | Kaliakoir | 230 | 242 | 27 | 2018-12-01 | 5:00 | 220 | 4 | 2018-12-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 139 | 18 | 2018-12-01 | 05:00 | 128 | 4 | 2018-12-01 | 11:00
2 | Munsiganj | 132 | 141 | 18 | 2018-12-01 | 6:00 | 128 | 4 | 2018-12-01 | 12:00
3 | Megnaghat | 132 | 140 | 29 | 2018-12-01 | 18:30 | 128 | 4 | 2018-12-01 | 12:00
4 | Shyampur | 132 | 138 | 30 | 2018-12-01 | 12:00 | 123 | 4 | 2018-12-01 | 11:00
5 | Bhulta | 132 | 141 | 30 | 2018-12-01 | 10:00 | 122 | 2 | 2018-12-01 | 12:00
6 | Madanganj | 132 | 141 | 21 | 2018-12-01 | 17:00 | 128 | 4 | 2018-12-01 | 12:00
7 | Shitalakhya | 132 | 144 | 18 | 2018-12-01 | 05:00 | 127 | 10 | 2018-12-01 | 12:00
8 | Rahim Steal | 132 | 140 | 28 | 2018-12-01 | 18:00 | 129 | 4 | 2018-12-01 | 12:00
9 | Matuail | 132 | 139 | 26 | 2018-12-01 | 6:00 | 127 | 4 | 2018-12-01 | 12:00
10 | Ghorasal | 132 | 145 | 29 | 2018-12-01 | 18:00 | 135 | 1 | 2018-12-01 | 7:00
11 | Narsinghdi | 132 | 143 | 31 | 2018-12-01 | 2:00 | 119 | 30 | 2018-12-01 | 1:00
12 | Haripur (SBU) | 132 | 139 | 18 | 2018-12-01 | 6:00 | 129 | 4 | 2018-12-01 | 12:00
13 | Ullon | 132 | 138 | 18 | 2018-12-01 | 3:00 | 128 | 24 | 2018-12-01 | 12:00
14 | Hasnabad | 132 | 142 | 18 | 2018-12-01 | 6:00 | 128 | 9 | 2018-12-01 | 12:00
15 | Magbazar | 132 | 138 | 20 | 2018-12-01 | 6:00 | 127 | 6 | 2018-12-01 | 12:00
16 | Maniknagar | 132 | 140 | 18 | 2018-12-01 | 4:00 | 125 | 6 | 2018-12-01 | 12:00
17 | Bangabhaban | 132 | 144 | 18 | 2018-12-01 | 6:00 | 126 | 3 | 2018-12-01 | 12:00
18 | Narinda | 132 | 138 | 15 | 2018-12-01 | 5:00 | 129 | 1 | 2018-12-01 | 12:00
19 | Dhanmondi | 132 | 139 | 31 | 2018-12-01 | 6:00 | 128 | 23 | 2018-12-01 | 12:00
20 | Lalbag | 132 | 144 | 18 | 2018-12-01 | 6:00 | 126 | 3 | 2018-12-01 | 12:00
21 | Madartek | 132 | 138 | 15 | 2018-12-01 | 05:00 | 129 | 1 | 2018-12-01 | 12:00
22 | Mirpur | 132 | 141 | 10 | 2018-12-01 | 3:00 | 128 | 15 | 2018-12-01 | 13:00
23 | Kalyanpur | 132 | 143 | 13 | 2018-12-01 | 1:00 | 130 | 8 | 2018-12-01 | 12:00
24 | Gulshan | 132 | 137 | 18 | 2018-12-01 | 6:00 | 125 | 11 | 2018-12-01 | 12:00
25 | Uttara | 132 | 141 | 27 | 2018-12-01 | 5:00 | 130 | 4 | 2018-12-01 | 12:00
26 | Uttara(New) | 132 | 138 | 13 | 2018-12-01 | 1:00 | 128 | 4 | 2018-12-01 | 12:00
27 | Kamrangirchar | 132 | 143 | 28 | 2018-12-01 | 6:00 | 125 | 4 | 2018-12-01 | 12:00
28 | Savar | 132 | 138 | 27 | 2018-12-01 | 3:00 | 127 | 2 | 2018-12-01 | 12:00
29 | Bhasantec | 132 | 141 | 11 | 2018-12-01 | 4:00 | 130 | 2 | 2018-12-01 | 11:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 141 | 10 | 2018-12-01 | 03:00 | 130 | 16 | 2018-12-01 | 12:00
31 | Satmosjid | 132 | 144 | 18 | 2018-12-01 | 06:00 | 130 | 2 | 2018-12-01 | 12:00
32 | Tongi | 132 | 141 | 19 | 2018-12-01 | 3:00 | 131 | 5 | 2018-12-01 | 16:00
33 | Kabirpur | 132 | 140 | 29 | 2018-12-01 | 2:00 | 127 | 12 | 2018-12-01 | 12:00
34 | Basundhara | 132 | 137 | 28 | 2018-12-01 | 14:00 | 123 | 6 | 2018-12-01 | 14:00
35 | Manikganj | 132 | 144 | 11 | 2018-12-01 | 5:00 | 127 | 12 | 2018-12-01 | 12:00
36 | Joydevpur | 132 | 145 | 28 | 2018-12-01 | 18:30 | 130 | 5 | 2018-12-01 | 16:00
37 | New Tongi | 132 | 142 | 31 | 2018-12-01 | 03:00 | 131 | 4 | 2018-12-01 | 15:00
38 | Kodda | 132 | 144 | 30 | 2018-12-01 | 17:00 | 130 | 2 | 2018-12-01 | 16:00
39 | Dhamrai | 132 | 140 | 15 | 2018-12-01 | 04:00 | 125 | 28 | 2018-12-01 | 13:00
40 | Tangail | 132 | 144 | 30 | 2018-12-01 | 5:00 | 130 | 9 | 2018-12-01 | 12:00
41 | Mymensing | 132 | 140 | 15 | 2018-12-01 | 8:00 | 128 | 10 | 2018-12-01 | 13:00
42 | Kishorganj | 132 | 140 | 1 | 2018-12-01 | 21:00 | 130 | 5 | 2018-12-01 | 17:00
43 | Netrokona | 132 | 140 | 15 | 2018-12-01 | 07:00 | 129 | 10 | 2018-12-01 | 10:00
44 | Jamalpur | 132 | 141 | 8 | 2018-12-01 | 17:00 | 121 | 22 | 2018-12-01 | 14:00
45 | Sherpur | 132 | 140 | 8 | 2018-12-01 | 17:00 | 121 | 17 | 2018-12-01 | 21:00
46 | Srimongal | 132 | 143 | 30 | 2018-12-01 | 10:00 | 135 | 3 | 2018-12-01 | 8:00
47 | Shahjibazar | 132 | 142 | 30 | 2018-12-01 | 18:30 | 135 | 1 | 2018-12-01 | 12:00
48 | Fenchuganj | 132 | 142 | 31 | 2018-12-01 | 05:00 | 130 | 3 | 2018-12-01 | 12:00
49 | Khulawara | 132 | 141 | 30 | 2018-12-01 | 24:00 | 131 | 3 | 2018-12-01 | 14:00
50 | Sylhet | 132 | 141 | 31 | 2018-12-01 | 4:00 | 130 | 3 | 2018-12-01 | 14:00
51 | Chattak | 132 | 140 | 31 | 2018-12-01 | 01:00 | 129 | 3 | 2018-12-01 | 15:00
52 | Sunamganj | 132 | 139 | 30 | 2018-12-01 | 01:00 | 129 | 3 | 2018-12-01 | 14:00
53 | Biani Bazar | 132 | 139 | 29 | 2018-12-01 | 24:00 | 126 | 3 | 2018-12-01 | 12:00
54 | Comilla(South) | 132 | 133 | 1 | 2018-12-01 | 23:00 | 124 | 14 | 2018-12-01 | 8:00
55 | Comilla (North) | 132 | 145 | 30 | 2018-12-01 | 8:00 | 136 | 1 | 2018-12-01 | 8:00
56 | Chandpur | 132 | 143 | 1 | 2018-12-01 | 21:00 | 131 | 6 | 2018-12-01 | 10:00
57 | Feni | 132 | 138 | 30 | 2018-12-01 | 23:00 | 127 | 6 | 2018-12-01 | 10:00
58 | Chowmuhani | 132 | 137 | 30 | 2018-12-01 | 08:00 | 125 | 6 | 2018-12-01 | 10:00
59 | Ashuganj | 132 | 145 | 31 | 2018-12-01 | 7:00 | 130 | 22 | 2018-12-01 | 13:00
60 | Daudkandi | 132 | 141 | 30 | 2018-12-01 | 7:00 | 130 | 6 | 2018-12-01 | 12:00
61 | Brahminbaria | 132 | 142 | 14 | 2018-12-01 | 23:00 | 134 | 1 | 2018-12-01 | 11:00
62 | Ramganj | 132 | 138 | 13 | 2018-12-01 | 12:00 | 121 | 5 | 2018-12-01 | 17:00
63 | Madanhat | 132 | 140 | 18 | 2018-12-01 | 18:00 | 126 | 17 | 2018-12-01 | 8:00
64 | Hathazari | 132 | 138 | 18 | 2018-12-01 | 18:00 | 126 | 1 | 2018-12-01 | 12:00
65 | Khulshi | 132 | 135 | 14 | 2018-12-01 | 18:00 | 122 | 1 | 2018-12-01 | 15:00
66 | Halishahar | 132 | 140 | 18 | 2018-12-01 | 18:00 | 125 | 1 | 2018-12-01 | 12:00
67 | Baraulia | 132 | 137 | 15 | 2018-12-01 | 22:00 | 124 | 1 | 2018-12-01 | 12:00
68 | Sikalbaha | 132 | 137 | 12 | 2018-12-01 | 20:00 | 124 | 18 | 2018-12-01 | 5:00
69 | Dohazari | 132 | 138 | 18 | 2018-12-01 | 18:00 | 123 | 18 | 2018-12-01 | 24:00
70 | Cox'sbazar | 132 | 137 | 18 | 2018-12-01 | 18:30 | 117 | 1 | 2018-12-01 | 4:00
71 | Chandraghona | 132 | 138 | 18 | 2018-12-01 | 18:00 | 126 | 6 | 2018-12-01 | 12:00
72 | Kaptai | 132 | 137 | 12 | 2018-12-01 | 19:30 | 127 | 18 | 2018-12-01 | 9:00
73 | A. Khaer Stl. | 132 | 136 | 18 | 2018-12-01 | 18:00 | 124 | 27 | 2018-12-01 | 8:00
74 | Bakulia | 132 | 136 | 18 | 2018-12-01 | 18:00 | 123 | 1 | 2018-12-01 | 11:00
75 | Julda | 132 | 138 | 13 | 2018-12-01 | 20:00 | 123 | 18 | 2018-12-01 | 07:00
76 | TK Chemical | 132 | 137 | 5 | 2018-12-01 | 14:00 | 125 | 1 | 2018-12-01 | 10:00
77 | Modern Steel | 132 | 137 | 12 | 2018-12-01 | 20:00 | 124 | 1 | 2018-12-01 | 10:00
78 | Shahmirpur | 132 | 139 | 18 | 2018-12-01 | 18:00 | 123 | 17 | 2018-12-01 | 7:00
79 | Khagrachhari | 132 | 138 | 18 | 2018-12-01 | 18:00 | 125 | 1 | 2018-12-01 | 15:00
80 | Matarbari | 132 | 137 | 18 | 2018-12-01 | 18:30 | 118 | 18 | 2018-12-01 | 6:00
81 | Baroiar Hat | 132 | 138 | 31 | 2018-12-01 | 02:00 | 124 | 28 | 2018-12-01 | 17:00
82 | Rangamati | 133 | 138 | 18 | 2018-12-01 | 18:00 | 125 | 1 | 2018-12-01 | 13:00
83 | Goalpara | 132 | 140 | 25 | 2018-12-01 | 17:00 | 122 | 22 | 2018-12-01 | 12:00
84 | Khulna Central | 132 | 140 | 21 | 2018-12-01 | 17:00 | 122 | 22 | 2018-12-01 | 12:00
85 | Noapara | 132 | 138 | 14 | 2018-12-01 | 17:00 | 120 | 22 | 2018-12-01 | 12:00
86 | Jessore | 132 | 135 | 31 | 2018-12-01 | 1:00 | 119 | 6 | 2018-12-01 | 07:00
87 | Jhenida | 132 | 139 | 31 | 2018-12-01 | 5:00 | 115 | 22 | 2018-12-01 | 12:00
88 | Bottail | 132 | 141 | 9 | 2018-12-01 | 4:00 | 127 | 3 | 2018-12-01 | 18:30
89 | G.K.Project | 132 | 144 | 28 | 2018-12-01 | 03:00 | 131 | 28 | 2018-12-01 | 12:00
90 | Faridpur | 132 | 139 | 18 | 2018-12-01 | 4:00 | 125 | 18 | 2018-12-01 | 19:30
91 | Madaripur | 132 | 139 | 30 | 2018-12-01 | 6:00 | 125 | 18 | 2018-12-01 | 20:00
92 | Gopalganj | 132 | 142 | 24 | 2018-12-01 | 17:00 | 120 | 18 | 2018-12-01 | 19:30
93 | Bagerhat | 132 | 140 | 21 | 2018-12-01 | 17:00 | 121 | 6 | 2018-12-01 | 7:00
94 | Mongla | 132 | 136 | 5 | 2018-12-01 | 17:00 | 120 | 22 | 2018-12-01 | 12:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: December '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
95 | Satkhira | 132 | 140 | 21 | 2018-12-01 | 17:00 | 123 | 2 | 2018-12-01 | 20:00
96 | Gallamari | 132 | 140 | 21 | 2018-12-01 | 17:00 | 124 | 20 | 2018-12-01 | 11:00
97 | Magura | 132 | 137 | 10 | 2018-12-01 | 3:00 | 118 | 25 | 2018-12-01 | 18:00
98 | Chuadanga | 132 | 136 | 5 | 2018-12-01 | 1:00 | 115 | 8 | 2018-12-01 | 18:00
99 | Barisal | 132 | 140 | 2 | 2018-12-01 | 5:00 | 129 | 21 | 2018-12-01 | 12:00
100 | Patuakhali | 132 | 140 | 24 | 2018-12-01 | 17:00 | 124 | 21 | 2018-12-01 | 12:00
101 | Bhandaria | 132 | 139 | 25 | 2018-12-01 | 17:00 | 120 | 22 | 2018-12-01 | 12:00
102 | Ishurdi | 132 | 144 | 18 | 2018-12-01 | 3:00 | 130 | 29 | 2018-12-01 | 8:00
103 | Ruppur paromanobik | 132 | 145 | 18 | 2018-12-01 | 3:00 | 130 | 15 | 2018-12-01 | 9:00
104 | Natore | 132 | 142 | 18 | 2018-12-01 | 3:00 | 129 | 20 | 2018-12-01 | 12:00
105 | Bogra | 132 | 141 | 18 | 2018-12-01 | 4:00 | 125 | 25 | 2018-12-01 | 12:00
106 | Noagaon | 132 | 140 | 31 | 2018-12-01 | 4:00 | 120 | 15 | 2018-12-01 | 14:00
107 | Rajshahi | 132 | 139 | 18 | 2018-12-01 | 9:00 | 124 | 29 | 2018-12-01 | 7:00
108 | C.Nawabganj | 132 | 135 | 3 | 2018-12-01 | 15:00 | 118 | 19 | 2018-12-01 | 13:00
109 | Amnura | 132 | 138 | 1 | 2018-12-01 | 18:00 | 116 | 21 | 2018-12-01 | 12:00
110 | Pabna | 132 | 140 | 18 | 2018-12-01 | 6:00 | 127 | 20 | 2018-12-01 | 18:00
111 | Shahjadpur | 132 | 146 | 8 | 2018-12-01 | 17:00 | 133 | 26 | 2018-12-01 | 1:00
112 | Serajganj | 132 | 140 | 18 | 2018-12-01 | 3:00 | 128 | 25 | 2018-12-01 | 18:30
113 | Niyamatpur | 132 | 139 | 18 | 2018-12-01 | 5:00 | 121 | 2 | 2018-12-01 | 19:00
114 | Joypurhat | 132 | 141 | 30 | 2018-12-01 | 5:00 | 124 | 8 | 2018-12-01 | 18:30
115 | Rangpur | 132 | 136 | 31 | 2018-12-01 | 5:00 | 113 | 8 | 2018-12-01 | 18:00
116 | Lalmonirhat | 132 | 135 | 18 | 2018-12-01 | 5:00 | 105 | 4 | 2018-12-01 | 18:00
117 | Saidpur | 132 | 135 | 18 | 2018-12-01 | 5:00 | 114 | 27 | 2018-12-01 | 18:00
118 | Purbasadipur | 132 | 138 | 31 | 2018-12-01 | 2:00 | 108 | 8 | 2018-12-01 | 18:30
119 | Thakurgaon | 132 | 134 | 30 | 2018-12-01 | 5:00 | 99 | 8 | 2018-12-01 | 18:30
120 | Palashbari | 132 | 136 | 18 | 2018-12-01 | 5:00 | 115 | 1 | 2018-12-01 | 18:00
121 | Barapukuria | 132 | 138 | 18 | 2018-12-01 | 5:00 | 120 | 8 | 2018-12-01 | 18:00
122 | Panchagar | 132 | 134 | 31 | 2018-12-01 | 3:00 | 95 | 8 | 2018-12-01 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:December' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 136 | 425
IP-299421 | Hasnabad | TR2 | 225 | 125 | 425 | 03.12.18 | 12:00
|  | TR3 | 225 | 125 | 410
|  | TR1 | 225 | 110 | 310
IP-299866 | Tongi | TR2 | 225 | 110 | 310 | 01.12.18 | 18:00
|  | TR3 | 225 | 110 | 310
|  | TR1 | 225 | 121 | 375 | 05.12.18 | 12:00
IP-299427 | Haripur | TR2 | 225 |  |  |  |  | S/D
|  | TR3 | 225 | 121 | 375
|  | TR1 | 225 | 120 | 330
IP-299728 | Rampura | TR2 | 225 | 120 | 330 | 03.12.18 | 12:00
|  | TR3 | 225 | 120 | 330
|  | TR1 | 225 | 134 | 360
IP-299264 | Aminbazar | TR2 | 225 | 134 | 360 | 23.12.18 | 12:00
|  | TR3 | 225 |  |  |  |  | S/D
| Maniknagar | TR1 | 300 | 83 | 250 | 13.12.18 | 13:00
|  | TR2 | 300 | 83 | 250
IP-399266 | Cumilla (N) | TR1 | 225 | 130 | 350 | 28.12.18 | 21:00
|  | TR2 | 225 | 132 | 341
| Fenchuganj | TR1 | 300 | 232 | 582 | 12.12.18 | 9:00
|  | TR1 | 150 | 140 | 395
IP-399428 | Hathazari | TR3 | 150 | 140 | 395 | 06.12.18 | 9:00
|  | TR4 | 150 | 140 | 395
|  | TR1 | 225 | 135 | 400
| Ishurdi | TR2 | 225 | 135 | 400 | 03.12.18 | 3:00
IP-499474 |  | TR3 | 225 | 135 | 400
| Khulna(S) | TR1 | 225 | 183 | 482
IP-58001/58002 |  | TR2 | 225 | 183 | 482 | 25.12.18 | 19:30
| Bogra | TR1 | 225 | 123 | 390 | 03.12.18 | 19:30
|  | TR2 | 225 | 123 | 390
IP-43002/499264 |  | TR3 | 225 | 164 | 453
IP-499224 | Baghabari | TR1 | 225 | 150 | 450 | 25.12.18 | 20:00
| Barapukuria | TR1 | 225 | 108 | 500 | 20.12.18 | 18:30 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 126 | 620 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 156 | 798
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:December' 2018
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 277.1 | 515 | 15.12.18 | 14:45 | Low power factor
|  | TR1(400/132 kV) | 325 | 195.4 | 306 | 18.12.18 | 11:00
|  | TR2(400/132 kV) | 325 | 195.4 | 306
| Bibiyana | ICT1(400/230 kV) | 520 | 176 | 293 | 05.12.18 | 12:00
|  | ICT2(400/230kV) | 520 | 176 | 298
| Bhulta | ATR1(400/230 kV) | 520 | 264 | 428 | 04.12.18 | 15:00
|  | ATR2(400/230kV) | 520 | 264 | 428
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:December' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:December' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-12-18 | 8347 | 8347 | - | - | - | - | - | - | - | - | - | - | - | - | 01-12-18 | 5956.2 | 5956.2 | - | - | - | - | - | - | - | - | - | - | - | -
02-12-18 | 8369 | 8369 | - | - | - | - | - | - | - | - | - | - | - | - | 02-12-18 | 6342 | 6342 | - | - | - | - | - | - | - | - | - | - | - | -
03-12-18 | 8418 | 8418 | - | - | - | - | - | - | - | - | - | - | - | - | 03-12-18 | 6448.4 | 6448.4 | - | - | - | - | - | - | - | - | - | - | - | -
04-12-18 | 8534 | 8534 | - | - | - | - | - | - | - | - | - | - | - | - | 04-12-18 | 6410.6 | 6410.6 | - | - | - | - | - | - | - | - | - | - | - | -
05-12-18 | 8458 | 8458 | - | - | - | - | - | - | - | - | - | - | - | - | 05-12-18 | 6622.4 | 6622.4 | - | - | - | - | - | - | - | - | - | - | - | -
06-12-18 | 8452 | 8452 | - | - | - | - | - | - | - | - | - | - | - | - | 06-12-18 | 6510.3 | 6510.3 | - | - | - | - | - | - | - | - | - | - | - | -
07-12-18 | 7505 | 7505 | - | - | - | - | - | - | - | - | - | - | - | - | 07-12-18 | 5266.2 | 5266.2 | - | - | - | - | - | - | - | - | - | - | - | -
08-12-18 | 8350 | 8350 | - | - | - | - | - | - | - | - | - | - | - | - | 08-12-18 | 5798.9 | 5798.9 | - | - | - | - | - | - | - | - | - | - | - | -
09-12-18 | 8421 | 8421 | - | - | - | - | - | - | - | - | - | - | - | - | 09-12-18 | 6498.3 | 6498.3 | - | - | - | - | - | - | - | - | - | - | - | -
10-12-18 | 8380 | 8380 | - | - | - | - | - | - | - | - | - | - | - | - | 10-12-18 | 6337.3 | 6337.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-12-18 | 8482 | 8482 | - | - | - | - | - | - | - | - | - | - | - | - | 11-12-18 | 6479.2 | 6479.2 | - | - | - | - | - | - | - | - | - | - | - | -
12-12-18 | 8349 | 8349 | - | - | - | - | - | - | - | - | - | - | - | - | 12-12-18 | 6519 | 6519 | - | - | - | - | - | - | - | - | - | - | - | -
13-12-18 | 8326 | 8326 | - | - | - | - | - | - | - | - | - | - | - | - | 13-12-18 | 6723.8 | 6723.6 | - | - | - | - | - | - | - | - | - | - | - | -
14-12-18 | 7596 | 7596 | - | - | - | - | - | - | - | - | - | - | - | - | 14-12-18 | 5599.7 | 5599.7 | - | - | - | - | - | - | - | - | - | - | - | -
15-12-18 | 8095 | 8095 | - | - | - | - | - | - | - | - | - | - | - | - | 15-12-18 | 6018.4 | 6018.4 | - | - | - | - | - | - | - | - | - | - | - | -
16-12-18 | 7194 | 7194 | - | - | - | - | - | - | - | - | - | - | - | - | 16-12-18 | 5456.3 | 5456.3 | - | - | - | - | - | - | - | - | - | - | - | -
17-12-18 | 7990 | 7990 | - | - | - | - | - | - | - | - | - | - | - | - | 17-12-18 | 6483.8 | 6483.8 | - | - | - | - | - | - | - | - | - | - | - | -
18-12-18 | 7865 | 7865 | - | - | - | - | - | - | - | - | - | - | - | - | 18-12-18 | 6300.7 | 6300.7 | - | - | - | - | - | - | - | - | - | - | - | -
19-12-18 | 8150 | 8150 | - | - | - | - | - | - | - | - | - | - | - | - | 19-12-18 | 6564.8 | 6564.8 | - | - | - | - | - | - | - | - | - | - | - | -
20-12-18 | 8096 | 8096 | - | - | - | - | - | - | - | - | - | - | - | - | 20-12-18 | 6405.2 | 6405.2 | - | - | - | - | - | - | - | - | - | - | - | -
21-12-18 | 7375 | 7375 | - | - | - | - | - | - | - | - | - | - | - | - | 21-12-18 | 5683.1 | 5683.1 | - | - | - | - | - | - | - | - | - | - | - | -
22-12-18 | 8296 | 8296 | - | - | - | - | - | - | - | - | - | - | - | - | 22-12-18 | 6109.1 | 6109.1 | - | - | - | - | - | - | - | - | - | - | - | -
23-12-18 | 8280 | 8280 | - | - | - | - | - | - | - | - | - | - | - | - | 23-12-18 | 6421.4 | 6421.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-12-19 | 8336 | 8336 | - | - | - | - | - | - | - | - | - | - | - | - | 24-12-19 | 6468.3 | 6468.3 | - | - | - | - | - | - | - | - | - | - | - | -
25-12-20 | 8188 | 8188 | - | - | - | - | - | - | - | - | - | - | - | - | 25-12-20 | 6407.1 | 6407.1 | - | - | - | - | - | - | - | - | - | - | - | -
26-12-18 | 8476 | 8476 | - | - | - | - | - | - | - | - | - | - | - | - | 26-12-18 | 6533 | 6533 | - | - | - | - | - | - | - | - | - | - | - | -
27-12-18 | 8178 | 8178 | - | - | - | - | - | - | - | - | - | - | - | - | 27-12-18 | 6676 | 6676 | - | - | - | - | - | - | - | - | - | - | - | -
28-12-18 | 7378 | 7378 | - | - | - | - | - | - | - | - | - | - | - | - | 28-12-18 | 5825.9 | 5825.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-12-18 | 7257 | 7257 | - | - | - | - | - | - | - | - | - | - | - | - | 29-12-18 | 5661.6 | 5661.6 | - | - | - | - | - | - | - | - | - | - | - | -
30-12-18 | 6317 | 6317 | - | - | - | - | - | - | - | - | - | - | - | - | 30-12-18 | 3894.8 | 3894.8 | - | - | - | - | - | - | - | - | - | - | - | -
31-12-19 | 7542 | 7542 | [12 empty] | 31-12-19 | 5748.4 | 5748.4

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:December' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 8534 | 04/12/18 | 19:00
2 | Maximum day peak Genaration | MW | 6723.8 | 13/12/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 8534 | 04/12/18 | 19:00
4 | Minimum Generation | MW | 3366 | 31/12/18 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8032.2581
6 | Average of the daily day peak Genaration | MW | 6134.5226
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 4537.8974
12 | Total Generation by IPP | MKWH | 983.7076 | % of total Gen. | 21.68%
13 | Total Generation by BPDB | MKWH | 2648.2572 | " | 58.36%
14 | A) Total Generation by RPCL | MKWH | 100.6564 | '' | 2.218%
| B) Total Generation by REB | MKWH | 129.6731 | " | 2.858%
| C) Total Generation by RENTAL | MKWH | 263.2062 | " | 5.8%
| D) Total Imported from India (HVDC) | MKWH | 349.9404 | " | 7.712%
| E) Total Imported from Tripura, India (A.C) | MKWH | 62.4566 | " | 1.376%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3591.186 | % of total Gen. | 79.14%
| B) Oil | MKWH | 372.626 | '' | 8.211%
| C) Hydro | MKWH | 31.5205 | '' | 0.6946%
| D) Solar | MKWH | 4.7165 | '' | 0.1039%
| E) Coal | MKWH | 125.4514 | '' | 2.765%
| F) HVDC (Import from India) | MKWH | 349.9404 | '' | 7.712%
| G) A.C (Import from Tripura, India) | MKWH | 62.4566 | '' | 1.376%
16 | Maximun of the daily total Generation . | MKWH | 156.0756 | 13/12/18
17 | Monthly Load factor | % | 71.4709
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 5770.5987
| A) Gas | M.Taka | 2610.2201
| B) Liquid fuel | M.Taka | 2652.5032
| C) Coal | M.Taka | 507.8754
| D) HVDC (Import from India) | M.Taka | 1784.6958
| E) Tripura(Import from India) | M.Taka | 427.2034
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 262.9903 | 12/12/18
| A) Gas | M.Taka | 94.9584 | 02/12/18
| B) Liquid fuel | M.Taka | 167.2335 | 12/12/18
| C) Coal | M.Taka | 24.7538 | 30/12/18
| D) HVDC (Import from India) | M.Taka | 67.5092 | 04-12-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.0386
| B) Excluding Hydro & Solar | Taka/KWHR | 2.055
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 103.1 | 31/12/18 | 06:00
b) | Actual | FT (MSL) | 98.53 | 31/12/18 | 06:00
22 | Peak Genaration of December 2017 | MW | 8028 | 11/12/17 | 19:00
23 | Peak Demand of December 2017 | MW | 8028 | 11/12/17 | 19:00
24 | Maximum peak Generation recorded upto 31/12/18 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 31/12/18 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 31/12/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.