## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:November' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | November 2018 |  | October 2018 |  | November 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9900 | 04/11/18 | 11485 | 02/10/18 | 9015 | 05/11/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:30
2 | Minimum Generation (MW) | 4789 | 24/11/18 | 5397.7 | 13/10/18 | 4424 | 25/11/17 | - | -
|  |  | 5:00 |  | 7:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9900 | 04/11/18 | 11485 | 02/10/18 | 9015 | 05/11/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 8017 | 05/11/18 | 9591.9 | 04/10/18 | 7101.1 | 06/11/17 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9900 | 04/11/18 | 11485 | 02/10/18 | 9015 | 05/11/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 8671.8333 |  | 9999.13 |  | 8127.47 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 6828.3637 |  | 8021.34 |  | 6293.96 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 704 | 21/11/18 | 772 | 05/10/18 | 500 | 07/11/17 | 788 | 11/09/18
|  |  | 22:00 |  | 14:00 |  | 9:00 |  | 22:00
9 | Maximum Power Import from Tripura, India (MW) | 150 | 04/11/18 | 178 | 06/10/18 | 154 | 19/11/17 | 188 | 29/05/18
|  |  | 18:30 |  | 18:30 |  | 18:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2521.836 |  | 3330.01 |  | 2300.17
21 | Station Use of BPDB (MKWH) | 62.9258 |  | 116.21 |  | 93.55
22 | Net Generation of BPDB (MKWH) | 2458.9102 |  | 3213.81 |  | 2206.62
23 | Net Generation of IPP & RPCL (MKWH) | 1344.3067 |  | 145.65 |  | 1084.1
24 | Net Generation of REB (MKWH) | 136.7663 |  | 142.92 |  | 107.83
24 | Net Generation of Rental Power Plant (MKWH) | 409.0027 |  | 556.87 |  | 741.28
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4348.9861 |  | 5365.25 |  | 4139.83 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 3478.7833 |  | 4224.64 |  | 3297.05 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 79.6684 |  | 233.56 |  | 111.48 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 691.8949 |  | 834.1 |  | 645.44 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 45.6942 |  | 69.33 |  | 114.66 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 4.0482 |  | 3.14 |  | 0.32 |  | 4.05 | 2018-11-16
31 | Energy Generation by Coal (MKWH) | 111.8229 |  | 116.7 |  | 64.42 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 478.6864 |  | 602.91 |  | 363.11 |  | 602.91 | Oct-18
33 | Monthly Load Factor (%) | 68.6111 |  | 71.21 |  | 70.82 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:November' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9900 | 04/11/18 | 19:00
Generation Period
| Dhaka | MW | 3776
| Chattogram | MW | 985
| Cumilla | MW | 823
| Mymensingh | MW | 541
| Sylhet | MW | 328
a) | Total supply in East zone | MW | 6453
| Khulna | MW | 1108
| Barisal | MW | 216
| Rajshahi | MW | 954
| Rangpur | MW | 543
b) | Total supply in West zone | MW | 2821
c) | Total supply in both zone ( a+b) | MW | 9274
Ref: | 27.21.2604.603.16.085.18.113 | Date: 20/12/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:November' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 960 | 18/11/18 | 20:00
| b) Ishurdi end | MW | 240 | 26/11/18 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 460 | 26/11/18 | 16:00
| b) Ishurdi end | MW | 390 | 18/11/18 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.9435 | 14/11/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 3.68 | 14/11/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 55.2729
| b) Ishurdi end | MKWH | 13.8505
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 13.4347
| b) Ishurdi end | MKWH | 53.663
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 600 | 11/11/18 | 18:00
| b)Serajganj end | MW | 120 | 27/11/18 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 110 | 27/11/18 | 15:00
| b)Sirajganj end | MW | 560 | 11/11/18 | 18:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 7.724 | 12/11/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 7.64 | 12/11/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 134.298
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 132.822
30 | Transmission loss of EWI /NO-2 | % | 1.099
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV Transformers-T1 & T2 | 2018-11-05 13:00 | 2018-11-05 13:27 | 0:27 | T | Tripped showing O/C relay | 68 | 30.6 | Power interruption
|  |  | Total : | 0:27 |  | Unserved Energy: |  | 30.6
Dhaka (South) Grid Circle :
Haripur | 132 kV Bus reseve bus | 2018-11-13 07:03 | 2018-11-13 07:03 | 0:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khagrachari | 132/33 kV Transformer-T2 | 2018-11-02 09:32 | 2018-11-05 16:14 | 78:42 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Sikalbaha | 132/33 kV Transformer-T3 | 2018-11-07 07:20 | 2018-11-07 07:35 | 0:15 | T | Tripped showing O/C relay | 24 | 6 | Power interruption
Baraulia | 132/33 kV Transformer-T3 | 2018-11-13 02:40 | 2018-11-13 14:01 | 11:21 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-17 10:33 | 2018-11-17 11:54 | 1:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2018-11-27 16:49 | 2018-11-27 19:13 | 2:24 | T | Tripped showing differential relay | 40 | 96 | Power interruption
|  |  | Total : | 94:03 |  | Unserved Energy: |  | 102
Cumilla Grid Circle :
Feni | 132/33 kV Transformer-T1 | 2018-11-01 20:37 | 2018-11-01 21:15 | 0:38 | T | Tripped showing PRD relay | 92 | 58.2667 | Power interruption
Chatak | 132/33 kV Transformer-T2 | 2018-11-17 21:12 | 2018-11-17 21:44 | 0:32 | E/O | Due to R-phase CT sparking | 3 | 1.6 | Power interruption
|  |  | Total : | 1:18 |  | Unserved Energy: |  | 59.8667
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T1 | 2018-11-03 14:09 | 2018-11-03 14:17 | 0:08 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 | 2018-11-19 03:42 | 2018-11-19 03:50 | 0:08 | T | Tripped showing inst.E/F relay | 28 | 3.7333 | Power interruption
|  |  | Total : | 0:08 |  | Unserved Energy: |  | 3.7333
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T1 | 2018-11-25 13:31 | 2018-11-25 13:57 | 0:26 | E/O | Due to Oil leakage | 10 | 4.3333 | Power interruption
Ishurdi | 230/132 kV Transformer-T2 | 2018-11-25 10:34 | 2018-11-25 15:23 | 4:49 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2018-11-25 21:47 | 2018-11-27 19:32 | 45:45 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 51:00 |  |  |  | 4.3333
Bogura Grid Circle:
Palshbari | 132 kV main bus | 2018-11-12 12:15 | 2018-11-12 15:10 | 2:55 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T02 | 2018-11-25 13:05 | 2018-11-25 13:43 | 0:38 | T | Tripped showing general trip | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T02 | 2018-11-29 06:57 | 2018-11-29 07:06 | 0:26 | E/O | Due to Oil level low | 50 | 21.6667 | Power interruption
|  |  | Total : | 3:59 |  | Unserved Energy: |  | 21.6667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 72:13 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2018-11-25 08:03 | 2018-11-25 13:24 | 5:21 | T | Tripped showing dist.(Z2) relay | 0 | 0 | No interruption
|  |  | Total : | 5:21 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Ullon 132 132 kV line-1 | 2018-11-05 19:48 | 2018-11-05 20:46 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-11-10 10:37 | 2018-11-10 10:43 | 0:06 | T | Tripped showing dist.(C-phase) relay | 58 | 5.8 | Power interruption
Shyampur(new) | Shyampur(new)-Shyampur (old) 132 kV line-1 | 2018-11-10 16:57 | 2018-11-10 17:05 | 0:08 | T | Tripped showing basbar protcetion relay | 82 | 19.1333 | Power interruption
| Shyampur(new)-Shyampur (old) 132 kV line-1 | 2018-11-10 17:12 | 2018-11-10 17:18 | 0:06 | T
Hasnabad | Hasnabad-Sitalakyha 132 kV line | 2018-11-13 06:00 | 2018-11-13 06:12 | 0:12 | T | Tripped showing dist. relay | 62 | 12.4 | Power interruption
Haripur | Haripur-Madanganj 132 kV line | 2018-11-14 10:27 | 2018-11-14 11:24 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur(new) | Shyampur(new)-Shyampur (old) 132 kV line-1 | 2018-11-18 15:14 | 2018-11-18 20:32 | 5:18 | T | Tripped showing dist. relay | 20 | 106 | Power interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-2 | 2018-11-24 06:51 | 2018-11-24 06:58 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-2 | 2018-11-26 11:14 | 2018-11-26 12:20 | 1:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 8:58 |  | Unserved Energy: |  | 143.3333
Chattogram Grid Circle :
Chandraghona | Chandraghona-Khgrachori 132 kV line | 2018-11-22 21:16 | 2018-11-22 21:27 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangamati | Rangamati-Khgrachori 132 kV line | 2018-11-22 21:16 | 2018-11-22 21:17 | 0:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Maduanaghat | Maduanaghat-Khulshi 132 kV line-2 | 2018-11-27 11:49 | 2018-11-27 12:04 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:16 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Comiila(N) | Comiila(N)-Meghnaghat 230 kV line-2 | 2018-11-06 10:57 | 2018-11-07 08:51 | 21:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(N) | Ashuganj(N)-400 kV line-2 | 2018-11-14 11:14 | 2018-11-14 14:10 | 2:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line- 2 | 2018-11-22 01:30 | 2018-11-22 03:37 | 2:07 | E/O | Due to Y-phase disk isolator damage | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line- 1 | 2018-11-22 01:30 | 2018-11-22 17:15 | 15:45 | E/O |  | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 & 2 | 2018-11-28 01:40 | 2018-11-28 04:04 | 2:24 | E/O | Due to B-phase PT bursting at Kulauara S/S | 20 | 48 | Power interruption 01:40 to 4:04
| Fenchuganj-Sylhet 132 kV line | 2018-11-28 01:40 | 2018-11-28 01:57 | 0:17 | E/O
Feni | Feni-Baroihat 132 kV line-2 | 2018-11-28 13:04 | 2018-11-28 15:05 | 2:01 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 47:24 |  | Unserved Energy: |  | 48
Khulna Grid Circle :
Barisal | Barisal-Patuakhali 132 kV line | 2018-11-16 08:21 | 2018-11-16 08:41 | 0:20 | T | Tripped showing E/F relay | 16 | 5.3333 | Power interruption
|  |  | Total : | 0:20 |  | Unserved Energy: |  | 5.3333
HVDC Grid Circle :
Ishurdi | Ishurdi-Bheramara 230 kV line-2 | 2018-11-11 11:54 | 2018-11-11 11:55 | 0:01 | E/O | Due to bursting at L/A | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-1 | 2018-11-11 11:56 | 2018-11-11 13:30 | 1:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-2 | 2018-11-11 11:56 | 2018-11-11 12:42 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishirdi-Baghabari 230 kV line-1 | 2018-11-11 11:56 | 2018-11-11 12:12 | 0:16 | T |  | 0 | 0 | No interruption
|  |  | Total : | 2:37 |  | Unserved Energy: |  | 0
Bogura Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 64:56 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: November 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV Transformer-T3 | 2018-11-03 09:21 | 2018-11-03 16:04 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-11-04 07:10 | 2018-11-04 18:47 | 11:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2018-11-04 09:01 | 2018-11-04 16:29 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2018-11-04 08:40 | 2018-11-04 14:40 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-11-05 06:36 | 2018-11-06 03:25 | 20:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2018-11-05 08:04 | 2018-11-05 19:33 | 11:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2018-11-05 12:01 | 2018-11-05 13:13 | 1:12 | S/O | Due to abnormal sound at Y-phase bushing | 8 | 9.6 | Power interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-11-06 08:51 | 2018-11-06 15:03 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-07 07:44 | 2018-11-07 09:28 | 1:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T1 | 2018-11-07 07:40 | 2018-11-07 20:18 | 12:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | 132/33 kV Transformer-T2 | 2018-11-07 10:01 | 2018-11-07 14:48 | 4:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargon | 132/33 kV Transformer-T1 | 2018-11-07 09:18 | 2018-11-07 20:19 | 11:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2018-11-08 15:25 | 2018-11-08 18:05 | 2:40 | S/O | Due to protection work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 | 2018-11-08 08:13 | 2018-11-08 20:02 | 11:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2018-11-11 09:12 | 2018-11-11 14:27 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 | 2018-11-14 08:58 | 2018-11-14 17:13 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2018-11-15 08:15 | 2018-11-15 15:35 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2018-11-17 07:55 | 2018-11-17 15:41 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2018-11-17 09:03 | 2018-11-17 16:26 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-11-17 08:14 | 2018-11-17 16:32 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-18 07:43 | 2018-11-18 23:33 | 15:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2018-11-18 09:02 | 2018-11-18 16:20 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2018-11-18 08:05 | 2018-11-18 13:30 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T2 | 2018-11-18 09:06 | 2018-11-18 13:05 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-11-19 09:14 | 2018-11-19 15:50 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T3 | 2018-11-19 09:03 | 2018-11-19 15:37 | 6:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-11-20 09:01 | 2018-11-20 16:32 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132 kV bus-1 | 2018-11-22 12:25 | 2018-11-22 14:38 | 2:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2018-11-23 08:04 | 2018-11-23 16:25 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Nerakona | 132/33 kV Transformer-T2 | 2018-11-23 08:06 | 2018-11-23 14:30 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2018-11-25 08:10 | 2018-11-25 16:50 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 | 2018-11-26 09:04 | 2018-11-26 16:36 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2018-11-26 08:02 | 2018-11-26 16:26 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknganj | 132/33 kV Transformers-T3 & T4 | 2018-11-26 08:19 | 2018-11-26 16:37 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T1 | 2018-11-26 09:45 | 2018-11-26 18:14 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | 132/33 kV Transformer-T3 | 2018-11-27 09:13 | 2018-11-27 15:20 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2018-11-27 08:11 | 2018-11-27 16:17 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensigh | 132/33 kV Transformer-T3 | 2018-11-28 09:35 | 2018-11-28 15:38 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2018-11-28 08:32 | 2018-11-28 16:01 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknganj | 132/33 kV Transformers-T3 & T4 | 2018-11-28 08:02 | 2018-11-28 16:29 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 308:12 |  | Unserved Energy: |  | 9.6
Dhaka (South) Grid Circle :
Haripur | 230/132 kV Transformer-TR1 | 2018-11-02 09:04 | 2018-11-02 12:36 | 3:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T1 | 2018-11-03 07:09 | 2018-11-03 14:48 | 7:39 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T01 | 2018-11-03 20:10 | 2018-11-03 22:44 | 2:34 | S/O | Due to replacement work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T1 | 2018-11-04 07:29 | 2018-11-04 17:29 | 10:00 | S/O | Due to gas shortage | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2018-11-05 07:26 | 2018-11-05 17:33 | 10:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T2 | 2018-11-08 08:43 | 2018-11-08 16:00 | 7:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | 132 kV bus-1 | 2018-11-09 10:07 | 2018-11-09 13:42 | 3:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/230/132 kV Transformer-TR1 | 2018-11-15 10:23 | 2018-11-15 13:57 | 3:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV Transformer-T01 | 2018-11-17 09:06 | 2018-11-17 20:12 | 11:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T02 | 2018-11-18 07:48 | 2018-11-18 08:06 | 0:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T1 | 2018-11-18 08:32 | 2018-11-18 16:35 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-26 08:23 | 2018-11-26 16:28 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 75:50 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Halishahar | 132/33 kV Transformer-T2 | 2018-11-02 07:10 | 2018-11-02 11:47 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | 132 kV main bus | 2018-11-02 07:00 | 2018-11-02 09:20 | 2:20 | S/O | Due to C/M work | 70 | 163.3333 | Power interruption
Hathazari | 230/132 kV Transformers-MT-3 | 2018-11-03 23:38 | 2018-11-04 00:37 | 0:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbha | 132 kV bus-B | 2018-11-08 06:30 | 2018-11-08 07:49 | 1:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T1 | 2018-11-08 09:53 | 2018-11-08 17:32 | 7:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-13 10:24 | 2018-11-13 15:32 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2018-11-24 07:24 | 2018-11-24 13:18 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV bus-A | 2018-11-28 09:49 | 2018-11-28 14:23 | 4:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | 132/33 kV Transformer-T2 | 2018-11-28 13:44 | 2018-11-28 17:52 | 4:08 | S/O | Due to SAS work | 0 | 0 | No interruption
Halishahar | 132 kV bus | 2018-11-30 06:32 | 2018-11-30 09:30 | 2:58 | S/O | Due to SAS work | 40 | 118.6667 | Power interruption
|  |  | Total : | 39:36 |  | Unserved Energy: |  | 282
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T2 | 2018-11-01 08:22 | 2018-11-01 14:57 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 230 kV Bus-2 | 2018-11-04 08:30 | 2018-11-04 20:09 | 11:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-11-05 07:15 | 2018-11-05 10:57 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 230 kV Bus-2 | 2018-11-05 08:31 | 2018-11-05 19:18 | 10:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2018-11-05 08:08 | 2018-11-05 15:52 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 230 kV Bus-2 | 2018-11-06 08:11 | 2018-11-06 20:14 | 12:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T2 | 2018-11-06 08:13 | 2018-11-06 15:47 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-08 09:23 | 2018-11-08 10:04 | 0:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2018-11-11 07:19 | 2018-11-11 15:11 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-TR2 | 2018-11-11 08:33 | 2018-11-11 20:19 | 11:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-TR2 | 2018-11-11 15:01 | 2018-11-11 21:06 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2018-11-12 09:46 | 2018-11-12 12:46 | 3:00 | S/O | Due to relay test | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-12 13:07 | 2018-11-12 20:27 | 7:20 | S/O |  | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-ICT-2 | 2018-11-13 08:50 | 2018-11-13 13:52 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2018-11-13 10:24 | 2018-11-13 15:32 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T3 | 2018-11-13 08:48 | 2018-11-13 20:23 | 11:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2018-11-13 15:39 | 2018-11-13 20:18 | 4:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400 kV Bus-1 | 2018-11-14 12:17 | 2018-11-29 10:13 | 357:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2018-11-15 08:35 | 2018-11-15 13:55 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-15 14:05 | 2018-11-15 16:36 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2018-11-17 07:16 | 2018-11-17 16:40 | 9:24 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2018-11-17 08:54 | 2018-11-17 16:44 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T2 | 2018-11-17 08:50 | 2018-11-17 15:41 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2018-11-19 08:59 | 2018-11-19 16:10 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T4 | 2018-11-20 07:49 | 2018-11-21 12:03 | 28:14 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2018-11-20 09:01 | 2018-11-20 13:22 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2018-11-20 09:01 | 2018-11-20 15:08 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T2 | 2018-11-20 08:44 | 2018-11-20 15:53 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2018-11-20 08:56 | 2018-11-20 16:58 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T1 | 2018-11-22 09:30 | 2018-11-22 15:42 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2018-11-22 08:35 | 2018-11-22 15:18 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2018-11-22 08:50 | 2018-11-22 16:57 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-23 08:32 | 2018-11-23 16:59 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2018-11-23 07:12 | 2018-11-23 17:42 | 10:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T1 | 2018-11-26 09:08 | 2018-11-26 15:48 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2018-11-26 10:14 | 2018-11-26 15:40 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2018-11-27 08:50 | 2018-11-27 15:25 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-28 08:48 | 2018-11-28 17:15 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total | 641:15 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Barisal | 230/132 kV Transformer-T-2 | 2018-11-01 08:08 | 2018-11-01 18:25 | 10:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 | 2018-11-01 09:10 | 2018-11-01 16:09 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-03 10:25 | 2018-11-03 17:06 | 6:41 | S/O | Due to A/M work | 10 | 66.8333 | Power interruption
| 132/33 kV Transformer-T2 | 2018-11-04 10:04 | 2018-11-04 12:42 | 2:38 | S/O | Due to A/M work | 10 | 26.3333 | Power interruption
Barisal(N) | 230/132 kV Transformer-T2 | 2018-11-03 09:00 | 2018-11-03 16:29 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2018-11-03 10:25 | 2018-11-03 17:06 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-03 17:10 | 2018-11-03 18:04 | 0:54 | S/O | Due to protection test | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformer-T2 | 2018-11-04 09:27 | 2018-11-04 16:22 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2018-11-04 10:04 | 2018-11-04 12:42 | 2:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformer-T2 | 2018-11-05 09:32 | 2018-11-05 18:16 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2018-11-06 08:56 | 2018-11-06 16:31 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | 230 kV bus-1 | 2018-11-06 09:38 | 2018-11-06 16:42 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformer-T1 | 2018-11-07 09:23 | 2018-11-07 16:46 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132 kV bus-2 | 2018-11-08 08:45 | 2018-11-08 16:45 | 8:00 | S/O | Due to project work | 0 | 0 | No interruption
| 132 kV bus-B | 2018-11-09 07:30 | 2018-11-09 19:10 | 11:40 | S/O | Due to project work | 0 | 0 | No interruption
Goaalpara | 132/33 kV Transformer-T5 | 2018-11-10 09:03 | 2018-11-10 16:16 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132 kV bus-B | 2018-11-11 07:16 | 2018-11-11 16:58 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Goaalpara | 132/33 kV Transformer-T5 | 2018-11-11 09:01 | 2018-11-11 15:57 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-TR1 | 2018-11-11 08:06 | 2018-11-11 15:14 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2018-11-12 08:40 | 2018-11-12 16:25 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2018-11-12 09:09 | 2018-11-12 15:16 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2018-11-12 09:12 | 2018-11-12 16:14 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T1 | 2018-11-12 09:42 | 2018-11-12 10:52 | 1:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Goaalpara | 132/33 kV Transformer-T6 | 2018-11-12 09:09 | 2018-11-12 15:52 | 6:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2018-11-13 08:13 | 2018-11-13 15:20 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2018-11-13 10:22 | 2018-11-13 16:30 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2018-11-13 09:08 | 2018-11-13 16:56 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T6 | 2018-11-13 09:02 | 2018-11-13 15:48 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2018-11-14 07:08 | 2018-11-14 11:45 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2018-11-14 08:50 | 2018-11-14 16:42 | 7:52 | S/O | Due to A/M work | 10 | 78.6667 | Power interruption
Madaripur | 132/33 kV Transformer-T2 | 2018-11-14 08:24 | 2018-11-14 16:02 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132 kV bus-A | 2018-11-14 08:05 | 2018-11-14 15:57 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2018-11-15 08:30 | 2018-11-15 15:43 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2018-11-15 08:35 | 2018-11-15 15:49 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T2 | 2018-11-15 09:30 | 2018-11-15 14:40 | 5:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2018-11-16 09:52 | 2018-11-16 16:15 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2018-11-17 07:32 | 2018-11-17 14:05 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2018-11-17 09:02 | 2018-11-17 16:20 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T1 | 2018-11-17 09:06 | 2018-11-17 14:48 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T1 | 2018-11-18 07:06 | 2018-11-18 16:47 | 9:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-19 07:19 | 2018-11-19 15:07 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2018-11-19 09:10 | 2018-11-19 15:46 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2018-11-19 08:51 | 2018-11-19 16:58 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2018-11-19 07:12 | 2018-11-19 15:12 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2018-11-20 09:18 | 2018-11-20 15:10 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T2 | 2018-11-20 10:04 | 2018-11-20 16:10 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T2 | 2018-11-22 08:31 | 2018-11-22 15:29 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2018-11-26 09:17 | 2018-11-26 17:00 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-11-27 07:01 | 2018-11-27 15:41 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2018-11-27 08:54 | 2018-11-27 14:23 | 5:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T2 | 2018-11-28 07:02 | 2018-11-28 15:23 | 8:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(old) | 132/33 kV Transformer-T2 | 2018-11-28 07:18 | 2018-11-28 09:40 | 2:22 | S/O | Due to D/W work | 10 | 23.6667 | Power interruption
Noapara | 132/33 kV Transformer-T2 | 2018-11-28 08:51 | 2018-11-28 14:07 | 5:16 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 359:44 |  | Unserved Energy : |  | 195.5
HVDC Grid Circle :
Kustia | 132/33 kV Transformer-T2 | 2018-11-05 08:03 | 2018-11-09 16:49 | 104:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 230 kV bus-1 | 2018-11-10 10:23 | 2018-11-10 15:48 | 5:25 | S/O | Due to protection test | 0 | 0 | No interruption
Bheramara | 132/33 kV Transformer-T1 | 2018-11-28 08:42 | 2018-11-28 13:59 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC | 400 kV bus-1 | 2018-11-30 12:12 | 2018-11-30 20:34 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 123:50 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Bogra | 132/33 kV Transformer-T1 | 2018-11-03 07:50 | 2018-11-03 17:09 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T1 | 2018-11-03 08:38 | 2018-11-03 15:49 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T1 | 2018-11-04 09:50 | 2018-11-04 18:10 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T1 | 2018-11-04 08:27 | 2018-11-04 11:30 | 3:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-11-04 11:37 | 2018-11-04 14:47 | 3:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T2 | 2018-11-05 09:20 | 2018-11-05 16:32 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T2 | 2018-11-05 10:41 | 2018-11-05 14:32 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 230 kV Bus coupler | 2018-11-05 10:40 | 2018-11-05 16:10 | 5:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T2 | 2018-11-06 09:23 | 2018-11-06 13:15 | 3:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-11-08 09:12 | 2018-11-08 20:03 | 10:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T3 | 2018-11-08 09:54 | 2018-11-08 14:54 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T3 | 2018-11-08 10:40 | 2018-11-08 14:44 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-11-10 08:10 | 2018-11-10 16:13 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T4 | 2018-11-11 08:39 | 2018-11-11 13:39 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T3 | 2018-11-13 08:40 | 2018-11-13 13:45 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-T2 | 2018-11-14 08:47 | 2018-11-14 18:29 | 9:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2018-11-16 06:20 | 2018-11-16 07:50 | 1:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T4 | 2018-11-16 07:30 | 2018-11-16 12:55 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T1 | 2018-11-20 09:01 | 2018-11-20 16:21 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132 kV Bus | 2018-11-23 06:37 | 2018-11-23 10:17 | 3:40 | S/O | Due to C/M work | 65 | 238.3333 | Power interruption
Noapara | 132/33 kV Transformer-T3 | 2018-11-26 09:17 | 2018-11-26 14:26 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 114:10 |  | Unserved Energy : |  | 238.3333
Page: 6/6 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: November 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Others :
Bashundhara | 132/33 kV Transformer-T1 | 2018-11-18 08:25 | 2018-11-18 16:05 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | 230/132 kV Transformer-AT12 | 2018-11-23 08:23 | 2018-11-23 11:27 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 10:44 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 1673:21 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: November 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-11-02 07:17 | 2018-11-03 20:23 | 37:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Basila 132 kV line | 2018-11-02 09:40 | 2018-11-02 16:13 | 6:33 | S/O | Due to project work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2018-11-03 07:18 | 2018-11-03 16:04 | 8:46 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bosila S/S | Bosila S/S-Bosila P/S 132 kV line | 2018-11-03 08:16 | 2018-11-03 15:58 | 7:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Sherpur 132 kV line-1 | 2018-11-03 08:59 | 2018-11-03 16:03 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2018-11-04 08:19 | 2018-11-04 14:55 | 6:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-1 | 2018-11-04 08:50 | 2018-11-04 16:45 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2018-11-05 08:23 | 2018-11-05 14:48 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-1 | 2018-11-05 08:32 | 2018-11-05 17:04 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Sherpur 132 kV line-1 | 2018-11-06 08:32 | 2018-11-06 16:17 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2018-11-07 07:27 | 2018-11-07 16:40 | 9:13 | S/O | Due to D/W work | 0 | 0 | No interruption
United Mymensingh | United Mymensingh-Sherpur 132 kV line-1 | 2018-11-07 08:13 | 2018-11-07 16:04 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-1 | 2018-11-07 09:05 | 2018-11-07 15:58 | 6:53 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Jamalpur-United Mymensingh 132 kV line-1 | 2018-11-08 08:04 | 2018-11-08 20:11 | 12:07 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-1 | 2018-11-08 08:44 | 2018-11-08 15:04 | 6:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Tongi-New Tongi 132 kV line-1 | 2018-11-10 10:45 | 2018-11-10 11:45 | 1:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV line-1 | 2018-11-10 08:38 | 2018-11-10 16:53 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2018-11-10 08:40 | 2018-11-10 16:31 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-2 | 2018-11-11 08:03 | 2018-11-11 16:16 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-2 | 2018-11-11 08:47 | 2018-11-11 16:17 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-Mymensingh 132 kV line-2 | 2018-11-11 08:18 | 2018-11-11 16:25 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-2 | 2018-11-12 08:12 | 2018-11-12 16:16 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV line-2 | 2018-11-12 09:45 | 2018-11-12 11:27 | 1:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2018-11-12 08:48 | 2018-11-12 17:20 | 8:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-2 | 2018-11-13 08:35 | 2018-11-13 16:07 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2018-11-13 09:45 | 2018-11-13 15:30 | 5:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2018-11-13 09:12 | 2018-11-13 17:12 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-11-14 07:37 | 2018-11-14 17:02 | 9:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2018-11-14 08:29 | 2018-11-14 15:58 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2018-11-14 09:06 | 2018-11-14 16:15 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh -Sherpur132 kV line-2 | 2018-11-14 08:18 | 2018-11-14 16:04 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV line-1 | 2018-11-15 09:22 | 2018-11-15 10:44 | 1:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh -Sherpur132 kV line-2 | 2018-11-15 08:31 | 2018-11-15 16:11 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Tangail 132 kV line-1 & 2 | 2018-11-15 10:54 | 2018-11-15 19:11 | 8:17 | S/O | Due to project work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh 132 kV line-1 & 2 | 2018-11-16 09:38 | 2018-11-16 16:35 | 6:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2018-11-17 09:35 | 2018-11-17 16:29 | 6:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2018-11-18 09:09 | 2018-11-18 16:47 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2018-11-18 08:55 | 2018-11-26 20:45 | 203:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-1 | 2018-11-18 08:44 | 2018-11-18 16:05 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2018-11-19 07:23 | 2018-11-19 13:24 | 6:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2018-11-19 09:43 | 2018-11-19 17:44 | 8:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2018-11-19 09:12 | 2018-11-19 17:45 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-1 | 2018-11-19 08:48 | 2018-11-19 15:44 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV line-2 | 2018-11-20 09:30 | 2018-11-20 16:50 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-11-22 07:25 | 2018-11-22 16:56 | 9:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2018-11-22 09:03 | 2018-11-22 15:45 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2018-11-22 09:53 | 2018-11-22 20:10 | 10:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 | 2018-11-23 08:10 | 2018-11-23 16:30 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2018-11-23 09:05 | 2018-11-23 13:41 | 4:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-2 | 2018-11-23 09:55 | 2018-11-23 16:50 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-11-25 08:39 | 2018-11-25 14:38 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line--1 | 2018-11-25 08:58 | 2018-11-25 17:08 | 8:10 | S/O | Due to A/M work | 12 | 98 | Power interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-11-25 08:18 | 2018-11-25 15:20 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2018-11-26 07:30 | 2018-11-26 14:42 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2018-11-26 08:43 | 2018-11-26 16:28 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2018-11-26 09:44 | 2018-11-26 10:41 | 0:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-11-26 07:30 | 2018-11-26 14:42 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Mymensingh RPCL 132 kV line-2 | 2018-11-26 08:50 | 2018-11-26 16:44 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV line-1 | 2018-11-27 09:00 | 2018-11-27 10:33 | 1:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Agargaon-Cantonment 132 kV line-2 | 2018-11-27 10:34 | 2018-11-27 10:58 | 0:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-2 | 2018-11-27 08:47 | 2018-11-27 13:40 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-2 | 2018-11-27 08:46 | 2018-11-27 15:56 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kabirpur 132 kV line-1 | 2018-11-27 08:15 | 2018-11-27 17:37 | 9:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2018-11-27 10:15 | 2018-11-27 19:21 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mirpur-Uttara 132 kV line | 2018-11-28 08:53 | 2018-11-28 17:01 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-2 | 2018-11-28 09:05 | 2018-11-28 16:06 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 685:05 |  | Unserved Energy: |  | 98
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Hasnabad 230 kV line | 2018-11-02 05:50 | 2018-11-02 17:05 | 11:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-APR 230 kV line 230 kV line | 2018-11-02 05:58 | 2018-11-02 17:08 | 11:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (new) 132 kV line-1 | 2018-11-02 06:32 | 2018-11-02 08:52 | 2:20 | S/O | Due to loop changing | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR 230 kV line | 2018-11-04 06:01 | 2018-11-04 17:18 | 11:17 | S/O | Due to project work | 0 | 0 | No interruption
| Meghnagat -Hasanad 230 kV line-1 | 2018-11-04 06:01 | 2018-11-04 17:15 | 11:14 | S/O | Due to project work | 0 | 0 | No interruption
| Meghnagat -Hasanad 230 kV line-2 | 2018-11-04 06:01 | 2018-11-04 17:18 | 11:17 | S/O
Lalbagh | Lalbagh-Kallyanpur 132 kV line-1 | 2018-11-05 09:27 | 2018-11-05 09:35 | 0:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-1 & 2 | 2018-11-06 07:21 | 2018-11-06 09:09 | 1:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-1 | 2018-11-06 09:10 | 2018-11-06 16:42 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 132 kV line-1 | 2018-11-06 09:50 | 2018-11-06 14:32 | 4:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Siddhirganj 132 kV line-2 | 2018-11-08 10:00 | 2018-11-08 12:22 | 2:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-1 | 2018-11-09 06:17 | 2018-11-09 16:39 | 10:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-1 | 2018-11-10 08:46 | 2018-11-10 14:36 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-1 | 2018-11-10 08:01 | 2018-11-10 16:34 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 230 kV line-1 | 2018-11-10 14:45 | 2018-11-10 18:20 | 3:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddirganj 132 kV line-2 | 2018-11-11 09:50 | 2018-11-11 15:45 | 5:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV line-2 | 2018-11-11 09:03 | 2018-11-11 15:45 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR 230 kV line | 2018-11-14 06:02 | 2018-11-14 17:08 | 11:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line | 2018-11-14 06:04 | 2018-11-14 17:05 | 11:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-APR 230 kV line | 2018-11-15 06:09 | 2018-11-15 17:08 | 10:59 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line | 2018-11-15 06:07 | 2018-11-15 17:04 | 10:57 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-APR 230 kV line | 2018-11-17 06:05 | 2018-11-17 13:02 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line | 2018-11-17 06:03 | 2018-11-17 11:02 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2018-11-17 09:32 | 2018-11-17 20:17 | 10:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2018-11-18 07:48 | 2018-11-18 16:24 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2018-11-18 08:54 | 2018-11-18 15:59 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Dautch Bangla 132 kV line | 2018-11-18 09:57 | 2018-11-18 13:20 | 3:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-Ghorashal 132 kV line-2 | 2018-11-20 09:45 | 2018-11-20 17:36 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2018-11-20 09:58 | 2018-11-20 17:19 | 7:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-3 | 2018-11-21 09:33 | 2018-11-21 15:22 | 5:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2018-11-22 09:06 | 2018-11-22 20:07 | 11:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-1 | 2018-11-22 08:57 | 2018-11-22 13:28 | 4:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2018-11-22 09:40 | 2018-11-22 14:32 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-2 | 2018-11-23 08:24 | 2018-11-23 19:33 | 11:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-1 | 2018-11-26 08:05 | 2018-11-26 18:11 | 10:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-2 | 2018-11-28 08:46 | 2018-11-28 13:38 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 269:22 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Kulshi | Kulshi-Baraulia 132 kV line-2 | 2018-11-01 08:30 | 2018-11-01 16:08 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2018-11-02 07:51 | 2018-11-02 16:16 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2018-11-03 07:56 | 2018-11-03 15:53 | 7:57 | S/O | Due to maintenance work | 0 | 0 | No interruption
Baraulia | Baraulia-Khulshi 132 kV line-2 | 2018-11-03 08:40 | 2018-11-03 14:01 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2018-11-03 09:59 | 2018-11-03 11:13 | 1:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Barulia 132 kV line-1 | 2018-11-04 08:26 | 2018-11-04 16:44 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2018-11-04 08:01 | 2018-11-04 15:50 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Baraulia 132 kV line-1 | 2018-11-04 08:32 | 2018-11-04 13:42 | 5:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-2 | 2018-11-05 07:18 | 2018-11-05 10:57 | 3:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2018-11-05 08:32 | 2018-11-05 15:45 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Abulkhair 132 kV line | 2018-11-05 08:32 | 2018-11-05 15:34 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Barulia 132 kV line-1 | 2018-11-06 08:18 | 2018-11-06 14:59 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV line-2 | 2018-11-06 09:03 | 2018-11-06 14:15 | 5:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-1 | 2018-11-07 10:08 | 2018-11-07 15:34 | 5:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madunaghat-T.K chemical 132 kV line | 2018-11-07 07:55 | 2018-11-07 15:58 | 8:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2018-11-07 08:21 | 2018-11-07 14:50 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-1 | 2018-11-08 08:44 | 2018-11-08 15:29 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2018-11-10 08:48 | 2018-11-10 15:50 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK chemical 132 kV line | 2018-11-11 08:36 | 2018-11-11 17:15 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2018-11-11 08:25 | 2018-11-11 15:42 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV line-1 | 2018-11-12 09:02 | 2018-11-12 14:41 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK chemical 132 kV line | 2018-11-12 08:47 | 2018-11-12 16:28 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-2 | 2018-11-12 08:29 | 2018-11-12 14:54 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV line | 2018-11-13 08:50 | 2018-11-13 13:52 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2018-11-14 07:08 | 2018-11-21 13:19 | 174:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kamrangirchar 132 kV line-2 | 2018-11-15 10:23 | 2018-11-15 13:58 | 3:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2018-11-19 08:57 | 2018-11-19 15:35 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-11-20 08:53 | 2018-11-20 15:52 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Modern steel 132 kV line | 2018-11-22 09:26 | 2018-11-22 15:06 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-Abulkhair 132 kV line | 2018-11-23 08:44 | 2018-11-23 12:27 | 3:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kamrangirchar 132 kV line-2 | 2018-11-23 11:42 | 2018-11-23 18:19 | 6:37 | S/O | Due to SAS work | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line | 2018-11-26 09:16 | 2018-11-26 15:08 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Modern steel 132 kV line | 2018-11-26 09:15 | 2018-11-26 15:09 | 5:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2018-11-26 08:33 | 2018-11-26 15:40 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Raozan | Raozan-Hathazari 230 kV line-1 | 2018-11-27 09:06 | 2018-11-27 16:08 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV line-1 | 2018-11-27 09:05 | 2018-11-27 14:39 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2018-11-28 09:11 | 2018-11-28 15:50 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kaghrachari 132 kV line-1 | 2018-11-28 10:01 | 2018-11-28 13:37 | 3:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-2 | 2018-11-30 10:45 | 2018-11-30 11:07 | 0:22 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 405:36 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-11-05 23:48 | 2018-11-06 01:44 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-2 | 2018-11-12 10:34 | 2018-11-12 12:51 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line | 2018-11-21 08:30 | 2018-11-21 10:37 | 2:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line | 2018-11-30 08:43 | 2018-11-30 16:41 | 7:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chatak 132 kV line-1 | 2018-11-30 09:55 | 2018-11-30 12:58 | 3:03 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 17:21 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-11-01 10:11 | 2018-11-01 10:59 | 0:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-11-02 07:55 | 2018-11-02 17:52 | 9:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerrhat 132 kV line | 2018-11-03 08:13 | 2018-11-03 17:41 | 9:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2018-11-03 09:35 | 2018-11-03 13:56 | 4:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-11-04 07:53 | 2018-11-04 17:00 | 9:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2018-11-05 07:44 | 2018-11-05 17:10 | 9:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2018-11-06 08:19 | 2018-11-06 17:06 | 8:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | Satkhira-Khulna(S) 132 kV line-2 | 2018-11-06 12:16 | 2018-11-06 13:22 | 1:06 | S/O | Due to tree trimming | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 Mw 132 kV line | 2018-11-11 08:12 | 2018-11-11 15:48 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna 25 MW 132 kV line-1 | 2018-11-12 10:41 | 2018-11-12 10:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 Mw 132 kV line | 2018-11-13 07:48 | 2018-11-13 13:19 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-11-30 10:19 | 2018-11-30 14:08 | 3:49 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 69:56 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bharamara | Bheramara-Faridpur 132 kV line-2 | 2018-11-08 12:44 | 2018-11-11 16:59 | 76:15 | S/O | Due to project work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2018-11-10 10:10 | 2018-11-10 10:32 | 0:22 | S/O | Due to isolator problem | 0 | 0 | No interruption
Bharamara | Bharamara-Faridpur 132 kV line-1 | 2018-11-12 08:41 | 2018-11-12 11:22 | 2:41 | S/O | Due to A/M work | 0 | 0 | No interruption
| BharamaraHVDC-Bharamara 230 kV line-1 | 2018-11-13 08:36 | 2018-11-13 17:32 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-Faridpur 132 kV line-2 | 2018-11-14 08:15 | 2018-11-14 11:45 | 3:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| BharamaraHVDC-Bharamara 230 kV line-1 | 2018-11-14 09:06 | 2018-11-14 18:48 | 9:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bharamara-NWGPCL 230 kV line-2 | 2018-11-15 08:25 | 2018-11-15 20:00 | 11:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2018-11-15 09:27 | 2018-11-15 13:03 | 3:36 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kustia-Jhenidah 132 kV line-1 | 2018-11-16 09:38 | 2018-11-16 11:27 | 1:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara HVDC | Bharamara-NWGPCL 230 kV line-2 | 2018-11-16 08:28 | 2018-11-16 20:26 | 11:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bharamara-Ishurdi 230 kV line-2 | 2018-11-17 09:28 | 2018-11-19 16:02 | 54:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bharamara-Ishurdi 230 kV line-3 | 2018-11-17 09:28 | 2018-11-18 22:45 | 37:17 | S/O |  | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 230 kV line-1 | 2018-11-17 08:05 | 2018-11-17 16:19 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baghabari-Ishurdi 230 kV line-1 | 2018-11-18 08:27 | 2018-11-18 17:13 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baghabari-Ishurdi 230 kV line-1 | 2018-11-19 10:11 | 2018-11-19 14:12 | 4:01 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bheramara | HVDC Bheramara-Khulna(s) 230 kV line-1 | 2018-11-26 08:33 | 2018-11-26 18:05 | 9:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 230 kV line-2 | 2018-11-26 08:36 | 2018-11-26 17:21 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ishurdi-Baghabari 230 kV line-2 | 2018-11-27 08:41 | 2018-11-27 19:14 | 10:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara | Bharamara-Khulna(S) 230 kV line-1 | 2018-11-27 09:10 | 2018-11-27 16:57 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bharamara-Khulna(S) 230 kV line-2 | 2018-11-28 08:43 | 2018-11-28 17:17 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 230 kV line-2 | 2018-11-28 10:06 | 2018-11-29 22:20 | 36:14 | S/O | Due to A/M work | 0 | 0 | No interruption
HVDC Bhahrampur | HVDC Bahrampur 400 kV line-1 | 2018-11-30 10:07 | 2018-11-30 20:18 | 10:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bharamara | Bharamara-GK 132 kV line | 2018-11-30 08:05 | 2018-11-30 16:43 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line | 2018-11-30 08:19 | 2018-11-30 15:25 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 274:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Naogaon | Naogaon-Bogra 132 kV line-1 | 2018-11-03 08:15 | 2018-11-03 17:12 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-1 | 2018-11-04 08:24 | 2018-11-04 15:15 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2018-11-04 08:01 | 2018-11-04 15:58 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Palashbari-Rangpur 132 kV line-1 | 2018-11-05 08:10 | 2018-11-05 15:40 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Palashbari-Rangpur 132 kV line-2 | 2018-11-06 07:40 | 2018-11-06 11:45 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogra 132 kV line-2 | 2018-11-06 07:36 | 2018-11-06 17:27 | 9:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur 132 kV line-2 | 2018-11-06 08:12 | 2018-11-06 15:20 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogra 132 kV line-2 | 2018-11-06 07:36 | 2018-11-06 17:27 | 9:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Naogaon-Bogra 132 kV line-2 | 2018-11-07 08:42 | 2018-11-07 15:08 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur 132 kV line-2 | 2018-11-07 08:05 | 2018-11-07 16:10 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2018-11-10 08:52 | 2018-11-10 16:16 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Barapukuria 230 kV line-1 | 2018-11-10 08:38 | 2018-11-10 16:06 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2018-11-11 09:15 | 2018-11-11 15:08 | 5:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Barapukuria 230 kV line-2 | 2018-11-12 08:04 | 2018-11-12 15:38 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-2 | 2018-11-13 08:06 | 2018-11-13 20:08 | 12:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Barapukuria 230 kV line-2 | 2018-11-13 08:10 | 2018-11-13 15:34 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-2 | 2018-11-14 08:25 | 2018-11-14 15:59 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Barapukuria 230 kV line-2 | 2018-11-14 08:25 | 2018-11-14 16:35 | 8:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogra-Palashbari 132 kV line-1 | 2018-11-15 07:02 | 2018-11-16 21:10 | 38:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Sherpur 132 kV line-2 | 2018-11-16 08:40 | 2018-11-16 12:48 | 4:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-11-17 08:38 | 2018-11-17 16:08 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2018-11-17 08:39 | 2018-11-17 16:21 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2018-11-17 08:33 | 2018-11-17 15:34 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2018-11-18 08:58 | 2018-11-18 16:34 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2018-11-18 08:43 | 2018-11-18 14:54 | 6:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-11-18 08:12 | 2018-11-18 15:58 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV line | 2018-11-19 08:57 | 2018-11-19 16:19 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2018-11-19 09:20 | 2018-11-19 13:24 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2018-11-19 08:10 | 2018-11-19 11:50 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Rajshahi RPP 132 kV line | 2018-11-20 08:36 | 2018-11-20 15:52 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Natore 132, kV line-1 | 2018-11-20 08:28 | 2018-11-20 15:32 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogra-Natore 132, kV line-2 | 2018-11-20 15:40 | 2018-11-20 17:32 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogra-Palashbari 132 kV line-1 | 2018-11-21 06:20 | 2018-11-21 17:08 | 10:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2018-11-23 11:49 | 2018-11-23 12:43 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-11-23 15:01 | 2018-11-23 15:58 | 0:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-11-24 07:58 | 2018-11-24 11:26 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV line | 2018-11-25 08:35 | 2018-11-25 15:10 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Barapukuria 132 kV line-1 | 2018-11-25 09:18 | 2018-11-25 20:58 | 11:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 132 kV line-1 | 2018-11-25 08:25 | 2018-11-25 16:29 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2018-11-25 09:02 | 2018-11-25 14:42 | 5:40 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line-2 | 2018-11-26 08:05 | 2018-11-26 14:41 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2018-11-26 09:03 | 2018-11-26 13:57 | 4:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj0Bogra 132 kV line-1 | 2018-11-26 06:55 | 2018-11-26 15:50 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 132 kV line-2 | 2018-11-27 08:14 | 2018-11-27 16:02 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line-2 | 2018-11-28 08:14 | 2018-11-28 13:52 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 132 kV line-2 | 2018-11-28 08:42 | 2018-11-28 16:29 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2018-11-28 10:19 | 2018-11-28 11:50 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 348:45 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Matuail 132 kV line | 2018-11-07 07:25 | 2018-11-07 16:54 | 9:29 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 9:29 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 2079:55 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:November' 2018
| Area | Previous Month (October 2018) |  |  |  | Current Month (November 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 11 | 6 | 24 | 41 | 2 | - | 106 | 108
2 | Dhaka (South) Grid Circle. | 16 | 6 | 28 | 50 | 9 | 1 | 48 | 58
3 | Chattogram Grid Circle. | 6 | 4 | 38 | 48 | 7 | 1 | 49 | 57
4 | Cumilla Grid Circle. | 16 | - | 51 | 67 | 3 | 6 | 43 | 52
5 | Khulna Grid Circle. | 6 | - | 28 | 34 | 2 |  | 65 | 67
6 | Bheramara HVDC Grid Circle | 1 | - | 14 | 15 | 2 | 2 | 28 | 32
7 | Bogura Grid Circle. | 6 | 2 | 46 | 54 | 1 | 2 | 68 | 71
8 | Others | - | - | - | 0 | - | - | 3 | 3
9 | Total | 62 | 18 | 229 | 309 | 26 | 12 | 410 | 448
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:November' 2018
| Area | Previous Month (September 2018) |  |  |  | Current Month (November 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 139.48 | - | - | 139.48 | 30.6 | - | 107.6 | 138.2
2 | Dhaka (South) Grid Circle. | 447.43 | 432.09 | 212.5 | 1092.02 | 143.33 | - | - | 143.33
3 | Chattogram Grid Circle. | - | - | 400 | 400 | 102 | - | 282 | 384
4 | Cumilla Grid Circle. | 5.5 | - | 69.17 | 74.67 | 58.27 | 49.6 | - | 107.87
5 | Khulna Grid Circle. | 13.67 | - | 22.8 | 36.47 | 9.06 |  | 195.5 | 204.56
6 | Bheramara HVDC Grid Circle | - | - | 74.93 | 74.93 | - | 4.33 | - | 4.33
7 | Bogura Grid Circle. | 166.07 | 354.58 | 160.92 | 681.57 | - | 21.67 | 238.33 | 260
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 772.15 | 786.67 | 940.32 | 2499.14 | 343.26 | 75.6 | 823.43 | 1242.29
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:November' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 | 1 | 2 | 1 | - | 1 | 40.2
2 | Dhaka (South) | 5031.6 | - | - | - | - | - | - | -
3 | Chattogram | 2042 | 2 | 2 | 4 | 1 | - | 3 | 384
4 | Khulna | 2434 | 1 | 4 | 5 | 1 |  | 4 | 199.23
5 | Bheramara (HVDC) | 2423.3 | 1 |  | 1 | 1 | - |  | 4.33
6 | Bogura | 3145.6 | 1 | 1 | 2 | 1 |  | 1 | 260
7 | Cumilla | 2981 | 2 |  | 2 |  | 2 |  | 59.87
| Total | 23365.5 | [6 empty] | 947.63
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 100%
3 | Chattogram | 99.74%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.8% | [6 empty] | Executive Engineer
6 | Bogura | 100% | [6 empty] | Information Management Division
7 | Cumilla | 100% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:November' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | - | 1 | 1 | - | - | 1 | 98
2 | Dhaka (South) | 990.29 |  | 4 | - | 6 | 3 | - | 1 | 143.33
3 | Chattogram | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 1 |  | 1 | 1 | - |  | 5.33
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | 17 | 1 | - | - | - | - | 1 | 48
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 294.66
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.9% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.97% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:November' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
November | 10 | - | 3 | 01hr34 min | 1 | 02hr24 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:November' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Savar | 1 | 0:27 | 68 | 30.6 | Due to tripping of 132/33 kV Transformers T1 & T2
Jamalpur | 1 | 1:12 | 8 | 9.6 | Due to S/D of 132/33 kV Transformer T3
Manikganj | 1 | 8:10 | 12 | 98 | Due to S/D of Manikganj-Kabirpur 132 kV line-1
Hasnabad | 1 | 0:06 | 58 | 5.8 | Due to tripping of Hasnabad-Kamrangirchar 132 kV line
Shyampur | 2 | 0:14 | 82 | 19.1333 | Due to tripping of Shyampur (Old)-Shyampur(new) 132 kV line
| 1 | 5:18 | 20 | 106
Hasnabad | 1 | 0:12 | 62 | 12.4 | Due to tripping of Hasnabad-Sitalkyha 132 kV line
Sikalbaha | 1 | 0:15 | 24 | 6 | Due to S/D of 132/33 kV Transformer T3
Bakulia | 1 | 2:24 | 40 | 96 | Due to tripping of 132/33 kV Transformer T2
Khulshi | 1 | 2:20 | 70 | 163.3333 | Due to S/D of 132 kV bus
Halishahar | 1 | 2:58 | 40 | 118.6667 | Due to S/D of 132 kV bus
Feni | 1 | 0:38 | 92 | 58.2667 | Due to tripping of 132/33 kV Transformer T1
Chatak | 1 | 0:32 | 3 | 1.6 | Due to R-phase CT sparking
Fenchuganj | 1 | 2:24 | 20 | 48 | Due to PT bursting at Fenchuganj-Kulaura 132 kV line-1 & 2
Mongla | 3 | 0:08 | 28 | 3.73 | Due to tripping of 132/33 kV Transformer T1
|  | 6:41 | 10 | 66.8333 | Due to tripping of 132/33 kV Transformer T2
|  | 2:38 | 10 | 26.3333
Barisal | 1 | 0:20 | 16 | 5.3333 | Due to tripping of Barisal-Patuakhali 132 kV line
Gopalganj | 1 | 7:52 | 10 | 78.6667 | Due to S/D of 132/33 kV Transformer T2
Barisal |  | 2:22 | 10 | 23.6667
Bottail | 1 | 0:26 | 10 | 4.3333 | Due to oil leakage of 132/33 kV Transformer T1
Barapukuria | 1 | 0:26 | 50 | 21.6667 | Due to Oil level low of 230/132 kV Transformer T2
Rajshahi | 1 | 3:40 | 65 | 238.3333 | Due to S/D of 132 kV bus
| Total unserved energy : |  |  | 1242.2967 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:November'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 122 | 5 | 2018-11-01 | 18:00
2 | Munsiganj | 129 | 28 | 2018-11-01 | 9:00
3 | Sonargaon | 50 | 1 | 2018-11-01 | 18:30
4 | Shyampur | 178 | 4 | 2018-11-01 | 11:00
5 | Bhulta | 176 | 4 | 2018-11-01 | 19:00
6 | Madanganj | 58 | 5 | 2018-11-01 | 11:00
7 | Shitalakhya | 141 | 13 | 2018-11-01 | 18:00
8 | Rahim steel | 20 | 20 | 2018-11-01 | 15:00
9 | Matuail | 96 | 13 | 2018-11-01 | 12:00
10 | Ghorasal | 66 | 4 | 2018-11-01 | 20:00
11 | Narsingdi | 124 | 3 | 2018-11-01 | 20:00
12 | Haripur (SBU) | 107 | 4 | 2018-11-01 | 18:30
13 | Ullon | 87 | 5 | 2018-11-01 | 18:30
14 | Hasnabad | 190 | 4 | 2018-11-01 | 19:30
15 | Magbazar | 119 | 6 | 2018-11-01 | 13:00
16 | Maniknagar | 98 | 4 | 2018-11-01 | 13:00
17 | Bangabhaban | 32 | 6 | 2018-11-01 | 10:00
18 | Narinda | 78 | 4 | 2018-11-01 | 12:00
19 | Dhanmondi | 124 | 5 | 2018-11-01 | 13:00
20 | Lalbag | 91 | 28 | 2018-11-01 | 13:00
21 | Madartek | 48 | 15 | 2018-11-01 | 21:00
22 | Mirpur | 104 | 4 | 2018-11-01 | 18:00
23 | Kalyanpur | 111 | 3 | 2018-11-01 | 18:00
24 | Gulshan | 100 | 1 | 2018-11-01 | 14:00
25 | Uttara | 77 | 6 | 2018-11-01 | 18:00
26 | Uttara(new) | 8 | 3 | 2018-11-01 | 10:00
27 | Kamrangirchar | 74 | 18 | 2018-11-01 | 18:00
28 | Savar | 146 | 4 | 2018-11-01 | 18:30
29 | Bhasantec | 151 | 4 | 2018-11-01 | 18:00
30 | Agargaon | 53 | 5 | 2018-11-01 | 12:00
31 | Satmosjid | 89 | 5 | 2018-11-01 | 18:00
32 | Tongi | 137 | 3 | 2018-11-01 | 11:00
33 | Kabirpur | 216 | 5 | 2018-11-01 | 15:00
34 | Basundhara | 131 | 1 | 2018-11-01 | 18:30
35 | Manikganj | 85 | 5 | 2018-11-01 | 18:00
36 | Joydevpur | 208 | 3 | 2018-11-01 | 19:00
37 | New Tongi | 113 | 5 | 2018-11-01 | 12:00
38 | Kodda | 265 | 4 | 2018-11-01 | 18:30
39 | Dhamrai | 46 | 3 | 2018-11-01 | 18:30
40 | Tangail | 137 | 2 | 2018-11-01 | 18:30
41 | Mymensing | 208 | 3 | 2018-11-01 | 18:00
42 | Kishorganj | 82 | 3 | 2018-11-01 | 18:30
43 | Netrokona | 66 | 1 | 2018-11-01 | 18:30
44 | Jamalpur | 98 | 3 | 2018-11-01 | 18:00
45 | Sherpur | 70 | 3 | 2018-11-01 | 18:30
46 | Srimongal | 28 | 1 | 2018-11-01 | 18:00
47 | Shahjibazar | 91 | 3 | 2018-11-01 | 18:00
48 | Fenchuganj | 35 | 3 | 2018-11-01 | 18:00
49 | Kulawara | 34 | 2 | 2018-11-01 | 18:00
50 | Sylhet | 118 | 1 | 2018-11-01 | 18:00
51 | Chatak | 22 | 1 | 2018-11-01 | 18:00
52 | Sunamganj | 27 | 1 | 2018-11-01 | 18:00
53 | Bianibazar | 32 | 1 | 2018-11-01 | 18:00
54 | Cumilla (S) | 150 | 4 | 2018-11-01 | 18:30
55 | Cumilla(N) | 93 | 1 | 2018-11-01 | 19:00
56 | Chandpur | 96 | 4 | 2018-11-01 | 19:30
57 | Feni | 106 | 4 | 2018-11-01 | 18:30
58 | Chowmuhani | 150 | 4 | 2018-11-01 | 19:00
59 | Ashuganj | 50 | 2 | 2018-11-01 | 18:30
60 | Daudkandi | 98 | 1 | 2018-11-01 | 18:00
61 | B.Baria | 109 | 3 | 2018-11-01 | 19:00
62 | Ramganj | 26 | 2 | 2018-11-01 | 18:30
63 | Madanhat | 62 | 7 | 2018-11-01 | 18:30
64 | Hathazari | 85 | 4 | 2018-11-01 | 18:30
65 | Khulshi | 200 | 7 | 2018-11-01 | 11:00
66 | Halishahar | 151 | 6 | 2018-11-01 | 18:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:November'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Baraulia | 162 | 29 | 2018-11-01 | 16:00
68 | Sikalbaha | 39 | 6 | 2018-11-01 | 18:00
69 | Dohazari | 78 | 2 | 2018-11-01 | 19:00
70 | Cox'sbazar | 72 | 13 | 2018-11-01 | 19:00
71 | Chandraghona | 26 | 6 | 2018-11-01 | 18:00
72 | Kaptai | 11 | 4 | 2018-11-01 | 18:00
73 | A. Khaer Stl. | 22 | 7 | 2018-11-01 | 9:00
74 | Bakulia | 103 | 5 | 2018-11-01 | 18:00
75 | Julda | 23 | 13 | 2018-11-01 | 12:00
76 | TK chemical | 5.6 | 27 | 2018-11-01 | 12:00
77 | Modern Steel | 18 | 21 | 2018-11-01 | 11:00
78 | Shahmirpur | 26 | 5 | 2018-11-01 | 18:00
79 | Khagrachhari | 17 | 3 | 2018-11-01 | 18:00
80 | Matarbari | 22 | 3 | 2018-11-01 | 18:00
81 | Baroiar Hat | 22 | 1 | 2018-11-01 | 18:00
82 | Rangamati | 10 | 1 | 2018-11-01 | 18:00
83 | Abul Khair 230 | 199 | 20 | 2018-11-01 | 10:00
84 | BSRM | 111 | 22 | 2018-11-01 | 16:00
85 | Goalpara | 24 | 19 | 2018-11-01 | 19:00
86 | Central s/s | 87 | 3 | 2018-11-01 | 18:30
87 | Noapara | 79 | 1 | 2018-11-01 | 19:00
88 | Jashore | 124 | 4 | 2018-11-01 | 18:30
89 | Jhenida | 86 | 5 | 2018-11-01 | 18:30
90 | Bottail | 96 | 11 | 2018-11-01 | 18:00
91 | G.K Project | 51 | 4 | 2018-11-01 | 18:00
92 | Faridpur | 132 | 5 | 2018-11-01 | 18:30
93 | Madaripur | 99 | 4 | 2018-11-01 | 19:30
94 | Gopalganj | 69 | 12 | 2018-11-01 | 18:30
95 | Bagerhat | 69 | 5 | 2018-11-01 | 18:00
96 | Mongla | 38 | 15 | 2018-11-01 | 13:00
97 | Satkhira | 76 | 5 | 2018-11-01 | 18:30
98 | Gallamari | 46 | 9 | 2018-11-01 | 22:00
99 | Magura | 65 | 14 | 2018-11-01 | 19:00
100 | Chuadanga | 76 | 1 | 2018-11-01 | 21:00
101 | Barishal | 96 | 3 | 2018-11-01 | 18:00
102 | Patuakhali | 68 | 5 | 2018-11-01 | 19:30
103 | Bhandaria | 44 | 2 | 2018-11-01 | 22:00
104 | Ishurdi | 45 | 4 | 2018-11-01 | 19:00
105 | Ruppur Paromanobik | 2 | 1 | 2018-11-01 | 7:00
106 | Natore | 94 | 4 | 2018-11-01 | 18:30
107 | Bogura | 202 | 5 | 2018-11-01 | 19:00
108 | Noagaon | 94 | 1 | 2018-11-01 | 19:30
109 | Rajshahi | 116 | 5 | 2018-11-01 | 19:30
110 | C.Nawabganj | 65 | 1 | 2018-11-01 | 18:30
111 | Amnura | 40 | 1 | 2018-11-01 | 18:30
112 | Pabna | 89 | 1 | 2018-11-01 | 18:30
113 | Shahjadpur | 79 | 1 | 2018-11-01 | 18:30
114 | Serajganj | 76 | 5 | 2018-11-01 | 18:30
115 | Niyamatpur | 54 | 1 | 2018-11-01 | 18:30
116 | Joypurhat | 42 | 4 | 2018-11-01 | 18:30
117 | Rangpur | 104 | 1 | 2018-11-01 | 18:00
118 | Lalmonirhat | 74 | 4 | 2018-11-01 | 18:00
119 | Saidpur | 103 | 4 | 2018-11-01 | 18:30
120 | Purbasadipur | 77 | 1 | 2018-11-01 | 18:30
121 | Thakurgaon | 57 | 28 | 2018-11-01 | 19:00
122 | Palashbari | 84 | 1 | 2018-11-01 | 18:30
123 | Barapukuria | 43 | 1 | 2018-11-01 | 18:00
124 | Panchagar | 36 | 1 | 2018-11-01 | 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:November' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 3870 | 04.11.18 | 18:30
Chittagong | 1066 | 03.11.18 | 23:00
Khulna | 1118 | 04.11.18 | 18:30
Rajshahi | 965 | 01.11.18 | 19:00
Comilla | 831 | 03.11.18 | 19:30
Mymensingh | 643 | 01.11.18 | 18:30
Sylhet | 382 | 01.11.18 | 18:00
Barisal | 224 | 03.11.18 | 19:00
Rangpur | 562 | 01.11.18 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 400 | 22 | 2018-11-01 | 20:00 | 374 | 11 | 2018-11-01 | 12:00
2 | Bheramara | 400 | 416 | 26 | 2018-11-01 | 1:00 | 388 | 30 | 2018-11-01 | 12:00
3 | Ashuganj(N) | 400 | 405 | 15 | 2018-11-01 | 6:00 | 380 | 17 | 2018-11-01 | 11:00
4 | Kaliakoir | 400 | 384 | 24 | 2018-11-01 | 04:00 | 354 | 1 | 2018-11-01 | 12:00
5 | Bhulta | 400 | 402 | 13 | 2018-11-01 | 17:00 | 371 | 1 | 2018-11-01 | 23:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 234 | 4 | 2018-11-01 | 18:30 | 222 | 5 | 2018-11-01 | 9:00
2 | Ishurdi | 230 | 237 | 16 | 2018-11-01 | 24:00 | 224 | 10 | 2018-11-01 | 20:00
3 | Ashuganj | 230 | 240 | 14 | 2018-11-01 | 19:00 | 229 | 1 | 2018-11-01 | 10:00
4 | Serajganj | 230 | 230 | 10 | 2018-11-01 | 3:00 | 219 | 11 | 2018-11-01 | 12:00
5 | Baghabari | 230 | 237 | 21 | 2018-11-01 | 24:00 | 219 | 18 | 2018-11-01 | 19:30
6 | Barapukuria | 230 | 235 | 10 | 2018-11-01 | 6:00 | 222 | 3 | 2018-11-01 | 18:30
7 | Bogra | 230 | 234 | 20 | 2018-11-01 | 13:00 | 212 | 3 | 2018-11-01 | 18:30
8 | Khulna South | 230 | 240 | 3 | 2018-11-01 | 21'00 | 215 | 27 | 2018-11-01 | 12:00
9 | Rampura | 230 | 229 | 23 | 2018-11-01 | 22:00 | 211 | 1 | 2018-11-01 | 11:00
10 | Haripur | 230 | 228 | 14 | 2018-11-01 | 19:00 | 211 | 1 | 2018-11-01 | 11:00
11 | Hasnabad | 230 | 232 | 29 | 2018-11-01 | 17:00 | 208 | 1 | 2018-11-01 | 12:00
12 | Aminbazar | 230 | 230 | 15 | 2018-11-01 | 04:00 | 209 | 1 | 2018-11-01 | 10:00
13 | Tongi | 230 | 233 | 9 | 2018-11-01 | 21:00 | 206 | 4 | 2018-11-01 | 10:00
14 | Comilla (N) | 230 | 238 | 11 | 2018-11-01 | 19:30 | 220 | 4 | 2018-11-01 | 15:00
15 | Hathazari | 230 | 227 | 8 | 2018-11-01 | 18:00 | 206 | 5 | 2018-11-01 | 11:00
16 | Megnaghat | 230 | 233 | 15 | 2018-11-01 | 6:00 | 215 | 6 | 2018-11-01 | 11:00
17 | Fenchuganj | 230 | 243 | 23 | 2018-11-01 | 22:00 | 228 | 1 | 2018-11-01 | 10:00
18 | Siddhirganj | 230 | 232 | 23 | 2018-11-01 | 05:00 | 211 | 1 | 2018-11-01 | 12:00
19 | Maniknagar | 230 | 229 | 24 | 2018-11-01 | 6:00 | 209 | 6 | 2018-11-01 | 15:00
20 | Old Airport | 230 | 230 | 24 | 2018-11-01 | 06:00 | 208 | 1 | 2018-11-01 | 10:00
21 | Barisal | 230 | 238 | 13 | 2018-11-01 | 04:00 | 209 | 2 | 2018-11-01 | 21:00
22 | AKSML | 230 | 225 | 30 | 2018-11-01 | 18:30 | 205 | 5 | 2018-11-01 | 11:00
23 | BSRM | 230 | 230 | 21 | 2018-11-01 | 04:00 | 207 | 5 | 2018-11-01 | 11:00
24 | Bibiyana | 230 | 239 | 23 | 2018-11-01 | 22:00 | 225 | 1 | 2018-11-01 | 6:00
25 | Bhulta | 230 | 232 | 24 | 2018-11-01 | 3:00 | 212 | 6 | 2018-11-01 | 11:00
26 | Ashuganj (S) | 230 | 240 | 23 | 2018-11-01 | 9:00 | 227 | 1 | 2018-11-01 | 11:00
27 | Kaliakoir | 230 | 235 | 14 | 2018-11-01 | 22:00 | 214 | 1 | 2018-11-01 | 9:00
132 kV Substation
1 | Siddhirganj | 132 | 139 | 8 | 2018-11-01 | 18:00 | 125 | 14 | 2018-11-01 | 11:00
2 | Munsiganj | 132 | 141 | 11 | 2018-11-01 | 18:00 | 123 | 17 | 2018-11-01 | 12:00
3 | Megnaghat | 132 | 140 | 11 | 2018-11-01 | 18:00 | 124 | 29 | 2018-11-01 | 19:00
4 | Shyampur | 132 | 137 | 6 | 2018-11-01 | 20:00 | 119 | 17 | 2018-11-01 | 12:00
5 | Bhulta | 132 | 136 | 25 | 2018-11-01 | 1:00 | 122 | 29 | 2018-11-01 | 19:00
6 | Madanganj | 132 | 139 | 5 | 2018-11-01 | 18:30 | 118 | 17 | 2018-11-01 | 11:00
7 | Shitalakhya | 132 | 141 | 13 | 2018-11-01 | 18:00 | 119 | 17 | 2018-11-01 | 11:00
8 | Rahim Steal | 132 | 139 | 8 | 2018-11-01 | 18:00 | 125 | 14 | 2018-11-01 | 12:00
9 | Matuail | 132 | 140 | 13 | 2018-11-01 | 8:00 | 124 | 14 | 2018-11-01 | 11:00
10 | Ghorasal | 132 | 140 | 13 | 2018-11-01 | 21:00 | 124 | 3 | 2018-11-01 | 12:00
11 | Narsinghdi | 132 | 141 | 23 | 2018-11-01 | 13:00 | 124 | 3 | 2018-11-01 | 3:00
12 | Haripur (SBU) | 132 | 139 | 6 | 2018-11-01 | 20:00 | 125 | 17 | 2018-11-01 | 12:00
13 | Ullon | 132 | 138 | 14 | 2018-11-01 | 6:00 | 124 | 17 | 2018-11-01 | 11:00
14 | Hasnabad | 132 | 138 | 13 | 2018-11-01 | 08:00 | 122 | 1 | 2018-11-01 | 11:00
15 | Magbazar | 132 | 139 | 14 | 2018-11-01 | 6:00 | 124 | 1 | 2018-11-01 | 11:00
16 | Maniknagar | 132 | 136 | 13 | 2018-11-01 | 4:00 | 121 | 3 | 2018-11-01 | 12:00
17 | Bangabhaban | 132 | 140 | 23 | 2018-11-01 | 18:00 | 117 | 17 | 2018-11-01 | 12:00
18 | Narinda | 132 | 138 | 6 | 2018-11-01 | 7:00 | 124 | 6 | 2018-11-01 | 12:00
19 | Dhanmondi | 132 | 137 | 13 | 2018-11-01 | 20:00 | 124 | 17 | 2018-11-01 | 11:00
20 | Lalbag | 132 | 140 | 23 | 2018-11-01 | 18:00 | 117 | 17 | 2018-11-01 | 12:00
21 | Madartek | 132 | 138 | 6 | 2018-11-01 | 7:00 | 124 | 6 | 2018-11-01 | 12:00
22 | Mirpur | 132 | 140 | 14 | 2018-11-01 | 6:00 | 123 | 1 | 2018-11-01 | 10:00
23 | Kalyanpur | 132 | 140 | 14 | 2018-11-01 | 4:00 | 126 | 17 | 2018-11-01 | 12:00
24 | Gulshan | 132 | 138 | 15 | 2018-11-01 | 6:00 | 123 | 1 | 2018-11-01 | 12:00
25 | Uttara | 132 | 139 | 24 | 2018-11-01 | 2:00 | 121 | 6 | 2018-11-01 | 12:00
26 | Uttara(New) | 132 | 137 | 14 | 2018-11-01 | 2:00 | 122 | 3 | 2018-11-01 | 13:00
27 | Kamrangirchar | 132 | 137 | 12 | 2018-11-01 | 18:00 | 117 | 17 | 2018-11-01 | 11:00
28 | Savar | 132 | 138 | 15 | 2018-11-01 | 6:00 | 121 | 17 | 2018-11-01 | 11:00
29 | Bhasantec | 132 | 139 | 12 | 2018-11-01 | 8:00 | 123 | 17 | 2018-11-01 | 10:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 140 | 14 | 2018-11-01 | 06:00 | 125 | 17 | 2018-11-01 | 10:00
31 | Satmosjid | 132 | 139 | 12 | 2018-11-01 | 06:00 | 125 | 1 | 2018-11-01 | 12:00
32 | Tongi | 132 | 140 | 24 | 2018-11-01 | 4:00 | 125 | 1 | 2018-11-01 | 11:00
33 | Kabirpur | 132 | 139 | 18 | 2018-11-01 | 4:00 | 123 | 20 | 2018-11-01 | 1:00
34 | Basundhara | 132 | 136 | 9 | 2018-11-01 | 13:00 | 120 | 17 | 2018-11-01 | 12:00
35 | Manikganj | 132 | 142 | 24 | 2018-11-01 | 1:00 | 114 | 10 | 2018-11-01 | 12:00
36 | Joydevpur | 132 | 144 | 5 | 2018-11-01 | 13:00 | 131 | 1 | 2018-11-01 | 10:00
37 | New Tongi | 132 | 140 | 24 | 2018-11-01 | 01:00 | 124 | 6 | 2018-11-01 | 12:00
38 | Kodda | 132 | 143 | 10 | 2018-11-01 | 13:00 | 125 | 28 | 2018-11-01 | 12:00
39 | Dhamrai | 132 | 139 | 15 | 2018-11-01 | 06:00 | 127 | 28 | 2018-11-01 | 12:00
40 | Tangail | 132 | 149 | 19 | 2018-11-01 | 1:00 | 128 | 3 | 2018-11-01 | 16:00
41 | Mymensing | 132 | 139 | 18 | 2018-11-01 | 02:00 | 120 | 2 | 2018-11-01 | 12:00
42 | Kishorganj | 132 | 138 | 10 | 2018-11-01 | 09:00 | 112 | 19 | 2018-11-01 | 19:30
43 | Netrokona | 132 | 139 | 18 | 2018-11-01 | 06:00 | 122 | 2 | 2018-11-01 | 13:00
44 | Jamalpur | 132 | 140 | 4 | 2018-11-01 | 08:00 | 116 | 2 | 2018-11-01 | 12:00
45 | Sherpur | 132 | 140 | 15 | 2018-11-01 | 17:00 | 116 | 2 | 2018-11-01 | 13:00
46 | Srimongal | 132 | 143 | 13 | 2018-11-01 | 05:00 | 135 | 3 | 2018-11-01 | 5:00
47 | Shahjibazar | 132 | 142 | 22 | 2018-11-01 | 08:00 | 134 | 2 | 2018-11-01 | 7:00
48 | Fenchuganj | 132 | 140 | 13 | 2018-11-01 | 06:00 | 132 | 29 | 2018-11-01 | 17:00
49 | Khulawara | 132 | 139 | 12 | 2018-11-01 | 6:00 | 132 | 29 | 2018-11-01 | 12:00
50 | Sylhet | 132 | 138 | 6 | 2018-11-01 | 7:00 | 130 | 24 | 2018-11-01 | 16:00
51 | Chattak | 132 | 139 | 14 | 2018-11-01 | 04:00 | 126 | 12 | 2018-11-01 | 11:00
52 | Sunamganj | 132 | 138 | 6 | 2018-11-01 | 07:00 | 125 | 15 | 2018-11-01 | 12:00
53 | Biani Bazar | 132 | 139 | 14 | 2018-11-01 | 5:00 | 131 | 24 | 2018-11-01 | 16:00
54 | Comilla(South) | 132 | 139 | 2 | 2018-11-01 | 8:00 | 124 | 4 | 2018-11-01 | 18:00
55 | Comilla (North) | 132 | 142 | 14 | 2018-11-01 | 20:00 | 130 | 17 | 2018-11-01 | 21:00
56 | Chandpur | 132 | 145 | 10 | 2018-11-01 | 21:00 | 126 | 3 | 2018-11-01 | 18:00
57 | Feni | 132 | 135 | 8 | 2018-11-01 | 22:00 | 117 | 3 | 2018-11-01 | 18:00
58 | Chowmuhani | 132 | 135 | 11 | 2018-11-01 | 09:00 | 120 | 2 | 2018-11-01 | 22:00
59 | Ashuganj | 132 | 144 | 17 | 2018-11-01 | 9:00 | 136 | 2 | 2018-11-01 | 22:00
60 | Daudkandi | 132 | 141 | 11 | 2018-11-01 | 18:00 | 126 | 1 | 2018-11-01 | 11:00
61 | Brahminbaria | 132 | 141 | 10 | 2018-11-01 | 13:00 | 133 | 2 | 2018-11-01 | 12:00
62 | Ramganj | 132 | 137 | 14 | 2018-11-01 | 08.:00 | 120 | 1 | 2018-11-01 | 20:00
63 | Madanhat | 132 | 139 | 29 | 2018-11-01 | 18:00 | 126 | 5 | 2018-11-01 | 11:00
64 | Hathazari | 132 | 136 | 30 | 2018-11-01 | 18:30 | 124 | 29 | 2018-11-01 | 19:00
65 | Khulshi | 132 | 134 | 14 | 2018-11-01 | 20:00 | 120 | 20 | 2018-11-01 | 10:00
66 | Halishahar | 132 | 138 | 11 | 2018-11-01 | 20:00 | 122 | 29 | 2018-11-01 | 19:00
67 | Baraulia | 132 | 135 | 29 | 2018-11-01 | 18:00 | 122 | 7 | 2018-11-01 | 15:00
68 | Sikalbaha | 132 | 138 | 29 | 2018-11-01 | 18:00 | 120 | 2 | 2018-11-01 | 15:00
69 | Dohazari | 132 | 138 | 7 | 2018-11-01 | 18:00 | 123 | 17 | 2018-11-01 | 11:00
70 | Cox'sbazar | 132 | 132 | 7 | 2018-11-01 | 18:00 | 117 | 5 | 2018-11-01 | 18:00
71 | Chandraghona | 132 | 136 | 14 | 2018-11-01 | 19:30 | 124 | 5 | 2018-11-01 | 11:00
72 | Kaptai | 132 | 138 | 29 | 2018-11-01 | 13:00 | 126 | 17 | 2018-11-01 | 10:00
73 | A. Khaer Stl. | 132 | 135 | 20 | 2018-11-01 | 09:00 | 122 | 15 | 2018-11-01 | 10:00
74 | Bakulia | 132 | 135 | 7 | 2018-11-01 | 18:00 | 122 | 15 | 2018-11-01 | 10:00
75 | Julda | 132 | 140 | 7 | 2018-11-01 | 18:00 | 122 | 17 | 2018-11-01 | 12:00
76 | TK Chemical | 132 | 138 | 14 | 2018-11-01 | 20:00 | 126 | 4 | 2018-11-01 | 9:00
77 | Modern Steel | 132 | 135 | 29 | 2018-11-01 | 07:00 | 122 | 3 | 2018-11-01 | 6:00
78 | Shahmirpur | 132 | 137 | 7 | 2018-11-01 | 18:00 | 122 | 17 | 2018-11-01 | 12:00
79 | Khagrachhari | 132 | 136 | 14 | 2018-11-01 | 20:00 | 123 | 10 | 2018-11-01 | 3:00
80 | Matarbari | 132 | 131 | 7 | 2018-11-01 | 18:00 | 119 | 5 | 2018-11-01 | 18:00
81 | Baroiar Hat | 132 | 135 | 9 | 2018-11-01 | 17:00 | 123 | 4 | 2018-11-01 | 15:00
82 | Rangamati | 133 | 136 | 14 | 2018-11-01 | 20:00 | 123 | 20 | 2018-11-01 | 9:00
83 | Goalpara | 132 | 139 | 11 | 2018-11-01 | 22:00 | 124 | 26 | 2018-11-01 | 12:00
84 | Khulna Central | 132 | 139 | 8 | 2018-11-01 | 18:00 | 123 | 27 | 2018-11-01 | 12:00
85 | Noapara | 132 | 138 | 16 | 2018-11-01 | 17:00 | 121 | 2 | 2018-11-01 | 21:00
86 | Jessore | 132 | 137 | 29 | 2018-11-01 | 6:00 | 117 | 18 | 2018-11-01 | 20:00
87 | Jhenida | 132 | 136 | 9 | 2018-11-01 | 6:00 | 120 | 1 | 2018-11-01 | 18:00
88 | Bottail | 132 | 142 | 22 | 2018-11-01 | 4:00 | 127 | 14 | 2018-11-01 | 18:00
89 | G.K.Project | 132 | 143 | 3 | 2018-11-01 | 04:00 | 128 | 29 | 2018-11-01 | 10:00
90 | Faridpur | 132 | 138 | 13 | 2018-11-01 | 4:00 | 125 | 17 | 2018-11-01 | 19:00
91 | Madaripur | 132 | 138 | 29 | 2018-11-01 | 5:00 | 125 | 2 | 2018-11-01 | 21:00
92 | Gopalganj | 132 | 141 | 27 | 2018-11-01 | 1700:00 | 123 | 2 | 2018-11-01 | 18:00
93 | Bagerhat | 132 | 140 | 4 | 2018-11-01 | 22:00 | 120 | 27 | 2018-11-01 | 12:00
94 | Mongla | 132 | 136 | 6 | 2018-11-01 | 22:00 | 119 | 27 | 2018-11-01 | 12:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
95 | Satkhira | 132 | 138 | 13 | 2018-11-01 | 17:00 | 121 | 2 | 2018-11-01 | 21:00
96 | Gallamari | 132 | 139 | 3 | 2018-11-01 | 21:00 | 124 | 26 | 2018-11-01 | 12:00
97 | Magura | 132 | 140 | 29 | 2018-11-01 | 18:00 | 117 | 5 | 2018-11-01 | 18:00
98 | Chuadanga | 132 | 138 | 29 | 2018-11-01 | 3:00 | 112 | 1 | 2018-11-01 | 18:00
99 | Barisal | 132 | 142 | 26 | 2018-11-01 | 6:00 | 125 | 11 | 2018-11-01 | 13:00
100 | Patuakhali | 132 | 140 | 15 | 2018-11-01 | 5:00 | 120 | 2 | 2018-11-01 | 21:00
101 | Bhandaria | 132 | 140 | 5 | 2018-11-01 | 8:00 | 121 | 2 | 2018-11-01 | 21:00
102 | Ishurdi | 132 | 142 | 25 | 2018-11-01 | 4:00 | 130 | 29 | 2018-11-01 | 1:00
103 | Ruppur paromanobik | 132 | 142 | 8 | 2018-11-01 | 14:00 | 131 | 20 | 2018-11-01 | 19:30
104 | Natore | 132 | 140 | 9 | 2018-11-01 | 2:00 | 121 | 11 | 2018-11-01 | 12:00
105 | Bogra | 132 | 139 | 29 | 2018-11-01 | 19:00 | 124 | 3 | 2018-11-01 | 18:30
106 | Noagaon | 132 | 138 | 29 | 2018-11-01 | 19:00 | 117 | 3 | 2018-11-01 | 13:00
107 | Rajshahi | 132 | 141 | 29 | 2018-11-01 | 7:00 | 122 | 11 | 2018-11-01 | 12:00
108 | C.Nawabganj | 132 | 140 | 29 | 2018-11-01 | 2:00 | 113 | 11 | 2018-11-01 | 12:00
109 | Amnura | 132 | 140 | 13 | 2018-11-01 | 17:00 | 115 | 11 | 2018-11-01 | 12:00
110 | Pabna | 132 | 138 | 30 | 2018-11-01 | 2:00 | 128 | 2 | 2018-11-01 | 18:30
111 | Shahjadpur | 132 | 143 | 10 | 2018-11-01 | 4:00 | 132 | 11 | 2018-11-01 | 12:00
112 | Serajganj | 132 | 139 | 24 | 2018-11-01 | 6:00 | 128 | 1 | 2018-11-01 | 18:30
113 | Niyamatpur | 132 | 137 | 29 | 2018-11-01 | 1:00 | 116 | 3 | 2018-11-01 | 12:00
114 | Joypurhat | 132 | 138 | 29 | 2018-11-01 | 3:00 | 119 | 3 | 2018-11-01 | 12:00
115 | Rangpur | 132 | 136 | 9 | 2018-11-01 | 16:00 | 115 | 3 | 2018-11-01 | 20:00
116 | Lalmonirhat | 132 | 141 | 29 | 2018-11-01 | 18:00 | 108 | 3 | 2018-11-01 | 19:00
117 | Saidpur | 132 | 140 | 29 | 2018-11-01 | 9:00 | 113 | 3 | 2018-11-01 | 18:00
118 | Purbasadipur | 132 | 135 | 11 | 2018-11-01 | 6:00 | 113 | 30 | 2018-11-01 | 18:00
119 | Thakurgaon | 132 | 134 | 27 | 2018-11-01 | 1:00 | 102 | 28 | 2018-11-01 | 19:00
120 | Palashbari | 132 | 140 | 29 | 2018-11-01 | 1:00 | 115 | 1 | 2018-11-01 | 18:00
121 | Barapukuria | 132 | 136 | 29 | 2018-11-01 | 18:00 | 118 | 7 | 2018-11-01 | 20:00
122 | Panchagar | 132 | 139 | 29 | 2018-11-01 | 1:00 | 101 | 30 | 2018-11-01 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:November' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 140 | 420
IP-299421 | Hasnabad | TR2 | 225 | 130 | 420 | 25.11.18 | 12:00
|  | TR3 | 225 | 125 | 400
|  | TR1 | 225 | 170 | 505
IP-299866 | Tongi | TR2 | 225 | 170 | 505 | 04.11.18 | 18:30
|  | TR3 | 225 | 170 | 505
|  | TR1 | 225 | 127 | 425
IP-299427 | Haripur | TR2 | 225 |  |  | 05.11.18 | 02:00 | S/D
|  | TR3 | 225 | 127 | 425
|  | TR1 | 225 | 155 | 475
IP-299728 | Rampura | TR2 | 225 | 155 | 475 | 05.11.18 | 12:00
|  | TR3 | 225 | 155 | 475
|  | TR1 | 225 | 93 | 266
IP-299264 | Aminbazar | TR2 | 225 | 93 | 266 | 26.11.18 | 14:00
|  | TR3 | 225 | 97 | 280
| Maniknagar | TR1 | 300 | 103 | 320 | 04.11.18 | 13:00
|  | TR2 | 300 | 103 | 320
IP-399266 | Cumilla (N) | TR1 | 225 | 140 | 400 | 05.11.18 | 20:00
|  | TR2 | 225 | 147 | 408
| Fenchuganj | TR1 | 300 | 249 | 628 | 10.11.18 | 7:00
|  | TR1 | 150 | 90 | 260
IP-399428 | Hathazari | TR3 | 150 | 90 | 260 | 24.11.18 | 18:00
|  | TR4 | 150 | 90 | 260
|  | TR1 | 225 | 144 | 410
| Ishurdi | TR2 | 225 | 144 | 410 | 16.11.18 | 20:00
IP-499474 |  | TR3 | 225 | 144 | 410
| Khulna(S) | TR1 | 225 | 153 | 418
IP-58001/58002 |  | TR2 | 225 | 153 | 418 | 02.11.18 | 21:00
| Bogra | TR1 | 225 | 112 | 310 | 22.11.18 | 19:30
|  | TR2 | 225 | 112 | 310
IP-43002/499264 |  | TR3 | 225 | 150 | 409
IP-499224 | Baghabari | TR1 | 225 | 140 | 430 | 01.11.18 | 20:00
| Barapukuria | TR1 | 225 | 150 | 720 | 03.11.18 | 18:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 118 | 540 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 134 | 695
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 253 | 503 | 07.11.18 | 7:15
|  | TR1(400/132 kV) | 325 | 137 | 230 | 07.11.18 | 7:15
|  | TR2(400/132 kV) | 325 | 137 | 230
| Bibiyana | ICT1(400/230 kV) | 520 | 147 | 245 | 28.11.18 | 18:00
|  | ICT2(400/230kV) | 520 | 147 | 244
| Bhulta | ATR1(400/230 kV) | 520 | 197 | 338 | 06.11.18 | 14:15
|  | ATR2(400/230kV) | 520 | 197 | 338
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:November' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:November' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-11-18 | 9670 | 9670 | - | - | - | - | - | - | - | - | - | - | - | - | 01-11-18 | 7922.3 | 7922.3 | - | - | - | - | - | - | - | - | - | - | - | -
02-11-18 | 8751 | 8751 | - | - | - | - | - | - | - | - | - | - | - | - | 02-11-18 | 6547.2 | 6547.2 | - | - | - | - | - | - | - | - | - | - | - | -
03-11-18 | 9760 | 9760 | - | - | - | - | - | - | - | - | - | - | - | - | 03-11-18 | 7768.7 | 7768.7 | - | - | - | - | - | - | - | - | - | - | - | -
04-11-18 | 9900 | 9900 | - | - | - | - | - | - | - | - | - | - | - | - | 04-11-18 | 7905.5 | 7905.5 | - | - | - | - | - | - | - | - | - | - | - | -
05-11-18 | 9454 | 9454 | - | - | - | - | - | - | - | - | - | - | - | - | 05-11-18 | 8017 | 8017 | - | - | - | - | - | - | - | - | - | - | - | -
06-11-18 | 9667 | 9667 | - | - | - | - | - | - | - | - | - | - | - | - | 06-11-18 | 7646.7 | 7646.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-11-18 | 9256 | 9256 | - | - | - | - | - | - | - | - | - | - | - | - | 07-11-18 | 7255.61 | 7255.61 | - | - | - | - | - | - | - | - | - | - | - | -
08-11-18 | 8956 | 8956 | - | - | - | - | - | - | - | - | - | - | - | - | 08-11-18 | 7388.1 | 7388.1 | - | - | - | - | - | - | - | - | - | - | - | -
09-11-18 | 7724 | 7724 | - | - | - | - | - | - | - | - | - | - | - | - | 09-11-18 | 5790.9 | 5790.9 | - | - | - | - | - | - | - | - | - | - | - | -
10-11-18 | 8723 | 8723 | - | - | - | - | - | - | - | - | - | - | - | - | 10-11-18 | 6680 | 6680 | - | - | - | - | - | - | - | - | - | - | - | -
11-11-18 | 8724 | 8724 | - | - | - | - | - | - | - | - | - | - | - | - | 11-11-18 | 6601.1 | 6601.1 | - | - | - | - | - | - | - | - | - | - | - | -
12-11-18 | 8815 | 8815 | - | - | - | - | - | - | - | - | - | - | - | - | 12-11-18 | 7026.1 | 7026.1 | - | - | - | - | - | - | - | - | - | - | - | -
13-11-18 | 8806 | 8806 | - | - | - | - | - | - | - | - | - | - | - | - | 13-11-18 | 7006.4 | 7006.4 | - | - | - | - | - | - | - | - | - | - | - | -
14-11-18 | 8909 | 8909 | - | - | - | - | - | - | - | - | - | - | - | - | 14-11-18 | 7158.6 | 7158.6 | - | - | - | - | - | - | - | - | - | - | - | -
15-11-18 | 8772 | 8772 | - | - | - | - | - | - | - | - | - | - | - | - | 15-11-18 | 7186.3 | 7186.3 | - | - | - | - | - | - | - | - | - | - | - | -
16-11-18 | 7696 | 7696 | - | - | - | - | - | - | - | - | - | - | - | - | 16-11-18 | 5770.8 | 5770.8 | - | - | - | - | - | - | - | - | - | - | - | -
17-11-18 | 8603 | 8603 | - | - | - | - | - | - | - | - | - | - | - | - | 17-11-18 | 6498.8 | 6498.8 | - | - | - | - | - | - | - | - | - | - | - | -
18-11-18 | 8656 | 8656 | - | - | - | - | - | - | - | - | - | - | - | - | 18-11-18 | 6985.6 | 6985.6 | - | - | - | - | - | - | - | - | - | - | - | -
19-11-18 | 8585 | 8585 | - | - | - | - | - | - | - | - | - | - | - | - | 19-11-18 | 6958.8 | 6958.8 | - | - | - | - | - | - | - | - | - | - | - | -
20-11-18 | 8441 | 8441 | - | - | - | - | - | - | - | - | - | - | - | - | 20-11-18 | 6824.7 | 6824.7 | - | - | - | - | - | - | - | - | - | - | - | -
21-11-18 | 8087 | 8087 | - | - | - | - | - | - | - | - | - | - | - | - | 21-11-18 | 6090.2 | 6090.2 | - | - | - | - | - | - | - | - | - | - | - | -
22-11-18 | 8433 | 8433 | - | - | - | - | - | - | - | - | - | - | - | - | 22-11-18 | 6838.9 | 6838.9 | - | - | - | - | - | - | - | - | - | - | - | -
23-11-18 | 7550 | 7550 | - | - | - | - | - | - | - | - | - | - | - | - | 23-11-18 | 5507.4 | 5507.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-11-19 | 8358 | 8358 | - | - | - | - | - | - | - | - | - | - | - | - | 24-11-19 | 6228.4 | 6228.4 | - | - | - | - | - | - | - | - | - | - | - | -
25-11-20 | 8361 | 8361 | - | - | - | - | - | - | - | - | - | - | - | - | 25-11-20 | 6710 | 6710 | - | - | - | - | - | - | - | - | - | - | - | -
26-11-18 | 8460 | 8460 | - | - | - | - | - | - | - | - | - | - | - | - | 26-11-18 | 6712.8 | 6712.8 | - | - | - | - | - | - | - | - | - | - | - | -
27-11-18 | 8502 | 8502 | - | - | - | - | - | - | - | - | - | - | - | - | 27-11-18 | 6719.7 | 6719.7 | - | - | - | - | - | - | - | - | - | - | - | -
28-11-18 | 8516 | 8516 | - | - | - | - | - | - | - | - | - | - | - | - | 28-11-18 | 6971.3 | 6971.3 | - | - | - | - | - | - | - | - | - | - | - | -
29-11-18 | 8464 | 8464 | - | - | - | - | - | - | - | - | - | - | - | - | 29-11-18 | 6762 | 6762 | - | - | - | - | - | - | - | - | - | - | - | -
30-11-18 | 7556 | 7556 | - | - | - | - | - | - | - | - | - | - | - | - | 30-11-18 | 5371 | 5371 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:November' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9900 | 04/11/18 | 19:00
2 | Maximum day peak Genaration | MW | 8017 | 05/11/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 9900 | 04/11/18 | 19:00
4 | Minimum Generation | MW | 4789 | 24/11/18 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8671.8333
6 | Average of the daily day peak Genaration | MW | 6828.3637
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 4890.5982
12 | Total Generation by IPP | MKWH | 1270.9862 | % of total Gen. | 25.99%
13 | Total Generation by BPDB | MKWH | 2521.836 | " | 51.56%
14 | A) Total Generation by RPCL | MKWH | 73.3205 | '' | 1.499%
| B) Total Generation by REB | MKWH | 136.7663 | " | 2.797%
| C) Total Generation by RENTAL | MKWH | 409.0027 | " | 8.363%
| D) Total Imported from India (HVDC) | MKWH | 415.0851 | " | 8.487%
| E) Total Imported from Tripura, India (A.C) | MKWH | 63.6013 | " | 1.3%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3478.7833 | % of total Gen. | 71.13%
| B) Oil | MKWH | 771.5633 | '' | 15.78%
| C) Hydro | MKWH | 45.6942 | '' | 0.9343%
| D) Solar | MKWH | 4.0482 | '' | 0.08278%
| E) Coal | MKWH | 111.8229 | '' | 2.286%
| F) HVDC (Import from India) | MKWH | 415.0851 | '' | 8.487%
| G) A.C (Import from Tripura, India) | MKWH | 63.6013 | '' | 1.3%
16 | Maximun of the daily total Generation . | MKWH | 187.6604 | 04/11/18
17 | Monthly Load factor | % | 68.6111
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 8750.6065
| A) Gas | M.Taka | 2602.5955
| B) Liquid fuel | M.Taka | 5716.3746
| C) Coal | M.Taka | 431.6364
| D) HVDC (Import from India) | M.Taka | 2116.9339
| E) Tripura(Import from India) | M.Taka | 435.0329
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 474.6688 | 08/11/18
| A) Gas | M.Taka | 102.0492 | 03/11/18
| B) Liquid fuel | M.Taka | 382.3787 | 08/11/18
| C) Coal | M.Taka | 18.0744 | 20/11/18
| D) HVDC (Import from India) | M.Taka | 84.8529 | 01-11-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.6657
| B) Excluding Hydro & Solar | Taka/KWHR | 2.6931
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 106.1 | 30/11/18 | 06:00
b) | Actual | FT (MSL) | 100.32 | 30/11/18 | 06:00
22 | Peak Genaration of November 2017 | MW | 9015 | 05/11/17 | 19:00
23 | Peak Demand of November 2017 | MW | 9015 | 05/11/17 | 19:00
24 | Maximum peak Generation recorded upto 30/11/18 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 30/11/18 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 30/11/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.