## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | October 2018 |  | September 2018 |  | October 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11485 | 02/10/18 | 11623 | 19/09/18 | 9507 | 18/10/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:30 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 5397.7 | 13/10/18 | 6739.4 | 22/08/18 | 3198 | 21/10/17 | - | -
|  |  | 7:00 |  | 9:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11485 | 02/10/18 | 11623 | 19/09/18 | 9507 | 18/10/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:30 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 9591.9 | 04/10/18 | 9788 | 19/09/18 | 8271.2 | 04/10/17 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 10:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11485 | 02/10/18 | 11623 | 19/09/18 | 9507 | 18/10/17 | 11623 | 19/09/18
|  |  | 19:00 |  | 19:30 |  | 19:30 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 9999.129 |  | 10919.57 |  | 8769.23 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 8021.3387 |  | 8779.26 |  | 7259.49 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India, HVDC (MW) | 772 | 05/10/18 | 788 | 11/09/18 | 501 | 15/10/17 | 788 | 11/09/18
|  |  | 14:00 |  | 22:00 |  | 7:00 |  | 22:00
9 | Maximum Power Import from Tripura, India (MW) | 178 | 06/10/18 | 186 | 18/09/18 | 172 | 04/1017 | 188 | 29/05/18
|  |  | 18:30 |  | 22:00 |  | 19:30 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3330.0147 |  | 3397.09 |  | 2597.56
21 | Station Use of BPDB (MKWH) | 116.2092 |  | 104.37 |  | 110.48
22 | Net Generation of BPDB (MKWH) | 3213.8055 |  | 3292.72 |  | 2487.07
23 | Net Generation of IPP & RPCL (MKWH) | 1451.6527 |  | 1811.95 |  | 1293.69
24 | Net Generation of REB (MKWH) | 142.9173 |  | 147.49 |  | 117.53
24 | Net Generation of Rental Power Plant (MKWH) | 556.8742 |  | 784.35 |  | 1138.93
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5365.2496 |  | 6036.51 |  | 5037.22 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 4224.636 |  | 4212.3 |  | 3531.44 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 233.5553 |  | 428.9 |  | 382.15 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 834.1018 |  | 1333.26 |  | 1058.61 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 69.327 |  | 100.16 |  | 119.14 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 3.1372 |  | 1.8 |  | 0.34 |  | 3.14 | 2018-10-16
31 | Energy Generation by Coal (MKWH) | 116.7015 |  | 64.46 |  | 56.03 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 602.9073 |  | 583.75 |  | 424.41 |  | 458.02 | Aug-18
33 | Monthly Load Factor (%) | 71.2052 |  | 80.36 |  | 78.78 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:October' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11485 | 02/10/18 | 19:00
Generation Period
| Dhaka | MW | 3713
| Chittagong | MW | 1109
| Comilla | MW | 991
| Mymensingh | MW | 772
| Sylhet | MW | 462
a) | Total supply in East zone | MW | 7047
| Khulna | MW | 1372
| Barisal | MW | 267
| Rajshahi | MW | 1097
| Rangpur | MW | 649
b) | Total supply in West zone | MW | 3385
c) | Total supply in both zone ( a+b) | MW | 10432
Ref: | 27.21.2604.603.16.085.18.108 | Date: 19/11/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 600 | 05/10/18 | 5:00
| b) Ishurdi end | MW | 280 | 11/10/18 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 600 | 11/10/18 | 10:00
| b) Ishurdi end | MW | 280 | 05/10/18 | 5:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 2.7935 | 05/10/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 2.4255 | 05/10/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 16.2251
| b) Ishurdi end | MKWH | 42.0858
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 12.7694
| b) Ishurdi end | MKWH | 40.8232
23 | Transmission loss of EWI/ NO-1 | % | 2.4999
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 390 | 05/10/18 | 5:00
| b)Serajganj end | MW | 160 | 31/10/18 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 140 | 31/10/18 | 16:00
| b)Sirajganj end | MW | 320 | 05/10/18 | 5:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.042 | 05/10/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 5.982 | 05/10/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 84.016
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 83.436
30 | Transmission loss of EWI /NO-2 | % | 0.69
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV Transformer-T1 | 2018-10-01 19:27 | 2018-10-01 21:08 | 1:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-10-02 10:20 | 2018-10-02 11:37 | 1:17 | E/O |  | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T1 | 2018-10-03 19:10 | 2018-10-04 05:55 | 10:45 | T | Tripped showing differential & O/C relay | 105 | 84 | Power interruption 19:10 to 19:58
| 132/33 kV Transformer-T2 | 2018-10-03 19:10 | 2018-10-03 19:58 | 0:48 | T | Tripped showing lockout relay
Tongi | 230/132 kV Transformer-T2 | 2018-10-04 12:32 | 2018-10-04 13:08 | 0:36 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformers-T1 & T2 | 2018-10-09 12:46 | 2018-10-09 13:30 | 0:44 | T |  | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-10-19 07:10 | 2018-10-19 09:22 | 2:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 18:03 |  | Unserved Energy: |  | 84
Dhaka (South) Grid Circle :
Bhulta | 132/33 kV Transformer-T1 | 2018-10-01 18:15 | 2018-10-01 18:50 | 0:35 | T | Tripped showing HVTHI,VAJ relay | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformers-T3 & T4 | 2018-10-06 08:30 | 2018-10-06 08:45 | 0:15 | T | Tripped showing O/C relay | 142 | 35.5 | Power interruption
Siddhirganj | 132/33 kV Transformers-T1 & T2 | 2018-10-20 20:38 | 2018-10-20 22:01 | 1:23 | E/O | Due to Emergency work | 112 | 154.9333 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2018-10-22 03:47 | 2018-10-22 04:49 | 1:02 | T | Tripped showing inst.E/F relay | 94 | 97.1333 | Power interruption
Shyampur | 132 kV bus | 2018-10-22 06:25 | 2018-10-22 08:00 | 1:35 | E/O | Due to red hot maintenance | 160 | 253.3333 | Power interruption
Munshiganj | 132/33 kV Transformer-T2 | 2018-10-23 12:54 | 2018-10-24 11:02 | 22:08 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Ghorashal | 230/132 kV Transformers-T1 | 2018-10-23 15:55 | 2018-10-23 16:07 | 0:12 | T | Tripped showing differential & E/F relay | 0 | 0 | No interruption
| 230/132 kV Transformers-T2 | 2018-10-23 15:55 | 2018-10-23 16:16 | 0:21 | T |  | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T1 | 2018-10-26 06:20 | 2018-10-26 09:57 | 3:37 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-27 11:39 | 2018-10-27 22:12 | 10:33 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 41:41 |  | Unserved Energy: |  | 540.9
Chittagong Grid Circle :
Hathazari | 230 kV bus-2 | 2018-10-08 06:50 | 2018-10-08 07:40 | 0:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 230/132 kV Transformer-T4 | 2018-10-17 10:14 | 2018-10-17 12:20 | 2:06 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Kaptai | 132 kV Tie bus | 2018-10-24 11:35 | 2018-10-24 12:28 | 0:53 | E/O | Due to gas filling | 0 | 0 | No interruption
|  |  | Total : | 3:49 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Shahjibazar | 132/33 kV Transformer-T2 | 2018-10-10 10:49 | 2018-10-10 11:00 | 0:11 | T | Tripped showing PRD relay | 30 | 5.5 | Power interruption
Kulaura | 132/33 kV Transformer-T1 | 2018-10-12 20:40 | 2018-10-12 20:59 | 0:19 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2018-10-13 08:11 | 2018-10-13 10:36 | 2:25 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-10-14 09:52 | 2018-10-14 10:40 | 0:48 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 3:43 |  | Unserved Energy: |  | 5.5
Khulna Grid Circle :
Khulna(S) | 230/132 kV Transformer-T2 | 2018-10-10 23:28 | 2018-10-11 12:35 | 13:07 | T | Tripped showing differential relay | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T-2 | 2018-10-16 07:34 | 2018-10-16 07:55 | 0:21 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 0:21 |  | Unserved Energy: |  | 0
HVDC Grid Circle : Nil
|  |  | Total : | 0:00
Bogra Grid Circle:
Barapukuria | 132/33 kV Transformer-T3 | 2018-10-08 14:58 | 2018-10-08 18:10 | 3:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-10-08 14:58 | 2018-10-08 19:35 | 4:37 | T | Tripped showing O/C relay | 28 | 129.2667 | Power interruption
Rajsahahi | 132/33 kV Transformer-T1 | 2018-10-11 02:08 | 2018-10-11 02:32 | 0:24 | T | Tripped showing O/C relay | 92 | 36.8 | Power interruption
Barapukuria | 230/132 kV Transformer-T2, | 2018-10-15 12:45 | 2018-10-15 14:40 | 1:55 | E/O | Due to bursting at L/A | 185 | 354.5833 | Power interruption
| 230/132 kV Transformer-T6 | 2018-10-15 12:45 | 2018-10-15 14:40 | 1:55 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 12:03 |  | Unserved Energy: |  | 520.65
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 79:40 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-10-01 13:05 | 2018-10-01 13:18 | 0:13 | T | Tripped showing dist. relay | 173 | 37.4833 | Power interruption
| Tongi-Kabirpur 132 kV line-2 | 2018-10-01 13:05 | 2018-10-01 13:20 | 0:15 | T
| Tongi-Kabirpur 132 kV line-1 & 2 | 2018-10-05 14:49 | 2018-10-05 14:58 | 0:09 | T | Tripped showing CD,CE,& CSW signal | 120 | 18 | Power interruption 14:49 to 14:58
| Tongi-Uttara 132 kV line | 2018-10-06 05:02 | 2018-10-06 07:02 | 2:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2018-10-09 11:10 | 2018-10-09 11:31 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kadda | Kadda-Kabirpur 132 kV line-1 | 2018-10-17 10:19 | 2018-10-17 12:50 | 2:31 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-10-21 12:25 | 2018-10-21 12:34 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2018-10-24 07:06 | 2018-10-24 12:46 | 5:40 | T | Tripped showing differential relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-10-28 04:06 | 2018-10-28 04:14 | 0:08 | T | Tripped showing CAT,CSW,E/F,CD relay | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-10-30 18:21 | 2018-10-30 23:54 | 5:33 | E/O | Due to bursting at L/A | 0 | 0 | No interruption
|  |  | Total : | 16:59 |  | Unserved Energy: |  | 55.4833
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 132 kV line | 2018-10-01 11:46 | 2018-10-01 11:55 | 0:09 | T | Tripped showing dist. relay | 100 | 15 | Power interruption
Ghorasal | Ghorasal -Ashuganj132 kV line-1 | 2018-10-21 07:50 | 2018-10-21 08:53 | 1:03 | T | Tripped showing dist.relay.at Ashuganj 132 kV bus tripped | 150 | 155 | Power interruption
| Ghorasal -Ashuganj132 kV line-1 | 2018-10-21 07:50 | 2018-10-21 08:52 | 1:02 | T
| Ghorasal-Joydevpur 132 kV line-2 | 2018-10-21 12:34 | 2018-10-22 08:11 | 19:37 | E/O | Due to flashing at PT | 0 | 0 | No interruption
| Ghorasal-Ishurdi 230 kV line-2 | 2018-10-22 15:21 | 2018-10-22 16:05 | 0:44 | T | Tripped showing dist.DT,PTaW signal | 0 | 0 | No interruption
Shyampur | Shyampur-Shyampur(new) 132 kV line-1 | 2018-10-23 06:25 | 2018-10-23 08:00 | 1:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Shyampur-Shyampur(new) 132 kV line-2 | 2018-10-23 06:25 | 2018-10-23 08:45 | 2:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Shyampur-Shyampur(new) 132 kV line-2 | 2018-10-24 06:15 | 2018-10-24 08:38 | 2:23 | E/O | Due to red hot maintenance | 10 | 23.8333 | Power interruption
Rampura | Rampura-Ullon 132 kV line-1 & 2 | 2018-10-25 00:51 | 2018-10-25 02:18 | 1:27 | T | Tripped showing dist. relay | 74 | 107.3 | Power interruption
| Rampura-Gulhsan 132 kV line-2 | 2018-10-29 03:49 | 2018-10-29 04:35 | 0:46 | T | Tripped showing 86T1,T3,Z1signal | 50 | 37.5 | Power interruption
Meghnaghat | Meghnaghat-APR Energy P/S 230 kV line | 2018-10-30 11:40 | 2018-10-30 12:15 | 0:35 | T | Tripped showing under voltage. relay | 0 | 0 | No interruption
|  |  | Total : | 31:41 |  | Unserved Energy: |  | 338.6333
Chittagong Grid Circle :
Juldah | Juldah-Halishahar 132 kV line | 2018-10-01 16:47 | 2018-10-01 16:55 | 0:08 | T | Tripped showing directional & O/C relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-10-14 02:54 | 2018-10-14 03:17 | 0:23 | T | Tripped showing dist. (3-phase)relay | 0 | 0 | No interruption
Khulshi | Khulshi-AKS steel 132 kV line | 2018-10-14 21:50 | 2018-10-14 22:40 | 0:50 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line | 2018-10-15 00:50 | 2018-10-15 09:34 | 8:44 | E/O | Due to breaker problem | 0 | 0 | No interruption
Bakulia | Bakulia-Modern Steel 132 kV line | 2018-10-25 11:17 | 2018-10-25 12:13 | 0:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2018-10-29 23:35 | 2018-10-30 16:37 | 17:02 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Sikalbaha P/S 132 kV line | 2018-10-30 23:25 | 2018-10-31 01:31 | 2:06 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 30:09 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2018-10-01 12:12 | 2018-10-01 12:24 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
B.baria | B.Baria-Ashuganj 132 kV line-1 | 2018-10-04 14:31 | 2018-10-04 15:17 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 | 2018-10-05 11:31 | 2018-10-05 11:43 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2018-10-06 20:50 | 2018-10-06 21:06 | 0:16 | T | Tripped showing Gen trip,DTT2 signal | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-2 | 2018-10-15 14:32 | 2018-10-15 14:52 | 0:20 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2018-10-21 07:50 | 2018-10-21 10:54 | 3:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-B.baria 132 kV line-1 | 2018-10-21 07:50 | 2018-10-21 08:36 | 0:46 | T |  | 0 | 0 | No interruption
| Ashuganj-B.baria 132 kV line-2 | 2018-10-21 07:50 | 2018-10-21 08:27 | 0:37 | T |  | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV line | 2018-10-21 07:50 | 2018-10-21 08:39 | 0:49 | T |  | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-10-30 11:53 | 2018-10-30 12:07 | 0:14 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2018-10-31 05:48 | 2018-10-31 06:06 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Comiila(N) 230 kV line-1 | 2018-10-31 10:43 | 2018-10-31 10:45 | 0:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 7:36 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(C) | Khulna(C)-Bheramra 230 kV line-1 | 2018-09-03 10:12 | 2018-09-03 15:26 | 5:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-10-07 09:56 | 2018-10-07 10:08 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-10-10 12:37 | 2018-10-10 20:58 | 8:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barisal 132 kV line | 2018-10-10 12:36 | 2018-10-10 13:17 | 0:41 | T | Tripped showing dist. relay | 20 | 13.6667 | Power interruption
|  |  | Total : | 14:28 |  | Unserved Energy: |  | 13.6667
HVDC Grid Circle :
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-10-01 08:44 | 2018-10-01 08:51 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:07 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Natore | Natore-Rajshahi 132 kV line-2 | 2018-10-11 02:07 | 2018-10-11 02:44 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogra | Bogra -Barapukuria 230 kV line-1 | 2018-10-15 12:45 | 2018-10-15 13:15 | 0:30 | T | Tripped showing AR block,E/F. relay | 0 | 0 | No interruption
| Bogra -Barapukuria 230 kV line-2 | 2018-10-15 12:45 | 2018-10-15 13:16 | 0:31 | T |  | 0 | 0 | No interruption
|  |  | Total : | 1:01 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 102:01 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: October 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV Transformers-T1 | 2018-10-05 10:02 | 2018-10-05 11:12 | 1:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-10-05 11:23 | 2018-10-05 12:34 | 1:11 | S/O |  | 0 | 0 | No interruption
Kadda | 132 kV bus-1 | 2018-10-06 14:04 | 2018-10-06 15:40 | 1:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2018-10-14 12:36 | 2018-10-14 14:30 | 1:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T1 | 2018-10-22 09:40 | 2018-10-22 16:00 | 6:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-26 10:15 | 2018-10-26 11:24 | 1:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2018-10-27 10:26 | 2018-10-27 18:34 | 8:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2018-10-27 11:35 | 2018-10-27 14:25 | 2:50 | S/O | Due to meter change | 0 | 0 | No interruption
|  |  | Total : | 24:18 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta | 132/33 kV Transformer-T-1 | 2018-10-02 09:35 | 2018-10-02 20:33 | 10:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR1 | 2018-10-13 11:51 | 2018-10-13 15:23 | 3:32 | S/O | Due to loop changing | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-TR2 | 2018-10-20 07:21 | 2018-10-20 15:01 | 7:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T2 | 2018-10-21 07:15 | 2018-10-22 22:46 | 39:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-2 | 2018-10-21 09:15 | 2018-10-21 19:28 | 10:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 71:54 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Hathazari | 230/132 kV Transformer-MT-3 | 2018-10-05 05:53 | 2018-10-05 08:20 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-MT-4 | 2018-10-05 08:52 | 2018-10-05 10:53 | 2:01 | S/O | Due to corrective maintenance work | 0 | 0
Halishahar | 132/33 kV Transformer-T1 | 2018-10-05 08:05 | 2018-10-05 13:05 | 5:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT-4 | 2018-10-05 08:52 | 2018-10-05 10:53 | 2:01 | S/O | Due to corrective maintenance work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T1 | 2018-10-05 08:05 | 2018-10-05 13:05 | 5:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 230 kV bus-2 | 2018-10-06 06:40 | 2018-10-06 07:35 | 0:55 | S/O | Due to corrective maintenance work | 0 | 0 | No interruption
Dohazari | 132 kV main bus | 2018-10-07 07:24 | 2018-10-07 09:34 | 2:10 | S/O |  | 100 | 216.6667 | Power interruption
Madunaghat | 132 kV main bus | 2018-10-08 07:19 | 2018-10-08 09:22 | 2:03 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2018-10-13 06:25 | 2018-10-13 07:10 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV bus-2 | 2018-10-15 06:50 | 2018-10-15 08:35 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformers-MT-1& MT3 | 2018-10-14 06:45 | 2018-10-14 08:35 | 1:50 | S/O | Due to C/M work | 100 | 183.3333 | Power interruption
Rangamati | 132/33 kV Transformer-T1 | 2018-10-20 11:35 | 2018-10-20 12:12 | 0:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2018-10-23 08:24 | 2018-10-23 16:52 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T3 | 2018-10-24 06:20 | 2018-10-24 07:37 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaghrachaori | 132/33 kV Transformer-T1 | 2018-10-25 19:08 | 2018-10-25 19:14 | 0:06 | S/O | Due to Isolator maintenance | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T3 | 2018-10-25 07:20 | 2018-10-25 11:37 | 4:17 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 40:42 |  | Unserved Energy: |  | 400
Comilla Grid Circle :
Bibiyana | 230 kV Bus-2 | 2018-10-03 11:10 | 2018-10-03 21:52 | 10:42 | S/O | Due to project work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2018-10-04 08:25 | 2018-10-04 17:20 | 8:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2018-10-07 07:03 | 2018-10-07 08:40 | 1:37 | S/O | Due to project work | 40 | 64.6667 | Power interruption
Cumilla(S) | 132/33 kV Transformer-T4 | 2018-10-09 07:13 | 2018-10-10 18:05 | 34:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformers-T4 & T6 | 2018-10-15 08:36 | 2018-10-15 09:32 | 0:56 | S/O | Due to project work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T1 | 2018-10-21 08:19 | 2018-10-21 18:30 | 10:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-22 08:16 | 2018-10-22 16:43 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2018-10-23 08:09 | 2018-10-23 16:04 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/132 kV Transformer-T2 | 2018-10-23 09:12 | 2018-10-23 16:56 | 7:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2018-10-24 08:04 | 2018-10-24 15:56 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-ICT2 | 2018-10-24 09:00 | 2018-10-24 16:51 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2018-10-25 09:08 | 2018-10-25 12:45 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2018-10-25 09:08 | 2018-10-25 16:05 | 6:57 | S/O | Due to project work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2018-10-28 08:46 | 2018-10-28 14:43 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 230 kV Bus-1 | 2018-10-28 10:14 | 2018-10-28 17:02 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2018-10-29 08:27 | 2018-10-29 17:24 | 8:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2018-10-29 08:24 | 2018-10-29 13:33 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | 230 kV Bus-1 | 2018-10-29 08:27 | 2018-10-29 17:24 | 8:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2018-10-29 08:24 | 2018-10-29 13:33 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-10-31 08:25 | 2018-10-31 17:15 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total | 167:23 |  | Unserved Energy : |  | 64.6667
Khulna Grid Circle :
Khulna(S) | 230/132 kV Transformer-TR-2 | 2018-10-03 10:04 | 2018-10-03 13:26 | 3:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T1 | 2018-10-05 08:34 | 2018-10-05 09:11 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T2 | 2018-10-05 10:32 | 2018-10-05 11:18 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T2 | 2018-10-08 08:06 | 2018-10-08 12:25 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2018-10-14 11:15 | 2018-10-14 16:06 | 4:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-10-20 07:17 | 2018-10-20 17:30 | 10:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-22 07:25 | 2018-10-22 13:28 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-23 07:36 | 2018-10-23 14:25 | 6:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T2 | 2018-10-23 10:41 | 2018-10-23 11:37 | 0:56 | S/O | Due to C/M work | 15 | 14 | Power interruption
| 132/33 kV Transformer-T3 | 2018-10-23 09:02 | 2018-10-23 10:30 | 1:28 | S/O | Due to C/M work | 6 | 8.8 | Power interruption
Faridpur | 132 kV bus-B | 2018-10-25 10:15 | 2018-10-25 13:15 | 3:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 | 2018-10-31 09:21 | 2018-10-31 16:06 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 47:03 |  | Unserved Energy : |  | 22.8
HVDC Grid Circle :
Bheramara | 132 kV bus-A | 2018-10-15 07:24 | 2018-10-15 13:22 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2018-10-20 07:05 | 2018-10-20 16:59 | 9:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 | 2018-10-20 16:59 | 2018-10-20 17:59 | 1:00 | S/O | Due to insulator problem | 22 | 2.9333 | Power interruption 16:59 to 17:07
| 132/33 kV Transformers-T2 | 2018-10-20 16:59 | 2018-10-20 17:07 | 0:08 | S/O
| 132/33 kV Transformer-T1 | 2018-10-22 07:04 | 2018-10-22 20:44 | 13:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-10-28 18:04 | 2018-10-28 18:14 | 1:12 | S/O | Due to CT maintenance | 60 | 72 | Power interruption
|  |  | Total : | 27:06 |  | Unserved Energy : |  | 74.9333
Bogra Grid Circle:
Baghabari | 230/132 kV Transformer-T02 | 2018-10-02 06:20 | 2018-10-02 10:28 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T2 | 2018-10-02 08:35 | 2018-10-02 13:30 | 4:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-T1 | 2018-10-02 08:38 | 2018-10-02 12:28 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T1 | 2018-10-03 07:48 | 2018-10-03 15:38 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-04 08:14 | 2018-10-04 14:36 | 6:22 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T2 | 2018-10-07 08:20 | 2018-10-07 15:34 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2018-10-07 08:12 | 2018-10-07 13:23 | 5:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T4 | 2018-10-07 08:35 | 2018-10-07 18:12 | 9:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 132 kV bus-1 & 2 | 2018-10-08 07:15 | 2018-10-08 09:55 | 2:40 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T3 | 2018-10-08 08:04 | 2018-10-08 15:41 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-10-09 08:17 | 2018-10-09 15:25 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T1 | 2018-10-09 08:07 | 2018-10-09 13:38 | 5:31 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2018-10-10 07:43 | 2018-10-10 14:22 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T5 | 2018-10-10 08:45 | 2018-10-10 14:35 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T1 | 2018-10-15 08:24 | 2018-10-15 16:03 | 7:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-10-16 08:31 | 2018-10-16 15:54 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T2 | 2018-10-16 06:29 | 2018-10-16 12:18 | 5:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T2 | 2018-10-17 08:07 | 2018-10-17 14:06 | 5:59 | S/O | Due to SCADA maint.work | 0 | 0 | No interruption
| 132 kV bus | 2018-10-19 08:51 | 2018-10-19 14:35 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T1 | 2018-10-21 08:15 | 2018-10-21 16:21 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T2 | 2018-10-21 09:22 | 2018-10-21 16:01 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132 kV main bus | 2018-10-22 07:17 | 2018-10-22 08:52 | 1:35 | S/O | Due to D/W work | 40 | 63.3333 | Power interruption
Niyamatpur | 132/33 kV Transformer-T1 | 2018-10-22 08:18 | 2018-10-22 12:35 | 4:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2018-10-22 07:50 | 2018-10-22 16:31 | 8:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T2 | 2018-10-24 08:20 | 2018-10-24 16:31 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132 kV mai bus | 2018-10-25 06:55 | 2018-10-25 08:30 | 1:35 | S/O | Due to D/W work | 39 | 61.75 | Power interruption
Niyamatpur | 132/33 kV Transformer-T3 | 2018-10-25 08:16 | 2018-10-25 16:13 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2018-10-25 08:55 | 2018-10-25 12:30 | 3:35 | S/O | Due to A/M work | 10 | 35.8333 | Power interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2018-10-25 09:26 | 2018-10-25 16:20 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T2 | 2018-10-25 15:51 | 2018-10-25 17:13 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 175:58 |  | Unserved Energy : |  | 160.9167
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 554:24 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-10-03 06:08 | 2018-10-03 09:58 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-10-03 07:30 | 2018-10-03 09:02 | 1:32 | S/O | Due to replacement work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-10-07 07:30 | 2018-10-20 16:14 | 320:44 | S/O | Due to project work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2018-10-14 10:12 | 2018-10-16 15:26 | 53:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoire 230 kV line-1 | 2018-10-16 10:06 | 2018-10-16 16:51 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoire 230 kV line-1 | 2018-10-17 08:46 | 2018-10-17 16:28 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-2 | 2018-10-17 08:23 | 2018-10-17 15:10 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2018-10-17 09:36 | 2018-10-17 19:57 | 10:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoire 230 kV line-1 | 2018-10-18 09:17 | 2018-10-18 15:18 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-2 | 2018-10-18 09:16 | 2018-10-18 14:38 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoire 230 kV line-2 | 2018-10-22 09:43 | 2018-10-22 16:52 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-2 | 2018-10-24 11:15 | 2018-10-24 17:40 | 6:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2018-10-27 08:35 | 2018-10-27 13:36 | 5:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-2 | 2018-10-30 10:33 | 2018-10-30 16:47 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Bosila P/S 132 kV line | 2018-10-31 07:28 | 2018-10-31 16:57 | 9:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi P/S | Tongi P/S-Tongi S/S 132 kV line | 2018-10-31 09:05 | 2018-10-31 15:05 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 462:17 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Ghorashal | Ghorashal-Narsingdi 132 kV line | 2018-10-01 06:17 | 2018-10-01 18:20 | 12:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | Shyampur-Bramangaon 132 kV line | 2018-10-05 08:27 | 2018-10-05 18:00 | 9:33 | S/O | Due to project work | 0 | 0 | No interruption
| Shyampur-Bramangaon P/S 132 kV line | 2018-10-06 06:30 | 2018-10-06 17:20 | 10:50 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line | 2018-10-11 07:11 | 2018-10-12 10:08 | 26:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line | 2018-10-13 08:33 | 2018-10-13 23:23 | 14:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2018-10-15 08:49 | 2018-10-15 11:29 | 2:40 | S/O | Due to project work | 0 | 0 | No interruption
Shyampur(Old) | Shyampur(Old)-Shyampur (new) 132 kV line | 2018-10-19 06:07 | 2018-10-19 10:14 | 4:07 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line | 2018-10-19 06:52 | 2018-10-19 09:41 | 2:49 | S/O | Due to corrective maintenance | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-2 | 2018-10-20 06:58 | 2018-10-20 15:01 | 8:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2018-10-20 07:12 | 2018-10-20 11:20 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line | 2018-10-20 06:15 | 2018-10-20 19:07 | 12:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-10-20 10:58 | 2018-10-20 13:33 | 2:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | Shyampur-Bramangaon Aggreko 132 kV line | 2018-10-20 17:42 | 2018-10-20 19:07 | 1:25 | S/O | Due to conductor maintenance | 150 | 212.5 | Power interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2018-10-25 08:39 | 2018-10-25 15:20 | 6:41 | S/O | Due to corrective maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Mainknagar 230 kV line-1 & 2 | 2018-10-27 08:27 | 2018-10-27 17:27 | 9:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR 230 kV line | 2018-10-28 06:15 | 2018-10-28 16:58 | 10:43 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line-1 | 2018-10-28 06:13 | 2018-10-28 16:57 | 10:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Meghnagat 230 kV line-2 | 2018-10-28 12:42 | 2018-10-28 15:21 | 2:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line | 2018-10-29 05:55 | 2018-10-29 16:36 | 10:41 | S/O | Due to project work | 0 | 0 | No interruption
| Meghnaghat-APR 230 kV line | 2018-10-29 06:04 | 2018-10-29 16:29 | 10:25 | S/O | Due to project work | 0 | 0 | No interruption
| Meghnaghat-APR 230 kV line | 2018-10-30 05:58 | 2018-10-30 17:09 | 11:11 | S/O | Due to project work | 0 | 0 | No interruption
| Meghnaghat-APR 230 kV line | 2018-10-31 06:09 | 2018-10-31 17:16 | 11:07 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line | 2018-10-31 06:14 | 2018-10-31 17:13 | 10:59 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 207:02 |  | Unserved Energy: |  | 212.5
Chittagong Grid Circle :
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2018-10-04 09:27 | 2018-10-04 12:57 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV line | 2018-10-04 10:42 | 2018-10-04 16:05 | 5:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2018-10-05 06:14 | 2018-10-05 07:53 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV line-1 | 2018-10-06 07:07 | 2018-10-06 08:59 | 1:52 | S/O | Due to correcttive maintenance work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2018-10-06 10:10 | 2018-10-21 11:22 | 361:12 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 & 2 | 2018-10-07 07:24 | 2018-10-07 09:34 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-1 | 2018-10-07 07:12 | 2018-10-07 09:36 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-2 | 2018-10-07 07:12 | 2018-10-07 09:38 | 2:26 | S/O |  | 0 | 0 | No interruption
Chanraghona | Chanraghona-Khagrachori 132 kV line-1 | 2018-10-08 07:16 | 2018-10-08 16:03 | 8:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV line-2 | 2018-10-10 10:25 | 2018-10-10 12:50 | 2:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-2 | 2018-10-17 08:11 | 2018-10-17 17:30 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaptai-Chandraghona 132 kV line-2 | 2018-10-18 08:14 | 2018-10-18 16:37 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-BSRM 132 kV line | 2018-10-19 09:32 | 2018-10-19 14:05 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-1 | 2018-10-21 09:56 | 2018-10-21 15:27 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2018-10-22 09:12 | 2018-10-22 13:05 | 3:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2018-10-23 08:23 | 2018-10-23 16:14 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2018-10-24 08:35 | 2018-10-24 16:27 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-1 | 2018-10-25 08:15 | 2018-10-25 15:32 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-AKSPL 132 kV line-1 | 2018-10-25 09:20 | 2018-10-25 14:54 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Baraulia-BSRM 132 kV line | 2018-10-25 09:05 | 2018-10-25 16:51 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2018-10-28 08:51 | 2018-10-28 16:06 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2018-10-31 09:03 | 2018-10-31 17:22 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 475:21 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 | 2018-10-01 11:05 | 2018-10-01 19:11 | 8:06 | S/O | Due to project work | 0 | 0 | No interruption
| Feni-Chowmuhani 132 kV line-2 | 2018-10-05 07:06 | 2018-10-05 07:36 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-10-05 10:38 | 2018-10-05 12:47 | 2:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2018-10-08 08:35 | 2018-10-08 16:40 | 8:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-2 | 2018-10-08 10:10 | 2018-10-08 17:18 | 7:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-1 | 2018-10-10 07:45 | 2018-10-10 11:42 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-11 08:39 | 2018-10-11 17:20 | 8:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-12 08:51 | 2018-10-12 17:28 | 8:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-10-12 11:01 | 2018-10-12 12:04 | 1:03 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2018-10-12 12:04 | 2018-10-12 12:35 | 0:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | Comiila(S)-Tripura 132 kV line-1 & 2 | 2018-10-13 06:02 | 2018-10-13 17:49 | 11:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-2 | 2018-10-13 06:41 | 2018-10-13 17:09 | 10:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-14 09:12 | 2018-10-14 18:07 | 8:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 | 2018-10-15 08:36 | 2018-10-15 13:50 | 5:14 | S/O | Due to project work | 0 | 0 | No interruption
| Shahjibazar-Sreemongal 132 kV line-2 | 2018-10-15 07:54 | 2018-10-15 13:50 | 5:56 | S/O | Due to project work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 132 kV line-1 | 2018-10-18 07:13 | 2018-10-18 07:33 | 0:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Feni-Cumilla(N) 132 kV line-2 | 2018-10-20 07:09 | 2018-10-20 07:09 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-21 10:10 | 2018-10-21 17:30 | 7:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Pabna 132 kV line | 2018-10-21 08:52 | 2018-10-21 16:20 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-22 10:17 | 2018-10-22 16:29 | 6:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-10-24 09:34 | 2018-10-24 10:12 | 0:38 | S/O | Due to replacement work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2018-10-24 20:57 | 2018-10-24 21:06 | 0:09 | S/O | Due to removing crane | 30 | 4.5 | Power interruption
Ramganj | Ramganj-Chandpur 132 kV line-2 | 2018-10-25 05:30 | 2018-10-25 16:18 | 10:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-27 08:50 | 2018-10-27 16:09 | 7:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV line-2 | 2018-10-27 08:50 | 2018-10-27 20:35 | 11:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroihat 132 kV line-2 | 2018-10-27 08:27 | 2018-10-27 13:19 | 4:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2018-10-30 09:25 | 2018-10-30 13:55 | 4:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-30 10:44 | 2018-10-30 20:28 | 9:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV line-1 | 2018-10-30 10:51 | 2018-10-30 20:28 | 9:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-2 | 2018-10-31 08:27 | 2018-10-31 16:57 | 8:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bibiyana-Fenchuganj 230 kV line-1 | 2018-10-31 08:27 | 2018-10-31 15:57 | 7:30 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 187:49 |  | Unserved Energy: |  | 4.5
Khulna Grid Circle :
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2018-10-07 08:44 | 2018-10-07 16:26 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-10-09 08:52 | 2018-10-09 14:04 | 5:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2018-10-09 06:58 | 2018-10-09 17:47 | 10:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | Khulna(C)-Satkhira 132 kV line-2 | 2018-10-10 09:21 | 2018-10-10 15:24 | 6:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna(C)-Noapara 132 kV line-2 | 2018-10-10 09:34 | 2018-10-10 13:44 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2018-10-15 07:04 | 2018-10-15 16:12 | 9:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-10-15 08:27 | 2018-10-15 16:10 | 7:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna© | Khulna©-225 MW P/S 132 kV line-2 | 2018-10-16 08:26 | 2018-10-16 13:33 | 5:07 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-10-16 09:16 | 2018-10-16 17:25 | 8:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2018-10-16 07:17 | 2018-10-16 15:46 | 8:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-10-17 09:18 | 2018-10-17 17:17 | 7:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2018-10-18 06:37 | 2018-10-18 15:59 | 9:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 & 2 | 2018-10-20 06:06 | 2018-10-20 14:03 | 7:57 | S/O | Due to D/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-10-21 09:11 | 2018-10-21 14:45 | 5:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulna(S)-Satkhira 132 kV line-2 | 2018-10-22 09:59 | 2018-10-22 15:27 | 5:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2018-10-25 07:03 | 2018-10-25 15:50 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 117:39 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Bheramara 230 kV line-1 | 2018-10-04 12:42 | 2018-10-04 16:44 | 4:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-1 | 2018-10-05 05:59 | 2018-10-05 11:26 | 5:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV line | 2018-10-10 08:27 | 2018-10-10 15:14 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 | 2018-10-24 08:12 | 2018-10-24 16:35 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjadpur-Baghabari 132 kV line-1 | 2018-10-25 08:33 | 2018-10-25 16:15 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV line | 2018-10-25 09:29 | 2018-10-25 16:35 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-2 | 2018-10-27 08:44 | 2018-10-27 16:27 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjadpur-Baghabari 132 kV line-2 | 2018-10-28 08:30 | 2018-10-28 15:46 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 54:26 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Baghabari | Baghabari-Ishurdi 132 kV line | 2018-10-02 06:25 | 2018-10-02 19:15 | 12:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Baghabari-Shahjadpur 132 kV line-1 | 2018-10-02 06:25 | 2018-10-02 18:26 | 12:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| Baghabari-Sirajganj 132 kV line | 2018-10-02 06:25 | 2018-10-02 18:30 | 12:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | Bogra-Serajganj 132 kV line-2 | 2018-10-13 08:30 | 2018-10-13 18:13 | 9:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2018-10-14 13:10 | 2018-10-14 13:54 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | Bogra-Serajganj 132 kV line-2 | 2018-10-15 07:23 | 2018-10-15 16:26 | 9:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2018-10-15 08:28 | 2018-10-15 17:07 | 8:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2018-10-15 08:01 | 2018-10-15 09:58 | 1:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Serajganj 132 kV line-2 | 2018-10-16 07:25 | 2018-10-16 15:24 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2018-10-16 08:35 | 2018-10-16 16:26 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 | 2018-10-17 07:26 | 2018-10-17 16:17 | 8:51 | S/O | Due to project work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2018-10-17 08:14 | 2018-10-17 16:44 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogra | Bogra-Serajganj 132 kV line-1 | 2018-10-18 07:27 | 2018-10-18 17:50 | 10:23 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogra-Serajganj 132 kV line-1 | 2018-10-19 07:10 | 2018-10-19 16:50 | 9:40 | S/O | Due to project work | 0 | 0 | No interruption
| Bogra-Serajganj 132 kV line-2 | 2018-10-20 07:20 | 2018-10-20 16:50 | 9:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogra-Confidence P/S 132 kV line | 2018-10-20 10:40 | 2018-10-20 15:05 | 4:25 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 134:11 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 1638:45 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October' 2018
| Area | Previous Month (September 2018) |  |  |  | Current Month (October 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 17 | 4 | 25 | 46 | 11 | 6 | 24 | 41
2 | Dhaka (South) Grid Circle. | 17 | 1 | 16 | 34 | 16 | 6 | 28 | 50
3 | Chittagong Grid Circle. | 5 | 6 | 8 | 19 | 6 | 4 | 38 | 48
4 | Comilla Grid Circle. | 13 | 6 | 18 | 37 | 16 | - | 51 | 67
5 | Khulna Grid Circle. | 15 | 2 | 29 | 46 | 6 | - | 28 | 34
6 | Bheramara HVDC Grid Circle | 5 | 2 | 8 | 15 | 1 | - | 14 | 15
7 | Bogra Grid Circle. | 14 | 5 | 11 | 30 | 6 | 2 | 46 | 54
8 | Others | 2 | - |  | 2 | - | - | - | 0
9 | Total | 88 | 26 | 115 | 229 | 62 | 18 | 229 | 309
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October' 2018
| Area | Previous Month (September 2018) |  |  |  | Current Month (October 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 236.87 | 31.33 | 274.75 | 542.95 | 139.48 | - | - | 139.48
2 | Dhaka ( South) grid circle | 200.58 | - | 26.67 | 227.25 | 447.43 | 432.09 | 212.5 | 1092.02
3 | Chittagong grid circle. | - | - | 51.67 | 51.67 | - | - | 400 | 400
4 | Comilla grid circle. | 23.39 | 125.92 | 186.67 | 335.98 | 5.5 | - | 69.17 | 74.67
5 | Khulna grid circle. | 78 | 18.33 | 156.77 | 253.1 | 13.67 | - | 22.8 | 36.47
6 | Bheramara HVDC grid circle | 1.67 | - | - | 1.67 | - | - | 74.93 | 74.93
7 | Bogra grid circle. | 571.66 | - | - | 571.66 | 166.07 | 354.58 | 160.92 | 681.57
8 | Others |  |  |  | 0 | - | - | - | 0
9 | Total | 1112.17 | 175.58 | 696.53 | 1984.28 | 772.15 | 786.67 | 940.32 | 2499.14
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 | - | 1 | - | 1 | 2 | 84
2 | Dhaka (South) | 5031.6 | 4 | - | 4 | 1 |  | 3 | 540.9
3 | Chittagong | 2042 |  | 2 | 2 | - | - | 2 | 400
4 | Khulna | 2434 |  | 2 | 2 |  | 1 | 1 | 22.8
5 | Bheramara (HVDC) | 2423.3 |  | 2 | 2 | 1 | - | 1 | 74.93
6 | Bogra | 3145.6 | 3 | 2 | 5 | 1 |  | 4 | 681.57
7 | Comilla | 2981 | 1 | 1 | 2 | 1 |  | 1 | 70.17
| Total | 23365.5 | [6 empty] | 1874.37
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.92%
3 | Chittagong | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.96% | [6 empty] | Information Management Division
7 | Comilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 |  | 2 | 2 | - | - | 55.48
2 | Dhaka (South) | 990.29 |  | 5 | 1 | 6 | 1 | 1 | 4 | 551.13
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 1 |  | 1 | 1 | - |  | 13.67
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogra | 1803.3 | 38 | - | - | - | - | - | - | -
7 | Comilla | 1648.16 | 17 |  | 1 | 1 | 1 | - |  | 4.5
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 624.78
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.89%
3 | Chittagong | 99.94%
4 | Khulna | 99.86%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogra | 99.99% | [7 empty] | Information Management Division
7 | Comilla | 99.97% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
October | 12 | - | 3 | 04hr13 min | 1 | 02hr23 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:October' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi (New) | 1 | 0:48 | 105 | 84 | Due to tripping of 132/33 kV Transformers T1 & T2
| 1 | 0:13 | 173 | 37.4833 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
| 1 | 0:09 | 120 | 18
Shyampur | 1 | 0:15 | 142 | 35.5 | Due to tripping of 132/33 kV Transformers T3 & T4
Siddhirganj | 2 | 1:23 | 112 | 154.9333 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 1:02 | 94 | 97.1333
Shyampur | 1 | 1:35 | 160 | 253.3333 | Due to red-hot maintenance of 132 kV bus
Haripur | 1 | 0:09 | 100 | 15 | Due to tripping of Haripur-Bhulta 132 kV line
Ghorashal | 1 | 1:02 | 150 | 155 | Due to tripping of Ghorashal-Ashuganj 132 kV line-1 & 2
Shyampur | 1 | 2:23 | 10 | 23.8333 | Due to red-hot maintenance Shyampur-Shyampur(new) 132 kV line-2
Rampura | 1 | 1:27 | 74 | 107.3 | Due to tripping of Rampura-Ullon 132 kV line-1 & 2
| 1 | 0:46 | 50 | 37.5 | Due to tripping of Rampura-Gulshahn 132 kV line-2
Shyampur | 1 | 1:25 | 150 | 212.5 | Due to S/D of Shyampur-Bramangaon kV line
Dohazari | 1 | 2:10 | 100 | 216.6667 | Due to S/D of Dohazari 132 kV bus
Hathazari | 1 | 1:50 | 100 | 183.3333 | Due to S/D of 230/132 kV Transformer MT1 & MT3
Shahjibazar | 2 | 0:11 | 30 | 5.5 | Due to tripping of 132/33 kV Transformer T2
|  | 1:37 | 40 | 64.6667 | Due to S/D of 132/33 kV Transformer T4
Ashuganj | 1 | 0:09 | 30 | 4.5 | Due to S/D of Ashuganj-Kishoreganj 132 kV line-2
Bhandaria | 1 | 0:41 | 20 | 13.6667 | Due to tripping of Bhandaria-Barisal 132 kV line
Patuakhali | 2 | 0:56 | 15 | 14 | Due to S/D of 132/33 kV Transformer T2
|  | 1:28 | 6 | 8.8 | Due to S/D of 132/33 kV Transformer T3
Jhenidah | 1 | 0:08 | 22 | 2.9333 | Due to S/D of 132/33 kV Transformer T2
| 1 | 1:12 | 60 | 72
Barapukuria | 1 | 4:37 | 28 | 129.2667 | Due to tripping of 132/33 kV Transformer T4
Rajshahi | 1 | 0:24 | 92 | 36.8 | Due to tripping of 132/33 kV Transformer T2
Barapukuria | 1 | 1:55 | 185 | 354.5833 | Due to bursting at 230/132 kV Transformer T2
Sirajganj | 2 | 1:35 | 40 | 63.3333 | Due to S/D of Sirajganj 132 kV bus
|  | 1:35 | 39 | 61.75
Rangpur | 1 | 3:35 | 10 | 35.8333 | Due to S/D of 132/33 kV Transformer T1
| Total unserved energy : |  |  | 2499.15 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 134 | 3 | 2018-10-01 | 15:00
2 | Munsiganj | 197 | 16 | 2018-10-01 | 20:00
3 | Megnaghat | 61 | 24 | 2018-10-01 | 19:30
4 | Shyampur | 185 | 8 | 2018-10-01 | 08:00
5 | Bhulta | 207 | 9 | 2018-10-01 | 20:00
6 | Madanganj | 62 | 17 | 2018-10-01 | 19:00
7 | Shitalakhya | 124 | 1 | 2018-10-01 | 16:00
8 | Rahim steel | 19 | 2 | 2018-10-01 | 18:00
9 | Matuail | 100 | 2 | 2018-10-01 | 9:00
10 | Ghorasal | 92 | 23 | 2018-10-01 | 10:00
11 | Narsingdi | 125 | 1 | 2018-10-01 | 19:30
12 | Haripur (SBU) | 116 | 6 | 2018-10-01 | 24:00
13 | Ullon | 101 | 6 | 2018-10-01 | 14:00
14 | Hasnabad | 211 | 2 | 2018-10-01 | 19:00
15 | Magbazar | 145 | 3 | 2018-10-01 | 13:00
16 | Maniknagar | 112 | 21 | 2018-10-01 | 12:00
17 | Bangabhaban | 44 | 7 | 2018-10-01 | 13:00
18 | Narinda | 90 | 2 | 2018-10-01 | 16:00
19 | Dhanmondi | 153 | 1 | 2018-10-01 | 12:00
20 | Lalbag | 94 | 1 | 2018-10-01 | 13:00
21 | Madartek | 52 | 2 | 2018-10-01 | 21:00
22 | Mirpur | 112 | 3 | 2018-10-01 | 18:30
23 | Kalyanpur | 148 | 3 | 2018-10-01 | 11:00
24 | Gulshan | 152 | 1 | 2018-10-01 | 12:00
25 | Uttara | 95 | 1 | 2018-10-01 | 16:00
26 | Uttara(new) | 8 | 27 | 2018-10-01 | 15:00
27 | Kamrangirchar | 88 | 6 | 2018-10-01 | 13:00
28 | Savar | 141 | 2 | 2018-10-01 | 18:30
29 | Bhasantec | 173 | 3 | 2018-10-01 | 18:00
30 | Agargaon | 52 | 1 | 2018-10-01 | 13:00
31 | Satmosjid | 103 | 1 | 2018-10-01 | 18:30
32 | Tongi | 154 | 2 | 2018-10-01 | 16:00
33 | Kabirpur | 210 | 2 | 2018-10-01 | 15:00
34 | Basundhara | 166 | 7 | 2018-10-01 | 21:00
35 | Manikganj | 103 | 2 | 2018-10-01 | 21:00
36 | Joydevpur | 241 | 7 | 2018-10-01 | 20:00
37 | New Tongi | 110 | 3 | 2018-10-01 | 16:00
38 | Kodda | 267 | 3 | 2018-10-01 | 18:00
39 | Dhamrai | 51 | 3 | 2018-10-01 | 19:30
40 | Tangail | 182 | 4 | 2018-10-01 | 20:00
41 | Mymensing | 257 | 1 | 2018-10-01 | 19:00
42 | Kishorganj | 108 | 7 | 2018-10-01 | 21:00
43 | Netrokona | 85 | 3 | 2018-10-01 | 18:30
44 | Jamalpur | 125 | 2 | 2018-10-01 | 18:30
45 | Sherpur | 82 | 1 | 2018-10-01 | 18:30
46 | Srimongal | 38 | 1 | 2018-10-01 | 18:30
47 | Shahjibazar | 109 | 1 | 2018-10-01 | 19:30
48 | Fenchuganj | 47 | 1 | 2018-10-01 | 18:30
49 | Kulawara | 46 | 2 | 2018-10-01 | 20:00
50 | Sylhet | 139 | 1 | 2018-10-01 | 19:00
51 | Chatak | 28 | 1 | 2018-10-01 | 20:00
52 | Sunamganj | 35 | 1 | 2018-10-01 | 19:00
53 | Bianibazar | 42 | 1 | 2018-10-01 | 19:30
54 | Cumilla (S) | 178 | 6 | 2018-10-01 | 20:00
55 | Cumilla(N) | 123 | 1 | 2018-10-01 | 21:00
56 | Chandpur | 123 | 2 | 2018-10-01 | 19:00
57 | Feni | 133 | 3 | 2018-10-01 | 21:00
58 | Chowmuhani | 194 | 7 | 2018-10-01 | 21:00
59 | Ashuganj | 61 | 2 | 2018-10-01 | 22:00
60 | Daudkandi | 116 | 3 | 2018-10-01 | 18:30
61 | B.Baria | 135 | 1 | 2018-10-01 | 20:00
62 | Ramganj | 38 | 1 | 2018-10-01 | 23:00
63 | Madanhat | 97 | 10 | 2018-10-01 | 18:00
64 | Hathazari | 97 | 1 | 2018-10-01 | 18:30
65 | Khulshi | 200 | 1 | 2018-10-01 | 14:00
66 | Halishahar | 147 | 1 | 2018-10-01 | 15:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Baraulia | 189 | 3 | 2018-10-01 | 5:00
68 | Sikalbaha | 40 | 1 | 2018-10-01 | 17:00
69 | Dohazari | 92 | 3 | 2018-10-01 | 20:00
70 | Cox'sbazar | 74 | 9 | 2018-10-01 | 19:00
71 | Chandraghona | 35 | 7 | 2018-10-01 | 18:30
72 | Kaptai | 6 | 1 | 2018-10-01 | 2:00
73 | A. Khaer Stl. | 20 | 22 | 2018-10-01 | 10:00
74 | Bakulia | 107 | 3 | 2018-10-01 | 18:30
75 | Julda | 23 | 24 | 2018-10-01 | 13:00
76 | TK chemical | 8 | 14 | 2018-10-01 | 11:00
77 | Modern Steel | 17 | 3 | 2018-10-01 | 8:00
78 | Shahmirpur | 32 | 4 | 2018-10-01 | 24:00
79 | Khagrachhari | 21 | 1 | 2018-10-01 | 18:30
80 | Matarbari | 26 | 2 | 2018-10-01 | 21:00
81 | Baroiar Hat | 15 | 3 | 2018-10-01 | 13:00
82 | Abul Khair 230 | 206 | 11 | 2018-10-01 | 17:00
83 | BSRM | 121 | 24 | 2018-10-01 | 13:00
84 | Rangamati | 11 | 14 | 2018-10-01 | 18:00
85 | Goalpara | 38 | 2 | 2018-10-01 | 18:30
86 | Central s/s | 97 | 6 | 2018-10-01 | 19:30
87 | Noapara | 97 | 2 | 2018-10-01 | 19:30
88 | Jashore | 152 | 2 | 2018-10-01 | 18:30
89 | Jhenida | 101 | 1 | 2018-10-01 | 19:00
90 | Bottail | 120 | 2 | 2018-10-01 | 19:00
91 | G.K Project | 57 | 4 | 2018-10-01 | 19:00
92 | Faridpur | 156 | 3 | 2018-10-01 | 19:30
93 | Madaripur | 150 | 3 | 2018-10-01 | 19:30
94 | Gopalganj | 87 | 1 | 2018-10-01 | 19:00
95 | Bagerhat | 81 | 2 | 2018-10-01 | 20:00
96 | Mongla | 40 | 3 | 2018-10-01 | 9:00
97 | Satkhira | 99 | 4 | 2018-10-01 | 21:00
98 | Gallamari | 49 | 3 | 2018-10-01 | 18:30
99 | Magura | 50 | 1 | 2018-10-01 | 18:30
100 | Chuadanga | 78 | 2 | 2018-10-01 | 19:00
101 | Barishal | 120 | 3 | 2018-10-01 | 18:30
102 | Patuakhali | 96 | 1 | 2018-10-01 | 21:00
103 | Bhandaria | 48 | 1 | 2018-10-01 | 21:00
104 | Ishurdi | 55 | 1 | 2018-10-01 | 19:00
105 | Ruppur Paromanobik | 2 | 2 | 2018-10-01 | 19:00
106 | Natore | 115 | 2 | 2018-10-01 | 19:30
107 | Bogura | 244 | 9 | 2018-10-01 | 19:00
108 | Noagaon | 114 | 1 | 2018-10-01 | 21:00
109 | Rajshahi | 149 | 3 | 2018-10-01 | 21:00
110 | C.Nawabganj | 74 | 1 | 2018-10-01 | 19:00
111 | Amnura | 46 | 3 | 2018-10-01 | 1:00
112 | Pabna | 119 | 3 | 2018-10-01 | 20:00
113 | Shahjadpur | 100 | 9 | 2018-10-01 | 20:00
114 | Serajganj | 100 | 3 | 2018-10-01 | 19:30
115 | Niyamatpur | 70 | 10 | 2018-10-01 | 20:00
116 | Joypurhat | 46 | 1 | 2018-10-01 | 21:00
117 | Rangpur | 128 | 2 | 2018-10-01 | 18:30
118 | Lalmonirhat | 88 | 2 | 2018-10-01 | 20:00
119 | Saidpur | 115 | 1 | 2018-10-01 | 18:30
120 | Purbasadipur | 87 | 10 | 2018-10-01 | 19:30
121 | Thakurgaon | 66 | 2 | 2018-10-01 | 20:00
122 | Palashbari | 103 | 2 | 2018-10-01 | 21:00
123 | Barapukuria | 52 | 3 | 2018-10-01 | 20:00
124 | Panchagar | 40 | 2 | 2018-10-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 4189 | 03.10.18 | 18:30
Chittagong | 1191 | 04.10.18 | 22:00
Khulna | 1377 | 02.10.18 | 20:00
Rajshahi | 1171 | 04.10.18 | 19:30
Comilla | 1053 | 06.10.18 | 20:00
Mymensingh | 791 | 06.10.18 | 20:00
Sylhet | 477 | 01.10.18 | 20:00
Barisal | 290 | 03.10.18 | 21:00
Rangpur | 849 | 09.10.18 | 18:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 396 | 5 | 2018-10-01 | 19:00 | 370 | 17 | 2018-09-01 | 12:00
2 | Bheramara | 400 | 407 | 27 | 2018-10-01 | 1500:00 | 388 | 3 | 2018-09-01 | 19:00
3 | Ashuganj(N) | 400 | 399 | 28 | 2018-10-01 | 22:00 | 364 | 17 | 2018-09-01 | 10:00
4 | Kaliakoir | 400 | 372 | 13 | 2018-10-01 | 06:00 | 350 | 7 | 2018-09-01 | 18:30
5 | Bhulta | 400 | 392 | 29 | 2018-10-01 | 7:00 | 360 | 3 | 2018-09-01 | 15:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 5 | 2018-10-01 | 23:00 | 220 | 9 | 2018-10-01 | 11:00
2 | Ishurdi | 230 | 237 | 11 | 2018-10-01 | 6:00 | 223 | 5 | 2018-10-01 | 20:00
3 | Ashuganj | 230 | 238 | 5 | 2018-10-01 | 7:00 | 225 | 20 | 2018-10-01 | 11:00
4 | Serajganj | 230 | 231 | 7 | 2018-10-01 | 6:00 | 214 | 15 | 2018-10-01 | 18:30
5 | Baghabari | 230 | 230 | 5 | 2018-10-01 | 6:00 | 215 | 1 | 2018-10-01 | 18:30
6 | Barapukuria | 230 | 238 | 12 | 2018-10-01 | 5:00 | 212 | 15 | 2018-10-01 | 18:30
7 | Bogra | 230 | 229 | 13 | 2018-10-01 | 6:00 | 199 | 6 | 2018-10-01 | 20:00
8 | Khulna South | 230 | 242 | 13 | 2018-10-01 | 06'00 | 218 | 5 | 2018-10-01 | 3:00
9 | Rampura | 230 | 224 | 14 | 2018-10-01 | 04:00 | 211 | 3 | 2018-10-01 | 12:00
10 | Haripur | 230 | 224 | 29 | 2018-10-01 | 7:00 | 211 | 20 | 2018-10-01 | 12:00
11 | Hasnabad | 230 | 228 | 12 | 2018-10-01 | 9:00 | 208 | 30 | 2018-10-01 | 12:00
12 | Aminbazar | 230 | 225 | 12 | 2018-10-01 | 06:00 | 209 | 31 | 2018-10-01 | 11:00
13 | Tongi | 230 | 225 | 25 | 2018-10-01 | 09:00 | 205 | 14 | 2018-10-01 | 15:00
14 | Comilla (N) | 230 | 235 | 24 | 2018-10-01 | 13:00 | 220 | 2 | 2018-10-01 | 16:00
15 | Hathazari | 230 | 222 | 12 | 2018-10-01 | 8:00 | 210 | 14 | 2018-10-01 | 16:00
16 | Megnaghat | 230 | 228 | 23 | 2018-10-01 | 18:30 | 210 | 20 | 2018-10-01 | 12:00
17 | Fenchuganj | 230 | 240 | 27 | 2018-10-01 | 16:00 | 226 | 3 | 2018-10-01 | 12:00
18 | Siddhirganj | 230 | 226 | 12 | 2018-10-01 | 08:00 | 212 | 3 | 2018-10-01 | 10:00
19 | Maniknagar | 230 | 224 | 29 | 2018-10-01 | 8:00 | 208 | 20 | 2018-10-01 | 15:00
20 | Old Airport | 230 | 226 | 12 | 2018-10-01 | 08:00 | 207 | 31 | 2018-10-01 | 11:00
21 | Barisal | 230 | 226 | 27 | 2018-10-01 | 16:00 | 209 | 3 | 2018-10-01 | 18:00
22 | AKSML | 230 | 221 | 12 | 2018-10-01 | 19:00 | 204 | 14 | 2018-10-01 | 17:00
23 | BSRM | 230 | 224 | 15 | 2018-10-01 | 08:00 | 207 | 14 | 2018-10-01 | 17:00
24 | Bibiyana | 230 | 235 | 28 | 2018-10-01 | 22:00 | 222 | 17 | 2018-10-01 | 12:00
25 | Bhulta | 230 | 227 | 28 | 2018-10-01 | 22:00 | 211 | 3 | 2018-10-01 | 12:00
26 | Ashuganj (S) | 230 | 235 | 22 | 2018-10-01 | 5:00 | 225 | 3 | 2018-10-01 | 11:00
27 | Kaliakoir | 230 | 229 | 23 | 2018-10-01 | 21:00 | 212 | 3 | 2018-10-01 | 16:00
132 kV Substation
1 | Siddhirganj | 132 | 138 | 28 | 2018-10-01 | 18:00 | 120 | 24 | 2018-10-01 | 12:00
2 | Munsiganj | 132 | 140 | 27 | 2018-10-01 | 18:00 | 127 | 16 | 2018-10-01 | 15:00
3 | Megnaghat | 132 | 137 | 25 | 2018-10-01 | 18:00 | 125 | 31 | 2018-10-01 | 9:00
4 | Shyampur | 132 | 137 | 23 | 2018-10-01 | 18:00 | 120 | 20 | 2018-10-01 | 6:00
5 | Bhulta | 132 | 134 | 29 | 2018-10-01 | 18:00 | 120 | 9 | 2018-10-01 | 11:00
6 | Madanganj | 132 | 139 | 23 | 2018-10-01 | 18:00 | 121 | 31 | 2018-10-01 | 18:00
7 | Shitalakhya | 132 | 139 | 1 | 2018-10-01 | 14:00 | 122 | 8 | 2018-10-01 | 17:00
8 | Rahim Steal | 132 | 137 | 2 | 2018-10-01 | 21:00 | 127 | 18 | 2018-10-01 | 12:00
9 | Matuail | 132 | 136 | 2 | 2018-10-01 | 21:00 | 125 | 18 | 2018-10-01 | 12:00
10 | Ghorasal | 132 | 138 | 12 | 2018-10-01 | 18:00 | 114 | 27 | 2018-10-01 | 12:00
11 | Narsinghdi | 132 | 137 | 12 | 2018-10-01 | 18:00 | 117 | 1 | 2018-10-01 | 15:00
12 | Haripur (SBU) | 132 | 138 | 12 | 2018-10-01 | 8:00 | 127 | 22 | 2018-10-01 | 10:00
13 | Ullon | 132 | 138 | 29 | 2018-10-01 | 6:00 | 123 | 3 | 2018-10-01 | 11:00
14 | Hasnabad | 132 | 136 | 10 | 2018-10-01 | 6:00 | 123 | 17 | 2018-10-01 | 10:00
15 | Magbazar | 132 | 137 | 29 | 2018-10-01 | 7:00 | 122 | 3 | 2018-10-01 | 12:00
16 | Maniknagar | 132 | 135 | 12 | 2018-10-01 | 8:00 | 121 | 20 | 2018-10-01 | 12:00
17 | Bangabhaban | 132 | 137 | 12 | 2018-10-01 | 8:00 | 118 | 18 | 2018-10-01 | 12:00
18 | Narinda | 132 | 138 | 12 | 2018-10-01 | 9:00 | 123 | 3 | 2018-10-01 | 11:00
19 | Dhanmondi | 132 | 138 | 29 | 2018-10-01 | 6:00 | 122 | 27 | 2018-10-01 | 12:00
20 | Lalbag | 132 | 137 | 12 | 2018-10-01 | 8:00 | 118 | 18 | 2018-10-01 | 12:00
21 | Madartek | 132 | 138 | 12 | 2018-10-01 | 9:00 | 123 | 3 | 2018-10-01 | 11:00
22 | Mirpur | 132 | 137 | 14 | 2018-10-01 | 3:00 | 120 | 31 | 2018-10-01 | 12:00
23 | Kalyanpur | 132 | 137 | 25 | 2018-10-01 | 4:00 | 123 | 3 | 2018-10-01 | 100:00
24 | Gulshan | 132 | 137 | 29 | 2018-10-01 | 6:00 | 123 | 2 | 2018-10-01 | 16:00
25 | Uttara | 132 | 134 | 29 | 2018-10-01 | 6:00 | 119 | 4 | 2018-10-01 | 12:00
26 | Uttara(New) | 132 | 133 | 10 | 2018-10-01 | 2:00 | 120 | 3 | 2018-10-01 | 11:00
27 | Kamrangirchar | 132 | 136 | 27 | 2018-10-01 | 18:00 | 122 | 4 | 2018-10-01 | 9:00
28 | Savar | 132 | 135 | 26 | 2018-10-01 | 18:00 | 122 | 3 | 2018-10-01 | 12:00
29 | Bhasantec | 132 | 137 | 13 | 2018-10-01 | 6:00 | 123 | 3 | 2018-10-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 138 | 29 | 2018-10-01 | 06:00 | 124 | 3 | 2018-10-01 | 12:00
31 | Satmosjid | 132 | 138 | 30 | 2018-10-01 | 03:00 | 124 | 3 | 2018-10-01 | 12:00
32 | Tongi | 132 | 135 | 28 | 2018-10-01 | 21:00 | 122 | 3 | 2018-10-01 | 16:00
33 | Kabirpur | 132 | 137 | 12 | 2018-10-01 | 14:00 | 119 | 9 | 2018-10-01 | 22:00
34 | Basundhara | 132 | 133 | 29 | 2018-10-01 | 4:00 | 120 | 3 | 2018-10-01 | 16:00
35 | Manikganj | 132 | 139 | 12 | 2018-10-01 | 9:00 | 122 | 1 | 2018-10-01 | 18:00
36 | Joydevpur | 132 | 144 | 12 | 2018-10-01 | 18:00 | 129 | 6 | 2018-10-01 | 14:00
37 | New Tongi | 132 | 136 | 12 | 2018-10-01 | 09:00 | 121 | 3 | 2018-10-01 | 16:00
38 | Kodda | 132 | 142 | 26 | 2018-10-01 | 18:00 | 125 | 6 | 2018-10-01 | 14:00
39 | Dhamrai | 132 | 137 | 13 | 2018-10-01 | 06:00 | 124 | 7 | 2018-10-01 | 18:30
40 | Tangail | 132 | 139 | 12 | 2018-10-01 | 14:00 | 120 | 1 | 2018-10-01 | 18:30
41 | Mymensing | 132 | 137 | 28 | 2018-10-01 | 08:00 | 108 | 5 | 2018-10-01 | 18:30
42 | Kishorganj | 132 | 136 | 28 | 2018-10-01 | 08:00 | 113 | 2 | 2018-10-01 | 20:00
43 | Netrokona | 132 | 137 | 28 | 2018-10-01 | 07:00 | 107 | 7 | 2018-10-01 | 18:30
44 | Jamalpur | 132 | 139 | 12 | 2018-10-01 | 18:00 | 114 | 11 | 2018-10-01 | 22:00
45 | Sherpur | 132 | 138 | 28 | 2018-10-01 | 22:00 | 113 | 11 | 2018-10-01 | 22:00
46 | Srimongal | 132 | 142 | 12 | 2018-10-01 | 18:00 | 130 | 3 | 2018-10-01 | 21:00
47 | Shahjibazar | 132 | 140 | 12 | 2018-10-01 | 18:00 | 128 | 2 | 2018-10-01 | 19:30
48 | Fenchuganj | 132 | 138 | 12 | 2018-10-01 | 09:00 | 129 | 7 | 2018-10-01 | 18:30
49 | Khulawara | 132 | 137 | 12 | 2018-10-01 | 18:00 | 128 | 7 | 2018-10-01 | 19:00
50 | Sylhet | 132 | 137 | 12 | 2018-10-01 | 18:00 | 125 | 7 | 2018-10-01 | 18:30
51 | Chattak | 132 | 137 | 12 | 2018-10-01 | 18:00 | 123 | 7 | 2018-10-01 | 18:30
52 | Sunamganj | 132 | 136 | 18 | 2018-10-01 | 02:00 | 122 | 7 | 2018-10-01 | 18:30
53 | Biani Bazar | 132 | 137 | 12 | 2018-10-01 | 18:00 | 124 | 7 | 2018-10-01 | 18:00
54 | Comilla(South) | 132 | 131 | 31 | 2018-10-01 | 24:00 | 118 | 7 | 2018-10-01 | 18:30
55 | Comilla (North) | 132 | 139 | 12 | 2018-10-01 | 8:00 | 131 | 2 | 2018-10-01 | 15:00
56 | Chandpur | 132 | 140 | 29 | 2018-10-01 | 24:00 | 116 | 1 | 2018-10-01 | 21:00
57 | Feni | 132 | 127 | 31 | 2018-10-01 | 7:00 | 112 | 1 | 2018-10-01 | 21:00
58 | Chowmuhani | 132 | 131 | 29 | 2018-10-01 | 24:00 | 111 | 1 | 2018-10-01 | 21:00
59 | Ashuganj | 132 | 141 | 28 | 2018-10-01 | 8:00 | 126 | 1 | 2018-10-01 | 1:00
60 | Daudkandi | 132 | 138 | 3 | 2018-10-01 | 19:00 | 126 | 4 | 2018-10-01 | 9:00
61 | Brahminbaria | 132 | 139 | 28 | 2018-10-01 | 18:00 | 124 | 2 | 2018-10-01 | 21:00
62 | Ramganj | 132 | 133 | 30 | 2018-10-01 | 21.:00 | 111 | 2 | 2018-10-01 | 18:30
63 | Madanhat | 132 | 135 | 12 | 2018-10-01 | 02:00 | 125 | 29 | 2018-10-01 | 16:00
64 | Hathazari | 132 | 133 | 15 | 2018-10-01 | 7:00 | 124 | 14 | 2018-10-01 | 16:00
65 | Khulshi | 132 | 130 | 12 | 2018-10-01 | 18:00 | 120 | 14 | 2018-10-01 | 14:00
66 | Halishahar | 132 | 134 | 15 | 2018-10-01 | 7:00 | 122 | 14 | 2018-10-01 | 16:00
67 | Baraulia | 132 | 132 | 12 | 2018-10-01 | 19:30 | 122 | 14 | 2018-10-01 | 16:00
68 | Sikalbaha | 132 | 133 | 12 | 2018-10-01 | 18:00 | 123 | 14 | 2018-10-01 | 16:00
69 | Dohazari | 132 | 132 | 12 | 2018-10-01 | 18:00 | 120 | 8 | 2018-10-01 | 7:00
70 | Cox'sbazar | 132 | 136 | 16 | 2018-10-01 | 7:00 | 113 | 2 | 2018-10-01 | 18:00
71 | Chandraghona | 132 | 133 | 12 | 2018-10-01 | 18:30 | 123 | 12 | 2018-10-01 | 13:00
72 | Kaptai | 132 | 134 | 12 | 2018-10-01 | 08:00 | 123 | 2 | 2018-10-01 | 21:00
73 | A. Khaer Stl. | 132 | 132 | 12 | 2018-10-01 | 18:00 | 120 | 31 | 2018-10-01 | 11:00
74 | Bakulia | 132 | 132 | 15 | 2018-10-01 | 07:00 | 121 | 14 | 2018-10-01 | 17:00
75 | Julda | 132 | 133 | 12 | 2018-10-01 | 19:00 | 122 | 11 | 2018-10-01 | 11:00
76 | TK Chemical | 132 | 135 | 12 | 2018-10-01 | 19:00 | 124 | 11 | 2018-10-01 | 16:00
77 | Modern Steel | 132 | 131 | 12 | 2018-10-01 | 19:00 | 121 | 14 | 2018-10-01 | 16:00
78 | Shahmirpur | 132 | 132 | 5 | 2018-10-01 | 08:00 | 122 | 11 | 2018-10-01 | 15:00
79 | Khagrachhari | 132 | 133 | 12 | 2018-10-01 | 18:30 | 123 | 12 | 2018-10-01 | 21:00
80 | Matarbari | 132 | 132 | 13 | 2018-10-01 | 14:00 | 115 | 27 | 2018-10-01 | 18:00
81 | Baroiar Hat | 132 | 132 | 12 | 2018-10-01 | 09:00 | 119 | 1 | 2018-10-01 | 18:00
82 | Rangamati | 133 | 132 | 19 | 2018-10-01 | 19:00 | 124 | 27 | 2018-10-01 | 12:00
83 | Goalpara | 132 | 140 | 16 | 2018-10-01 | 5:00 | 125 | 20 | 2018-10-01 | 11:00
84 | Khulna Central | 132 | 139 | 11 | 2018-10-01 | 9:00 | 125 | 21 | 2018-10-01 | 8:00
85 | Noapara | 132 | 137 | 4 | 2018-10-01 | 18:00 | 124 | 5 | 2018-10-01 | 03:00
86 | Jessore | 132 | 133 | 12 | 2018-10-01 | 8:00 | 120 | 2 | 2018-10-01 | 18:30
87 | Jhenida | 132 | 136 | 11 | 2018-10-01 | 7:00 | 116 | 2 | 2018-10-01 | 20:00
88 | Bottail | 132 | 140 | 13 | 2018-10-01 | 4:00 | 125 | 2 | 2018-10-01 | 20:00
89 | G.K.Project | 132 | 144 | 13 | 2018-10-01 | 05:00 | 132 | 5 | 2018-10-01 | 20:00
90 | Faridpur | 132 | 137 | 11 | 2018-10-01 | 6:00 | 122 | 2 | 2018-10-01 | 21:00
91 | Madaripur | 132 | 140 | 20 | 2018-10-01 | 5:00 | 123 | 3 | 2018-10-01 | 20:00
92 | Gopalganj | 132 | 141 | 11 | 2018-10-01 | 6:00 | 119 | 7 | 2018-10-01 | 18:30
93 | Bagerhat | 132 | 140 | 11 | 2018-10-01 | 6:00 | 120 | 20 | 2018-10-01 | 11:00
94 | Mongla | 132 | 137 | 11 | 2018-10-01 | 6:00 | 120 | 20 | 2018-10-01 | 11:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
95 | Satkhira | 132 | 138 | 10 | 2018-10-01 | 6:00 | 123 | 20 | 2018-10-01 | 12:00
96 | Gallamari | 132 | 139 | 10 | 2018-10-01 | 6:00 | 124 | 13 | 2018-10-01 | 17:00
97 | Magura | 132 | 137 | 11 | 2018-10-01 | 8:00 | 115 | 2 | 2018-10-01 | 18:30
98 | Chuadanga | 132 | 134 | 11 | 2018-10-01 | 9:00 | 108 | 2 | 2018-10-01 | 20:00
99 | Barisal | 132 | 142 | 11 | 2018-10-01 | 6:00 | 131 | 1 | 2018-10-01 | 15:00
100 | Patuakhali | 132 | 140 | 11 | 2018-10-01 | 5:00 | 123 | 26 | 2018-10-01 | 19:30
101 | Bhandaria | 132 | 141 | 11 | 2018-10-01 | 7:00 | 125 | 20 | 2018-10-01 | 11:00
102 | Ishurdi | 132 | 142 | 12 | 2018-10-01 | 8:00 | 126 | 19 | 2018-10-01 | 11:00
103 | Ruppur paromanobik | 132 | 143 | 14 | 2018-10-01 | 1:00 | 131 | 5 | 2018-10-01 | 20:00
104 | Natore | 132 | 138 | 13 | 2018-10-01 | 6:00 | 122 | 2 | 2018-10-01 | 20:00
105 | Bogra | 132 | 136 | 12 | 2018-10-01 | 5:00 | 113 | 1 | 2018-10-01 | 19:00
106 | Noagaon | 132 | 133 | 12 | 2018-10-01 | 6:00 | 107 | 4 | 2018-10-01 | 19:30
107 | Rajshahi | 132 | 136 | 15 | 2018-10-01 | 6:00 | 118 | 2 | 2018-10-01 | 20:00
108 | C.Nawabganj | 132 | 135 | 12 | 2018-10-01 | 18:00 | 117 | 31 | 2018-10-01 | 18:30
109 | Amnura | 132 | 139 | 13 | 2018-10-01 | 18:00 | 118 | 31 | 2018-10-01 | 20:00
110 | Pabna | 132 | 136 | 7 | 2018-10-01 | 16:00 | 118 | 10 | 2018-10-01 | 12:00
111 | Shahjadpur | 132 | 143 | 13 | 2018-10-01 | 4:00 | 107 | 2 | 2018-10-01 | 12:00
112 | Serajganj | 132 | 138 | 14 | 2018-10-01 | 6:00 | 111 | 2 | 2018-10-01 | 10:00
113 | Niyamatpur | 132 | 132 | 12 | 2018-10-01 | 6:00 | 101 | 4 | 2018-10-01 | 19:30
114 | Joypurhat | 132 | 135 | 12 | 2018-10-01 | 6:00 | 105 | 4 | 2018-10-01 | 19:30
115 | Rangpur | 132 | 134 | 12 | 2018-10-01 | 4:00 | 101 | 1 | 2018-10-01 | 18:30
116 | Lalmonirhat | 132 | 135 | 12 | 2018-10-01 | 5:00 | 90 | 1 | 2018-10-01 | 18:30
117 | Saidpur | 132 | 135 | 12 | 2018-10-01 | 6:00 | 99 | 2 | 2018-10-01 | 18:30
118 | Purbasadipur | 132 | 139 | 16 | 2018-10-01 | 7:00 | 109 | 10 | 2018-10-01 | 19:00
119 | Thakurgaon | 132 | 132 | 13 | 2018-10-01 | 6:00 | 100 | 1 | 2018-10-01 | 18:30
120 | Palashbari | 132 | 134 | 12 | 2018-10-01 | 12:00 | 100 | 1 | 2018-10-01 | 18:30
121 | Barapukuria | 132 | 138 | 12 | 2018-10-01 | 5:00 | 112 | 15 | 2018-10-01 | 18:30
122 | Panchagar | 132 | 131 | 12 | 2018-10-01 | 6:00 | 95 | 1 | 2018-10-01 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:October' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 136 | 455
IP-299421 | Hasnabad | TR2 | 225 | 124 | 445 | 08.10.18 | 17:00
|  | TR3 | 225 | 122 | 420
|  | TR1 | 225 | 190 | 600
IP-299866 | Tongi | TR2 | 225 | 190 | 600 | 08.10.18 | 18:00
|  | TR3 | 225 | 190 | 600
|  | TR1 | 225 | 139 | 420
IP-299427 | Haripur | TR2 | 225 |  |  | 18.10.18 | 02:00 | S/D
|  | TR3 | 225 | 139 | 420
|  | TR1 | 225 | 170 | 525
IP-299728 | Rampura | TR2 | 225 | 170 | 525 | 09.10.18 | 13:00
|  | TR3 | 225 | 170 | 525
|  | TR1 | 225 | 134 | 400
IP-299264 | Aminbazar | TR2 | 225 | 134 | 400 | 03.10.18 | 19:00
|  | TR3 | 225 | 139 | 414
| Maniknagar | TR1 | 300 | 117 | 360 | 01.10.18 | 18:00
|  | TR2 | 300 | 117 | 360
IP-399266 | Cumilla (N) | TR1 | 225 | 165 | 500 | 15.10.18 | 18:00
|  | TR2 | 225 | 165 | 480
| Fenchuganj | TR1 | 300 | 244 | 636 | 31.10.18 | 8:00
|  | TR1 | 150 | 133 | 370
IP-399428 | Hathazari | TR3 | 150 | 133 | 370 | 02.10.18 | 20:00
|  | TR4 | 150 | 133 | 370
|  | TR1 | 225 | 150 | 450
| Ishurdi | TR2 | 225 | 150 | 450 | 05.10.18 | 5:00
IP-499474 |  | TR3 | 225 | 150 | 450
| Khulna(S) | TR1 | 225 | 150 | 410
IP-58001/58002 |  | TR2 | 225 | 150 | 410 | 05.10.18 | 5:00
| Bogra | TR1 | 225 | 133 | 406 | 02.10.18 | 14:00
|  | TR2 | 225 | 133 | 406
IP-43002/499264 |  | TR3 | 225 | 180 | 543
IP-499224 | Baghabari | TR1 | 225 | 166 | 550 | 08.10.18 | 8:00
| Barapukuria | TR1 | 225 | 150 | 900 | 02.10.18 | 19:30 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 122 | 640 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 152 | 821
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
| Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 278.9 | 537 | 20.10.18 | 9:15
|  | TR1(400/132 kV) | 325 | 221.3 | 410 | 01.10.18 | 18:15
|  | TR2(400/132 kV) | 325 | 221.8 | 408
| Bibiyana | ICT1(400/230 kV) | 520 | 170 | 301 | 18.10.18 | 12:00
|  | ICT2(400/230kV) | 520 | 172 | 298
| Bhulta | ATR1(400/230 kV) | 520 | 179 | 312 | 22.10.18 | 15:30
|  | ATR2(400/230kV) | 520 | 180 | 313
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:October' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:October' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-10-18 | 11198 | 11198 | - | - | - | - | - | - | - | - | - | - | - | - | 01-10-18 | 9532.8 | 9532.8 | - | - | - | - | - | - | - | - | - | - | - | -
02-10-18 | 11485 | 11485 | - | - | - | - | - | - | - | - | - | - | - | - | 02-10-18 | 9227.2 | 9227.2 | - | - | - | - | - | - | - | - | - | - | - | -
03-10-18 | 11472 | 11472 | - | - | - | - | - | - | - | - | - | - | - | - | 03-10-18 | 9498.1 | 9498.1 | - | - | - | - | - | - | - | - | - | - | - | -
04-10-18 | 11394 | 11394 | - | - | - | - | - | - | - | - | - | - | - | - | 04-10-18 | 9591.9 | 9591.9 | - | - | - | - | - | - | - | - | - | - | - | -
05-10-18 | 10548 | 10548 | - | - | - | - | - | - | - | - | - | - | - | - | 05-10-18 | 8271 | 8271 | - | - | - | - | - | - | - | - | - | - | - | -
06-10-18 | 11431 | 11431 | - | - | - | - | - | - | - | - | - | - | - | - | 06-10-18 | 9091.1 | 9091 | - | - | - | - | - | - | - | - | - | - | - | -
07-10-18 | 11400 | 11400 | - | - | - | - | - | - | - | - | - | - | - | - | 07-10-18 | 9086.3 | 9086 | - | - | - | - | - | - | - | - | - | - | - | -
08-10-18 | 11205 | 11205 | - | - | - | - | - | - | - | - | - | - | - | - | 08-10-18 | 9028.3 | 9028.3 | - | - | - | - | - | - | - | - | - | - | - | -
09-10-18 | 10891 | 10891 | - | - | - | - | - | - | - | - | - | - | - | - | 09-10-18 | 8722.1 | 8722.1 | - | - | - | - | - | - | - | - | - | - | - | -
10-10-18 | 9966 | 9966 | - | - | - | - | - | - | - | - | - | - | - | - | 10-10-18 | 8081 | 8081 | - | - | - | - | - | - | - | - | - | - | - | -
11-10-18 | 9110 | 9110 | - | - | - | - | - | - | - | - | - | - | - | - | 11-10-18 | 7199.3 | 7199.3 | - | - | - | - | - | - | - | - | - | - | - | -
12-10-18 | 8103 | 8103 | - | - | - | - | - | - | - | - | - | - | - | - | 12-10-18 | 6052.1 | 6052.1 | - | - | - | - | - | - | - | - | - | - | - | -
13-10-18 | 8830 | 8830 | - | - | - | - | - | - | - | - | - | - | - | - | 13-10-18 | 6948.2 | 6948.2 | - | - | - | - | - | - | - | - | - | - | - | -
14-10-18 | 9456 | 9456 | - | - | - | - | - | - | - | - | - | - | - | - | 14-10-18 | 7300.4 | 7300.4 | - | - | - | - | - | - | - | - | - | - | - | -
15-10-18 | 9862 | 9862 | - | - | - | - | - | - | - | - | - | - | - | - | 15-10-18 | 8012.3 | 8012.3 | - | - | - | - | - | - | - | - | - | - | - | -
16-10-18 | 9886 | 9886 | - | - | - | - | - | - | - | - | - | - | - | - | 16-10-18 | 7746.1 | 7746.1 | - | - | - | - | - | - | - | - | - | - | - | -
17-10-18 | 9821 | 9821 | - | - | - | - | - | - | - | - | - | - | - | - | 17-10-18 | 7863.8 | 7863.8 | - | - | - | - | - | - | - | - | - | - | - | -
18-10-18 | 9842 | 9842 | - | - | - | - | - | - | - | - | - | - | - | - | 18-10-18 | 8102.8 | 8102.8 | - | - | - | - | - | - | - | - | - | - | - | -
19-10-18 | 9086 | 9086 | - | - | - | - | - | - | - | - | - | - | - | - | 19-10-18 | 6786.4 | 6786.4 | - | - | - | - | - | - | - | - | - | - | - | -
20-10-18 | 10158 | 10158 | - | - | - | - | - | - | - | - | - | - | - | - | 20-10-18 | 7755.8 | 7755.8 | - | - | - | - | - | - | - | - | - | - | - | -
21-10-18 | 10286 | 10286 | - | - | - | - | - | - | - | - | - | - | - | - | 21-10-18 | 8222.9 | 8222.9 | - | - | - | - | - | - | - | - | - | - | - | -
22-10-18 | 10237 | 10237 | - | - | - | - | - | - | - | - | - | - | - | - | 22-10-18 | 8321 | 8321 | - | - | - | - | - | - | - | - | - | - | - | -
23-10-18 | 10198 | 10198 | - | - | - | - | - | - | - | - | - | - | - | - | 23-10-18 | 8353 | 8353 | - | - | - | - | - | - | - | - | - | - | - | -
24-10-19 | 10075 | 10075 | - | - | - | - | - | - | - | - | - | - | - | - | 24-10-19 | 8374.9 | 8374.9 | - | - | - | - | - | - | - | - | - | - | - | -
25-10-20 | 9582 | 9582 | - | - | - | - | - | - | - | - | - | - | - | - | 25-10-20 | 8111.9 | 8111.9 | - | - | - | - | - | - | - | - | - | - | - | -
26-10-18 | 8584 | 8584 | - | - | - | - | - | - | - | - | - | - | - | - | 26-10-18 | 6716.9 | 6716.9 | - | - | - | - | - | - | - | - | - | - | - | -
27-10-18 | 9879 | 9879 | - | - | - | - | - | - | - | - | - | - | - | - | 27-10-18 | 7390.2 | 7390 | - | - | - | - | - | - | - | - | - | - | - | -
28-10-18 | 8651 | 8651 | - | - | - | - | - | - | - | - | - | - | - | - | 28-10-18 | 7231 | 7231 | - | - | - | - | - | - | - | - | - | - | - | -
29-10-18 | 8776 | 8776 | - | - | - | - | - | - | - | - | - | - | - | - | 29-10-18 | 7159 | 7159 | - | - | - | - | - | - | - | - | - | - | - | -
30-10-18 | 9101 | 9101 | - | - | - | - | - | - | - | - | - | - | - | - | 30-10-18 | 7247.5 | 7247.5 | - | - | - | - | - | - | - | - | - | - | - | -
31-10-19 | 9460 | 9460 | [12 empty] | 31-10-19 | 7636.2 | 7636.2

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11485 | 02/10/18 | 19:00
2 | Maximum day peak Genaration | MW | 9591.9 | 04/10/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 11485 | 02/10/18 | 19:00
4 | Minimum Generation | MW | 5397.7 | 13/10/18 | 7:00
5 | Average of the daily evening peak Genaration | MW | 10017.1
6 | Average of the daily day peak Genaration | MW | 8021.3387
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6084.3661
12 | Total Generation by IPP | MKWH | 1396.1584 | % of total Gen. | 22.95%
13 | Total Generation by BPDB | MKWH | 3330.0147 | " | 54.73%
14 | A) Total Generation by RPCL | MKWH | 55.4943 | '' | 0.9121%
| B) Total Generation by REB | MKWH | 142.9173 | " | 2.349%
| C) Total Generation by RENTAL | MKWH | 556.8742 | " | 9.153%
| D) Total Imported from India (HVDC) | MKWH | 516.9011 | " | 8.496%
| E) Total Imported from Tripura, India (A.C) | MKWH | 86.0062 | " | 1.414%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4224.636 | % of total Gen. | 69.43%
| B) Oil | MKWH | 1067.6571 | '' | 17.55%
| C) Hydro | MKWH | 69.327 | '' | 1.139%
| D) Solar | MKWH | 3.1372 | '' | 0.05156%
| E) Coal | MKWH | 116.7015 | '' | 1.918%
| F) HVDC (Import from India) | MKWH | 516.9011 | '' | 8.496%
| G) A.C (Import from Tripura, India) | MKWH | 86.0062 | '' | 1.414%
16 | Maximun of the daily total Generation . | MKWH | 239.3922 | 01/10/18
17 | Monthly Load factor | % | 71.2052
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 13264.7191
| A) Gas | M.Taka | 3121.2215
| B) Liquid fuel | M.Taka | 9693.0298
| C) Coal | M.Taka | 450.4678
| D) HVDC (Import from India) | M.Taka | 2636.1955
| E) Tripura(Import from India) | M.Taka | 588.2827
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 809.5001 | 01/10/18
| A) Gas | M.Taka | 142.7166 | 28/10/18
| B) Liquid fuel | M.Taka | 686.341 | 01/10/18
| C) Coal | M.Taka | 17.3642 | 04/10/18
| D) HVDC (Import from India) | M.Taka | 93.5359 | 04-10-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.7957
| B) Excluding Hydro & Solar | Taka/KWHR | 2.8294
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 108.9 | 31/10/18 | 06:00
b) | Actual | FT (MSL) | 102.58 | 31/10/18 | 06:00
22 | Peak Genaration of October 2017 | MW | 9507 | 18/10/17 | 19:30
23 | Peak Demand of October 2017 | MW | 9507 | 18/10/17 | 19:30
24 | Maximum peak Generation recorded upto 31/10/18 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 31/10/18 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 31/10/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.