## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | September 2018 |  | August 2018 |  | September 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11623 | 19/09/18 | 11217 | 13/08/18 | 9431 | 26/09/17 | 11623 | 19/09/18
|  |  | 19:30 |  | 22:00 |  | 21:00 |  | 19:30
2 | Minimum Generation (MW) | 6739.4 | 21/09/18 | 5450.6 | 22/08/18 | 4928 | 02/09/17 | - | -
|  |  | 9:00 |  | 9:00 |  | 10:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11623 | 19/09/18 | 11174 | 13/08/18 | 9431 | 26/09/17 | 11623 | 19/09/18
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 9788 | 19/09/18 | 9621.4 | 19/08/18 | 8684.2 | 28/09/17 | 9788 | 19/09/18
|  |  | 12:00 |  | 12:00 |  | 11:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11623 | 19/09/18 | 11174 | 13/08/18 | 9431 | 26/09/17 | 11623 | 19/09/18
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 10919.5667 |  | 10324.52 |  | 8743.39 |  | 10919.57 | Sept -18
7 | Average Generation (MW) at Day Peak | 8779.26 |  | 8305.85 |  | 7323.81 |  | 8779.26 | Sept -18
8 | Maximum Power Import from India (MW) | 788 | 11/09/18 | 494 | 10/08/18 | 492 | 03/09/17 | 788 | 11/09/18
|  |  | 22:00 |  | 8:00 |  | 2:00 |  | 22:00
9 | Maximum Power Import from Tripura, India (MW) | 186 | 18/09/18 | 188 | 21/08/18 | 168 | 14/09/17 | 188 | 29/05/18
|  |  | 22:00 |  | 21:00 |  | 20:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3397.0912 |  | 3413.62 |  | 2695.82
21 | Station Use of BPDB (MKWH) | 104.3735 |  | 109.14 |  | 102.17
22 | Net Generation of BPDB (MKWH) | 3292.7177 |  | 3304.48 |  | 2593.65
23 | Net Generation of IPP & RPCL (MKWH) | 1811.9534 |  | 1876.55 |  | 1169.93
24 | Net Generation of REB (MKWH) | 147.4859 |  | 142.89 |  | 117.9
24 | Net Generation of Rental Power Plant (MKWH) | 784.3493 |  | 731.21 |  | 1144.63
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6036.5064 |  | 6055.13 |  | 5026.12 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 4212.297 |  | 4226.29 |  | 3432.58 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 428.8996 |  | 549.03 |  | 389.61 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1333.2574 |  | 1252.68 |  | 1107.93 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 100.1635 |  | 125.53 |  | 114.41 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 1.8049 |  | 0.32 |  | 0.17 |  | 1.8
31 | Energy Generation by Coal (MKWH) | 64.4576 |  | 10.42 |  | 83.59 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 583.7488 |  | 458.02 |  | 436.15 |  | 458.02 | Aug-18
33 | Monthly Load Factor (%) | 80.3559 |  | 79.35 |  | 81.95 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11623 | 19/09/18 | 19:30
Generation Period
| Dhaka | MW | 4062
| Chittagong | MW | 1062
| Comilla | MW | 1021
| Mymensingh | MW | 802
| Sylhet | MW | 491
a) | Total supply in East zone | MW | 7438
| Khulna | MW | 1344
| Barisal | MW | 268
| Rajshahi | MW | 1155
| Rangpur | MW | 636
b) | Total supply in West zone | MW | 3403
c) | Total supply in both zone ( a+b) | MW | 10841
Ref: | 27.21.2604.603.16.084.18.102 | Date: 21/10/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 920 | 01/09/18 | 19:00
| b) Ishurdi end | MW | 220 | 21/09/18 | 12:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 500 | 21/09/18 | 12:00
| b) Ishurdi end | MW | 380 | 01/09/18 | 19:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.28 | 01/09/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 5.0684 | 01/09/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 51.7133
| b) Ishurdi end | MKWH | 13.1644
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 12.7694
| b) Ishurdi end | MKWH | 50.3943
23 | Transmission loss of EWI/ NO-1 | % | 2.5506
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 495 | 01/09/18 | 19:00
| b)Serajganj end | MW | 160 | 21/09/18 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 140 | 21/09/18 | 16:00
| b)Sirajganj end | MW | 480 | 01/09/18 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 9.164 | 02/09/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 9.032 | 02/09/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 160.226
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 158.52
30 | Transmission loss of EWI /NO-2 | % | 1.065
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-T1 | 2018-09-08 08:20 | 2018-09-08 08:31 | 0:11 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T2 | 2018-09-10 06:30 | 2018-09-10 07:30 | 1:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T1,T3 & T4 | 2018-09-18 18:47 | 2018-09-18 19:05 | 0:18 | T | Tripped showing O/C relay | 169 | 50.7 | Power interruption
Manikganj | 132/33 kV Transformer-T1 | 2018-09-26 07:06 | 2018-09-26 08:40 | 1:34 | E/O | Due to red hot maintenance | 20 | 31.3333 | Power interruption
Kabirpur | 132/33 kV Transformer-T3 | 2018-09-26 19:59 | 2018-09-26 20:17 | 0:18 | T | Tripped showing O/C relay | 70 | 21 | Power interruption
Tongi(New) | 132/33 kV Transformers-T1,T2, | 2018-09-29 00:41 | 2018-09-29 00:59 | 0:18 | T | Tripped showing O/C & E/F relay | 77 | 23.1 | Power interruption
|  |  | Total : | 3:39 |  | Unserved Energy: |  | 126.1333
Dhaka (South) Grid Circle :
Sonargaon | 132/33 kV Transformer-T2 | 2018-09-02 06:39 | 2018-09-02 17:17 | 10:38 | T | Tripped showing differential relay | 0 | 0 | No interruption
Siddirganj | 230/132 kV Transformer-MTR1 | 2018-09-04 02:27 | 2018-09-04 08:22 | 5:55 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Sonargaon | 132 kV Bus-A | 2018-09-06 00:32 | 2018-09-06 02:25 | 1:53 | T | Tripped showing busbar protcetion relay | 36 | 67.8 | Power interruption
Bhulta | 132/33 kV Transformer-T1 | 2018-09-10 06:52 | 2018-09-10 07:02 | 0:10 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T1 | 2018-09-16 20:37 | 2018-09-16 22:20 | 1:43 | T | Tripped showing REF relay | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T1 | 2018-09-21 19:02 | 2018-09-21 19:13 | 0:11 | T | Tripped showing HVTHI,VAJ relay | 45 | 8.25 | Power interruption
Haripur | 230/132 kV Transformer-T01 | 2018-09-26 11:04 | 2018-09-26 13:29 | 2:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Narisingdi | 132/33 kV Transformer-T2 | 2018-09-27 11:21 | 2018-09-27 12:38 | 1:17 | T | Tripped showing O/C relay | 25 | 32.0833 | Power interruption
Bhulta | 132/33 kV Transformer-T1 | 2018-09-27 11:52 | 2018-09-27 12:35 | 0:43 | T | Tripped showing gen.trip relay | 25 | 17.9167 | Power interruption
|  |  | Total : | 24:55 |  | Unserved Energy: |  | 126.05
Chittagong Grid Circle :
Sikalbaha | 132/33 kV Transformer-T1 | 2018-09-02 09:26 | 2018-09-02 10:06 | 0:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T1 | 2018-09-22 19:52 | 2018-09-22 21:08 | 1:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 0:40 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Comilla (S) | 132/33 kV Transformers-T1 & T2 | 2018-09-01 17:35 | 2018-09-01 18:11 | 0:36 | T | Tripped showing E/F relay | 80 | 48 | Power interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2018-09-10 05:48 | 2018-09-10 06:46 | 0:58 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-09-11 16:00 | 2018-09-11 16:27 | 0:27 | T | Tripped showing back-up protection relay | 0 | 0 | No interruption
Feni | 132/33 kV Transformers-T1 | 2018-09-18 19:57 | 2018-09-18 20:04 | 0:07 | T | Tripped showing O/C relay | 130 | 15.1667 | Power interruption 19:57 to 20:04
| 132/33 kV Transformers-T2 | 2018-09-18 19:57 | 2018-09-18 20:08 | 0:11 | T
Ashuganj | 230 kV bus-2 | 2018-09-22 10:08 | 2018-09-22 10:56 | 0:48 | T | Tripped showing differential relay | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformers-T2 | 2018-09-27 10:15 | 2018-09-27 11:40 | 1:25 | E/O | Due to red hot maintenance | 55 | 77.9167 | Power interruption
|  |  | Total : | 4:32 |  | Unserved Energy: |  | 141.0833
Khulna Grid Circle :
Khulna© | 132/33 kV Transformer-T-1 | 2018-09-01 09:27 | 2018-09-01 10:41 | 1:14 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformers-T1 | 2018-09-12 15:53 | 2018-09-12 16:04 | 0:11 | T | Tripped showing O/C relay | 42 | 7.7 | Power interruption
| 132/33 kV Transformers-T2 | 2018-09-12 15:53 | 2018-09-12 16:05 | 0:12 | T
Nopara | 132/33 kV Transformer-T4 | 2018-09-11 09:06 | 2018-09-11 10:23 | 1:17 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformers-T1 & T2 | 2018-09-12 05:15 | 2018-09-12 06:15 | 1:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformers-T1 & T2 | 2018-09-16 19:57 | 2018-09-16 20:04 | 0:07 | T | Tripped showing REF relay | 154 | 17.9667 | Power interruption
Barisal | 132/33 kV Transformer-T2 | 2018-09-26 07:20 | 2018-09-26 08:15 | 0:55 | E/O | Due to red hot maintenance | 20 | 18.3333 | Power interruption
|  |  | Total : | 4:56 |  | Unserved Energy: |  | 44
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Jhenidah | 132/33 kV Transformer-T1 | 2018-09-25 10:03 | 2018-09-25 11:14 | 1:11 | E/O | Due to Oil leakage | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T2 | 2018-09-26 16:53 | 2018-09-26 16:58 | 0:05 | T | Tripped showing O/C relay | 20 | 1.6667 | Power interruption
|  |  | Total : | 1:16 |  | Unserved Energy: |  | 1.6667
Bogra Grid Circle:
Palashbari | 132/33 kV Transformer-T-2 | 2018-09-02 06:40 | 2018-09-02 10:29 | 3:49 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | 230/132 kV Transformers-T3 | 2018-09-03 19:06 | 2018-09-03 20:16 | 1:10 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2018-09-06 10:20 | 2018-09-06 10:41 | 0:21 | T | Tripped showing differential relay | 11 | 3.85 | Power interruption
Barapukuria | 132/33 kV Transformer-T5 | 2018-09-07 16:50 | 2018-09-07 19:20 | 2:30 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | 230/132 kV Transformers-T1, | 2018-09-12 02:16 | 2018-09-12 02:20 | 0:04 | T | Tripped showing differential relay | 0 | 0 | No interruption
| 230/132 kV Transformers-T2, | 2018-09-12 02:16 | 2018-09-12 02:22 | 0:06 | T |  | 0 | 0 | No interruption
| 230/132 kV Transformers-T1, | 2018-09-12 02:16 | 2018-09-12 09:38 | 7:22 | T |  | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformers-T01 | 2018-09-13 00:59 | 2018-09-13 02:15 | 1:16 | T | Tripped showing O/C relay | 44 | 6.6 | Power interruption
Rangpur | 132/33 kV Transformer-T2 | 2018-09-13 10:07 | 2018-09-13 10:27 | 0:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformers-T1 | 2018-09-21 15:21 | 2018-09-21 15:43 | 0:22 | T | Tripped showing O/C relay | 44 | 16.1333 | Power interruption
| 132/33 kV Transformers-T2 | 2018-09-21 15:21 | 2018-09-21 17:36 | 2:15 | T
Barapukuria | 132/33 kV Transformer-T-4 | 2018-09-22 09:20 | 2018-09-22 10:22 | 1:02 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 20:37 |  | Unserved Energy: |  | 26.5833
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 60:35 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-09-01 11:25 | 2018-09-01 11:39 | 0:14 | T | Tripped showing dist. relay | 146 | 34.0667 | Power interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2018-09-04 13:40 | 2018-09-04 13:47 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2018-09-09 06:24 | 2018-09-09 07:56 | 1:32 | E/O | Due to bursting at L/A | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2018-09-09 13:45 | 2018-09-09 13:59 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2018-09-13 05:36 | 2018-09-13 05:50 | 0:14 | T | Tripped showing dist.(R-phase) relay | 40 | 4 | Power interruption 05:36 to 05:42
| Kaliakoir-Tangail 132 kV line-2 | 2018-09-13 05:36 | 2018-09-13 05:42 | 0:06 | T
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-09-17 12:35 | 2018-09-17 12:44 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 & 2 | 2018-09-18 23:20 | 2018-09-18 23:50 | 0:30 | T |  | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-09-21 08:30 | 2018-09-21 11:37 | 3:07 | E/O | Due to air leakage | 0 | 0 | No interruption
Jamalpur | Jamalpur-Jamalpur Unite 132 kV line-1 | 2018-09-22 12:50 | 2018-09-22 16:18 | 3:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Jamalpur-Jamalpur Unite 132 kV line-2 | 2018-09-22 12:50 | 2018-09-22 13:55 | 1:05 | T | Tripped showing breaker protection relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2018-09-23 12:21 | 2018-09-23 12:59 | 0:38 | T | Tripped showing gen trip.67N. relay | 130 | 82.3333 | Power interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 & 2 | 2018-09-26 08:37 | 2018-09-26 08:50 | 0:13 | T | Tripped showing dist. relay | 100 | 21.6667 | Power interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-09-27 12:19 | 2018-09-27 12:38 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sherpur | Sherpur-Jamalpur unite 132 kV line-1 | 2018-09-28 14:58 | 2018-09-28 15:13 | 0:15 | T | Tripped showing dist. & O/C relay | 0 | 0 | No interruption
|  |  | Total : | 12:11 |  | Unserved Energy: |  | 142.0667
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 132 kV line | 2018-09-04 10:52 | 2018-09-04 11:04 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line | 2018-09-05 02:27 | 2018-09-05 02:57 | 0:30 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
| Siddhirganj-Matuail 132 kV line | 2018-09-06 16:44 | 2018-09-06 16:54 | 0:10 | T | Tripped showing dist. relay | 84 | 14 | Power interruption
Meghnaghat | Meghnaghat-APR 230 kV line | 2018-09-11 16:50 | 2018-09-11 16:59 | 0:09 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
| Meghnaghat-Aminbazar 230 kV line-1 | 2018-09-13 08:33 | 2018-09-13 08:42 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat 132 kV line | 2018-09-13 15:56 | 2018-09-13 16:16 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV line | 2018-09-17 12:44 | 2018-09-17 12:52 | 0:08 | T |  | 79 | 10.5333 | Power interruption
Ghorashal | Ghorashal-Bhulta 132 kV line | 2018-09-25 05:25 | 2018-09-25 06:15 | 0:50 | T | Tripped showing dist. relay | 60 | 50 | Power interruption
| Ghorashal-Narsingdi 132 kV line | 2018-09-28 12:53 | 2018-09-29 10:21 | 21:28 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
|  |  | Total : | 23:56 |  | Unserved Energy: |  | 74.5333
Chittagong Grid Circle :
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2018-09-03 16:00 | 2018-09-03 16:11 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-2 | 2018-09-02 09:14 | 2018-09-02 12:05 | 2:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2018-09-06 06:46 | 2018-09-06 08:45 | 1:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bakulia | Bakulia-Modern steel 132 kV line | 2018-09-10 14:14 | 2018-09-10 14:25 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV line-1 & 2 | 2018-09-20 11:14 | 2018-09-20 12:24 | 1:10 | E/O | Due to fire a house under the 132 kV line | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2018-09-21 09:29 | 2018-09-21 10:22 | 0:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halisahar 132 kV line-1 | 2018-09-23 15:32 | 2018-09-23 15:47 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2018-09-23 15:32 | 2018-09-23 15:47 | 0:15 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Hathazari | Hathazari-Bagerhat 132 kV line-1 | 2018-09-27 11:37 | 2018-09-27 11:58 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 8:06 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Sylhet | Sylhet-Fenchuganj 132 kV line | 2018-09-04 00:29 | 2018-09-04 00:54 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Daudkandi 132 kV line-2 | 2018-09-06 00:32 | 2018-09-06 01:03 | 0:31 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2018-09-06 00:32 | 2018-09-07 19:05 | 42:33 | E/O | Due to breaker bursting | 0 | 0 | No interruption
| Daudkandi-Sonargaon 132 kV line-2 | 2018-09-06 00:32 | 2018-09-07 18:38 | 42:06 | E/O |  | 0 | 0 | No interruption
Chandpur | Chandpur-Ramganj 132 kV line | 2018-09-07 08:28 | 2018-09-07 15:24 | 6:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2018-09-08 11:18 | 2018-09-08 12:08 | 0:50 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line | 2018-09-12 19:26 | 2018-09-12 19:55 | 0:29 | T | Tripped showing dist. relay | 17 | 8.2167 | Power interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2018-09-16 12:13 | 2018-09-16 12:28 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirjganj 230 kV line-1 | 2018-09-18 11:12 | 2018-09-18 11:42 | 0:30 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-1 | 2018-09-22 18:25 | 2018-09-23 04:37 | 10:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Feni 132 kV line-2 | 2018-09-23 08:15 | 2018-09-23 10:34 | 2:19 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2018-09-26 11:49 | 2018-09-26 12:12 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Comiila(N) 230 kV line-1 | 2018-09-28 08:03 | 2018-09-28 08:19 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2018-09-30 11:55 | 2018-09-30 12:10 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 108:00 |  | Unserved Energy: |  | 8.2167
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Bheramra 230 kV line-1 | 2018-09-03 10:12 | 2018-09-03 15:26 | 5:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-09-03 10:25 | 2018-09-03 15:26 | 5:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2018-09-12 15:15 | 2018-09-12 15:26 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Patuakhali 132 kV line | 2018-09-17 21:08 | 2018-09-17 21:15 | 0:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-09-20 13:25 | 2018-09-20 13:53 | 0:28 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-1 | 2018-09-20 13:25 | 2018-09-20 13:45 | 0:20 | T | Tripped showing E/F relay | 157 | 52.3333 | Power interruption
| Khulna©-Noapara 132 kV line-2 | 2018-09-20 13:25 | 2018-09-20 13:45 | 0:20 | T
Khulna(S) | Khulna(S)-Khulna© 132 kV line-1 | 2018-09-20 13:25 | 2018-09-20 13:45 | 0:20 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Khulna(S)-Khulna© 132 kV line-2 | 2018-09-20 13:25 | 2018-09-20 13:46 | 0:21 | T |  | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-2 | 2018-09-20 13:25 | 2018-09-20 13:45 | 0:20 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
|  |  | Total : | 1:41 |  | Unserved Energy: |  | 52.3333
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2018-09-08 14:14 | 2018-09-08 14:42 | 0:28 | T | Tripped showing dist. CAS,CAR,CD signal | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2018-09-12 11:57 | 2018-09-12 12:54 | 0:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2018-09-25 14:37 | 2018-09-26 04:58 | 14:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2018-09-25 14:37 | 2018-09-25 15:13 | 0:36 | T |  | 0 | 0 | No interruption
| Ishuedi-Natore 132 kV line-2 | 2018-09-26 08:52 | 2018-09-26 09:01 | 0:09 | T |  | 0 | 0 | No interruption
|  |  | Total : | 16:31 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Sirajganj | Sirajganj-Baghabari 132 kV line | 2018-09-04 12:42 | 2018-09-04 13:08 | 0:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-09-11 09:02 | 2018-09-11 11:07 | 2:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-2 | 2018-09-12 00:19 | 2018-09-12 00:55 | 0:36 | T | Tripped showing dist. relay | 85 | 51 | Power interruption
| Bogra (new)-Bogra (Old) 132 kV line-1,2 | 2018-09-12 00:59 | 2018-09-12 02:16 | 1:17 | T | Tripped showing dist(B-phase). relay | 385 | 494.0833 | Power interruption
Natore | Natore-Bogra 132 kV line-1 & 2 | 2018-09-13 00:59 | 2018-09-13 02:26 | 1:27 | T | Tripped showing dist. Cat,CE,Cd & E/F relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 & 2 | 2018-09-13 00:59 | 2018-09-13 02:12 | 1:13 | T | Tripped showing dist(B-phase). relay | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 230 kV line-2 | 2018-09-21 07:01 | 2018-09-21 10:32 | 3:31 | T | Tripped showing dist. Cat,CE,Cd & E/F relay | 0 | 0 | No interruption
|  |  | Total : | 10:35 |  | Unserved Energy: |  | 545.0833
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 181:00 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Uttara | 132/33 kV Transformer-T1 | 2018-09-01 12:28 | 2018-09-01 15:45 | 3:17 | S/O | Due to checking work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-09-02 11:45 | 2018-09-02 13:35 | 1:50 | S/O | Due to project work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2018-09-03 07:20 | 2018-09-03 09:35 | 2:15 | S/O | Due to D/W work | 35 | 78.75 | Power interruption
| 132/33 kV Transformer-T1 | 2018-09-04 06:03 | 2018-09-06 21:45 | 63:42 | S/O | Due to project work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2018-09-07 08:29 | 2018-09-07 18:39 | 10:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2018-09-11 08:03 | 2018-09-11 08:23 | 0:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Uttara | 132/33 kV Transformer-T1 | 2018-09-12 11:02 | 2018-09-12 13:42 | 2:40 | S/O | Due to protection work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-09-12 11:50 | 2018-09-12 16:50 | 5:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-2 | 2018-09-14 12:51 | 2018-09-14 17:23 | 4:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2018-09-18 07:40 | 2018-09-18 13:05 | 5:25 | S/O | Due to D/W work | 24 | 130 | Power interruption
Kabirpur | 132/33 kV Transformers-T1 | 2018-09-21 08:56 | 2018-09-21 10:34 | 1:38 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-09-21 10:40 | 2018-09-21 15:58 | 5:18 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 106:07 |  | Unserved Energy: |  | 208.75
Dhaka (South) Grid Circle :
Manikganj | 132/33 kV Transformer-T-2 | 2018-09-01 10:40 | 2018-09-01 12:28 | 1:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T2 | 2018-09-13 07:10 | 2018-09-13 08:30 | 1:20 | S/O | Due to C/M work | 20 | 26.6667 | Power interruption
| 132/33 kV Transformer-T1 | 2018-09-28 08:30 | 2018-09-28 08:57 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 3:35 |  | Unserved Energy: |  | 26.6667
Chittagong Grid Circle :
Juldah | 132 kV bus | 2018-09-13 07:05 | 2018-09-13 09:40 | 2:35 | S/O | Due to D/W work | 20 | 51.6667 | Power interruption
Khagrachori | 132/33 kV Transformer-T1 | 2018-09-11 14:07 | 2018-09-11 15:00 | 0:53 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-09-11 14:01 | 2018-09-11 15:10 | 1:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T02 | 2018-09-27 12:19 | 2018-09-27 15:51 | 3:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 8:09 |  | Unserved Energy: |  | 51.6667
Comilla Grid Circle :
Comiila(N) | 230/132 kV Transformer-T02 | 2018-09-03 08:05 | 2018-09-03 10:29 | 2:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2018-09-24 07:41 | 2018-09-24 08:38 | 0:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-09-24 08:44 | 2018-09-24 10:11 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2018-09-27 11:30 | 2018-09-27 11:45 | 0:15 | S/O | Due to transformer problem | 0 | 0 | No interruption
Shahjbazar | 132/33 kV Transformers-T2,T-4,& T6 | 2018-09-27 09:11 | 2018-09-27 12:55 | 3:44 | S/O | Due to D/W work | 50 | 186.6667 | Power interruption
|  |  | Total | 138:22 |  | Unserved Energy : |  | 186.6667
Khulna Grid Circle :
Khulna(S) | 230/132 kV Transformer-TR-2 | 2018-09-09 16:28 | 2018-09-09 17:48 | 1:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2018-09-11 07:05 | 2018-09-11 08:49 | 1:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2018-09-13 07:21 | 2018-09-13 12:25 | 5:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-09-14 07:48 | 2018-09-14 18:15 | 10:27 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-09-14 07:48 | 2018-09-14 18:15 | 10:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna(s) 132 kV line-1 | 2018-09-15 13:20 | 2018-09-15 17:48 | 4:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Gopalganj | 132 kV bus | 2018-09-21 06:42 | 2018-09-21 08:13 | 1:31 | S/O | Due to D/W work | 40 | 60.6667 | Power interruption
Satkhira | 132/33 kV Transformer-T1 | 2018-09-28 08:08 | 2018-09-28 11:53 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 38:46 |  | Unserved Energy : |  | 60.6667
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Jhenidah | 132/33 kV Transformer-T1 | 2018-09-02 08:30 | 2018-09-02 09:42 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-TR-1 | 2018-09-13 10:12 | 2018-09-13 14:46 | 4:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 5:46 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Barapukuria | 230/132 kV Transformer-TR-1 | 2018-09-10 11:52 | 2018-09-10 13:40 | 1:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 230/132 kV Transformer-TR-1 | 2018-09-11 06:32 | 2018-09-11 09:18 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2018-09-20 08:55 | 2018-09-20 15:40 | 6:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-09-22 08:20 | 2018-09-22 15:58 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-09-24 08:12 | 2018-09-24 15:25 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Noapara | 132 kV bus-B | 2018-09-27 07:10 | 2018-09-27 13:20 | 6:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Panchagar | 132 kV main bus-B | 2018-09-28 07:04 | 2018-09-28 15:10 | 8:06 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 40:26 |  | Unserved Energy : |  | 0
Others :
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 341:11 | Hours
S/O=Schedule Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2018-09-05 13:27 | 2018-09-05 13:37 | 0:10 | S/O | Due to energy meter problem | 0 | 0 | No interruption
| Kaliakoir-Dhamrai 132 kV line-2 | 2018-09-05 13:41 | 2018-09-05 13:51 | 0:10 | S/O |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-09-07 11:27 | 2018-09-07 21:02 | 9:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikgnaj 132 kV line-2 | 2018-09-10 06:37 | 2018-09-10 07:56 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2018-09-12 09:05 | 2018-09-12 12:05 | 3:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2018-09-15 09:00 | 2018-09-15 17:16 | 8:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 & 2 | 2018-09-18 23:20 | 2018-09-18 23:50 | 0:30 | S/O | Due to maintenance work | 132 | 66 | Power interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-09-19 08:42 | 2018-09-19 17:22 | 8:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-1 | 2018-09-25 08:28 | 2018-09-25 18:03 | 9:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2018-09-25 12:27 | 2018-09-25 14:21 | 1:54 | S/O | Due to carryout induction voltage test | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-09-27 08:57 | 2018-09-27 14:57 | 6:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2018-09-28 09:20 | 2018-09-28 12:35 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| Joydevpur-Ghorashal 132 kV line-2 | 2018-09-28 12:37 | 2018-09-28 16:08 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 55:55 |  | Unserved Energy: |  | 66
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj -Siddhirganj P/S 132 kV line-1 | 2018-09-03 14:15 | 2018-09-03 15:51 | 1:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-09-07 08:28 | 2018-09-07 15:24 | 6:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shyampur | Shyampur-Brahmongaon P/S 132 kV line | 2018-09-08 08:52 | 2018-09-08 18:26 | 9:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Shitalakhya | Shitalakhya-Madanganj 132 kV line | 2018-09-08 16:20 | 2018-09-08 22:28 | 6:08 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shyampur | Shyampur-Brahmongaon P/S 132 kV line | 2018-09-21 08:45 | 2018-09-21 19:19 | 10:34 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat IEL | Meghnaghat IEL-Sonargaon 132 kV line | 2018-09-22 09:36 | 2018-09-22 13:14 | 3:38 | S/O | Due to replacement work | 0 | 0 | No interruption
Shyampur | Shyampur-Brahmongaon P/S 132 kV line | 2018-09-22 11:01 | 2018-09-22 17:55 | 6:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line | 2018-09-25 13:30 | 2018-09-25 17:25 | 3:55 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2018-09-27 07:34 | 2018-09-28 13:05 | 29:31 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-09-28 07:33 | 2018-09-28 21:05 | 13:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line | 2018-09-28 08:18 | 2018-09-28 13:23 | 5:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2018-09-29 07:42 | 2018-09-29 12:59 | 5:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Shitalakhya 132 kV line | 2018-09-29 07:13 | 2018-09-29 16:36 | 9:23 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 112:03 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2018-09-06 08:51 | 2018-09-06 10:02 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulshi | Kulshi-Halishahar 132 kV line | 2018-09-15 22:50 | 2018-09-16 07:16 | 8:26 | S/O | Due to project work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2018-09-15 07:40 | 2018-09-15 13:04 | 5:24 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madunaghat-Chandraghona 132 kV line-1 | 2018-09-29 07:16 | 2018-09-29 16:10 | 8:54 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 23:55 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2018-09-06 10:31 | 2018-09-06 14:00 | 3:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Daudkandi 132 kV line-2 | 2018-09-06 10:16 | 2018-09-06 12:24 | 2:08 | S/O | Due to replacement work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-2 | 2018-09-10 13:28 | 2018-09-10 14:24 | 0:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2018-09-13 11:35 | 2018-09-13 15:39 | 4:04 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2018-09-14 08:14 | 2018-09-14 08:14 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-2 | 2018-09-14 08:15 | 2018-09-14 17:53 | 9:38 | S/O |  | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Feni | Feni-Hathazari 132 kV line-2 | 2018-09-21 06:48 | 2018-09-21 16:23 | 9:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Feni-Bagerhat 132 kV line-2 | 2018-09-23 07:05 | 2018-09-23 08:07 | 1:02 | S/O | Due to replacement work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-2 | 2018-09-25 07:17 | 2018-09-25 14:07 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Cumilla(N)-Feni 132 kV line-1 | 2018-09-26 06:12 | 2018-09-26 11:20 | 5:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-2 | 2018-09-27 07:24 | 2018-09-27 13:30 | 6:06 | S/O | Due to project work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2018-09-27 11:31 | 2018-09-27 13:50 | 2:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| Chowmuhani-Ramganj 132 kV line | 2018-09-29 06:15 | 2018-09-29 18:01 | 11:46 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 63:01 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(C) | Khulna©-Khulna(S) 132 kV line-1 | 2018-09-04 07:11 | 2018-09-04 11:42 | 4:31 | S/O | Due to project work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV line-1 | 2018-09-07 06:28 | 2018-09-07 18:31 | 12:03 | S/O | Due to project work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2018-09-07 08:40 | 2018-09-13 15:45 | 151:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | Noapara-Khulna© 132 kV line-1 | 2018-09-07 09:48 | 2018-09-07 12:05 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Noapara-Khulna© 132 kV line-2 | 2018-09-07 12:05 | 2018-09-07 12:57 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-1 | 2018-09-07 09:49 | 2018-09-07 14:38 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gapalganj-Khuna(S) 132 kV line-1 | 2018-09-08 06:28 | 2018-09-09 18:49 | 36:21 | S/O | Due to D/W work | 0 | 0 | No interruption
| Khulna(S)-Gallamari 132 kV line-1 | 2018-09-09 06:26 | 2018-09-09 18:49 | 12:23 | S/O | Due to project work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV line-1 | 2018-09-09 06:26 | 2018-09-09 18:49 | 12:23 | S/O | Due to project work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2018-09-10 06:28 | 2018-09-10 21:28 | 15:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Khulna(S)-Gallamari 132 kV line-1 | 2018-09-11 06:24 | 2018-09-11 18:29 | 12:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-2 | 2018-09-13 06:25 | 2018-09-13 16:28 | 10:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2018-09-14 06:23 | 2018-09-14 18:29 | 12:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Khulna(S)-Gallamari 132 kV line-1 | 2018-09-15 06:32 | 2018-09-15 18:45 | 12:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2018-09-15 07:09 | 2018-09-15 08:53 | 1:44 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Bagerhat-Goalpara 132 kV line-1 | 2018-09-15 07:12 | 2018-09-15 08:47 | 1:35 | S/O | Due to maintenance work | 62 | 96.1 | Power interruption 07:12 to 08:45
| Bagerhat-Goalpara 132 kV line-2 | 2018-09-15 07:12 | 2018-09-15 08:45 | 1:33 | S/O
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2018-09-16 06:23 | 2018-09-16 22:12 | 15:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-2 | 2018-09-21 07:07 | 2018-09-21 15:05 | 7:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna© 132 kV line-2 | 2018-09-24 16:01 | 2018-09-24 17:24 | 1:23 | S/O | Due to protcetion test | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformers-T4 & T5 | 2018-09-30 12:57 | 2018-09-30 17:00 | 4:03 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 332:16 |  | Unserved Energy: |  | 96.1
HVDC Grid Circle :
Bheramara | Bheramara-Kustia 132 kV line-1 | 2018-09-01 07:15 | 2018-09-01 11:19 | 4:04 | S/O | Due to project work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2018-09-08 05:58 | 2018-09-08 12:08 | 6:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Bheramara 400 kV line-1 | 2018-09-08 09:26 | 2018-09-08 12:27 | 3:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | Gallamari-Khulna(S) 132 kV line | 2018-09-12 06:24 | 2018-09-12 18:29 | 12:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 230 kV line-2 | 2018-09-21 15:16 | 2018-09-21 20:44 | 5:28 | S/O | Due to DFDR works | 0 | 0 | No interruption
| Bheramara HVDC-Khulna(S) 230 kV line-1 | 2018-09-23 10:34 | 2018-09-23 18:30 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 38:44 |  | Unserved Energy: |  | 0
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogra Grid Circle :
Amnura | Amnura-C.nawabganj 132 kV line | 2018-09-11 09:02 | 2018-09-11 11:07 | 2:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-1 | 2018-09-21 07:01 | 2018-09-21 08:26 | 1:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-2 | 2018-09-21 08:57 | 2018-09-21 10:25 | 1:28 | S/O | Due to project work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-09-22 08:23 | 2018-09-22 09:04 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 5:39 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 631:33 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September' 2018
| Area | Previous Month (August 2018) |  |  |  | Current Month (September 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 8 | 4 | 32 | 44 | 17 | 4 | 25 | 46
2 | Dhaka (South) Grid Circle. | 9 | 6 | 7 | 22 | 17 | 1 | 16 | 34
3 | Chittagong Grid Circle. | 5 | 6 | 5 | 16 | 5 | 6 | 8 | 19
4 | Comilla Grid Circle. | 18 | 6 | 26 | 50 | 14 | 6 | 18 | 38
5 | Khulna Grid Circle. | 7 | 6 | 20 | 33 | 15 | 2 | 29 | 46
6 | Bheramara HVDC Grid Circle | 4 | 1 | 14 | 19 | 5 | 2 | 8 | 15
7 | Bogra Grid Circle. | 3 | 7 | 11 | 21 | 14 | 5 | 11 | 30
8 | Others | 2 | - | 2 | 4 | - | - | - | 0
9 | Total | 56 | 36 | 117 | 209 | 87 | 26 | 115 | 228
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September' 2018
| Area | Previous Month (August 2018) |  |  |  | Current Month (September 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 73.15 | 193.33 | 407.23 | 673.71 | 236.87 | 31.33 | 274.75 | 542.95
2 | Dhaka ( South) grid circle | 101.43 | - | - | 101.43 | 200.58 | - | 26.67 | 227.25
3 | Chittagong grid circle. | 30.13 | 42.83 | 76.33 | 149.29 | - | - | 51.67 | 51.67
4 | Comilla grid circle. | 603.26 | 59.2 | - | 662.46 | 23.39 | 125.92 | 186.67 | 335.98
5 | Khulna grid circle. | 593.47 | 205.17 | 58.58 | 857.22 | 78 | 18.33 | 156.77 | 253.1
6 | Bheramara HVDC grid circle | 166.27 | 16.67 | 267.07 | 450.01 | 1.67 | - | - | 1.67
7 | Bogra grid circle. | 10.83 | 592.85 | 370.25 | 973.93 | 571.66 | - | - | 571.66
8 | Others | Energy unserved ( MWH ) due to T: -; Energy unserved ( MWH ) due to E/O: -; Energy unserved ( MWH ) due to S/O: -; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1578.54 | 1110.05 | 1179.46 | 3868.05 | 1112.17 | 175.58 | 696.53 | 1984.28
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 4 | 2 | 6 | 4 | - | 2 | 334.88
2 | Dhaka (South) | 5031.6 | 4 | 1 | 5 | 1 | 1 | 3 | 152.72
3 | Chittagong | 2042 | 1 | - | 1 | - | - | 1 | 51.67
4 | Khulna | 2434 | 3 | 1 | 4 | 2 | 1 | 1 | 104.67
5 | Bheramara (HVDC) | 2423.3 | 1 |  | 1 | 1 | - | - | 1.67
6 | Bogra | 3145.6 | 3 |  | 3 | 2 |  | 1 | 26.58
7 | Comilla | 2981 | 3 | 1 | 4 | 1 | 1 | 2 | 327.75
| Total | 23365.5 | [6 empty] | 999.94
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.91%
3 | Chittagong | 99.99%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.9% | [6 empty] | Information Management Division
7 | Comilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 4 | 1 | 5 | 4 | 1 | - | 208.07
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 2 | 1 |  | 74.53
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 1 | 1 | 2 | 1 | - | 1 | 148.43
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogra | 1803.3 | 38 | 2 |  | 2 | - | 1 | 1 | 545.08
7 | Comilla | 1648.16 | 17 | 1 | - | 1 | 1 | - |  | 8.22
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 984.33
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.95%
3 | Chittagong | 99.99%
4 | Khulna | 99.76%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogra | 99.95% | [7 empty] | Information Management Division
7 | Comilla | 99.42% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
September | 15 | - | 3 | 02hr01 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:September' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 0:18 | 169 | 50.7 | Due to tripping of 132/33 kV Transformers T1,T2 & T3
Kabirpur | 1 | 0:18 | 70 | 21 | Due to tripping of 132/33 kV Transformer T3
Tongi (New) | 1 | 0:18 | 77 | 23.1 | Due to tripping of 132/33 kV Transformer T2
Manikganj | 1 | 1:34 | 20 | 31.3333 | Due to tripping of 132/33 kV Transformers T1 & T2
Tongi | 1 | 0:14 | 146 | 34.0667 | Due to tripping of Tongi-Kabirpur 132 kV line-1
Kaliakoir | 1 | 0:06 | 40 | 4 | Due to tripping of kaliakoir-Tangail 132 kV line-1 & 2
Aminbazar | 1 | 0:38 | 130 | 82.3333 | Due to tripping of Aminbazar-Kaliakoir 230 kV line-1
Mymensingh | 1 | 0:13 | 100 | 21.6667 | Due to tripping of Mymensingh-Jamalpur 132 kV line-1 & 2
Jamalpur | 1 | 2:15 | 35 | 78.75 | Due to S/D of 132/33 kV Transformer T3
Tongi | 1 | 5:25 | 24 | 130 | Due to S/D of 132/33 kV Transformer T3
Aminbazar | 1 | 0:30 | 132 | 66 | Due to S/D of Aminbazar-Kallyanpur 132 kV line-1 & 2
Sonargaon | 1 | 1:53 | 36 | 67.8 | Due to tripping of 132 kV Bus-A
Bhulta | 2 | 0:11 | 45 | 8.25 | Due to tripping of 132/33 kV Transformer T1
|  | 0:43 | 25 | 17.9167
Narsingdi | 1 | 1:17 | 25 | 32.0833 | Due to tripping of 132/33 kV Transformer T2
Siddhirganj | 1 | 0:10 | 84 | 14 | Due to tripping of Siddhirganj-Matuail 132 kV line
Haripur | 1 | 0:08 | 79 | 10.5333 | Due to tripping of Haripur-Narsingdi 132 kV line
Ghorashal | 1 | 0:50 | 60 | 50 | Due to tripping of Ghorashalm-Bhulta 132 kV line
Munshiganj | 1 | 1:20 | 20 | 26.6667 | Due to tripping of 132/33 kV Transformer T2
Juldah | 1 | 2:35 | 20 | 51.6667 | Due to S/D of Juldah 132 kV bus
Comiila(S) | 1 | 0:36 | 80 | 48 | Due to tripping of 132/33 kV Transformers T1 & T2
Feni | 1 | 0:07 | 130 | 15.1667 | Due to tripping of 132/33 kV Transformers T1 & T2
Chandpur | 1 | 1:25 | 55 | 77.9167 | Due to tripping of 132/33 kV Transformer T2
Chatak | 1 | 0:29 | 17 | 8.2167 | Due to tripping of Chatak-Sunamganj 132 kV line
Shahjibazar | 1 | 3:44 | 50 | 186.6667 | Due to S/D of 132/33 kV Transformer T2,T4 & T6
Gallamari | 1 | 0:11 | 7.7 | 7.7 | Due to tripping of 132/33 kV Transformers T1 & T2
Faridpur | 1 | 0:07 | 154 | 17.9667 | Due to tripping of 132/33 kV Transformers T1 ,& T2
Barisal | 1 | 0:55 | 20 | 18.3333 | Due to red-hot maintenance of 132/33 Transformer T2
Khulna(C) | 1 | 0:20 | 157 | 52.3333 | Due to tripping of Khulna©-Noapara 132 kV line-1 & 2
Gopalganj | 1 | 1:31 | 40 | 60.6667 | Due to S/D of Juldah 132 kV bus
Bagerhat | 1 | 1:33 | 62 | 96.1 | Due to S/D of Bagerhat-Goalpara 132 kV line-1 & 2
Jhenidah | 1 | 0:05 | 20 | 1.6667 | Due to tripping of 132/33 kV Transformers T1 & T2
Shahjadpur | 1 | 0:21 | 11 | 3.85 | Due to tripping of 132/33 kV Transformer T1
Barapukuria | 1 | 1:16 | 44 | 6.6 | Due to tripping of 230/132 kV Transformer T1
Chuadanga | 2 | 0:22 | 44 | 16.1333 | Due to tripping of 132/33 kV Transformers T1 & T2
Bogra |  | 0:36 | 85 | 51 | Due to Bogra-Naogaon 132 kV line-2
Bogra(new) | 1 | 1:17 | 385 | 494.0833 | Due to tripping of Bogra(new)-Bogra (Old) 132 kV line-1 & 2
| Total unserved energy : |  |  | 1984.2667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 146 | 17 | 2018-09-01 | 16:00
2 | Munsiganj | 119 | 19 | 2018-09-01 | 20:00
3 | Megnaghat | 61 | 13 | 2018-09-01 | 22:00
4 | Shyampur | 192 | 20 | 2018-09-01 | 12:00
5 | Bhulta | 193 | 10 | 2018-09-01 | 19:30
6 | Madanganj | 64 | 30 | 2018-09-01 | 21:00
7 | Shitalakhya | 122 | 24 | 2018-09-01 | 15:00
8 | Rahim steel | 21 | 12 | 2018-09-01 | 11:00
9 | Matuail | 102 | 26 | 2018-09-01 | 11:00
10 | Ghorasal | 92 | 24 | 2018-09-01 | 21:00
11 | Narsingdi | 131 | 8 | 2018-09-01 | 21:00
12 | Haripur (SBU) | 114 | 20 | 2018-09-01 | 01:00
13 | Ullon | 102 | 30 | 2018-09-01 | 20:00
14 | Hasnabad | 220 | 17 | 2018-09-01 | 21:00
15 | Magbazar | 145 | 17 | 2018-09-01 | 16:00
16 | Maniknagar | 112 | 19 | 2018-09-01 | 12:00
17 | Bangabhaban | 44 | 18 | 2018-09-01 | 11:00
18 | Narinda | 90 | 23 | 2018-09-01 | 13:00
19 | Dhanmondi | 171 | 19 | 2018-09-01 | 13:00
20 | Lalbag | 97 | 16 | 2018-09-01 | 19:30
21 | Madartek | 69 | 19 | 2018-09-01 | 23:00
22 | Mirpur | 114 | 19 | 2018-09-01 | 16:00
23 | Kalyanpur | 132 | 30 | 2018-09-01 | 18:30
24 | Gulshan | 164 | 19 | 2018-09-01 | 15:00
25 | Uttara | 100 | 17 | 2018-09-01 | 16:00
26 | Uttara(new) | 7 | 5 | 2018-09-01 | 19:00
27 | Kamrangirchar | 122 | 3 | 2018-09-01 | 16:00
28 | Savar | 130 | 17 | 2018-09-01 | 15:00
29 | Bhasantec | 177 | 18 | 2018-09-01 | 18:30
30 | Agargaon | 97 | 3 | 2018-09-01 | 19:00
31 | Satmosjid | 113 | 17 | 2018-09-01 | 18:00
32 | Tongi | 151 | 29 | 2018-09-01 | 15:00
33 | Kabirpur | 217 | 4 | 2018-09-01 | 15:00
34 | Basundhara | 137 | 20 | 2018-09-01 | 22:00
35 | Manikganj | 116 | 10 | 2018-09-01 | 21:00
36 | Joydevpur | 243 | 12 | 2018-09-01 | 9:00
37 | New Tongi | 113 | 9 | 2018-09-01 | 19:00
38 | Kodda | 279 | 26 | 2018-09-01 | 21:00
39 | Dhamrai | 53 | 15 | 2018-09-01 | 20:00
40 | Tangail | 189 | 30 | 2018-09-01 | 21:00
41 | Mymensing | 254 | 29 | 2018-09-01 | 21:00
42 | Kishorganj | 108 | 7 | 2018-09-01 | 19:00
43 | Netrokona | 89 | 9 | 2018-09-01 | 20:00
44 | Jamalpur | 132 | 24 | 2018-09-01 | 23:00
45 | Sherpur | 86 | 5 | 2018-09-01 | 20:00
46 | Srimongal | 43 | 24 | 2018-09-01 | 20:00
47 | Shahjibazar | 113 | 17 | 2018-09-01 | 19:30
48 | Fenchuganj | 51 | 16 | 2018-09-01 | 20:00
49 | Kulawara | 46 | 8 | 2018-09-01 | 18:30
50 | Sylhet | 151 | 18 | 2018-09-01 | 19:00
51 | Chatak | 29 | 18 | 2018-09-01 | 20:00
52 | Sunamganj | 38 | 18 | 2018-09-01 | 20:00
53 | Bianibazar | 45 | 22 | 2018-09-01 | 22:00
54 | Cumilla (S) | 186 | 18 | 2018-09-01 | 18:30
55 | Cumilla(N) | 137 | 18 | 2018-09-01 | 22:00
56 | Chandpur | 128 | 9 | 2018-09-01 | 19:30
57 | Feni | 140 | 19 | 2018-09-01 | 20:00
58 | Chowmuhani | 204 | 18 | 2018-09-01 | 23:00
59 | Ashuganj | 62 | 18 | 2018-09-01 | 18:30
60 | Daudkandi | 118 | 15 | 2018-09-01 | 21:00
61 | B.Baria | 143 | 18 | 2018-09-01 | 19:00
62 | Ramganj | 38 | 17 | 2018-09-01 | 19:00
63 | Madanhat | 66 | 29 | 2018-09-01 | 18:30
64 | Hathazari | 98 | 30 | 2018-09-01 | 15:00
65 | Khulshi | 205 | 24 | 2018-09-01 | 15:00
66 | Halishahar | 148 | 17 | 2018-09-01 | 9:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Baraulia | 171 | 26 | 2018-09-01 | 18:30
68 | Sikalbaha | 40 | 28 | 2018-09-01 | 20:00
69 | Dohazari | 94 | 13 | 2018-09-01 | 21:00
70 | Cox'sbazar | 79 | 23 | 2018-09-01 | 21:00
71 | Chandraghona | 36 | 15 | 2018-09-01 | 1:00
72 | Kaptai | 8 | 15 | 2018-09-01 | 13:00
73 | A. Khaer Stl. | 28 | 16 | 2018-09-01 | 20:00
74 | Bakulia | 119 | 18 | 2018-09-01 | 09:00
75 | Julda | 23 | 30 | 2018-09-01 | 23:00
76 | TK chemical | 12 | 22 | 2018-09-01 | 10:00
77 | Modern Steel | 17 | 4 | 2018-09-01 | 1:00
78 | Shahmirpur | 36 | 9 | 2018-09-01 | 21:00
79 | Abul Khair 230 | 215 | 27 | 2018-09-01 | 13:00
80 | BSRM | 122 | 14 | 2018-09-01 | 21:00
81 | Khagrachhari | 24 | 22 | 2018-09-01 | 19:30
82 | Matarbari | 30.5 | 3 | 2018-09-01 | 18:30
83 | Baroiar Hat | 121 | 9 | 2018-09-01 | 19:30
84 | Goalpara | 40 | 17 | 2018-09-01 | 20:00
85 | Central s/s | 96 | 23 | 2018-09-01 | 19:30
86 | Noapara | 98 | 4 | 2018-09-01 | 20:00
87 | Jashore | 158 | 19 | 2018-09-01 | 20:00
88 | Jhenida | 100 | 4 | 2018-09-01 | 19:00
89 | Bottail | 134 | 8 | 2018-09-01 | 20:00
90 | G.K Project | 59 | 19 | 2018-09-01 | 20:00
91 | Faridpur | 166 | 19 | 2018-09-01 | 19:00
92 | Madaripur | 151 | 24 | 2018-09-01 | 21:00
93 | Gopalganj | 90 | 18 | 2018-09-01 | 19:00
94 | Bagerhat | 85 | 8 | 2018-09-01 | 12:00
95 | Mongla | 40 | 5 | 2018-09-01 | 19:30
96 | Satkhira | 101 | 17 | 2018-09-01 | 13:00
97 | Gallamari | 51 | 19 | 2018-09-01 | 20:00
98 | Magura | 117 | 11 | 2018-09-01 | 21:00
99 | Chuadanga | 113 | 11 | 2018-09-01 | 19:30
100 | Barishal | 128 | 15 | 2018-09-01 | 21:00
101 | Patuakhali | 98 | 18 | 2018-09-01 | 19:00
102 | Bhandaria | 50 | 17 | 2018-09-01 | 19:30
103 | Ishurdi | 58 | 8 | 2018-09-01 | 17:00
104 | Ruppur Paromanobik | 2 | 1 | 2018-09-01 | 20:00
105 | Natore | 121 | 29 | 2018-09-01 | 19:30
106 | Bogura | 252 | 18 | 2018-09-01 | 21:00
107 | Noagaon | 110 | 29 | 2018-09-01 | 21:00
108 | Rajshahi | 157 | 9 | 2018-09-01 | 21:00
109 | C.Nawabganj | 169 | 15 | 2018-09-01 | 21:00
110 | Amnura | 46 | 29 | 2018-09-01 | 20:00
111 | Pabna | 125 | 16 | 2018-09-01 | 21:00
112 | Shahjadpur | 98 | 23 | 2018-09-01 | 21:00
113 | Serajganj | 105 | 25 | 2018-09-01 | 19:30
114 | Niyamatpur | 62 | 18 | 2018-09-01 | 20:00
115 | Joypurhat | 49 | 18 | 2018-09-01 | 20:00
116 | Rangpur | 128 | 20 | 2018-09-01 | 19:00
117 | Lalmonirhat | 89 | 4 | 2018-09-01 | 19:30
118 | Saidpur | 118 | 19 | 2018-09-01 | 19:30
119 | Purbasadipur | 89 | 14 | 2018-09-01 | 21:00
120 | Thakurgaon | 71 | 24 | 2018-09-01 | 20:00
121 | Palashbari | 104 | 29 | 2018-09-01 | 20:00
122 | Barapukuria | 54 | 23 | 2018-09-01 | 19:00
123 | Panchagar | 44 | 21 | 2018-09-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 4274 | 19.09.18 | 15:00
Chittagong | 1292 | 17.09.18 | 23:00
Khulna | 1378 | 08.09.18 | 20:00
Rajshahi | 1223 | 18.09.18 | 20:00
Comilla | 1063 | 16.09.18 | 22:00
Mymensingh | 820 | 28.09.18 | 20:00
Sylhet | 496 | 18.09.18 | 19:00
Barisal | 302 | 18.09.18 | 21:00
Rangpur | 659 | 19.09.18 | 22:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 399 | 13 | 2018-09-01 | 07:00 | 377 | 20 | 2018-09-01 | 20:00
2 | Bheramara | 400 | 417 | 7 | 2018-09-01 | 6:00 | 387 | 26 | 2018-09-01 | 19:00
3 | Ashuganj(N) | 400 | 396 | 1 | 2018-09-01 | 7:00 | 365 | 27 | 2018-09-01 | 12:00
4 | Kaliakoir | 400 | 382 | 3 | 2018-09-01 | 04:00 | 345 | 25 | 2018-09-01 | 21:00
5 | Bhulta | 400 | 389 | 9 | 2018-09-01 | 2:00 | 360 | 27 | 2018-09-01 | 11:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 233 | 23 | 2018-09-01 | 24:00 | 222 | 22 | 2018-09-01 | 12:00
2 | Ishurdi | 230 | 236 | 10 | 2018-09-01 | 17:00 | 213 | 23 | 2018-09-01 | 11:00
3 | Ashuganj | 230 | 239 | 1 | 2018-09-01 | 5:00 | 212 | 23 | 2018-09-01 | 11:00
4 | Serajganj | 230 | 230 | 13 | 2018-09-01 | 1:00 | 209 | 5 | 2018-09-01 | 20:00
5 | Baghabari | 230 | 229 | 21 | 2018-09-01 | 17:00 | 211 | 5 | 2018-09-01 | 4:00
6 | Barapukuria | 230 | 236 | 20 | 2018-09-01 | 8:00 | 202 | 7 | 2018-09-01 | 19:00
7 | Bogra | 230 | 228 | 13 | 2018-09-01 | 1:00 | 188 | 7 | 2018-09-01 | 19:00
8 | Khulna South | 230 | 237 | 2 | 2018-09-01 | 15'00 | 212 | 23 | 2018-09-01 | 11:00
9 | Rampura | 230 | 225 | 1 | 2018-09-01 | 06:00 | 211 | 27 | 2018-09-01 | 11:00
10 | Haripur | 230 | 237 | 23 | 2018-09-01 | 6:00 | 212 | 25 | 2018-09-01 | 10:00
11 | Hasnabad | 230 | 230 | 3 | 2018-09-01 | 20:00 | 210 | 25 | 2018-09-01 | 11:00
12 | Aminbazar | 230 | 230 | 14 | 2018-09-01 | 24:00 | 210 | 25 | 2018-09-01 | 11:00
13 | Tongi | 230 | 226 | 1 | 2018-09-01 | 04:00 | 206 | 26 | 2018-09-01 | 11:00
14 | Comilla (N) | 230 | 235 | 3 | 2018-09-01 | 10:00 | 213 | 23 | 2018-09-01 | 19:00
15 | Hathazari | 230 | 222 | 6 | 2018-09-01 | 18:00 | 208 | 16 | 2018-09-01 | 12:00
16 | Megnaghat | 230 | 230 | 3 | 2018-09-01 | 19:30 | 211 | 23 | 2018-09-01 | 11:00
17 | Fenchuganj | 230 | 240 | 1 | 2018-09-01 | 13:00 | 218 | 13 | 2018-09-01 | 15:00
18 | Siddhirganj | 230 | 227 | 1 | 2018-09-01 | 07:00 | 213 | 19 | 2018-09-01 | 10:00
19 | Maniknagar | 230 | 232 | 23 | 2018-09-01 | 6:00 | 210 | 3 | 2018-09-01 | 15:00
20 | Old Airport | 230 | 228 | 23 | 2018-09-01 | 06:00 | 208 | 25 | 2018-09-01 | 11:00
21 | Barisal | 230 | 234 | 7 | 2018-09-01 | 16:00 | 197 | 7 | 2018-09-01 | 13:00
22 | AKSML | 230 | 220 | 6 | 2018-09-01 | 04:00 | 200 | 20 | 2018-09-01 | 11:00
23 | BSRM | 230 | 223 | 2 | 2018-09-01 | 03:00 | 207 | 20 | 2018-09-01 | 11:00
24 | Bibiyana | 230 | 238 | 1 | 2018-09-01 | 05:00 | 226 | 17 | 2018-09-01 | 19:30
25 | Bhulta | 230 | 227 | 1 | 2018-09-01 | 7:00 | 211 | 27 | 2018-09-01 | 12:00
26 | Ashuganj (S) | 230 | 237 | 1 | 2018-09-01 | 7:00 | 224 | 22 | 2018-09-01 | 11:00
27 | Kaliakoir | 230 | 232 | 2 | 2018-09-01 | 7:00 | 212 | 25 | 2018-09-01 | 13:00
132 kV Substation
1 | Siddhirganj | 132 | 136 | 22 | 2018-09-01 | 20:00 | 126 | 20 | 2018-09-01 | 9:00
2 | Munsiganj | 132 | 137 | 2 | 2018-09-01 | 19:00 | 126 | 20 | 2018-09-01 | 9:00
3 | Megnaghat | 132 | 135 | 8 | 2018-09-01 | 20:00 | 124 | 29 | 2018-09-01 | 9:00
4 | Shyampur | 132 | 135 | 30 | 2018-09-01 | 19:00 | 120 | 8 | 2018-09-01 | 12:00
5 | Bhulta | 132 | 133 | 7 | 2018-09-01 | 18:00 | 121 | 3 | 2018-09-01 | 12:00
6 | Madanganj | 132 | 139 | 21 | 2018-09-01 | 18:30 | 123 | 5 | 2018-09-01 | 18:00
7 | Shitalakhya | 132 | 142 | 3 | 2018-09-01 | 19:30 | 122 | 11 | 2018-09-01 | 17:00
8 | Rahim Steal | 132 | 136 | 22 | 2018-09-01 | 18:00 | 127 | 11 | 2018-09-01 | 11:00
9 | Matuail | 132 | 135 | 8 | 2018-09-01 | 21:00 | 121 | 25 | 2018-09-01 | 9:00
10 | Ghorasal | 132 | 138 | 1 | 2018-09-01 | 18:00 | 130 | 10 | 2018-09-01 | 12:00
11 | Narsinghdi | 132 | 136 | 27 | 2018-09-01 | 14:00 | 119 | 20 | 2018-09-01 | 9:00
12 | Haripur (SBU) | 132 | 136 | 27 | 2018-09-01 | 20:00 | 126 | 20 | 2018-09-01 | 9:00
13 | Ullon | 132 | 135 | 4 | 2018-09-01 | 6:00 | 123 | 20 | 2018-09-01 | 12:00
14 | Hasnabad | 132 | 140 | 3 | 2018-09-01 | 19:00 | 125 | 11 | 2018-09-01 | 12:00
15 | Magbazar | 132 | 136 | 13 | 2018-09-01 | 5:00 | 122 | 20 | 2018-09-01 | 11:00
16 | Maniknagar | 132 | 135 | 1 | 2018-09-01 | 6:00 | 123 | 27 | 2018-09-01 | 12:00
17 | Bangabhaban | 132 | 135 | 1 | 2018-09-01 | 6:00 | 123 | 27 | 2018-09-01 | 1200:00
18 | Narinda | 132 | 135 | 1 | 2018-09-01 | 6:00 | 123 | 27 | 2018-09-01 | 12:00
19 | Dhanmondi | 132 | 135 | 2 | 2018-09-01 | 6:00 | 123 | 27 | 2018-09-01 | 12:00
20 | Lalbag | 132 | 140 | 3 | 2018-09-01 | 19:30 | 118 | 25 | 2018-09-01 | 11:00
21 | Madartek | 132 | 136 | 4 | 2018-09-01 | 6:00 | 123 | 20 | 2018-09-01 | 11:00
22 | Mirpur | 132 | 138 | 2 | 2018-09-01 | 6:00 | 124 | 25 | 2018-09-01 | 12:00
23 | Kalyanpur | 132 | 138 | 19 | 2018-09-01 | 5:00 | 125 | 11 | 2018-09-01 | 17:00
24 | Gulshan | 132 | 135 | 4 | 2018-09-01 | 4:00 | 123 | 20 | 2018-09-01 | 12:00
25 | Uttara | 132 | 134 | 3 | 2018-09-01 | 2:00 | 119 | 25 | 2018-09-01 | 12:00
26 | Uttara(New) | 132 | 133 | 3 | 2018-09-01 | 20:00 | 121 | 11 | 2018-09-01 | 17:00
27 | Kamrangirchar | 132 | 139 | 3 | 2018-09-01 | 4:00 | 119 | 11 | 2018-09-01 | 10:00
28 | Savar | 132 | 135 | 3 | 2018-09-01 | 3:00 | 120 | 5 | 2018-09-01 | 17:00
29 | Bhasantec | 132 | 136 | 15 | 2018-09-01 | 7:00 | 120 | 11 | 2018-09-01 | 17:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 137 | 13 | 2018-09-01 | 3:00 | 122 | 11 | 2018-09-01 | 12:00
31 | Satmosjid | 132 | 137 | 15 | 2018-09-01 | 19:00 | 123 | 11 | 2018-09-01 | 11:00
32 | Tongi | 132 | 138 | 7 | 2018-09-01 | 7:00 | 122 | 26 | 2018-09-01 | 18:30
33 | Kabirpur | 132 | 133 | 13 | 2018-09-01 | 3:00 | 123 | 22 | 2018-09-01 | 11:00
34 | Basundhara | 132 | 140 | 8 | 2018-09-01 | 7:00 | 120 | 20 | 2018-09-01 | 11:00
35 | Manikganj | 132 | 143 | 13 | 2018-09-01 | 7:00 | 122 | 1 | 2018-09-01 | 12:00
36 | Joydevpur | 132 | 136 | 13 | 2018-09-01 | 22:00 | 127 | 8 | 2018-09-01 | 18:00
37 | New Tongi | 132 | 140 | 7 | 2018-09-01 | 21:00 | 122 | 20 | 2018-09-01 | 12:00
38 | Kodda | 132 | 138 | 1 | 2018-09-01 | 07:00 | 126 | 8 | 2018-09-01 | 18:30
39 | Dhamrai | 132 | 140 | 13 | 2018-09-01 | 07:00 | 123 | 22 | 2018-09-01 | 18:30
40 | Tangail | 132 | 136 | 13 | 2018-09-01 | 05:00 | 119 | 23 | 2018-09-01 | 20:00
41 | Mymensing | 132 | 134 | 20 | 2018-09-01 | 04:00 | 106 | 4 | 2018-09-01 | 20:00
42 | Kishorganj | 132 | 137 | 25 | 2018-09-01 | 03:00 | 112 | 28 | 2018-09-01 | 20:00
43 | Netrokona | 132 | 140 | 3 | 2018-09-01 | 03:00 | 104 | 4 | 2018-09-01 | 18:30
44 | Jamalpur | 132 | 140 | 13 | 2018-09-01 | 04:00 | 112 | 4 | 2018-09-01 | 18:30
45 | Sherpur | 132 | 140 | 20 | 2018-09-01 | 6:00 | 111 | 4 | 2018-09-01 | 19:00
46 | Srimongal | 132 | 139 | 2 | 2018-09-01 | 09:00 | 130 | 29 | 2018-09-01 | 21:00
47 | Shahjibazar | 132 | 139 | 6 | 2018-09-01 | 07:00 | 127 | 27 | 2018-09-01 | 18:30
48 | Fenchuganj | 132 | 137 | 12 | 2018-09-01 | 09:00 | 128 | 16 | 2018-09-01 | 19:00
49 | Khulawara | 132 | 136 | 3 | 2018-09-01 | 1:00 | 131 | 9 | 2018-09-01 | 21:00
50 | Sylhet | 132 | 137 | 1 | 2018-09-01 | 4:00 | 130 | 25 | 2018-09-01 | 20:00
51 | Chattak | 132 | 136 | 1 | 2018-09-01 | 05:00 | 128 | 9 | 2018-09-01 | 20:00
52 | Sunamganj | 132 | 137 | 1 | 2018-09-01 | 05:00 | 127 | 6 | 2018-09-01 | 18:30
53 | Biani Bazar | 132 | 132 | 1 | 2018-09-01 | 5:00 | 128 | 9 | 2018-09-01 | 18:30
54 | Comilla(South) | 132 | 137 | 21 | 2018-09-01 | 19:00 | 118 | 3 | 2018-09-01 | 18:00
55 | Comilla (North) | 132 | 132 | 4 | 2018-09-01 | 8:00 | 127 | 29 | 2018-09-01 | 21:00
56 | Chandpur | 132 | 127 | 13 | 2018-09-01 | 7:00 | 111 | 29 | 2018-09-01 | 22:00
57 | Feni | 132 | 128 | 9 | 2018-09-01 | 7:00 | 111 | 18 | 2018-09-01 | 21:00
58 | Chowmuhani | 132 | 140 | 20 | 2018-09-01 | 7:00 | 102 | 22 | 2018-09-01 | 21:00
59 | Ashuganj | 132 | 139 | 2 | 2018-09-01 | 18:30 | 125 | 27 | 2018-09-01 | 13:00
60 | Daudkandi | 132 | 139 | 22 | 2018-09-01 | 9:00 | 123 | 9 | 2018-09-01 | 22:00
61 | Brahminbaria | 132 | 130 | 6 | 2018-09-01 | 8:00 | 123 | 27 | 2018-09-01 | 21:00
62 | Ramganj | 132 | 133 | 23 | 2018-09-01 | 14.:00 | 105 | 22 | 2018-09-01 | 16:00
63 | Madanhat | 132 | 131 | 2 | 2018-09-01 | 09:00 | 124 | 18 | 2018-09-01 | 10:00
64 | Hathazari | 132 | 129 | 1 | 2018-09-01 | 15:00 | 123 | 17 | 2018-09-01 | 11:00
65 | Khulshi | 132 | 132 | 3 | 2018-09-01 | 19:00 | 118 | 20 | 2018-09-01 | 11:00
66 | Halishahar | 132 | 130 | 8 | 2018-09-01 | 18:00 | 122 | 13 | 2018-09-01 | 11:00
67 | Baraulia | 132 | 133 | 6 | 2018-09-01 | 18:00 | 120 | 20 | 2018-09-01 | 10:00
68 | Sikalbaha | 132 | 130 | 12 | 2018-09-01 | 13:00 | 122 | 17 | 2018-09-01 | 10:00
69 | Dohazari | 132 | 129 | 6 | 2018-09-01 | 9:00 | 121 | 20 | 2018-09-01 | 18:30
70 | Cox'sbazar | 132 | 132 | 2 | 2018-09-01 | 14:00 | 111 | 17 | 2018-09-01 | 10:00
71 | Chandraghona | 132 | 132 | 2 | 2018-09-01 | 14:00 | 115 | 17 | 2018-09-01 | 15:00
72 | Kaptai | 132 | 130 | 2 | 2018-09-01 | 07:00 | 125 | 13 | 2018-09-01 | 9:00
73 | A. Khaer Stl. | 132 | 130 | 30 | 2018-09-01 | 19:30 | 122 | 13 | 2018-09-01 | 11:00
74 | Bakulia | 132 | 131 | 12 | 2018-09-01 | 18:00 | 120 | 20 | 2018-09-01 | 10:00
75 | Julda | 132 | 132 | 6 | 2018-09-01 | 07:00 | 120 | 20 | 2018-09-01 | 24:00
76 | TK Chemical | 132 | 130 | 1 | 2018-09-01 | 06:00 | 116 | 18 | 2018-09-01 | 10:00
77 | Modern Steel | 132 | 132 | 30 | 2018-09-01 | 14:00 | 121 | 17 | 2018-09-01 | 11:00
78 | Shahmirpur | 132 | 131 | 15 | 2018-09-01 | 13:00 | 121 | 20 | 2018-09-01 | 21:00
79 | Khagrachhari | 132 | 128 | 2 | 2018-09-01 | 13:00 | 116 | 17 | 2018-09-01 | 18:30
80 | Matarbari | 132 | 130 | 2 | 2018-09-01 | 21:00 | 115 | 9 | 2018-09-01 | 16:00
81 | Baroiar Hat | 132 | 139 | 12 | 2018-09-01 | 01:00 | 113 | 16 | 2018-09-01 | 5:00
82 | Goalpara | 132 | 139 | 5 | 2018-09-01 | 17:00 | 127 | 3 | 2018-09-01 | 19:30
83 | Khulna Central | 132 | 137 | 4 | 2018-09-01 | 18:30 | 128 | 1 | 2018-09-01 | 11:00
84 | Noapara | 132 | 132 | 2 | 2018-09-01 | 17:00 | 125 | 1 | 2018-09-01 | 20:00
85 | Jessore | 132 | 133 | 1 | 2018-09-01 | 16:00 | 117 | 1 | 2018-09-01 | 19:00
86 | Jhenida | 132 | 139 | 2 | 2018-09-01 | 8:00 | 114 | 1 | 2018-09-01 | 19:00
87 | Bottail | 132 | 143 | 4 | 2018-09-01 | 15:00 | 125 | 1 | 2018-09-01 | 19:30
88 | G.K.Project | 132 | 135 | 2 | 2018-09-01 | 14:00 | 133 | 5 | 2018-09-01 | 19:30
89 | Faridpur | 132 | 137 | 2 | 2018-09-01 | 8:00 | 120 | 15 | 2018-09-01 | 20:00
90 | Madaripur | 132 | 138 | 7 | 2018-09-01 | 18:00 | 120 | 9 | 2018-09-01 | 20:00
91 | Gopalganj | 132 | 138 | 6 | 2018-09-01 | 12:00 | 118 | 9 | 2018-09-01 | 20:00
92 | Bagerhat | 132 | 135 | 22 | 2018-09-01 | 14:00 | 120 | 2 | 2018-09-01 | 20:00
93 | Mongla | 132 | 137 | 3 | 2018-09-01 | 10:00 | 122 | 2 | 2018-09-01 | 20:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
94 | Satkhira | 132 | 137 | 4 | 2018-09-01 | 10:00 | 124 | 1 | 2018-09-01 | 19:00
95 | Gallamari | 132 | 139 | 4 | 2018-09-01 | 16:00 | 128 | 1 | 2018-09-01 | 19:30
96 | Magura | 132 | 133 | 2 | 2018-09-01 | 4:00 | 112 | 5 | 2018-09-01 | 19:30
97 | Chuadanga | 132 | 134 | 20 | 2018-09-01 | 6:00 | 106 | 1 | 2018-09-01 | 19:30
98 | Barisal | 132 | 140 | 1 | 2018-09-01 | 7:00 | 130 | 15 | 2018-09-01 | 19:30
99 | Patuakhali | 132 | 138 | 3 | 2018-09-01 | 8:00 | 123 | 15 | 2018-09-01 | 20:00
100 | Bhandaria | 132 | 137 | 4 | 2018-09-01 | 17:00 | 123 | 30 | 2018-09-01 | 20:00
101 | Ishurdi | 132 | 141 | 19 | 2018-09-01 | 15:00 | 130 | 5 | 2018-09-01 | 18:30
102 | Ruppur paromanobik | 132 | 141 | 2 | 2018-09-01 | 17:00 | 130 | 24 | 2018-09-01 | 20:00
103 | Natore | 132 | 138 | 22 | 2018-09-01 | 8:00 | 122 | 5 | 2018-09-01 | 21:00
104 | Bogra | 132 | 139 | 25 | 2018-09-01 | 7:00 | 111 | 7 | 2018-09-01 | 20:00
105 | Noagaon | 132 | 130 | 20 | 2018-09-01 | 18:00 | 102 | 8 | 2018-09-01 | 18:30
106 | Rajshahi | 132 | 135 | 7 | 2018-09-01 | 17:00 | 118 | 30 | 2018-09-01 | 15:00
107 | C.Nawabganj | 132 | 134 | 8 | 2018-09-01 | 9:00 | 116 | 27 | 2018-09-01 | 18:30
108 | Amnura | 132 | 139 | 29 | 2018-09-01 | 17:00 | 120 | 12 | 2018-09-01 | 20:00
109 | Pabna | 132 | 136 | 26 | 2018-09-01 | 6:00 | 122 | 1 | 2018-09-01 | 19:00
110 | Shahjadpur | 132 | 141 | 13 | 2018-09-01 | 7:00 | 130 | 1 | 2018-09-01 | 19:00
111 | Serajganj | 132 | 137 | 20 | 2018-09-01 | 16:00 | 119 | 8 | 2018-09-01 | 19:00
112 | Niyamatpur | 132 | 128 | 20 | 2018-09-01 | 7:00 | 101 | 11 | 2018-09-01 | 20:00
113 | Joypurhat | 132 | 130 | 13 | 2018-09-01 | 8:00 | 101 | 8 | 2018-09-01 | 21:00
114 | Rangpur | 132 | 133 | 20 | 2018-09-01 | 8:00 | 95 | 8 | 2018-09-01 | 19:30
115 | Lalmonirhat | 132 | 135 | 20 | 2018-09-01 | 9:00 | 84 | 9 | 2018-09-01 | 1:00
116 | Saidpur | 132 | 133 | 20 | 2018-09-01 | 9:00 | 92 | 6 | 2018-09-01 | 21:00
117 | Purbasadipur | 132 | 134 | 20 | 2018-09-01 | 9:00 | 92 | 8 | 2018-09-01 | 21:00
118 | Thakurgaon | 132 | 130 | 20 | 2018-09-01 | 9:00 | 86 | 8 | 2018-09-01 | 21:00
119 | Palashbari | 132 | 130 | 20 | 2018-09-01 | 8:00 | 96 | 8 | 2018-09-01 | 21:00
120 | Barapukuria | 132 | 136 | 20 | 2018-09-01 | 9:00 | 100 | 8 | 2018-09-01 | 1:00
121 | Panchagar | 133 | 129 | 20 | 2018-09-01 | 10:00 | 83 | 9 | 2018-09-01 | 2:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:September' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 130 | 410
IP-299421 | Hasnabad | TR2 | 225 | 120 | 410 | 10.09.18 | 09:00
|  | TR3 | 225 | 120 | 390
|  | TR1 | 225 | 170 | 550
IP-299866 | Tongi | TR2 | 225 | 170 | 550 | 20.09.18 | 18:00
|  | TR3 | 225 | 170 | 550
|  | TR1 | 225 | 126 | 340
IP-299427 | Haripur | TR2 | 225 |  |  | 17.09.18 | 06:00 | S/D
|  | TR3 | 225 | 126 | 340
|  | TR1 | 225 | 170 | 510
IP-299728 | Rampura | TR2 | 225 | 170 | 510 | 18.09.18 | 16:00
|  | TR3 | 225 | 170 | 510
|  | TR1 | 225 | 133 | 394
IP-299264 | Aminbazar | TR2 | 225 | 133 | 394 | 28.09.18 | 13:00
|  | TR3 | 225 | 140 | 411
| Maniknagar | TR1 | 300 | 120 | 380 | 19.09.18 | 13:00
|  | TR2 | 300 | 120 | 380
IP-399266 | Comilla (N) | TR1 | 225 | 175 | 550 | 27.09.18 | 2:00
|  | TR2 | 225 | 176 | 525
| Fenchuganj | TR1 | 300 | 180 | 448 | 24.09.18 | 13:00
|  | TR1 | 150 | 105 | 290
IP-399428 | Hathazari | TR3 | 150 | 105 | 290 | 18.09.18 | 18:30
|  | TR4 | 150 | 105 | 290
|  | TR1 | 225 | 130 | 400
| Ishurdi | TR2 | 225 | 130 | 400 | 18.09.18 | 20:00
IP-499474 |  | TR3 | 225 | 130 | 400
| Khulna(S) | TR1 | 225 | 152 | 416
IP-58001/58002 |  | TR2 | 225 | 152 | 416 | 02.098.18 | 4:00
| Bogra | TR1 | 225 | 128 | 405 | 18.09.18 | 20:00
|  | TR2 | 225 | 128 | 405
IP-43002/499264 |  | TR3 | 225 | 171 | 542
IP-499224 | Baghabari | TR1 | 225 | 165 | 490 | 04.09.18 | 19:30
| Barapukuria | TR1 | 225 | 160 | 800 | 17.09.18 | 19:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 126 | 620 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 154 | 823
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 kV, 400/132 kV Transformer
| Name of the | Auto transofrmer |  | Recorded maximum load |  |  |  | Remarks
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kv side ) | Date | Time
| Kaliakoir | TR1(400/230 kV) | 520 | 292 | 597 | 20.09.18 | 5:00
IP-299421 | Kaliakoir | TR1(400/132 kV) | 325 | 225 | 406 | 26.09.18 | 18:15
|  | TR2(400/132 kV) | 325 | 225 | 406
IP-299866 | Bibiyana | ICT1(400/230 kV) | 520 | 118 | 366 | 25.09.18 | 8:00
|  | ICT2(400/230kV) | 520 | 117 | 366
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:September' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:September' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-09-18 | 10617 | 10617 | - | - | - | - | - | - | - | - | - | - | - | - | 01-09-18 | 8471.5 | 8471.5 | - | - | - | - | - | - | - | - | - | - | - | -
02-09-18 | 10225 | 10225 | - | - | - | - | - | - | - | - | - | - | - | - | 02-09-18 | 8252 | 8252 | - | - | - | - | - | - | - | - | - | - | - | -
03-09-18 | 11015 | 11015 | - | - | - | - | - | - | - | - | - | - | - | - | 03-09-18 | 8996.9 | 8996.9 | - | - | - | - | - | - | - | - | - | - | - | -
04-09-18 | 10892 | 10892 | - | - | - | - | - | - | - | - | - | - | - | - | 04-09-18 | 8985 | 8985 | - | - | - | - | - | - | - | - | - | - | - | -
05-09-18 | 10852 | 10852 | - | - | - | - | - | - | - | - | - | - | - | - | 05-09-18 | 9046 | 9046 | - | - | - | - | - | - | - | - | - | - | - | -
06-09-18 | 10637 | 10637 | - | - | - | - | - | - | - | - | - | - | - | - | 06-09-18 | 8589.7 | 8589.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-09-18 | 10266 | 10266 | - | - | - | - | - | - | - | - | - | - | - | - | 07-09-18 | 7449 | 7449 | - | - | - | - | - | - | - | - | - | - | - | -
08-09-18 | 10898 | 10898 | - | - | - | - | - | - | - | - | - | - | - | - | 08-09-18 | 8500.3 | 8500.3 | - | - | - | - | - | - | - | - | - | - | - | -
09-09-18 | 11129 | 11129 | - | - | - | - | - | - | - | - | - | - | - | - | 09-09-18 | 9043.1 | 9043.1 | - | - | - | - | - | - | - | - | - | - | - | -
10-09-18 | 11169 | 11169 | - | - | - | - | - | - | - | - | - | - | - | - | 10-09-18 | 8854.6 | 8854.6 | - | - | - | - | - | - | - | - | - | - | - | -
11-09-18 | 10630 | 10630 | - | - | - | - | - | - | - | - | - | - | - | - | 11-09-18 | 8774.6 | 8774.6 | - | - | - | - | - | - | - | - | - | - | - | -
12-09-18 | 10625 | 10625 | - | - | - | - | - | - | - | - | - | - | - | - | 12-09-18 | 8852.4 | 8852.4 | - | - | - | - | - | - | - | - | - | - | - | -
13-09-18 | 10830 | 10830 | - | - | - | - | - | - | - | - | - | - | - | - | 13-09-18 | 8553 | 8553 | - | - | - | - | - | - | - | - | - | - | - | -
14-09-18 | 10277 | 10277 | - | - | - | - | - | - | - | - | - | - | - | - | 14-09-18 | 7335.9 | 7335.9 | - | - | - | - | - | - | - | - | - | - | - | -
15-09-18 | 11292 | 11292 | - | - | - | - | - | - | - | - | - | - | - | - | 15-09-18 | 8572.1 | 8572.1 | - | - | - | - | - | - | - | - | - | - | - | -
16-09-18 | 11289 | 11289 | - | - | - | - | - | - | - | - | - | - | - | - | 16-09-18 | 9302.3 | 9302.3 | - | - | - | - | - | - | - | - | - | - | - | -
17-09-18 | 11534 | 11534 | - | - | - | - | - | - | - | - | - | - | - | - | 17-09-18 | 9625.4 | 9625.4 | - | - | - | - | - | - | - | - | - | - | - | -
18-09-18 | 11363 | 11363 | - | - | - | - | - | - | - | - | - | - | - | - | 18-09-18 | 9440.1 | 9440.1 | - | - | - | - | - | - | - | - | - | - | - | -
19-09-18 | 11623 | 11623 | - | - | - | - | - | - | - | - | - | - | - | - | 19-09-18 | 9788 | 9788 | - | - | - | - | - | - | - | - | - | - | - | -
20-09-18 | 10420 | 10420 | - | - | - | - | - | - | - | - | - | - | - | - | 20-09-18 | 8790.6 | 8790.6 | - | - | - | - | - | - | - | - | - | - | - | -
21-09-18 | 9864 | 9864 | - | - | - | - | - | - | - | - | - | - | - | - | 21-09-18 | 7258.5 | 7258.5 | - | - | - | - | - | - | - | - | - | - | - | -
22-09-18 | 11006 | 11006 | - | - | - | - | - | - | - | - | - | - | - | - | 22-09-18 | 8554 | 8554 | - | - | - | - | - | - | - | - | - | - | - | -
23-09-18 | 11432 | 11432 | - | - | - | - | - | - | - | - | - | - | - | - | 23-09-18 | 9167 | 9167 | - | - | - | - | - | - | - | - | - | - | - | -
24-09-19 | 11557 | 11557 | - | - | - | - | - | - | - | - | - | - | - | - | 24-09-19 | 9380.8 | 9380.8 | - | - | - | - | - | - | - | - | - | - | - | -
25-09-20 | 11140 | 11140 | - | - | - | - | - | - | - | - | - | - | - | - | 25-09-20 | 9477.5 | 9477.5 | - | - | - | - | - | - | - | - | - | - | - | -
26-09-18 | 11348 | 11348 | - | - | - | - | - | - | - | - | - | - | - | - | 26-09-18 | 9537.3 | 9537.3 | - | - | - | - | - | - | - | - | - | - | - | -
27-09-18 | 10946 | 10946 | - | - | - | - | - | - | - | - | - | - | - | - | 27-09-18 | 9125 | 9125 | - | - | - | - | - | - | - | - | - | - | - | -
28-09-18 | 10891 | 10891 | - | - | - | - | - | - | - | - | - | - | - | - | 28-09-18 | 7896 | 7896 | - | - | - | - | - | - | - | - | - | - | - | -
29-09-18 | 11280 | 11280 | - | - | - | - | - | - | - | - | - | - | - | - | 29-09-18 | 9050.9 | 9050.9 | - | - | - | - | - | - | - | - | - | - | - | -
30-09-18 | 10540 | 10540 | - | - | - | - | - | - | - | - | - | - | - | - | 30-09-18 | 8708.3 | 8708.3 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:September' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11623 | 19/09/18 | 19:30
2 | Maximum day peak Genaration | MW | 9788 | 19/09/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 11623 | 19/09/18 | 19:30
4 | Minimum Generation | MW | 6739.4 | 21/09/18 | 9:00
5 | Average of the daily evening peak Genaration | MW | 10919.5667
6 | Average of the daily day peak Genaration | MW | 8779.26
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW | -
11 | Total Generation | MKWH | 6724.6287
12 | Total Generation by IPP | MKWH | 1775.3801 | % of total Gen. | 26.4%
13 | Total Generation by BPDB | MKWH | 3397.0912 | " | 50.52%
14 | A) Total Generation by RPCL | MKWH | 36.5733 | '' | 0.5439%
| B) Total Generation by REB | MKWH | 147.4859 | " | 2.193%
| C) Total Generation by RENTAL | MKWH | 784.3493 | " | 11.66%
| D) Total Imported from India (HVDC) | MKWH | 490.4429 | " | 7.293%
| E) Total Imported from Tripura, India (A.C) | MKWH | 93.3059 | " | 1.388%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4212.297 | % of total Gen. | 62.64%
| B) Oil | MKWH | 1762.157 | '' | 26.2%
| C) Hydro | MKWH | 100.1635 | '' | 1.49%
| D) Solar | MKWH | 1.8049 | '' | 0.02684%
| E) Coal | MKWH | 64.4576 | '' | 0.9585%
| F) HVDC (Import from India) | MKWH | 490.4429 | '' | 7.293%
| G) A.C (Import from Tripura, India) | MKWH | 93.3059 | '' | 1.388%
16 | Maximun of the daily total Generation . | MKWH | 246.4715 | 19/09/18
17 | Monthly Load factor | % | 80.3559
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 19100.0855
| A) Gas | M.Taka | 2936.1885
| B) Liquid fuel | M.Taka | 15943.0395
| C) Coal | M.Taka | 220.8575
| D) HVDC (Import from India) | M.Taka | 2501.2588
| E) Tripura(Import from India) | M.Taka | 638.2125
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 902.4851 | 19/09/18
| A) Gas | M.Taka | 107.7417 | 10/09/18
| B) Liquid fuel | M.Taka | 786.3647 | 19/09/18
| C) Coal | M.Taka | 17.0944 | 19/09/18
| D) HVDC (Import from India) | M.Taka | 95.7279 | 10-09-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.4712
| B) Excluding Hydro & Solar | Taka/KWHR | 3.5246
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 105.28 | 30/09/18 | 06:00
b) | Actual | FT (MSL) | 103.58 | 30/09/18 | 06:00
22 | Peak Genaration of September 2017 | MW | 9431 | 26/09/17 | 21:00
23 | Peak Demand of September 2017 | MW | 9431 | 26/09/17 | 21:00
24 | Maximum peak Generation recorded upto 30/09/18 | MW | 11623 | 19/09/18 | 19:30
25 | Maximum peak Demand recorded upto 30/09/18 | MW | 11623 | 19/09/18 | 19:30
26 | Maximum load shed recorded upto 30/09/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.