## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:August' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | August 2018 |  | July 2018 |  | August 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11217 | 13/08/18 | 11387 | 18/07/18 | 9470 | 05/08/17 | 11387 | 18/07/18
|  |  | 22:00 |  | 22:00 |  | 21:00 |  | 22:00
2 | Minimum Generation (MW) | 5450.6 | 22/08/18 | 6777 | 03/07/18 | 6149 | 13/08/17 | - | -
|  |  | 9:00 |  | 7:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11174 | 13/08/18 | 11306 | 14/07/18 | 9470 | 05/08/17 | 11306 | 14/07/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9621.4 | 19/08/18 | 9735.4 | 19/07/2018 | 8385 | 21/08/2017 | 9735.4 | 19/07/18
|  |  | 12:00 |  | 11:00 |  | 11:00 |  | 21:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11174 | 13/08/18 | 11306 | 14/07/18 | 9470 | 05/08/17 | 11306 | 14/07/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 10324.5161 |  | 10632.13 |  | 9035.13 |  | 10632.13 | July -18
7 | Average Generation (MW) at Day Peak | 8305.8548 |  | 8546.27 |  | 7706.23 |  | 8546.27 | July -18
8 | Maximum Power Import from India (MW) | 494 | 10/08/18 | 476 | 27/07/18 | 502 | 13/08/17 | 509 | 2017-07-03
|  |  | 8:00 |  | 14:00 |  | 8:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 188 | 21/08/18 | 172 | 25/07/18 | 166 | 23/08/17 | 188 | 29/05/18
|  |  | 21:00 |  | 21:00 |  | 19:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3413.6201 |  | 3249.92 |  | 2692.85
21 | Station Use of BPDB (MKWH) | 109.1413 |  | 101.95 |  | 107.31
22 | Net Generation of BPDB (MKWH) | 3304.4788 |  | 3147.97 |  | 2585.54
23 | Net Generation of IPP & RPCL (MKWH) | 1876.5521 |  | 2054.67 |  | 1490.79
24 | Net Generation of REB (MKWH) | 142.8918 |  | 145.54 |  | 124.58
24 | Net Generation of Rental Power Plant (MKWH) | 731.208 |  | 793.03 |  | 1243.26
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6055.1307 |  | 6141.21 |  | 5444.17 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 4226.2932 |  | 3894.56 |  | 3647.29 |  | 4226.29 | August-18
27 | Energy Generation by Diesel (MKWH) | 549.0349 |  | 736.56 |  | 407.18 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1252.6763 |  | 1431.49 |  | 1273.84 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 125.5278 |  | 118.24 |  | 119.54 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.32205 |  | 0.26 |  |  |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 10.4177 |  | 80.03 |  | 103.63 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 458.0207 |  | 435.2 |  | 449.86 |  | 458.02 | Aug-18
33 | Monthly Load Factor (%) | 79.3522 |  | 78.83 |  | 85.18 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:August' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11217 | 13/08/18 | 22:00
Generation Period
| Dhaka | MW | 4171
| Chittagong | MW | 1224
| Comilla | MW | 983
| Mymensingh | MW | 749
| Sylhet | MW | 474
a) | Total supply in East zone | MW | 7601
| Khulna | MW | 1279
| Barisal | MW | 283
| Rajshahi | MW | 1023
| Rangpur | MW | 553
b) | Total supply in West zone | MW | 3138
c) | Total supply in both zone ( a+b) | MW | 10739
Ref: | 27.21.2604.603.16.084.18.96 | Date: 19/09/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 980 | 19/08/18 | 20:00
| b) Ishurdi end | MW | 100 | 01/08/18 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 180 | 01/08/18 | 16:00
| b) Ishurdi end | MW | 400 | 19/08/18 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 6.633 | 26/08/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 6.2895 | 26/08/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 128.9036
| b) Ishurdi end | MKWH | 0.40145
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.38941
| b) Ishurdi end | MKWH | 125.4824
23 | Transmission loss of EWI/ NO-1 | % | 2.654
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 520 | 30/08/18 | 5:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 510 | 30/08/18 | 5:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 11.176 | 30/08/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 10.92 | 30/08/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 225.802
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 222.488
30 | Transmission loss of EWI /NO-2 | % | 1.468
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 230/132 kV Transformer-T1 | 2018-08-03 18:17 | 2018-08-03 21:31 | 3:14 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2018-08-08 19:28 | 2018-08-08 19:54 | 0:26 | T | Tripped showing R-phase lockout relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-08-10 20:05 | 2018-08-10 20:53 | 0:48 | E/O | Due to red hot maintenance | 25 | 20 | Power interruption
Kabirpur | 132 kV reserve | 2018-08-12 06:07 | 2018-08-12 07:33 | 1:26 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kadda | 132/33 kV Transformers-T1,T2,T3 & T4 | 2018-08-13 10:29 | 2018-08-13 10:40 | 0:11 | T | Tripped showing O/C relay | 213 | 39.05 | Power interruption
|  |  | Total : | 6:05 |  | Unserved Energy: |  | 59.05
Dhaka (South) Grid Circle :
Madanganj | 132/33 kV Transformer-GT2 | 2018-08-16 03:50 | 2018-08-16 10:18 | 6:28 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Ghorashal | 132 kV Bus-1 | 2018-08-16 15:21 | 2018-08-16 15:50 | 0:29 | T | Tripped showing O/C relay | 150 | 72.5 | Power interruption
Manikganj | 132/33 kV Transformer-GT4 | 2018-08-18 11:07 | 2018-08-18 13:06 | 1:59 | E/O | Due to Oil filling | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T1 | 2018-08-18 16:08 | 2018-08-18 17:00 | 0:52 | T | Tripped showing differential relay | 0 | 0 | No interruption
Basantec | 132/33 kV Transformer-T1 | 2018-08-25 13:05 | 2018-08-25 16:09 | 3:04 | T |  | 0 | 0 | No interruption
|  |  | Total : | 12:52 |  | Unserved Energy: |  | 72.5
Chittagong Grid Circle :
Madunaghat | 132/33 kV Transformer-T1 | 2018-08-03 08:38 | 2018-08-03 10:30 | 1:52 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barulia | 132/33 kV Transformer-T1 | 2018-08-04 12:35 | 2018-08-04 14:52 | 2:17 | E/O | Due to red hot maintenance | 10 | 22.8333 | Power interruption
Chandraghona | 132/33 kV Transformer-T2 | 2018-08-08 17:14 | 2018-08-08 17:15 | 0:01 | T | Tripped showing differential relay | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2018-08-08 20:18 | 2018-08-08 20:42 | 0:24 | E/O | Due to red hot maintenance | 50 | 20 | Power interruption
|  |  | Total : | 4:34 |  | Unserved Energy: |  | 42.8333
Comilla Grid Circle :
Chatak | 132/33 kV Transformer-T3 | 2018-08-09 14:09 | 2018-08-09 18:05 | 3:56 | E/O | Due to Breaker problem | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 & T6 | 2018-08-15 22:50 | 2018-08-15 23:04 | 2:57 | T | Tripped showing E/F relay | 54 | 159.3 | Power interruption
Comilla(N) | 132/33 kV Transformer-T-4 | 2018-08-16 09:59 | 2018-08-16 12:06 | 2:07 | E/O | Due to red hot maintenance | 20 | 42.3333 | Power interruption
Sylhet | 132/33 kV Transformer-T-4 | 2018-08-19 05:01 | 2018-08-19 05:37 | 0:36 | T | Tripped showing inst. E/F relay | 48 | 28.8 | Power interruption
Feni | 132/33 kV Transformers-T1 & T2 | 2018-08-21 04:49 | 2018-08-21 04:56 | 0:07 | T | Tripped showing E/F relay | 30 | 3.5 | Power interruption
| 132/33 kV Transformer-T1 | 2018-08-21 08:15 | 2018-08-21 09:31 | 1:16 | E/O | Due to red hot maintenance | 10 | 12.6667 | Power interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-08-23 13:32 | 2018-08-23 14:42 | 1:10 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2018-08-23 23:36 | 2018-08-23 23:52 | 0:16 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2018-08-24 09:42 | 2018-08-24 10:10 | 0:28 | E/O | Tripped showing PRD relay | 9 | 4.2 | Power interruption
Sylhet | 132/33 kV Transformer-T-2 | 2018-08-28 10:46 | 2018-08-28 12:14 | 1:28 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T-2 | 2018-08-31 06:56 | 2018-08-31 07:10 | 0:14 | T | Tripped showing E/F relay | 16 | 3.7333 | Power interruption
|  |  | Total : | 14:35 |  | Unserved Energy: |  | 254.5333
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-T-1 | 2018-08-03 20:15 | 2018-08-03 21:55 | 1:40 | E/O | Due to red hot maintenance | 70 | 116.6667 | Power interruption
Khulna© | 132/33 kV Transformer-T1 | 2018-08-14 20:02 | 2018-08-14 22:59 | 2:57 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 & T2 | 2018-08-22 20:50 | 2018-08-22 22:25 | 1:35 | T | Tripped showing O/C relay | 110 | 174.1667 | Power interruption
Gopalganj | 132/33 kV Transformer-T1 | 2018-08-24 20:32 | 2018-08-24 21:21 | 0:49 | E/O | Due to red hot maintenance | 50 | 40.8333 | Power interruption
Noapara | 132/33 kV Transformer-T4 | 2018-08-27 09:04 | 2018-08-27 11:34 | 2:30 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2018-08-30 11:07 | 2018-08-30 13:40 | 2:33 | T | Tripped showing PRD relay | 14 | 35.7 | Power interruption
|  |  | Total : | 12:04 |  | Unserved Energy: |  | 367.3667
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T1 | 2018-08-02 11:59 | 2018-08-02 12:08 | 0:09 | T | Tripped showing E/F relay | 44 | 6.6 | Power interruption
| 132/33 kV Transformer-T1 | 2018-08-03 09:45 | 2018-08-03 10:25 | 0:40 | E/O | Due to red hot maintenance | 25 | 16.6667 | Power interruption
|  |  | Total : | 0:49 |  | Unserved Energy: |  | 23.2667
Bogra Grid Circle:
Bogra | 230 kV bus-2 | 2018-08-04 12:16 | 2018-08-04 13:56 | 1:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T2 & T6 | 2018-08-04 19:30 | 2018-08-04 22:17 | 2:47 | E/O | Due to bursting at Y-phase lightning arrester | 213 | 592.85 | Power interruption
Bogra | 132/33 kV Transformer-T-4 | 2018-08-16 09:47 | 2018-08-16 15:20 | 5:33 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 10:00 |  | Unserved Energy: |  | 592.85
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 60:59 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-08-18 14:06 | 2018-08-18 14:17 | 0:11 | T | Tripped showing dist. relay | 186 | 34.1 | Power interruption 14:06 to 1 4:17
| Tongi-Kabirpur 132 kV line-1 | 2018-08-18 14:06 | 2018-08-18 14:20 | 0:14 | T
| Tongi-Kabirpur 132 kV line-1 | 2018-08-19 18:50 | 2018-08-20 00:10 | 5:20 | E/O | Due to bursting at L/A | 200 | 173.3333 | Power interruption 18:50 to 1 9:42
| Tongi-Kabirpur 132 kV line-2 | 2018-08-19 18:50 | 2018-08-19 19:42 | 0:52 | E/O
Jamalpur | Jamalpur-United Mymensingh 132 kV line-2 | 2018-08-20 09:30 | 2018-08-20 09:54 | 0:24 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2018-08-23 17:26 | 2018-08-23 21:37 | 4:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Jamalpur | Jamalpur-United Mymensingh 132 kV line-1 | 2018-08-24 20:06 | 2018-08-24 20:25 | 0:19 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 11:31 |  | Unserved Energy: |  | 207.4333
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj -Ullon 132 kV line-1 | 2018-08-01 13:47 | 2018-08-01 17:11 | 3:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-08-04 10:38 | 2018-08-04 13:39 | 3:01 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-1 | 2018-08-05 11:45 | 2018-08-05 12:33 | 0:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-4 | 2018-08-13 03:35 | 2018-08-13 12:45 | 9:10 | E/O | Due to bursting at L/A | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2018-08-13 03:32 | 2018-08-13 06:05 | 2:33 | T | Tripped showing differential relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-08-18 17:34 | 2018-08-18 19:58 | 2:24 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bashundahara 132 kV line-1 | 2018-08-19 17:28 | 2018-08-19 17:44 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-08-20 20:32 | 2018-08-20 22:32 | 2:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2018-08-27 06:40 | 2018-08-27 07:23 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Haripur-Ullon 132 kV line | 2018-08-27 06:40 | 2018-08-27 07:11 | 0:31 | T |  | 56 | 28.9333 | Power interruption
|  |  | Total : | 24:50 |  | Unserved Energy: |  | 28.9333
Chittagong Grid Circle :
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-08-01 09:45 | 2018-08-01 10:04 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV line-1 | 2018-08-02 21:56 | 2018-08-02 22:31 | 0:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-08-07 21:24 | 2018-08-07 22:06 | 0:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-2 | 2018-08-14 10:35 | 2018-08-14 10:49 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-08-15 22:54 | 2018-08-16 00:20 | 1:26 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Chandraghona | Chandraghona-Khagrachori 132 kV line-1 & 2 | 2018-08-17 21:10 | 2018-08-17 21:27 | 0:17 | T | Tripped showing dist. relay | 16 | 4.5333 | Power interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 & 2 | 2018-08-19 02:06 | 2018-08-19 02:14 | 0:08 | T | Tripped showing dist.& E/F relay | 54 | 7.2 | Power interruption
Chandraghona | Chandraghona-Khagrachori 132 kV line-1 & 2 | 2018-08-19 05:20 | 2018-08-19 06:38 | 1:18 | T | Tripped showing dist.& E/F relay | 8 | 18.4 | Power interruption
|  |  | Total : | 4:59 |  | Unserved Energy: |  | 30.1333
Comilla Grid Circle :
Comilla(N) | Comilla(N)-BSRM 230 kV line-2 | 2018-08-13 11:33 | 2018-08-13 16:22 | 4:49 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
| Comilla(N)-BSRM 230 kV line-1 | 2018-08-13 11:36 | 2018-08-13 11:57 | 0:21 | T |  | 1070 | 392.3333 | Power interruption 11:33 to 11:55
Daudkandi | Daudkandi-Comilla(N) 132 kV line-1 | 2018-08-14 10:16 | 2018-08-14 11:31 | 1:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-08-14 12:49 | 2018-08-14 13:14 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-1 & 2 | 2018-08-14 18:51 | 2018-08-14 18:59 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Feni-Hathazari 132 kV line-1 & 2 | 2018-08-13 11:33 | 2018-08-13 11:55 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-BSRM 230 kV line-1 | 2018-08-15 15:15 | 2018-08-15 15:39 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-08-17 13:20 | 2018-08-17 13:33 | 0:13 | T | Tripped showing dist.(C-phase) relay | 72 | 15.6 | Power interruption
Comilla(N) | Comilla(N)-Feni 132 kV line-1 | 2018-08-18 03:26 | 2018-08-18 06:15 | 2:49 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
| Comilla(N)-Feni 132 kV line-2 | 2018-08-18 03:26 | 2018-08-18 04:05 | 0:39 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-2 | 2018-08-18 11:53 | 2018-08-18 12:17 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-2 | 2018-08-31 14:25 | 2018-08-31 14:33 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Feni-Hathazari 132 kV line-2 | 2018-08-31 14:35 | 2018-08-31 21:27 | 6:52 | T | Tripped showing Diff. & E/F relay | 0 | 0 | No interruption
|  |  | Total : | 18:49 |  | Unserved Energy: |  | 407.9333
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2018-08-06 18:13 | 2018-08-06 18:26 | 0:10 | E/O | Tripped showing air pressure low | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-08-11 20:28 | 2018-08-12 03:31 | 7:03 | T | Tripped showing O/C & E/F relay | 53 | 371 | Power interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-08-12 04:31 | 2018-08-13 18:22 | 37:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-08-14 14:28 | 2018-08-14 16:51 | 2:23 | E/O | Due to red hot maintenance | 20 | 47.6667 | Power interruption
| Barisal-Patuakhali 132 kV line | 2018-08-19 05:10 | 2018-08-19 05:31 | 0:21 | T | Tripped showing O/C & E/F relay | 36 | 12.6 | Power interruption
Madaripur | Madaripur-Faridpur 132 kV line-2 | 2018-08-19 07:46 | 2018-08-19 08:10 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-1 | 2018-08-30 09:05 | 2018-08-30 11:41 | 2:36 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  |  | 50:48 |  | Unserved Energy: |  | 431.2667
HVDC Grid Circle :
Bottail | Bottail-Jhenidah 132 kV line-1 & 2 | 2018-08-12 21:18 | 2018-08-12 21:51 | 0:33 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-1 & 2 | 2018-08-12 21:17 | 2018-08-12 21:42 | 0:25 | T | Tripped showing O/C & E/F relay | 360 | 150 | Power interruption
Jhenidah | Jhenidah-Chuadanga 132 kV line | 2018-08-22 01:39 | 2018-08-22 01:49 | 0:10 | T | Tripped showing dist. relay | 58 | 9.6667 | Power interruption
|  |  | Total : | 1:08 |  | Unserved Energy: |  | 159.6667
Bogra Grid Circle :
Naogaon | Naogaon-Santahar P/S 132 kV line | 2018-08-03 08:50 | 2018-08-03 09:40 | 0:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra -Barapukuria 230 kV line-1 | 2018-08-04 12:35 | 2018-08-04 13:55 | 1:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-08-07 13:52 | 2018-08-07 17:36 | 3:44 | E/O | Due to Breaker problem | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2018-08-11 07:19 | 2018-08-11 07:25 | 0:06 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 & 2 | 2018-08-11 07:18 | 2018-08-11 07:28 | 0:10 | T | Tripped showing O/C. relay | 65 | 10.8333 | Power interruption
Bogra | Bogra -Natore 132 kV line-2 | 2018-08-14 09:10 | 2018-08-14 12:57 | 3:47 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra -Palashbari 132 kV line-2 | 2018-08-17 14:53 | 2018-08-17 15:02 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-08-19 10:29 | 2018-08-19 15:04 | 4:35 | T | Tripped showing dist.(3-phase) Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 14:41 |  | Unserved Energy: |  | 10.8333
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-1 & 2 | 2018-08-17 01:38 | 2018-08-17 01:54 | 0:16 | T | Tripped showing mai protection realy | 65 | 17.3333 | Power interruption
| Maniknagar-Bangabhaban 132 kV line-1 | 2018-08-22 02:02 | 2018-08-22 06:14 | 4:12 | T |  | 5 | 21 | Power interruption
|  |  | Total : | 4:28 |  | Unserved Energy: |  | 38.3333
Total outage period of Sub-station Equipment : |  |  |  | 131:14 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: August 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV Transformer-T2 | 2018-08-02 07:05 | 2018-08-02 09:05 | 2:00 | S/O | Due to maintenance work | 35 | 70 | Power interruption
| 132 kV Bus | 2018-08-04 06:39 | 2018-08-04 08:22 | 1:43 | S/O | Due to maintenance work | 50 | 85.8333 | Power interruption
Kishoreganj | 132 kV Bus-A | 2018-08-08 09:25 | 2018-08-08 11:46 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2018-08-08 11:51 | 2018-08-08 12:33 | 0:42 | S/O | Due to C/M work | 50 | 35 | Power interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2018-08-08 09:20 | 2018-08-08 14:45 | 5:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 & T3 | 2018-08-09 07:04 | 2018-08-09 09:40 | 2:36 | S/O | Due to D/W work | 35 | 91 | Power interruption
New Tongi | 132/33 kV Transformer-T2 | 2018-08-10 06:55 | 2018-08-10 16:02 | 9:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-08-10 08:36 | 2018-08-10 19:54 | 11:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-1 | 2018-08-10 10:40 | 2018-08-10 18:23 | 7:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2018-08-11 07:58 | 2018-08-11 11:06 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T2 | 2018-08-11 06:38 | 2018-08-11 16:56 | 10:18 | S/O | Due to C/M work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T1 | 2018-08-11 08:42 | 2018-08-11 13:37 | 4:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T2 | 2018-08-11 10:04 | 2018-08-11 18:46 | 8:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2018-08-12 09:24 | 2018-08-12 11:31 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2018-08-14 08:29 | 2018-08-14 13:37 | 5:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-08-17 06:30 | 2018-08-17 18:05 | 11:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A | 2018-08-17 10:31 | 2018-08-17 17:20 | 6:49 | S/O | Due to project work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-08-18 09:43 | 2018-08-18 15:18 | 5:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2018-08-27 09:04 | 2018-08-27 13:18 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-08-27 13:21 | 2018-08-27 14:45 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-08-29 08:40 | 2018-08-29 19:05 | 10:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2018-08-30 10:15 | 2018-08-30 11:15 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 118:15 |  | Unserved Energy: |  | 281.8333
Dhaka (South) Grid Circle :
Shyampur | 132/33 kV Transformer-T-3 | 2018-08-11 10:41 | 2018-08-11 18:31 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T1 | 2018-08-21 12:10 | 2018-08-21 13:50 | 1:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 9:30 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Khulshi | 132/33 kV Transformer-T2 | 2018-08-04 06:56 | 2018-08-04 10:45 | 3:49 | S/O | Due to replacement work | 20 | 76.3333 | Power interruption
Hathazari | 132/33 kV Transformer-T1 | 2018-08-10 06:18 | 2018-08-10 10:40 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 8:11 |  | Unserved Energy: |  | 76.3333
Comilla Grid Circle :
Shahjibazar | 132/33 kV Transformer-T4 | 2018-08-17 07:11 | 2018-08-17 08:56 | 1:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-08-18 06:01 | 2018-08-18 18:08 | 12:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-08-27 07:10 | 2018-08-27 10:26 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 17:08 |  | Unserved Energy : |  | 0
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: August 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal | 132 kV bus-1 | 2018-07-08 10:52 | 2018-07-08 16:04 | 5:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2018-08-10 09:06 | 2018-08-10 10:49 | 1:43 | S/O | Due to C/M work | 50 | 33.3333 | Power interruption 22:03 to 22:43
| 132/33 kV Transformer-T2 | 2018-08-17 22:03 | 2018-08-17 22:43 | 0:40 | S/O | Due to maintenance work
| 132/33 kV Transformer-T1 | 2018-08-18 07:03 | 2018-08-18 10:37 | 3:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barisal(N) | 132 kV bus-2 | 2018-08-18 11:14 | 2018-08-18 13:09 | 1:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2018-08-19 08:30 | 2018-08-19 12:23 | 3:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-08-19 12:43 | 2018-08-19 13:46 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2018-08-19 12:42 | 2018-08-19 13:47 | 1:05 | S/O | Due to C/M work | 15 | 16.25 | Power interruption
| 132/33 kV Transformer-T2 | 2018-08-27 07:02 | 2018-08-27 07:29 | 0:27 | S/O | Due to C/M work | 20 | 9 | Power interruption
Faridpur | 132/33 kV Transformer-T1 | 2018-08-28 07:20 | 2018-08-28 17:26 | 10:06 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-08-30 07:05 | 2018-08-30 13:35 | 6:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalaganj | 132/33 kV Transformer-T1 | 2018-08-31 07:10 | 2018-08-31 10:16 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 39:14 |  | Unserved Energy : |  | 58.5833
HVDC Grid Circle :
Kustia | 132/33 kV Transformer-T2 | 2018-08-10 08:18 | 2018-08-10 11:36 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2018-08-16 07:40 | 2018-08-16 08:41 | 1:01 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2018-08-17 07:12 | 2018-08-17 13:08 | 5:56 | S/O | Due to maintenance work | 20 | 118.6667 | Power interruption
| 132/33 kV Transformer-T-2 | 2018-08-18 06:12 | 2018-08-18 10:40 | 4:28 | S/O | Due to maintenance work | 30 | 134 | Power interruption
Ishurdi | 132 kV Bus-1 | 2018-08-19 06:24 | 2018-08-19 09:54 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2018-08-20 08:43 | 2018-08-20 09:37 | 0:54 | S/O | Due to maintenance work | 16 | 14.4 | Power interruption
|  |  | Total : | 18:55 |  | Unserved Energy : |  | 267.0667
Bogra Grid Circle:
C.nawabganj | 132/33 kV Transformer-T-2 | 2018-08-01 08:02 | 2018-08-01 08:19 | 0:17 | S/O | Due to C/M work | 15 | 4.25 | Power interruption
Barapukuria | 230/132 kV Transformer-T2 & T6 | 2018-08-07 07:02 | 2018-08-07 10:00 | 2:58 | S/O | Due to replacement work | 120 | 356 | Power interruption
Bogra | 132/33 kV Transformers-T-3 | 2018-08-07 13:56 | 2018-08-07 14:22 | 0:26 | S/O | Due to ratio test | 0 | 0 | No interruption
| 132/33 kV Transformers-T-4 | 2018-08-07 14:25 | 2018-08-07 14:50 | 0:25 | S/O |  | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-TR1 | 2018-08-10 08:24 | 2018-08-10 16:34 | 8:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T3 | 2018-08-11 16:25 | 2018-08-11 21:20 | 4:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | 132 kV main bus | 2018-08-13 09:50 | 2018-08-13 13:30 | 3:40 | S/O | Due to project work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2018-08-16 08:20 | 2018-08-16 08:50 | 0:30 | S/O | Due to maintenance work | 20 | 10 | Power interruption
Barapukuria | 230/132 kV Transformer-T2 | 2018-08-17 06:38 | 2018-08-19 02:14 | 43:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T-3 | 2018-08-18 15:20 | 2018-08-18 17:24 | 2:04 | S/O | Due to replacement work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-3 | 2018-08-21 08:51 | 2018-08-21 10:34 | 1:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 68:44 |  | Unserved Energy : |  | 370.25
Others :
Ghorashal | 230/132 kV Transformer-AT-2 | 2018-06-12 13:59 | 2018-06-13 09:50 | 19:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 19:51 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 299:48 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: August 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2018-08-01 10:29 | 2018-08-01 13:42 | 3:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2018-08-03 07:36 | 2018-08-03 08:58 | 1:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2018-08-08 09:21 | 2018-08-08 09:27 | 0:06 | S/O | Due to C/M work | 50 | 5 | Power interruption
Joydevpur | Joydevpur-Kodda 132 kV line-1 & 2 | 2018-08-10 07:27 | 2018-08-10 18:05 | 10:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2018-08-12 06:11 | 2018-08-12 11:56 | 5:45 | S/O | Due to project work | 0 | 0 | No interruption
| Mirpur-Aminbazar 132 kV line-2 | 2018-08-13 12:26 | 2018-08-13 13:11 | 0:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2018-08-13 15:56 | 2018-08-13 17:22 | 1:26 | S/O | Due to replacement work | 84 | 120.4 | Power interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-08-21 07:30 | 2018-08-21 10:13 | 2:43 | S/O | Due to replacement work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2018-08-28 11:32 | 2018-08-28 14:06 | 2:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 & 2 | 2018-08-29 04:11 | 2018-08-29 19:36 | 15:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 43:57 |  | Unserved Energy: |  | 125.4
Dhaka (South) Grid Circle :
Kodda | Kodda-Joydevpur 132 kV line-1 & 2 | 2018-08-02 11:16 | 2018-08-02 17:41 | 6:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2018-08-07 06:32 | 2018-08-07 09:36 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2018-08-09 14:41 | 2018-08-09 17:57 | 3:16 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR Meghnaghat 230 kV line | 2018-08-17 10:28 | 2018-08-17 14:55 | 4:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2018-08-30 16:07 | 2018-08-30 16:41 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 17:46 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2018-08-03 07:50 | 2018-08-03 18:52 | 11:02 | S/O | Due to project work | 0 | 0 | No interruption
| Dohazari-Sikalbaha 132 kV line-2 | 2018-08-04 07:40 | 2018-08-04 17:54 | 10:14 | S/O | Due to project work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-08-19 07:43 | 2018-08-19 09:42 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 23:15 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 & 2 | 2018-08-01 09:36 | 2018-08-01 09:44 | 0:08 | S/O | Due to project work | 0 | 0 | No interruption
Sunamganj | Sunamganj-Daudkandi 132 kV line-1 | 2018-08-05 10:57 | 2018-08-05 15:05 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.baria 132 kV line-1 | 2018-08-06 10:14 | 2018-08-06 12:20 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
| Shahjibazar-Sreemongal 132 kV line-1 & 2 | 2018-08-07 08:17 | 2018-08-07 17:17 | 9:00 | S/O | Due to project work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoire 400 kV line-2 | 2018-08-11 10:04 | 2018-08-11 19:13 | 9:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Feni 132 kV line-2 | 2018-08-12 06:56 | 2018-08-12 07:37 | 0:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoire 400 kV line-1 | 2018-08-12 11:40 | 2018-08-12 17:15 | 5:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-1 | 2018-08-13 16:57 | 2018-08-13 20:44 | 3:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Feni 132 kV line-1 | 2018-08-14 07:23 | 2018-08-14 09:50 | 2:27 | S/O | Due to isolator maintenance | 0 | 0 | No interruption
Chandpur | Chandpur-Ramganj 132 kV line | 2018-08-17 03:39 | 2018-08-17 16:03 | 12:24 | S/O | Due to project work | 0 | 0 | No interruption
| Chandpur-Chowmuhani 132 kV line | 2018-08-17 03:55 | 2018-08-17 15:22 | 11:27 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Midland 230 kV line | 2018-08-17 10:11 | 2018-08-17 17:12 | 7:01 | S/O | Due to project work | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-1 | 2018-08-18 09:10 | 2018-08-18 16:58 | 7:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-08-18 11:12 | 2018-08-18 13:22 | 2:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-1 | 2018-08-27 05:06 | 2018-08-27 14:40 | 9:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2018-08-27 19:00 | 2018-08-29 14:16 | 43:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Feni 132 kV line-1 | 2018-08-30 09:44 | 2018-08-30 17:30 | 7:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| Cumilla(N)-Feni 132 kV line-1 | 2018-08-31 06:20 | 2018-08-31 12:09 | 5:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: August 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-1 | 2018-08-31 08:08 | 2018-08-31 15:56 | 7:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| Fenchuganj-Fenchuganj S/S 132 kV line-1 | 2018-08-31 09:15 | 2018-08-31 15:25 | 6:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Fenchuganj-Fenchuganj S/S 132 kV line-3 | 2018-08-31 08:46 | 2018-08-31 15:26 | 6:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Cumilla(N) 12 kV line-2 | 2018-08-31 12:14 | 2018-08-31 16:50 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
| Feni-Hathazari 132 kV line-1 | 2018-08-31 09:11 | 2018-08-31 19:10 | 9:59 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 92:04 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gallamari | Gallamari-Khulna(S) 132 kV line-1 | 2018-08-02 08:06 | 2018-08-02 18:47 | 10:41 | S/O | Due to project work | 0 | 0 | No interruption
| Gallamari-Khulna(S) 132 kV line-1 | 2018-08-03 07:09 | 2018-08-03 18:19 | 11:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line | 2018-08-06 06:39 | 2018-08-06 18:33 | 11:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Khulna(S)-Gallamari 132 kV line-1 | 2018-08-07 06:42 | 2018-08-07 18:44 | 12:02 | S/O | Due to project work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 | 2018-08-07 07:28 | 2018-08-07 18:14 | 10:46 | S/O | Due to project work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2018-08-09 07:41 | 2018-08-09 08:58 | 1:17 | S/O | Due to project work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-1 | 2018-08-10 07:39 | 2018-08-13 17:54 | 82:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barisal 132 kV line | 2018-08-26 07:45 | 2018-08-26 21:22 | 13:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 153:42 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2018-08-09 08:23 | 2018-08-09 08:29 | 0:06 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Ishurdi 132 kV line-2 | 2018-08-09 09:12 | 2018-08-09 09:18 | 0:06 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Kustia 132 kV line-2 | 2018-08-28 07:08 | 2018-08-28 14:00 | 6:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Ishurdi 230 kV line-1 | 2018-08-28 09:44 | 2018-08-28 15:30 | 5:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Ishurdi 230 kV line-2 | 2018-08-29 09:16 | 2018-08-29 15:47 | 6:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-2 | 2018-08-31 07:14 | 2018-08-31 11:19 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC -Ishurdi 230 kV line-1 | 2018-08-31 07:25 | 2018-08-31 09:19 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 230 kV line-2 | 2018-08-31 11:07 | 2018-08-31 12:58 | 1:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 27:11 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2018-08-03 06:18 | 2018-08-03 16:04 | 9:46 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 | 2018-08-09 07:27 | 2018-08-09 18:14 | 10:47 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sirajganj-Bogra 132 kV line-1 | 2018-08-10 07:30 | 2018-08-10 17:40 | 10:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 132 kV line-1 | 2018-08-11 08:02 | 2018-08-11 17:26 | 9:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-2 | 2018-08-12 07:08 | 2018-08-12 17:40 | 10:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogra | Bogra-Natore 132 kV line-2 | 2018-08-13 14:42 | 2018-08-13 17:36 | 2:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-2 | 2018-08-14 07:46 | 2018-08-14 17:36 | 9:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-1 | 2018-08-14 12:50 | 2018-08-14 13:26 | 0:36 | S/O | Due to PT problem | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 132 kV line-2 | 2018-08-15 07:40 | 2018-08-15 10:50 | 3:10 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-08-17 07:01 | 2018-08-17 13:57 | 6:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 230 kV line-1 | 2018-08-20 07:10 | 2018-08-20 11:12 | 4:02 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Natore 132 kV line-1 | 2018-08-28 11:04 | 2018-08-28 17:29 | 6:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bogra-Sirajganj 132 kV line-2 | 2018-08-29 11:25 | 2018-08-29 12:56 | 1:31 | S/O | Due to maintenance work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2018-08-31 07:05 | 2018-08-31 08:19 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-08-31 06:44 | 2018-08-31 11:40 | 4:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Rangpur 132 kV line-2 | 2018-08-31 11:46 | 2018-08-31 13:10 | 1:24 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 93:37 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Narindah 132 kV line-1 | 2018-08-07 06:44 | 2018-08-07 08:01 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 1:17 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 435:03 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August' 2018
| Area | Previous Month (July 2018) |  |  |  | Current Month (August 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 13 | 1 | 21 | 35 | 8 | 4 | 32 | 44
2 | Dhaka (South) Grid Circle. | 16 | 4 | 25 | 45 | 9 | 6 | 7 | 22
3 | Chittagong Grid Circle. | 4 | 6 | 18 | 28 | 5 | 6 | 5 | 16
4 | Comilla Grid Circle. | 15 | 4 | 13 | 32 | 18 | 6 | 26 | 50
5 | Khulna Grid Circle. | 10 | 4 | 15 | 29 | 7 | 6 | 20 | 33
6 | Bheramara HVDC Grid Circle | 6 | 2 | 4 | 12 | 4 | 1 | 14 | 19
7 | Bogra Grid Circle. | 9 | 5 | 21 | 35 | 3 | 7 | 11 | 21
8 | Others | - | - | 2 | 2 | 2 | - | 2 | 4
9 | Total | 73 | 26 | 119 | 218 | 56 | 36 | 117 | 209
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August' 2018
| Area | Previous Month (July 2018) |  |  |  | Current Month (August 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 134.96 | - | 402.75 | 537.71 | 73.15 | 193.33 | 407.23 | 673.71
2 | Dhaka ( South) grid circle | 133.67 | 29 | 151 | 313.67 | 101.43 | - | - | 101.43
3 | Chittagong grid circle. | 18.25 | 61.84 | 197.42 | 277.51 | 30.13 | 42.83 | 76.33 | 149.29
4 | Comilla grid circle. | 244.67 | 590.5 | 63.15 | 898.32 | 603.26 | 59.2 | - | 662.46
5 | Khulna grid circle. | 106.33 | - | 172.58 | 278.91 | 593.47 | 205.17 | 58.58 | 857.22
6 | Bheramara HVDC grid circle | 364.58 | 58.92 | - | 423.5 | 166.27 | 16.67 | 267.07 | 450.01
7 | Bogra grid circle. | 51.74 | 283.67 | 526.3 | 861.71 | 10.83 | 592.85 | 370.25 | 973.93
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 1054.2 | 1023.93 | 1513.2 | 3591.33 | 1578.54 | 1110.05 | 1179.46 | 3868.05
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 3 | 3 | 6 | 3 | - | 3 | 10 | 11
1 | Dhaka (North) | 5308 | 2 | 4 | 6 | 1 | 2 | 3 | 340.88
2 | Dhaka (South) | 5031.6 | 1 |  | 1 | 1 |  |  | 72.5
3 | Chittagong | 2042 | 2 | 1 | 3 | 1 |  | 2 | 119.16
4 | Khulna | 2434 | 4 | 3 | 7 | 1 | 1 | 5 | 425.95
5 | Bheramara (HVDC) | 2423.3 | 2 | 3 | 5 | 1 | 2 | 2 | 290.34
6 | Bogra | 3145.6 | 1 | 3 | 4 | 1 |  | 3 | 963.1
7 | Comilla | 2981 | 3 |  | 3 | 1 | - | 2 | 254.53
| Total | 23365.5 | [6 empty] | 2466.46
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chittagong | 99.98%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.93% | [6 empty] | Information Management Division
7 | Comilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 | 2 | 4 | 2 | - | 2 | 332.83
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 |  | 1 |  | 28.93
3 | Chittagong | 917 | 20+9(Partial) | 3 | - | 3 | 3 | - | - | 30.13
4 | Khulna | 1238.4 | 21 | 4 | - | 4 | 2 | - | 2 | 581.27
5 | Bheramara (HVDC) | 598.7 |  | 1 | - | 1 | 1 | - | - | 9.67
6 | Bogra | 1803.3 | 38 | 1 |  | 1 | 1 | - |  | 10.83
7 | Comilla | 1648.16 | 17 | 2 | - | 2 | 2 | - |  | 407.93
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1401.59
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.89%
3 | Chittagong | 99.96%
4 | Khulna | 99.84%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogra | 99.96% | [7 empty] | Information Management Division
7 | Comilla | 99.87% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
August | 12 | - | 9 | 10hr01 min | 2 | 03hr15 min | - | - | 1 | 22min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:August' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishoreganj | 1 | 0:48 | 25 | 20 | Due to tripping of 132/33 kV Transformer T4
Kadda | 1 | 0:04 | 213 | 39.05 | Due to tripping of 132/33 kV Transformers T1 ,T2,T3 & T4
Tongi | 1 | 0:11 | 186 | 34.1 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
|  | 0:52 | 200 | 173.3333 | Due to bursting at L/A
Kishoreganj | 6 | 2:00 | 35 | 70 | Due to S/D of 132/33 kV Transformer T2
|  | 1:43 | 50 | 85.8333 | Due to S/D of 132 kV Bus-A
|  | 0:42 | 50 | 35 | Due to S/D of 132 kV Bus-B
|  | 2:36 | 35 | 91 | Due to S/D of 132/33 kV Transformer T1 & T2
|  | 0:06 | 50 | 5 | Due to S/D of Kishoregang -Ashuganj 132 kV line-1
Mymensingh | 1 | 1:26 | 84 | 120.4 | Due to S/D of Mymensingh-Kishoregang 132 kV line-2
Madanganj | 1 | 0:29 | 150 | 72.5 | Due to tripping of 132 kV Bus-1
Haripur | 1 | 0:31 | 56 | 28.9333 | Due to tripping of Haripur-Ullon 132 kV line
Baraulia | 1 | 2:17 | 10 | 22.8333 | Due to red-hot mainteanance of 132/33 kV Transformer T1
Hathazari | 1 | 0:24 | 50 | 20 | Due to tripping of 132/33 kV Transformer T1
Chandraghona | 2 | 0:17 | 16 | 4.5333 | Due to tripping of Chandraghona-Kghrachori 132 kV line-1 & 2
|  | 1:18 | 8 | 18.4
Kaptai | 1 | 0:08 | 54 | 7.2 | Due to tripping of Kaptai -Hathazari 132 kV line-1 & 2
Khulshi | 1 | 3:49 | 20 | 76.3333 | Due to S/D of 132/33 kV Transformer T2
Shahjibazar | 1 | 1:57 | 54 | 159.3 | Due to tripping of 132/33 kV Transformers T4 &, T6
Comilla(N) | 1 | 2:07 | 20 | 42.3333 | Due to red-hot mainteanance of 132/33 kV Transformer T4
Sylhet | 1 | 0:36 | 48 | 28.8 | Due to tripping of 132/33 kV Transformer T4
Feni | 2 | 0:07 | 30 | 3.5 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 1:16 | 10 | 12.6667 | Due to tripping of 132/33 kV Transformer T1
Chatak | 1 | 0:28 | 9 | 4.2 | Due to tripping of 132/33 kV Transformer T3
Fenchuganj | 1 | 0:14 | 16 | 3.7333 | Due to tripping of 132/33 kV Transformer T2
Comiila(N) | 1 | 0:22 | 1070 | 392.3333 | Due to tripping of Comill(N)-BSRM 230 kV line-1 & 2
Ashuganj | 1 | 0:13 | 72 | 15.6 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-1
Faridpur | 1 | 1:40 | 70 | 116.6667 | Due to red-hot mainteanance of 132/33 kV Transformer T4
Madaripur | 2 | 1:35 | 110 | 174.1667 | Due to tripping of 132/33 kV Transformers T1 ,& T2
|  | 2:33 | 14 | 35.7 | Due to tripping of 132/33 kV Transformer T3
Gopalganj | 1 | 0:49 | 50 | 40.8333 | Due to red-hot mainteanance of 132/33 kV Transformer T1
Barisal | 3 | 7:03 | 53 | 371 | Due to tripping of Barisal-Patuakhali 132 kV line
|  | 2:23 | 20 | 47.6667
|  | 0:21 | 36 | 12.6
Jessore | 1 | 0:25 | 360 | 150 | Due to tripping of Jessore-Noapara 132 kV line-1 & 2
Faridpur | 1 | 0:40 | 50 | 33.3333 | Due to S/D of 132/33 kV Transformer T1 & T2
Barisal | 2 | 1:05 | 15 | 16.25 | Due to S/D of 132/33 kV Transformer T2
|  | 0:27 | 20 | 9
Bottail | 2 | 0:40 | 25 | 16.6667 | Due to red-hot mainteanance of 132/33 kV Transformer T1
|  | 0:09 | 44 | 6.6 | Due to tripping of 132/33 kV Transformer T1
Jhenidah | 1 | 0:10 | 58 | 9.6667 | Due to tripping of Jhenidah-Chuadanga 132 kV line
Bottail | 2 | 5:56 | 20 | 118.6667 | Due to S/D of 132/33 kV Transformer T2
|  | 4:28 | 30 | 134
Ishurdi | 1 | 0:54 | 16 | 14.4 | Due to tripping of 132/33 kV Transformer T1
Barapukuria | 1 | 2:47 | 213 | 592.85 | Due to bursting at L/A.of 230/132 kV Transformers T2& T6
Purbasadipur | 1 | 0:10 | 65 | 10.8333 | Due to tripping of Purbasadipur-Thakurgaon 132 kV line-1 & 2
C.nawabganj | 1 | 0:17 | 15 | 4.25 | Due to S/D of 132/33 kV Transformer T2
Barapukuria | 1 | 2:58 | 120 | 356 | Due to S/D of 132/33 kV Transformers T2 & T6
Rangpur | 1 | 0:30 | 20 | 10 | Due to S/D of 132/33 kV Transformer T1
| Total unserved energy : |  |  | 3868.0667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 140 | 16 | 2018-08-01 | 16:00
2 | Munsiganj | 138 | 19 | 2018-08-01 | 18:00
3 | Megnaghat | 68 | 13 | 2018-08-01 | 21:00
4 | Shyampur | 182 | 12 | 2018-08-01 | 11:00
5 | Bhulta | 203 | 13 | 2018-08-01 | 21:00
6 | Madanganj | 65 | 13 | 2018-08-01 | 21:00
7 | Shitalakhya | 126 | 16 | 2018-08-01 | 16:00
8 | Rahim steel | 14 | 18 | 2018-08-01 | 13:00
9 | Matuail | 140 | 27 | 2018-08-01 | 21:00
10 | Ghorasal | 137 | 19 | 2018-08-01 | 18:00
11 | Narsingdi | 131 | 13 | 2018-08-01 | 19:30
12 | Haripur (SBU) | 112 | 13 | 2018-08-01 | 09:00
13 | Ullon | 102 | 18 | 2018-08-01 | 21:00
14 | Hasnabad | 223 | 11 | 2018-08-01 | 21:00
15 | Magbazar | 137 | 16 | 2018-08-01 | 13:00
16 | Maniknagar | 106 | 13 | 2018-08-01 | 11:00
17 | Bangabhaban | 42 | 12 | 2018-08-01 | 13:00
18 | Narinda | 98 | 8 | 2018-08-01 | 13:00
19 | Dhanmondi | 151 | 12 | 2018-08-01 | 13:00
20 | Lalbag | 99 | 16 | 2018-08-01 | 20:00
21 | Madartek | 54 | 1 | 2018-08-01 | 15:00
22 | Mirpur | 115 | 18 | 2018-08-01 | 21:00
23 | Kalyanpur | 135 | 18 | 2018-08-01 | 15:00
24 | Gulshan | 154 | 13 | 2018-08-01 | 19:30
25 | Uttara | 102 | 18 | 2018-08-01 | 18:00
26 | Kamrangirchar | 93 | 13 | 2018-08-01 | 18:30
27 | Savar | 129 | 4 | 2018-08-01 | 19:30
28 | Bhasantec | 170 | 16 | 2018-08-01 | 15:00
29 | Agargaon | 49 | 13 | 2018-08-01 | 19:00
30 | Satmosjid | 106 | 18 | 2018-08-01 | 18:00
31 | Tongi | 155 | 11 | 2018-08-01 | 15:00
32 | Kabirpur | 238 | 13 | 2018-08-01 | 14:00
33 | Basundhara | 132 | 7 | 2018-08-01 | 21:00
34 | Manikganj | 110 | 13 | 2018-08-01 | 20:00
35 | Joydevpur | 243 | 13 | 2018-08-01 | 18:30
36 | New Tongi | 114 | 8 | 2018-08-01 | 12:00
37 | Kodda | 275 | 13 | 2018-08-01 | 21:00
38 | Dhamrai | 54 | 11 | 2018-08-01 | 20:00
39 | Tangail | 206 | 19 | 2018-08-01 | 21:00
40 | Mymensing | 258 | 19 | 2018-08-01 | 21:00
41 | Kishorganj | 108 | 11 | 2018-08-01 | 22:00
42 | Netrokona | 91 | 16 | 2018-08-01 | 20:00
43 | Jamalpur | 118 | 17 | 2018-08-01 | 23:00
44 | Sherpur | 86 | 13 | 2018-08-01 | 20:00
45 | Srimongal | 41 | 18 | 2018-08-01 | 20:00
46 | Shahjibazar | 120 | 8 | 2018-08-01 | 22:00
47 | Fenchuganj | 53 | 19 | 2018-08-01 | 22:00
48 | Kulawara | 46 | 19 | 2018-08-01 | 21:00
49 | Sylhet | 148 | 16 | 2018-08-01 | 19:00
50 | Chatak | 30 | 19 | 2018-08-01 | 21:00
51 | Sunamganj | 38 | 18 | 2018-08-01 | 20:00
52 | Bianibazar | 46 | 8 | 2018-08-01 | 20:00
53 | Cumilla (S) | 188 | 18 | 2018-08-01 | 21:00
54 | Cumilla(N) | 129 | 23 | 2018-08-01 | 18:30
55 | Chandpur | 130 | 9 | 2018-08-01 | 20:00
56 | Feni | 138 | 9 | 2018-08-01 | 21:00
57 | Chowmuhani | 208 | 9 | 2018-08-01 | 21:00
58 | Ashuganj | 64 | 19 | 2018-08-01 | 22:00
59 | Daudkandi | 124 | 9 | 2018-08-01 | 22:00
60 | B.Baria | 144 | 22 | 2018-08-01 | 20:00
61 | Ramganj | 38 | 9 | 2018-08-01 | 20:00
62 | Madanhat | 63 | 24 | 2018-08-01 | 20:00
63 | Hathazari | 96 | 4 | 2018-08-01 | 19:30
64 | Khulshi | 206 | 13 | 2018-08-01 | 11:00
65 | Halishahar | 142 | 9 | 2018-08-01 | 15:00
66 | Baraulia | 181 | 17 | 2018-08-01 | 4:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:August'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Sikalbaha | 43 | 12 | 2018-08-01 | 19:00
68 | Dohazari | 94 | 8 | 2018-08-01 | 20:00
69 | Cox'sbazar | 84 | 29 | 2018-08-01 | 21:00
70 | Chandraghona | 36 | 15 | 2018-08-01 | 19:00
71 | Kaptai | 6.5 | 4 | 2018-08-01 | 19:00
72 | A. Khaer Stl. | 16 | 8 | 2018-08-01 | 1:00
73 | Bakulia | 115 | 13 | 2018-08-01 | 19:30
74 | Julda | 23 | 8 | 2018-08-01 | 21:00
75 | TK chemical | 6 | 8 | 2018-08-01 | 12:00
76 | Modern Steel | 14 | 16 | 2018-08-01 | 17:00
77 | Shahmirpur | 31 | 15 | 2018-08-01 | 2:00
78 | Abul Khair 230 | 210 | 19 | 2018-08-01 | 2:00
79 | BSRM | 122 | 31 | 2018-08-01 | 22:00
80 | Khagrachhari | 21 | 31 | 2018-08-01 | 21:00
81 | Matarbari | 26.5 | 10 | 2018-08-01 | 21:00
82 | Goalpara | 40 | 2 | 2018-08-01 | 19:30
83 | Central s/s | 94 | 11 | 2018-08-01 | 20:00
84 | Noapara | 98 | 4 | 2018-08-01 | 19:30
85 | Jashore | 150 | 17 | 2018-08-01 | 20:00
86 | Jhenida | 100 | 17 | 2018-08-01 | 21:00
87 | Bottail | 137 | 12 | 2018-08-01 | 20:00
88 | G.K Project | 61 | 18 | 2018-08-01 | 21:00
89 | Faridpur | 166 | 22 | 2018-08-01 | 21:00
90 | Madaripur | 160 | 12 | 2018-08-01 | 21:00
91 | Gopalganj | 88 | 22 | 2018-08-01 | 22:00
92 | Bagerhat | 91 | 12 | 2018-08-01 | 20:00
93 | Mongla | 40 | 7 | 2018-08-01 | 14:00
94 | Satkhira | 100 | 12 | 2018-08-01 | 22:00
95 | Gallamari | 55 | 13 | 2018-08-01 | 13:00
96 | Magura | 56 | 4 | 2018-08-01 | 19:30
97 | Chuadanga | 83 | 4 | 2018-08-01 | 20:00
98 | Barishal | 144 | 9 | 2018-08-01 | 22:00
99 | Patuakhali | 106 | 20 | 2018-08-01 | 20:00
100 | Bhandaria | 51 | 8 | 2018-08-01 | 21:00
101 | Ishurdi | 57 | 12 | 2018-08-01 | 21:00
102 | Ruppur Paromanobik | 2 | 3 | 2018-08-01 | 19:30
103 | Natore | 120 | 5 | 2018-08-01 | 19:30
104 | Bogura | 253 | 12 | 2018-08-01 | 21:00
105 | Noagaon | 118 | 16 | 2018-08-01 | 20:00
106 | Rajshahi | 169 | 12 | 2018-08-01 | 21:00
107 | C.Nawabganj | 77 | 12 | 2018-08-01 | 21:00
108 | Amnura | 43 | 12 | 2018-08-01 | 21:00
109 | Pabna | 139 | 12 | 2018-08-01 | 20:00
110 | Shahjadpur | 105 | 12 | 2018-08-01 | 21:00
111 | Serajganj | 118 | 12 | 2018-08-01 | 21:00
112 | Niyamatpur | 62 | 16 | 2018-08-01 | 19:30
113 | Joypurhat | 47 | 16 | 2018-08-01 | 20:00
114 | Rangpur | 135 | 4 | 2018-08-01 | 20:00
115 | Lalmonirhat | 88 | 9 | 2018-08-01 | 19:00
116 | Saidpur | 116 | 8 | 2018-08-01 | 19:30
117 | Purbasadipur | 83 | 6 | 2018-08-01 | 19:30
118 | Thakurgaon | 71 | 9 | 2018-08-01 | 21:00
119 | Palashbari | 108 | 24 | 2018-08-01 | 20:00
120 | Barapukuria | 54 | 19 | 2018-08-01 | 19:00
121 | Panchagar | 36 | 1 | 2018-08-01 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:August' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 4363 | 13.08.18 | 19:30
Chittagong | 1263 | 16.08.18 | 15:00
Khulna | 1431 | 12.08.18 | 21:00
Rajshahi | 1196 | 12.08.18 | 20:00
Comilla | 1105 | 09.08.18 | 21:00
Mymensingh | 811 | 16.08.18 | 21:00
Sylhet | 496 | 18.08.18 | 20:00
Barisal | 291 | 08.08.18 | 21:00
Rangpur | 617 | 09.08.18 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 400 | 21 | 2018-08-01 | 06:00 | 370 | 11 | 2018-08-01 | 19:00
2 | Bheramara | 400 | 412 | 19 | 2018-08-01 | 16:00 | 386 | 9 | 2018-08-01 | 21:00
3 | Ashuganj(N) | 400 | 401 | 25 | 2018-08-01 | 18:00 | 357 | 22 | 2018-08-01 | 9:00
4 | Kaliakoir | 400 | 386 | 25 | 2018-08-01 | 07:00 | 351 | 11 | 2018-08-01 | 18:00
5 | Bhulta | 400 | 394 | 25 | 2018-08-01 | 17:00 | 366 | 11 | 2018-08-01 | 14:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 234 | 21 | 2018-08-01 | 07:00 | 215 | 15 | 2018-08-01 | 20:00
2 | Ishurdi | 230 | 237 | 15 | 2018-08-01 | 18:00 | 214 | 11 | 2018-08-01 | 14:00
3 | Ashuganj | 230 | 241 | 26 | 2018-08-01 | 18:00 | 215 | 15 | 2018-08-01 | 1:00
4 | Serajganj | 230 | 230 | 7 | 2018-08-01 | 7:00 | 210 | 9 | 2018-08-01 | 22:00
5 | Baghabari | 230 | 229 | 21 | 2018-08-01 | 16:00 | 199 | 16 | 2018-08-01 | 20:00
6 | Barapukuria | 230 | 230 | 3 | 2018-08-01 | 10:00 | 187 | 15 | 2018-08-01 | 20:00
7 | Bogra | 230 | 239 | 15 | 2018-08-01 | 18:00 | 190 | 19 | 2018-08-01 | 22:00
8 | Khulna South | 230 | 241 | 10 | 2018-08-01 | 18'00 | 212 | 18 | 2018-08-01 | 19:30
9 | Rampura | 230 | 231 | 23 | 2018-08-01 | 18:30 | 215 | 2 | 2018-08-01 | 10:00
10 | Haripur | 230 | 230 | 22 | 2018-08-01 | 8:00 | 215 | 3 | 2018-08-01 | 18:30
11 | Hasnabad | 230 | 230 | 21 | 2018-08-01 | 5:00 | 215 | 1 | 2018-08-01 | 16:00
12 | Aminbazar | 230 | 230 | 22 | 2018-08-01 | 09:00 | 216 | 1 | 2018-08-01 | 15:00
13 | Tongi | 230 | 233 | 15 | 2018-08-01 | 18:00 | 208 | 7 | 2018-08-01 | 15:00
14 | Comilla (N) | 230 | 239 | 22 | 2018-08-01 | 10:00 | 213 | 15 | 2018-08-01 | 15:00
15 | Hathazari | 230 | 228 | 15 | 2018-08-01 | 7:00 | 208 | 12 | 2018-08-01 | 13:00
16 | Megnaghat | 230 | 240 | 15 | 2018-08-01 | 18:00 | 220 | 1 | 2018-08-01 | 12:00
17 | Fenchuganj | 230 | 241 | 26 | 2018-08-01 | 18:00 | 221 | 15 | 2018-08-01 | 10:00
18 | Siddhirganj | 230 | 230 | 21 | 2018-08-01 | 07:00 | 217 | 1 | 2018-08-01 | 15:00
19 | Maniknagar | 230 | 229 | 22 | 2018-08-01 | 8:00 | 215 | 1 | 2018-08-01 | 15:00
20 | Old Airport | 230 | 231 | 15 | 2018-08-01 | 17:00 | 214 | 2 | 2018-08-01 | 9:00
21 | Barisal | 230 | 236 | 1 | 2018-08-01 | 13:00 | 208 | 31 | 2018-08-01 | 12:00
22 | AKSML | 230 | 229 | 13 | 2018-08-01 | 12:00 | 203 | 12 | 2018-08-01 | 12:00
23 | BSRM | 230 | 236 | 15 | 2018-08-01 | 17:00 | 208 | 3 | 2018-08-01 | 19:30
24 | Bibiyana | 230 | 238 | 22 | 2018-08-01 | 08:00 | 220 | 15 | 2018-08-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 138 | 21 | 2018-08-01 | 07:00 | 129 | 2 | 2018-08-01 | 12:00
2 | Munsiganj | 132 | 138 | 19 | 2018-08-01 | 18:00 | 128 | 6 | 2018-08-01 | 9:00
3 | Megnaghat | 132 | 137 | 10 | 2018-08-01 | 19:30 | 126 | 7 | 2018-08-01 | 11:00
4 | Shyampur | 132 | 136 | 29 | 2018-08-01 | 19:30 | 122 | 7 | 2018-08-01 | 12:00
5 | Bhulta | 132 | 134 | 20 | 2018-08-01 | 18:00 | 124 | 11 | 2018-08-01 | 13:00
6 | Madanganj | 132 | 140 | 29 | 2018-08-01 | 20:00 | 127 | 2 | 2018-08-01 | 17:00
7 | Shitalakhya | 132 | 142 | 30 | 2018-08-01 | 19:30 | 125 | 27 | 2018-08-01 | 13:00
8 | Rahim Steal | 132 | 140 | 17 | 2018-08-01 | 21:00 | 129 | 2 | 2018-08-01 | 16:00
9 | Matuail | 132 | 137 | 21 | 2018-08-01 | 9:00 | 127 | 2 | 2018-08-01 | 10:00
10 | Ghorasal | 132 | 142 | 22 | 2018-08-01 | 8:00 | 130 | 23 | 2018-08-01 | 1:00
11 | Narsinghdi | 132 | 136 | 21 | 2018-08-01 | 6:00 | 121 | 7 | 2018-08-01 | 12:00
12 | Haripur (SBU) | 132 | 138 | 8 | 2018-08-01 | 1:00 | 129 | 7 | 2018-08-01 | 12:00
13 | Ullon | 132 | 138 | 21 | 2018-08-01 | 7:00 | 126 | 1 | 2018-08-01 | 17:00
14 | Hasnabad | 132 | 139 | 18 | 2018-08-01 | 21:00 | 127 | 6 | 2018-08-01 | 9:00
15 | Magbazar | 132 | 137 | 21 | 2018-08-01 | 2:00 | 124 | 9 | 2018-08-01 | 17:00
16 | Maniknagar | 132 | 142 | 20 | 2018-08-01 | 18:00 | 132 | 29 | 2018-08-01 | 13:00
17 | Bangabhaban | 132 | 142 | 20 | 2018-08-01 | 18:00 | 132 | 29 | 2018-08-01 | 13:00
18 | Narinda | 132 | 142 | 20 | 2018-08-01 | 18:00 | 132 | 29 | 2018-08-01 | 13:00
19 | Dhanmondi | 132 | 142 | 20 | 2018-08-01 | 18:00 | 126 | 1 | 2018-08-01 | 17:00
20 | Lalbag | 132 | 141 | 30 | 2018-08-01 | 19:30 | 124 | 1 | 2018-08-01 | 17:00
21 | Madartek | 132 | 138 | 21 | 2018-08-01 | 6:00 | 125 | 1 | 2018-08-01 | 15:00
22 | Mirpur | 132 | 139 | 26 | 2018-08-01 | 6:00 | 127 | 12 | 2018-08-01 | 16:00
23 | Kalyanpur | 132 | 139 | 27 | 2018-08-01 | 7:00 | 128 | 1 | 2018-08-01 | 15:00
24 | Gulshan | 132 | 137 | 21 | 2018-08-01 | 9:00 | 125 | 1 | 2018-08-01 | 15:00
25 | Uttara | 132 | 135 | 21 | 2018-08-01 | 7:00 | 120 | 13 | 2018-08-01 | 10:00
26 | Kamrangirchar | 132 | 138 | 17 | 2018-08-01 | 1:00 | 124 | 2 | 2018-08-01 | 10:00
27 | Savar | 132 | 136 | 20 | 2018-08-01 | 7:00 | 125 | 1 | 2018-08-01 | 15:00
28 | Bhasantec | 132 | 136 | 21 | 2018-08-01 | 9:00 | 124 | 11 | 2018-08-01 | 12:00
29 | Agargaon | 132 | 137 | 22 | 2018-08-01 | 8:00 | 126 | 1 | 2018-08-01 | 16:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 137 | 22 | 2018-08-01 | 9:00 | 125 | 13 | 2018-08-01 | 12:00
31 | Tongi | 132 | 137 | 15 | 2018-08-01 | 08:00 | 122 | 13 | 2018-08-01 | 12:00
32 | Kabirpur | 132 | 139 | 16 | 2018-08-01 | 6:00 | 123 | 11 | 2018-08-01 | 19:00
33 | Basundhara | 132 | 135 | 23 | 2018-08-01 | 21:00 | 120 | 13 | 2018-08-01 | 12:00
34 | Manikganj | 132 | 140 | 3 | 2018-08-01 | 18:00 | 124 | 13 | 2018-08-01 | 10:00
35 | Joydevpur | 132 | 142 | 24 | 2018-08-01 | 19:00 | 120 | 16 | 2018-08-01 | 16:00
36 | New Tongi | 132 | 138 | 11 | 2018-08-01 | 06:00 | 122 | 13 | 2018-08-01 | 12:00
37 | Kodda | 132 | 143 | 25 | 2018-08-01 | 21:00 | 121 | 13 | 2018-08-01 | 22:00
38 | Dhamrai | 132 | 138 | 16 | 2018-08-01 | 06:00 | 123 | 11 | 2018-08-01 | 19:00
39 | Tangail | 132 | 138 | 2 | 2018-08-01 | 14:00 | 121 | 13 | 2018-08-01 | 20:00
40 | Mymensing | 132 | 134 | 2 | 2018-08-01 | 14:00 | 108 | 18 | 2018-08-01 | 23:00
41 | Kishorganj | 132 | 135 | 9 | 2018-08-01 | 09:00 | 113 | 17 | 2018-08-01 | 19:30
42 | Netrokona | 132 | 135 | 2 | 2018-08-01 | 14:00 | 105 | 7 | 2018-08-01 | 19:30
43 | Jamalpur | 132 | 139 | 15 | 2018-08-01 | 20:00 | 112 | 18 | 2018-08-01 | 18:30
44 | Sherpur | 132 | 138 | 15 | 2018-08-01 | 20:00 | 110 | 18 | 2018-08-01 | 18:30
45 | Srimongal | 132 | 140 | 1 | 2018-08-01 | 9:00 | 131 | 11 | 2018-08-01 | 20:00
46 | Shahjibazar | 132 | 139 | 1 | 2018-08-01 | 10:00 | 128 | 18 | 2018-08-01 | 20:00
47 | Fenchuganj | 132 | 138 | 1 | 2018-08-01 | 06:00 | 130 | 11 | 2018-08-01 | 20:00
48 | Khulawara | 132 | 137 | 1 | 2018-08-01 | 05:00 | 129 | 31 | 2018-08-01 | 21:00
49 | Sylhet | 132 | 137 | 20 | 2018-08-01 | 15:00 | 128 | 31 | 2018-08-01 | 20:00
50 | Chattak | 132 | 138 | 20 | 2018-08-01 | 14:00 | 124 | 31 | 2018-08-01 | 21:00
51 | Sunamganj | 132 | 135 | 9 | 2018-08-01 | 07:00 | 123 | 31 | 2018-08-01 | 21:00
52 | Biani Bazar | 132 | 137 | 16 | 2018-08-01 | 06:00 | 125 | 31 | 2018-08-01 | 21:00
53 | Comilla(South) | 132 | 129 | 5 | 2018-08-01 | 6:00 | 118 | 13 | 2018-08-01 | 19:00
54 | Comilla (North) | 132 | 139 | 22 | 2018-08-01 | 10:00 | 130 | 24 | 2018-08-01 | 23:00
55 | Chandpur | 132 | 131 | 17 | 2018-08-01 | 10:00 | 115 | 29 | 2018-08-01 | 20:00
56 | Feni | 132 | 124 | 19 | 2018-08-01 | 7:00 | 113 | 7 | 2018-08-01 | 22:00
57 | Chowmuhani | 132 | 129 | 19 | 2018-08-01 | 7:00 | 110 | 23 | 2018-08-01 | 22:00
58 | Ashuganj | 132 | 140 | 22 | 2018-08-01 | 9:00 | 121 | 9 | 2018-08-01 | 20:00
59 | Daudkandi | 132 | 140 | 18 | 2018-08-01 | 1:00 | 125 | 6 | 2018-08-01 | 23:00
60 | Brahminbaria | 132 | 139 | 1 | 2018-08-01 | 13:00 | 128 | 11 | 2018-08-01 | 22:00
61 | Ramganj | 132 | 139 | 1 | 2018-08-01 | 13:00 | 110 | 29 | 2018-08-01 | 22:00
62 | Madanhat | 132 | 138 | 13 | 2018-08-01 | 13.:00 | 126 | 13 | 2018-08-01 | 16:00
63 | Hathazari | 132 | 132 | 15 | 2018-08-01 | 18:00 | 124 | 12 | 2018-08-01 | 12:00
64 | Khulshi | 132 | 130 | 22 | 2018-08-01 | 5:00 | 121 | 4 | 2018-08-01 | 15:00
65 | Halishahar | 132 | 136 | 16 | 2018-08-01 | 6:00 | 122 | 12 | 2018-08-01 | 12:00
66 | Baraulia | 132 | 131 | 19 | 2018-08-01 | 5:00 | 121 | 13 | 2018-08-01 | 16:00
67 | Sikalbaha | 132 | 132 | 17 | 2018-08-01 | 7:00 | 123 | 12 | 2018-08-01 | 12:00
68 | Dohazari | 132 | 131 | 30 | 2018-08-01 | 6:00 | 122 | 4 | 2018-08-01 | 16:00
69 | Cox'sbazar | 132 | 127 | 1 | 2018-08-01 | 6:00 | 112 | 13 | 2018-08-01 | 18:30
70 | Chandraghona | 132 | 133 | 19 | 2018-08-01 | 4:00 | 118 | 30 | 2018-08-01 | 15:00
71 | Kaptai | 132 | 134 | 22 | 2018-08-01 | 3:00 | 126 | 6 | 2018-08-01 | 12:00
72 | A. Khaer Stl. | 132 | 130 | 17 | 2018-08-01 | 18:00 | 121 | 12 | 2018-08-01 | 12:00
73 | Bakulia | 132 | 131 | 22 | 2018-08-01 | 6:00 | 121 | 12 | 2018-08-01 | 12:00
74 | Julda | 132 | 132 | 17 | 2018-08-01 | 18:00 | 123 | 4 | 2018-08-01 | 15:00
75 | TK Chemical | 132 | 135 | 16 | 2018-08-01 | 08:00 | 125 | 12 | 2018-08-01 | 12:00
76 | Modern Steel | 132 | 131 | 19 | 2018-08-01 | 04:00 | 121 | 12 | 2018-08-01 | 12:00
77 | Shahmirpur | 132 | 131 | 17 | 2018-08-01 | 18:00 | 121 | 12 | 2018-08-01 | 13:00
78 | Khagrachhari | 132 | 133 | 20 | 2018-08-01 | 06:00 | 124 | 13 | 2018-08-01 | 16:00
79 | Matarbari | 132 | 137 | 9 | 2018-08-01 | 07:00 | 115 | 4 | 2018-08-01 | 20:00
80 | Goalpara | 132 | 139 | 16 | 2018-08-01 | 17:00 | 119 | 19 | 2018-08-01 | 2:00
81 | Khulna Central | 132 | 138 | 8 | 2018-08-01 | 14:00 | 119 | 22 | 2018-08-01 | 18:30
82 | Noapara | 132 | 137 | 16 | 2018-08-01 | 17:00 | 115 | 18 | 2018-08-01 | 19:30
83 | Jessore | 132 | 134 | 16 | 2018-08-01 | 17:00 | 111 | 18 | 2018-08-01 | 19:30
84 | Jhenida | 132 | 136 | 31 | 2018-08-01 | 7:00 | 109 | 12 | 2018-08-01 | 19:30
85 | Bottail | 132 | 138 | 3 | 2018-08-01 | 10:00 | 116 | 28 | 2018-08-01 | 20:00
86 | G.K.Project | 132 | 144 | 10 | 2018-08-01 | 09:00 | 126 | 11 | 2018-08-01 | 14:00
87 | Faridpur | 132 | 136 | 12 | 2018-08-01 | 18:00 | 118 | 18 | 2018-08-01 | 19:00
88 | Madaripur | 132 | 136 | 2 | 2018-08-01 | 11:00 | 117 | 18 | 2018-08-01 | 19:00
89 | Gopalganj | 132 | 140 | 11 | 2018-08-01 | 17:00 | 115 | 22 | 2018-08-01 | 15:00
90 | Bagerhat | 132 | 136 | 1 | 2018-08-01 | 15:00 | 117 | 12 | 2018-08-01 | 21:00
91 | Mongla | 132 | 136 | 7 | 2018-08-01 | 6:00 | 115 | 12 | 2018-08-01 | 19:30
92 | Satkhira | 132 | 137 | 17 | 2018-08-01 | 6:00 | 115 | 18 | 2018-08-01 | 19:30
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
93 | Gallamari | 132 | 138 | 8 | 2018-08-01 | 14:00 | 120 | 12 | 2018-08-01 | 19:30
94 | Magura | 132 | 135 | 7 | 2018-08-01 | 8:00 | 105 | 12 | 2018-08-01 | 19:30
95 | Chuadanga | 132 | 132 | 3 | 2018-08-01 | 11:00 | 99 | 16 | 2018-08-01 | 19:30
96 | Barisal | 132 | 141 | 18 | 2018-08-01 | 18:00 | 126 | 23 | 2018-08-01 | 21:00
97 | Patuakhali | 132 | 137 | 2 | 2018-08-01 | 14:00 | 120 | 18 | 2018-08-01 | 19:00
98 | Bhandaria | 132 | 138 | 19 | 2018-08-01 | 8:00 | 119 | 25 | 2018-08-01 | 22:00
99 | Ishurdi | 132 | 141 | 7 | 2018-08-01 | 7:00 | 127 | 11 | 2018-08-01 | 15:00
100 | Ruppur Paromanobik | 132 | 141 | 3 | 2018-08-01 | 10:00 | 126 | 19 | 2018-08-01 | 16:00
101 | Natore | 132 | 137 | 3 | 2018-08-01 | 6:00 | 119 | 15 | 2018-08-01 | 20:00
102 | Bogra | 132 | 133 | 7 | 2018-08-01 | 7:00 | 107 | 15 | 2018-08-01 | 20:00
103 | Noagaon | 132 | 130 | 24 | 2018-08-01 | 8:00 | 102 | 19 | 2018-08-01 | 19:00
104 | Rajshahi | 132 | 137 | 18 | 2018-08-01 | 7:00 | 117 | 15 | 2018-08-01 | 20:00
105 | C.Nawabganj | 132 | 136 | 7 | 2018-08-01 | 18:30 | 116 | 11 | 2018-08-01 | 15:00
106 | Amnura | 132 | 139 | 13 | 2018-08-01 | 7:00 | 118 | 20 | 2018-08-01 | 13:00
107 | Pabna | 132 | 135 | 2 | 2018-08-01 | 17:00 | 120 | 12 | 2018-08-01 | 20:00
108 | Shahjadpur | 132 | 140 | 3 | 2018-08-01 | 16:00 | 125 | 10 | 2018-08-01 | 15:00
109 | Serajganj | 132 | 135 | 3 | 2018-08-01 | 11:00 | 116 | 15 | 2018-08-01 | 20:00
110 | Niyamatpur | 132 | 128 | 7 | 2018-08-01 | 7:00 | 98 | 19 | 2018-08-01 | 19:00
111 | Joypurhat | 132 | 130 | 20 | 2018-08-01 | 10:00 | 98 | 19 | 2018-08-01 | 19:00
112 | Rangpur | 132 | 128 | 24 | 2018-08-01 | 8:00 | 92 | 17 | 2018-08-01 | 8:00
113 | Lalmonirhat | 132 | 125 | 3 | 2018-08-01 | 11:00 | 84 | 17 | 2018-08-01 | 8:00
114 | Saidpur | 132 | 129 | 24 | 2018-08-01 | 8:00 | 93 | 17 | 2018-08-01 | 8:00
115 | Purbasadipur | 132 | 135 | 24 | 2018-08-01 | 6:00 | 92 | 15 | 2018-08-01 | 19:00
116 | Thakurgaon | 132 | 130 | 24 | 2018-08-01 | 6:00 | 84 | 15 | 2018-08-01 | 20:00
117 | Palashbari | 132 | 128 | 24 | 2018-08-01 | 8:00 | 95 | 15 | 2018-08-01 | 20:00
118 | Barapukuria | 132 | 133 | 24 | 2018-08-01 | 8:00 | 99 | 15 | 2018-08-01 | 20:00
119 | Panchagar | 132 | 126 | 20 | 2018-08-01 | 7:00 | 82 | 9 | 2018-08-01 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:August' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 140 | 410
IP-299421 | Hasnabad | TR2 | 225 | 120 | 400 | 06.08.18 | 24:00
|  | TR3 | 225 | 115 | 380
|  | TR1 | 225 | 180 | 600
IP-299866 | Tongi | TR2 | 225 | 180 | 600 | 13.08.18 | 12:00
|  | TR3 | 225 | 180 | 600
|  | TR1 | 225 | 76 | 225
IP-299427 | Haripur | TR2 | 225 | 76 | 225 | 06.08.18 | 23:00
|  | TR3 | 225 | 76 | 225
|  | TR1 | 225 | 165 | 490
IP-299728 | Rampura | TR2 | 225 | 165 | 490 | 27.08.18 | 15:00
|  | TR3 | 225 | 165 | 490
|  | TR1 | 225 | 136 | 410
IP-299264 | Aminbazar | TR2 | 225 | 136 | 410 | 18.08.18 | 19:00
|  | TR3 | 225 | 144 | 429
| Maniknagar | TR1 | 300 | 119 | 380 | 08.08.18 | 13:00
|  | TR2 | 300 | 119 | 380
IP-399266 | Comilla (N) | TR1 | 225 | 170 | 540 | 06.08.18 | 24:00
|  | TR2 | 225 | 174 | 517
| Fenchuganj | TR1 | 300 | 235 | 602 | 09.08.18 | 9:00
|  | TR1 | 150 | 87 | 260
IP-399428 | Hathazari | TR3 | 150 | 87 | 260 | 14.08.18 | 12:00
|  | TR4 | 150 | 87 | 260
|  | TR1 | 225 | 144 | 430
| Ishurdi | TR2 | 225 | 144 | 430 | 19.08.18 | 20:00
IP-499474 |  | TR3 | 225 | 144 | 430
| Khulna(S) | TR1 | 225 | 177 | 487
IP-58001/58002 |  | TR2 | 225 | 177 | 487 | 28.08.18 | 14:00
| Bogra | TR1 | 225 | 122 | 368 | 20.08.18 | 19:30
|  | TR2 | 225 | 122 | 368
IP-43002/499264 |  | TR3 | 225 | 166 | 483
IP-499224 | Baghabari | TR1 | 225 | 175 | 540 | 19.08.18 | 21:00
| Barapukuria | TR1 | 225 | 180 | 1100 | 17.08.18 | 8:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 95 | 500 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 120 | 672
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:August' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:August' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-08-18 | 10115 | 10115 | - | - | - | - | - | - | - | - | - | - | - | - | 01-08-18 | 8569.9 | 8569.9 | - | - | - | - | - | - | - | - | - | - | - | -
02-08-18 | 10086 | 10086 | - | - | - | - | - | - | - | - | - | - | - | - | 02-08-18 | 8295.1 | 8295.1 | - | - | - | - | - | - | - | - | - | - | - | -
03-08-18 | 9727 | 9727 | - | - | - | - | - | - | - | - | - | - | - | - | 03-08-18 | 6834.7 | 6834.7 | - | - | - | - | - | - | - | - | - | - | - | -
04-08-18 | 10518 | 10518 | - | - | - | - | - | - | - | - | - | - | - | - | 04-08-18 | 8216 | 8216 | - | - | - | - | - | - | - | - | - | - | - | -
05-08-18 | 10862 | 10862 | - | - | - | - | - | - | - | - | - | - | - | - | 05-08-18 | 8831.3 | 8831.3 | - | - | - | - | - | - | - | - | - | - | - | -
06-08-18 | 10646 | 10646 | - | - | - | - | - | - | - | - | - | - | - | - | 06-08-18 | 8980.5 | 8980.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-08-18 | 10862 | 10862 | - | - | - | - | - | - | - | - | - | - | - | - | 07-08-18 | 8652 | 8652 | - | - | - | - | - | - | - | - | - | - | - | -
08-08-18 | 10902 | 10902 | - | - | - | - | - | - | - | - | - | - | - | - | 08-08-18 | 9019.8 | 9019.8 | - | - | - | - | - | - | - | - | - | - | - | -
09-08-18 | 11045 | 11045 | - | - | - | - | - | - | - | - | - | - | - | - | 09-08-18 | 9314.4 | 9314.4 | - | - | - | - | - | - | - | - | - | - | - | -
10-08-18 | 10617 | 10617 | - | - | - | - | - | - | - | - | - | - | - | - | 10-08-18 | 8030.7 | 8030.7 | - | - | - | - | - | - | - | - | - | - | - | -
11-08-18 | 11095 | 11095 | - | - | - | - | - | - | - | - | - | - | - | - | 11-08-18 | 8777.1 | 8777.1 | - | - | - | - | - | - | - | - | - | - | - | -
12-08-18 | 11097 | 11097 | - | - | - | - | - | - | - | - | - | - | - | - | 12-08-18 | 9558.9 | 9558.9 | - | - | - | - | - | - | - | - | - | - | - | -
13-08-18 | 11174 | 11174 | - | - | - | - | - | - | - | - | - | - | - | - | 13-08-18 | 9326 | 9326 | - | - | - | - | - | - | - | - | - | - | - | -
14-08-18 | 11099 | 11099 | - | - | - | - | - | - | - | - | - | - | - | - | 14-08-18 | 9621.4 | 9621.4 | - | - | - | - | - | - | - | - | - | - | - | -
15-08-18 | 10512 | 10512 | - | - | - | - | - | - | - | - | - | - | - | - | 15-08-18 | 8645.2 | 8645.2 | - | - | - | - | - | - | - | - | - | - | - | -
16-08-18 | 11152 | 11152 | - | - | - | - | - | - | - | - | - | - | - | - | 16-08-18 | 9558.9 | 9558.9 | - | - | - | - | - | - | - | - | - | - | - | -
17-08-18 | 10940 | 10940 | - | - | - | - | - | - | - | - | - | - | - | - | 17-08-18 | 8502.7 | 8502.7 | - | - | - | - | - | - | - | - | - | - | - | -
18-08-18 | 10885 | 10885 | - | - | - | - | - | - | - | - | - | - | - | - | 18-08-18 | 9510.7 | 9510.7 | - | - | - | - | - | - | - | - | - | - | - | -
19-08-18 | 10727 | 10727 | - | - | - | - | - | - | - | - | - | - | - | - | 19-08-18 | 9261.4 | 9261.4 | - | - | - | - | - | - | - | - | - | - | - | -
20-08-18 | 9839 | 9839 | - | - | - | - | - | - | - | - | - | - | - | - | 20-08-18 | 8325 | 8325 | - | - | - | - | - | - | - | - | - | - | - | -
21-08-18 | 9064 | 9064 | - | - | - | - | - | - | - | - | - | - | - | - | 21-08-18 | 6644.9 | 6644.9 | - | - | - | - | - | - | - | - | - | - | - | -
22-08-18 | 8955 | 8955 | - | - | - | - | - | - | - | - | - | - | - | - | 22-08-18 | 5700.9 | 5700.9 | - | - | - | - | - | - | - | - | - | - | - | -
23-08-18 | 9040 | 9040 | - | - | - | - | - | - | - | - | - | - | - | - | 23-08-18 | 6999.4 | 6999.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-08-19 | 8996 | 8996 | - | - | - | - | - | - | - | - | - | - | - | - | 24-08-19 | 6543 | 6543 | - | - | - | - | - | - | - | - | - | - | - | -
25-08-20 | 9330 | 9330 | - | - | - | - | - | - | - | - | - | - | - | - | 25-08-20 | 7091.3 | 7091.3 | - | - | - | - | - | - | - | - | - | - | - | -
26-08-18 | 9725 | 9725 | - | - | - | - | - | - | - | - | - | - | - | - | 26-08-18 | 7670 | 7670 | - | - | - | - | - | - | - | - | - | - | - | -
27-08-18 | 9901 | 9901 | - | - | - | - | - | - | - | - | - | - | - | - | 27-08-18 | 7939.2 | 7939.2 | - | - | - | - | - | - | - | - | - | - | - | -
28-08-18 | 10127 | 10127 | - | - | - | - | - | - | - | - | - | - | - | - | 28-08-18 | 8186.8 | 8186.8 | - | - | - | - | - | - | - | - | - | - | - | -
29-08-18 | 10340 | 10340 | - | - | - | - | - | - | - | - | - | - | - | - | 29-08-18 | 8430.4 | 8430.4 | - | - | - | - | - | - | - | - | - | - | - | -
30-08-18 | 10540 | 10540 | - | - | - | - | - | - | - | - | - | - | - | - | 30-08-18 | 8708.3 | 8708.3 | - | - | - | - | - | - | - | - | - | - | - | -
31-08-18 | 10142 | 10142 | - | - | - | - | - | - | - | - | - | - | - | - | 31-08-18 | 7735.6 | 7735.6 | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:August' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11217 | 13/08/18 | 22:00
2 | Maximum day peak Genaration | MW | 9621.4 | 19/08/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 11174 | 13/08/18 | 21:00
4 | Minimum Generation | MW | 5450.6 | 22/08/18 | 9:00
5 | Average of the daily evening peak Genaration | MW | 10324.5161
6 | Average of the daily day peak Genaration | MW | 8305.8548
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6622.2928
12 | Total Generation by IPP | MKWH | 1811.3636 | % of total Gen. | 27.35%
13 | Total Generation by BPDB | MKWH | 3413.6201 | " | 51.55%
14 | A) Total Generation by RPCL | MKWH | 65.1885 | '' | 0.9844%
| B) Total Generation by REB | MKWH | 142.8918 | " | 2.158%
| C) Total Generation by RENTAL | MKWH | 731.208 | " | 11.04%
| D) Total Imported from India (HVDC) | MKWH | 358.5287 | " | 5.414%
| E) Total Imported from Tripura, India (A.C) | MKWH | 99.492 | " | 1.502%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4226.2932 | % of total Gen. | 63.82%
| B) Oil | MKWH | 1801.7112 | '' | 27.21%
| C) Hydro | MKWH | 125.5278 | '' | 1.896%
| D) Solar | MKWH | 0.32205 | '' | 0.004863%
| E) Coal | MKWH | 10.4177 | '' | 0.1573%
| F) HVDC (Import from India) | MKWH | 358.5287 | '' | 5.414%
| G) A.C (Import from Tripura, India) | MKWH | 99.492 | '' | 1.502%
16 | Maximun of the daily total Generation . | MKWH | 249.4998 | 05/08/18
17 | Monthly Load factor | % | 79.3522
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 21850.8262
| A) Gas | M.Taka | 3221.8479
| B) Liquid fuel | M.Taka | 18549.468
| C) Coal | M.Taka | 79.5102
| D) HVDC (Import from India) | M.Taka | 1828.4965
| E) Tripura(Import from India) | M.Taka | 680.5251
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1257.1505 | 05/08/18
| A) Gas | M.Taka | 315.4236 | 27/08/18
| B) Liquid fuel | M.Taka | 1161.4341 | 05/08/18
| C) Coal | M.Taka | 16.2745 | 07/08/18
| D) HVDC (Import from India) | M.Taka | 60.5472 | 10-08-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.6693
| B) Excluding Hydro & Solar | Taka/KWHR | 3.7404
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.67 | 31/08/18 | 06:00
b) | Actual | FT (MSL) | 105.12 | 31/08/18 | 06:00
22 | Peak Genaration of August 2017 | MW | 9470 | 05/08/17 | 21:00
23 | Peak Demand of August 2017 | MW | 9470 | 05/08/17 | 21:00
24 | Maximum peak Generation recorded upto 31/08/18 | MW | 11387 | 18/07/18 | 22:00
25 | Maximum peak Demand recorded upto 31/08/18 | MW | 11306 | 14/07/18 | 21:00
26 | Maximum load shed recorded upto 31/08/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.