## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:July' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | July 2018 |  | June 2018 |  | July 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11387 | 18/07/18 | 10949 | 06/06/18 | 9334 | 16/07/17 | 11387 | 18/07/18
|  |  | 22:00 |  | 22:00 |  | 21:00 |  | 22:00
2 | Minimum Generation (MW) | 6777 | 03/07/18 | 4876 | 16/06/18 | 5106 | 27/07/17 | - | -
|  |  | 7:00 |  | 17:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11306 | 14/07/18 | 10948 | 28/05/18 | 9334 | 16/07/17 | 11306 | 14/07/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9735.4 | 19/07/18 | 9128.2 | 07/06/2018 | 8455 | 18/07/2017 | 9735.4 | 19/07/18
|  |  | 11:00 |  | 12:00 |  | 12:00 |  | 21:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11306 | 14/07/18 | 10958 | 06/06/2018 | 9334 | 16/07/17 | 11306 | 14/07/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 10632.129 |  | 9879.5 |  | 8818.16 |  | 10632.13 | July -18
7 | Average Generation (MW) at Day Peak | 8546.2742 |  | 7768.98 |  | 7316.81 |  | 8546.27 | July -18
8 | Maximum Power Import from India (MW) | 476 | 27/07/18 | 481 | 17/06/18 | 505 | 10/07/17 | 509 | 2017-07-03
|  |  | 14:00 |  | 12:00 |  | 15:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 25/07/18 | 186 | 06/06/18 | 166 | 15/07/17 | 188 | 29/05/18
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3249.9156 |  | 3122.95 |  | 2540.33
21 | Station Use of BPDB (MKWH) | 101.9466 |  | 101.45 |  | 106.11
22 | Net Generation of BPDB (MKWH) | 3147.969 |  | 3021.5 |  | 2434.23
23 | Net Generation of IPP & RPCL (MKWH) | 2054.6654 |  | 1704.95 |  | 1404.81
24 | Net Generation of REB (MKWH) | 145.5424 |  | 132.51 |  | 112.41
24 | Net Generation of Rental Power Plant (MKWH) | 793.0297 |  | 634.29 |  | 1186.13
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6141.2065 |  | 5493.25 |  | 5137.57 |  | 6141.21 | July-18
26 | Energy Generation by Gas (MKWH) | 3894.5643 |  | 3635.45 |  | 3501.99 |  | 3894.56 | July-18
27 | Energy Generation by Diesel (MKWH) | 736.5643 |  | 538.47 |  | 366.55 |  | 736.56 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1413.4924 |  | 1128.82 |  | 1155.48 |  | 1413.49 | July-18
29 | Energy Generation by Hydro (MKWH) | 118.2449 |  | 99.13 |  | 121.44 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.25555 |  | 0.32 |  | 98.23 |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 80.0316 |  | 192.5 |  | 445.04 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 435.2008 |  | 419.73 |  | 77.88 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 78.8292 |  | 76.29 |  | 77.88 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11387 | 18/07/18 | 22:00
Generation Period
| Dhaka | MW | 3965
| Chittagong | MW | 1094
| Comilla | MW | 998
| Mymensingh | MW | 767
| Sylhet | MW | 475
a) | Total supply in East zone | MW | 7299
| Khulna | MW | 1342
| Barisal | MW | 273
| Rajshahi | MW | 1106
| Rangpur | MW | 577
b) | Total supply in West zone | MW | 3298
c) | Total supply in both zone ( a+b) | MW | 10597
Ref: | 27.21.0603.2604.16.084.18.86 | Date: 18/08/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1200 | 19/07/18 | 1:00
| b) Ishurdi end | MW | 140 | 22/07/18 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 340 | 22/07/18 | 17:00
| b) Ishurdi end | MW | 500 | 19/07/18 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 7.4745 | 19/07/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 6.5905 | 19/07/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 117.8567
| b) Ishurdi end | MKWH | 1.5055
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 1.4603
| b) Ishurdi end | MKWH | 114.178
23 | Transmission loss of EWI/ NO-1 | % | 3.12
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 680 | 19/07/18 | 1:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 640 | 19/07/18 | 1:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 12.28 | 19/07/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 11.842 | 19/07/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 236.138
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 232.142
30 | Transmission loss of EWI /NO-2 | % | 1.6922
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | 132/33 kV Transformer-T4 | 2018-07-01 12:18 | 2018-07-01 12:21 | 0:03 | T | Tripped showing lockout relay | 26 | 1.3 | Power interruption
Jamalpur | 132/33 kV Transformers-T1 & T2 | 2018-07-02 18:40 | 2018-07-02 18:44 | 0:04 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2018-07-04 06:30 | 2018-07-04 06:55 | 0:25 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformers-T1 & T2 | 2018-07-07 20:58 | 2018-07-07 21:02 | 0:04 | T | Tripped showing O/C relay | 176 | 11.7333 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2018-07-11 07:40 | 2018-07-11 08:01 | 0:21 | T | Tripped showing O/C relay | 112 | 39.2 | Power interruption
|  |  | Total : | 0:57 |  | Unserved Energy: |  | 52.2333
Dhaka (South) Grid Circle :
Siddhirganj | 132/33 kV Transformer-T1 | 2018-07-02 10:15 | 2018-07-02 10:37 | 0:22 | T | Tripped showing lockout relay | 95 | 34.8333 | Power interruption
Moghbazar | 132/33 kV Transformers-T1 , T2 & T3 | 2018-07-15 17:10 | 2018-07-15 17:30 | 0:20 | T | Tripped showing O/C relay | 134 | 44.6667 | Power interruption
Madanganj | 132/33 kV Transformer-T1 | 2018-07-23 16:35 | 2018-07-23 20:11 | 3:36 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformers-, T2 & T3 | 2018-07-27 21:10 | 2018-07-27 21:16 | 0:06 | T | Tripped showing O/C relay | 44 | 4.4 | Power interruption
Narshingdi | 132/33 kV Transformer-T2 | 2018-07-28 04:40 | 2018-07-28 09:07 | 4:27 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 8:51 |  | Unserved Energy: |  | 83.9
Chittagong Grid Circle :
Madunaghat | 132/33 kV Transformers-T1 | 2018-07-04 12:55 | 2018-07-04 13:05 | 0:10 | T | Tripped showing O/C relay | 32 | 5.3333 | Power interruption 12:55 to 13:05
| 132/33 kV Transformer-T2 | 2018-07-04 12:55 | 2018-07-04 22:17 | 9:22 | T
Halishahar | 132/33 kV Transformer-T3 | 2018-07-04 20:08 | 2018-07-04 20:48 | 0:40 | E/O | Due to red hot maintenance | 10 | 1.6667 | Power interruption 20:08 to 20:18
Hathazari | 132 kV mai Bus secetion-2 | 2018-07-06 05:40 | 2018-07-06 07:38 | 1:58 | E/O | Due to red hot maintenance | 20 | 39.3333 | Power interruption
Khulshi | 132/33 kV Transformer-T1 | 2018-07-29 22:45 | 2018-07-29 23:10 | 0:25 | E/O | Due to red hot maintenance | 50 | 20.8333 | Power interruption
|  |  | Total : | 0:10 |  | Unserved Energy: |  | 67.1667
Comilla Grid Circle :
Fenchuganj | 132/33 kV Transformer-T2 | 2018-07-05 10:53 | 2018-07-05 11:06 | 0:13 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T1 | 2018-07-06 07:30 | 2018-07-06 07:57 | 0:27 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Ashuganj | 132 kV bus-2 | 2018-07-10 14:42 | 2018-07-10 15:46 | 1:04 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T2 | 2018-07-22 17:39 | 2018-07-22 17:59 | 0:20 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-07-28 09:52 | 2018-07-28 10:52 | 1:00 | E/O | Due to red hot maintenance
|  |  | Total : | 3:04 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | 132/33 kV Transformers-T-1 & T2 | 2018-07-03 01:05 | 2018-07-03 01:08 | 0:03 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Patuakahli | 132/33 kV Transformers-T-2 | 2018-07-28 11:23 | 2018-07-28 12:19 | 0:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 0:59 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | 132/33 kV Transformer-T-2 | 2018-07-02 07:07 | 2018-07-02 08:48 | 1:41 | E/O | Due to red hot maintenance | 35 | 58.9167 | Power interruption
Ishurdi | 230/132 kV Transformer-T03 | 2018-07-02 12:50 | 2018-07-02 14:01 | 1:11 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 2:52 |  | Unserved Energy: |  | 58.9167
Bogra Grid Circle:
Palashbari | 132/33 kV Transformer-T-2 | 2018-07-02 17:26 | 2018-07-02 18:40 | 1:14 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformers-T-1 | 2018-07-07 19:35 | 2018-07-07 19:39 | 0:04 | T | Tripped showing O/C relay | 110 | 3.6667 | Power interruption
| 132/33 kV Transformers-T-2 | 2018-07-07 19:35 | 2018-07-07 19:37 | 0:02 | T
Barapukuria | 230/132 kV Transformer-T01 | 2018-07-07 21:43 | 2018-07-07 22:29 | 0:46 | E/O | Due to Oil leakage | 370 | 283.6667 | Power interruption
Shahjadpur | 132/33 kV Transformers-T-4 | 2018-07-09 10:20 | 2018-07-09 11:35 | 1:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2018-07-10 20:15 | 2018-07-10 21:08 | 0:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformers-T-R1 & TR-2 | 2018-07-20 19:16 | 2018-07-20 19:36 | 0:20 | T | Tripped showing O/C relay | 110 | 36.6667 | Power interruption
| 132/33 kV Transformers-T-R1 & TR-2 | 2018-07-21 19:53 | 2018-07-21 19:59 | 0:06 | T | Tripped showing O/C relay | 114 | 11.4 | Power interruption
Bogra | 230/132 kV Transformer-T02 | 2018-07-23 09:46 | 2018-07-23 14:04 | 4:18 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 8:58 |  | Unserved Energy: |  | 335.4
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 25:51 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-07-02 18:11 | 2018-07-02 18:50 | 0:39 | T | Tripped showing O/C & .E/F relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Sherpur 132 kV line-1 & 2 | 2018-07-03 00:25 | 2018-07-03 00:44 | 0:19 | T |  | 200 | 63.3333 | Power interruption
Jamalpur S/S | Jamalpur S/S-Jamalpur P/S 132 kV line-1 & 2 | 2018-07-11 07:43 | 2018-07-11 07:57 | 0:14 | T | Tripped showing dist. relay | 26 | 6.0667 | Power interruption
Tongi | Tongi-Kabirpur 132 kV line-1 & 2 | 2018-07-12 13:08 | 2018-07-12 13:24 | 0:16 | T | Tripped showing dist. relay | 50 | 13.3333 | Power interruption
| Tongi-Kabirpur 132 kV line-2 | 2018-07-17 04:08 | 2018-07-17 04:23 | 0:15 | T | Tripped showing O/C & .E/F relay | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2018-07-18 15:00 | 2018-07-18 16:15 | 1:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-07-19 11:05 | 2018-07-19 11:13 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2018-07-19 12:18 | 2018-07-19 17:58 | 5:40 | T |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2018-07-24 12:01 | 2018-07-24 12:54 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:39 |  | Unserved Energy: |  | 82.7333
Dhaka (South) Grid Circle :
Bashundhara | Bashundhara-Tongi 132 kV line-1 | 2018-07-06 13:27 | 2018-07-06 14:35 | 1:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bashundhara-Tongi 132 kV line-2 | 2018-07-07 13:27 | 2018-07-07 15:53 | 2:26 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2018-07-07 21:03 | 2018-07-07 22:33 | 1:30 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2018-07-09 10:03 | 2018-07-09 10:11 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-1 | 2018-07-12 10:58 | 2018-07-12 12:05 | 1:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2018-07-15 17:57 | 2018-07-15 20:17 | 2:20 | T | Tripped showing O/C & E/F relay | 20 | 46.6667 | Power interruption
| Rampura-Moghbazar 132 kV line-1 | 2018-07-16 06:30 | 2018-07-16 08:55 | 2:25 | E/O | Due to red hot maintenance | 12 | 29 | Power interruption
| Rampura-Moghbazar 132 kV line-2 | 2018-07-17 07:58 | 2018-07-17 09:50 | 1:52 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Hasnabad 132 kV line | 2018-07-19 09:51 | 2018-07-21 00:06 | 38:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2018-07-19 10:36 | 2018-07-19 11:43 | 1:07 | T | Tripped showing DT,PT3,PTAW signal | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2018-07-19 11:15 | 2018-07-19 11:35 | 0:20 | T |  | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2018-07-19 12:12 | 2018-07-19 16:00 | 3:48 | T |  | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2018-07-19 13:14 | 2018-07-19 14:05 | 0:51 | T |  | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-07-28 17:43 | 2018-07-28 17:46 | 0:03 | T | Tripped showing O/C & E/F relay | 62 | 3.1 | Power interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2018-07-30 06:00 | 2018-07-30 08:10 | 2:10 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 59:30 |  | Unserved Energy: |  | 78.7667
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Chandraghona | Chandraghona-Kaptai 132 kV line-2 | 2018-07-14 11:12 | 2018-07-14 18:01 | 6:49 | E/O | Due to SF6 gas filling | 0 | 0 | No interruption
| Chandraghona-Kaptai 132 kV line-1 | 2018-07-14 10:23 | 2018-07-14 10:58 | 0:35 | E/O | Due to SF6 gas filling | 0 | 0 | No interruption
| Chandraghona-Kagrachori 132 kV line-2 | 2018-07-14 09:18 | 2018-07-14 10:13 | 0:55 | E/O | Due to SF6 gas filling | 0 | 0 | No interruption
Khagrachari | Khagrachari-Chandraghona 132 kV line | 2018-07-14 18:34 | 2018-07-14 18:56 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Baraulia | Baraulia-BSRM 132 kV line | 2018-07-21 17:30 | 2018-07-21 18:01 | 0:31 | T | Tripped showing O/C. relay | 25 | 12.9167 | Power interruption
|  |  | Total : | 1:48 |  | Unserved Energy: |  | 12.9167
Comilla Grid Circle :
Chatak | Chatak-Sylhet 132 kV line-1 | 2018-07-01 02:58 | 2018-07-01 03:41 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-2 | 2018-07-04 23:11 | 2018-07-04 23:26 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line-2 | 2018-07-04 23:15 | 2018-07-04 23:17 | 0:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-S.M.Nagar 132 kV line-2 | 2018-07-07 19:47 | 2018-07-08 01:54 | 6:07 | T | Tripped showing dist. relay | 40 | 244.6667 | Power interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2018-07-08 17:46 | 2018-07-08 18:28 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2018-07-10 08:20 | 2018-07-10 16:27 | 8:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2018-07-10 14:42 | 2018-07-10 15:28 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-B.baria 132 kV line-2 | 2018-07-10 14:42 | 2018-07-10 15:28 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV line | 2018-07-10 14:42 | 2018-07-10 15:28 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 | 2018-07-10 14:42 | 2018-07-10 15:35 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Daudkandi 132 kV line-2 | 2018-07-16 20:41 | 2018-07-17 14:57 | 18:16 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-07-19 14:27 | 2018-07-19 23:03 | 8:36 | E/O | Due to bursting of CT at Kishoreganj S/S | 30 | 258 | Power interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2018-07-22 21:10 | 2018-07-22 23:23 | 2:13 | E/O | Due to red hot maintenance | 150 | 332.5 | Power interruption
Chandpur | Chandpur-Comiila(N) 132 kV line-2 | 2018-07-28 07:14 | 2018-07-28 08:02 | 0:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 51:19 |  | Unserved Energy: |  | 835.1667
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-07-13 14:25 | 2018-07-13 15:51 | 0:10 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2018-07-13 18:54 | 2018-07-13 19:01 | 0:07 | T |  | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2018-07-19 15:01 | 2018-07-19 15:24 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Barisal (N) 132 kV line-2 | 2018-07-20 01:23 | 2018-07-20 02:11 | 0:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2018-07-20 04:30 | 2018-07-20 05:54 | 1:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-07-20 12:57 | 2018-07-20 13:17 | 0:20 | T | Tripped showing dist. relay | 319 | 106.3333 | Power interruption
Goalpara | Goalpara-NWPGCL 132 kV line | 2018-07-24 16:29 | 2018-07-24 20:26 | 3:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2018-07-25 04:40 | 2018-07-25 13:37 | 8:57 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-HVDC 230 kV line-1 | 2018-07-26 11:54 | 2018-07-26 12:56 | 1:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Khulna(S)-HVDC 230 kV line-2 | 2018-07-26 11:54 | 2018-07-26 12:54 | 1:00 | T |  | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-07-30 17:15 | 2018-07-30 19:14 | 1:59 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-1 | 2018-07-31 13:22 | 2018-07-31 14:28 | 0:10 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  |  | 20:17 |  | Unserved Energy: |  | 106.3333
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2018-07-01 13:18 | 2018-07-01 16:42 | 3:24 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-07-02 00:21 | 2018-07-02 00:33 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2018-07-19 13:44 | 2018-07-19 14:18 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 230 kV line-1 | 2018-07-26 11:54 | 2018-07-26 12:41 | 0:47 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
| Ishurdi-Bheramara 230 kV line-2 | 2018-07-26 11:54 | 2018-07-26 18:48 | 6:54 | T |  | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 & 2 | 2018-07-26 11:54 | 2018-07-26 12:19 | 0:25 | T | Tripped showing E/F. relay | 875 | 364.5833 | Power interruption
|  |  | Total : | 12:16 |  | Unserved Energy: |  | 364.5833
Bogra Grid Circle :
Sirajganj | Sirajganj-Bagerhat 230 kV line-1 | 2018-07-02 11:03 | 2018-07-02 13:54 | 2:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-07-07 21:43 | 2018-07-07 21:53 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bogra-Palashbari 132 kV line-2 | 2018-07-07 21:43 | 2018-07-07 21:50 | 0:07 | T |  | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-1 | 2018-07-24 23:25 | 2018-07-24 23:52 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Palashbari 132 kV line-2 | 2018-07-30 12:17 | 2018-07-30 12:20 | 0:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 3:38 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | #REF! | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: June 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV Transformer-T-2 | 2018-07-05 11:56 | 2018-07-05 16:48 | 4:52 | S/O | Due to project work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T2 | 2018-07-06 06:07 | 2018-07-06 11:40 | 5:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T2 | 2018-07-13 06:58 | 2018-07-13 10:50 | 3:52 | S/O | Due to high temperature at 132 kV CT | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-07-13 08:51 | 2018-07-13 10:30 | 1:39 | S/O | Due to maintenance work | 15 | 24.75 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2018-07-13 08:51 | 2018-07-13 17:15 | 8:24 | S/O | Due to maintenance work | 40 | 126 | Power interruption
Netrakona | 132/33 kV Transformers-T1 & T2 | 2018-07-14 06:35 | 2018-07-14 11:05 | 4:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2018-07-14 07:48 | 2018-07-14 13:03 | 5:15 | S/O | Due to project work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2018-07-16 12:27 | 2018-07-16 13:56 | 1:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-07-19 06:15 | 2018-07-22 03:06 | 68:51 | S/O | Due to project work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2018-07-20 21:58 | 2018-07-21 04:44 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-B | 2018-07-22 07:33 | 2018-07-22 11:45 | 4:12 | S/O | Due to maintenance work | 60 | 252 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2018-07-23 06:44 | 2018-07-23 07:52 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-07-23 09:53 | 2018-07-23 17:41 | 7:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-07-24 08:49 | 2018-07-24 12:05 | 3:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-07-28 10:28 | 2018-07-28 18:38 | 8:10 | S/O | Due to project work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2018-07-30 06:02 | 2018-07-30 07:52 | 1:50 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2018-07-30 06:40 | 2018-07-30 07:58 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 138:53 |  | Unserved Energy: |  | 402.75
Dhaka (South) Grid Circle :
Bashundhara | 132/33 kV Transformer-T-3 | 2018-07-09 05:17 | 2018-07-09 06:00 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2018-07-10 05:49 | 2018-07-10 08:09 | 2:20 | S/O | Due to C/M work | 40 | 93.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2018-07-11 06:00 | 2018-07-11 08:40 | 2:40 | S/O | Due to C/M work | 15 | 40 | Power interruption
Moghbazar | 132 kV reserve Bus | 2018-07-18 05:43 | 2018-07-18 08:20 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T3 | 2018-07-19 05:14 | 2018-07-19 06:33 | 1:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T1 | 2018-07-28 10:16 | 2018-07-28 10:21 | 0:05 | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-07-28 18:45 | 2018-07-28 19:38 | 0:53 | S/O | Due to maintenance work | 20 | 17.6667 | Power interruption
Rampura | 230/132 kV Transformer-T1 | 2018-07-30 06:06 | 2018-07-30 07:42 | 1:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 12:13 |  | Unserved Energy: |  | 151
Chittagong Grid Circle :
Halishahar | 132 kV Bus | 2018-07-06 06:19 | 2018-07-06 08:02 | 1:43 | S/O | Due to C/M work | 90 | 154.5 | Power interruption
Dohazari | 132/33 kV Transformers-T1 | 2018-07-07 08:28 | 2018-07-07 10:02 | 1:34 | S/O | Due to C/M work | 15 | 17.25 | Power interruption
| 132/33 kV Transformers-T2 | 2018-07-07 10:36 | 2018-07-07 11:45 | 1:09 | S/O
Bakulia | 132/33 kV Transformer-T2 | 2018-07-10 06:11 | 2018-07-10 07:28 | 1:17 | S/O | Due to C/M work | 20 | 25.6667 | Power interruption
Madunaghat | 132/33 kV Transformer-T1 | 2018-07-13 09:45 | 2018-07-13 12:13 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-07-13 09:45 | 2018-07-13 12:13 | 2:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T2 | 2018-07-15 14:25 | 2018-07-15 15:18 | 0:53 | S/O | Due to installation work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T1 | 2018-07-20 07:03 | 2018-07-20 12:45 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2018-07-20 07:43 | 2018-07-20 11:25 | 3:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | 132 kV Bus | 2018-07-28 07:07 | 2018-07-28 13:22 | 6:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2018-07-28 09:15 | 2018-07-28 17:50 | 8:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 34:03 |  | Unserved Energy: |  | 197.4167
Page:2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Bibiyana | 230 kV bus-1 | 2018-07-07 10:18 | 2018-07-07 16:50 | 6:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T2 | 2018-07-11 10:46 | 2018-07-11 12:59 | 7:01 | S/O | Due to project work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T1 & T2 | 2018-07-28 05:55 | 2018-07-28 14:52 | 7:01 | S/O | Due to project work | 9 | 63.15 | Power interruption
|  |  | Total | 20:34 |  | Unserved Energy : |  | 63.15
Khulna Grid Circle :
Magura | 132 kV Bus-B | 2018-07-06 07:32 | 2018-07-06 09:28 | 1:56 | S/O | Due to D/W work | 20 | 38.6667 | Power interruption 07:32 to 9:28
Mongla | 132/33 kV Transformer-T1 | 2018-07-10 17:45 | 2018-07-10 18:05 | 7:01 | S/O | Due to project work | 15 | 105.25 | Power interruption
Barisal | 132 kV Bus-1 | 2018-07-13 09:25 | 2018-07-13 15:08 | 7:01 | S/O | Due to project work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-A | 2018-07-24 08:49 | 2018-07-24 12:09 | 3:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T2 | 2018-07-29 00:38 | 2018-07-29 02:04 | 1:26 | S/O | Due to maintenance work | 20 | 28.6667 | Power interruption
|  |  | Total : | 18:48 |  | Unserved Energy : |  | 172.5833
HVDC Grid Circle :
Jhenidah | 132/33 kV Transformer-T1 | 2018-07-20 09:10 | 2018-07-20 15:59 | 7:01 | S/O | Due to project work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 | 2018-07-24 07:21 | 2018-07-24 08:06 | 7:01 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 14:02 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Palashbari | 132/33 kV Transformer-T2 | 2018-07-07 10:10 | 2018-07-07 13:25 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T1 | 2018-07-10 07:25 | 2018-07-10 10:09 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2018-07-11 10:12 | 2018-07-11 11:44 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 | 2018-07-13 06:58 | 2018-07-13 15:36 | 8:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T1 | 2018-07-16 12:40 | 2018-07-16 17:00 | 4:20 | S/O | Due to C/W work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2018-07-19 07:13 | 2018-07-19 15:36 | 8:23 | S/O | Due to project work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 | 2018-07-20 07:36 | 2018-07-20 09:47 | 2:11 | S/O | Due to project work | 0 | 0 | No interruption
Natore | 132 kV main Bus | 2018-07-21 07:15 | 2018-07-21 10:25 | 3:10 | S/O | Due to project work | 68 | 477.1333 | Power interruption
|  |  | Total : | 34:13 |  | Unserved Energy : |  | 477.1333
Others :
Ghorashal | 230/132 kV Transformer-AT-2 | 2018-06-12 13:59 | 2018-06-13 09:50 | 19:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 19:51 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 292:37 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Uttara | Uttara-Tongi 132 kV line | 2018-07-05 08:38 | 2018-07-05 10:36 | 1:58 | S/O | Due to maintenance work | 0 | 0 | No interruption
United Mymensingh | United Mymensingh-Sherpur S/S 132 kV line-1 | 2018-07-06 08:20 | 2018-07-06 10:54 | 2:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-07-14 09:36 | 2018-07-14 11:05 | 1:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-1 | 2018-07-17 13:50 | 2018-07-17 20:17 | 6:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 12:28 |  | Unserved Energy: |  | 0
QF-LDC-26
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Siddhirganj Peaking 132 kV line | 2018-07-03 10:17 | 2018-07-03 17:03 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-07-04 09:18 | 2018-07-04 17:43 | 8:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj P/S 132 kV line | 2018-07-05 10:07 | 2018-07-05 17:41 | 7:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Siddhirganj-Haripur 132 kV line-2 | 2018-07-06 09:55 | 2018-07-06 12:25 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR Hasnabad 230 kV line | 2018-07-07 06:47 | 2018-07-07 09:59 | 3:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Dutch Bangla 132 kV line | 2018-07-13 08:37 | 2018-07-13 13:05 | 4:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Siddhirganj-Matuail 132 kV line | 2018-07-13 10:01 | 2018-07-13 17:24 | 7:23 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR Energy 230 kV line | 2018-07-15 10:39 | 2018-07-15 11:46 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Lalbagh 132 kV line | 2018-07-18 05:35 | 2018-07-18 17:38 | 12:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Lalbagh 132 kV line | 2018-07-19 09:10 | 2018-07-19 10:11 | 1:01 | S/O | Due to DPDC work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-07-20 07:05 | 2018-07-20 09:21 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR Hasnabad 230 kV line | 2018-07-20 10:04 | 2018-07-20 17:16 | 7:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line | 2018-07-20 17:26 | 2018-07-20 19:46 | 2:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2018-07-25 14:57 | 2018-07-25 16:49 | 1:52 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2018-07-27 05:34 | 2018-07-27 08:34 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR Hasnabad 230 kV line | 2018-07-27 06:34 | 2018-07-27 18:25 | 11:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kamrangirchar 132 kV line | 2018-07-31 11:23 | 2018-07-31 14:20 | 2:57 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 85:57 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Hathazari S/S | Hathazari S/S-Hathazari P/S 132 kV line | 2018-07-07 12:08 | 2018-07-07 14:04 | 1:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-07-09 06:06 | 2018-07-09 06:06 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132 kV line-1 | 2018-07-11 09:51 | 2018-07-11 18:04 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-1 | 2018-07-12 09:17 | 2018-07-12 10:41 | 1:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Kaptai-Chandraghona 132 kV line-2 | 2018-07-12 10:46 | 2018-07-12 11:13 | 0:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kagrachori 132 kV line-2 | 2018-07-12 08:59 | 2018-07-12 21:51 | 12:52 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV line-1 | 2018-07-23 09:41 | 2018-07-23 10:22 | 0:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 25:33 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Sunamganj | Sunamganj-Chatak 132 kV line | 2018-07-05 09:58 | 2018-07-05 13:23 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2018-07-06 12:35 | 2018-07-06 14:58 | 2:23 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Comiila(N) 230 kV line-1 | 2018-07-06 10:20 | 2018-07-06 17:30 | 7:10 | S/O | Due to project work | 0 | 0 | No interruption
| Shahjibazar-Comiila(N) 230 kV line-2 | 2018-07-06 17:34 | 2018-07-06 18:49 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2018-07-07 11:31 | 2018-07-07 16:39 | 5:08 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-1 | 2018-07-08 22:12 | 2018-07-09 00:14 | 2:02 | S/O | Due to project work | 0 | 0 | No interruption
Chatak | Chatak-Sylhet 132 kV line-2 | 2018-07-11 08:43 | 2018-07-11 09:13 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Ramganj 132 kV line-2 | 2018-07-28 10:20 | 2018-07-28 16:13 | 5:53 | S/O | Due to project work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line | 2018-07-29 09:32 | 2018-07-29 17:40 | 8:08 | S/O | Due to project work | 0 | 0 | No interruption
| Ramganj-Chowmuhani 132 kV line-2 | 2018-07-31 09:46 | 2018-07-31 18:40 | 8:54 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 199:39 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Khulna Grid Circle :
Noapara | Noapara-Khulna© 132 kV line-1 | 2018-07-11 08:02 | 2018-07-11 09:34 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna 225 P/S 132 kV line | 2018-07-13 07:13 | 2018-07-13 08:52 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Faridpur 132 kV line-2 | 2018-07-17 07:24 | 2018-07-17 11:43 | 4:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari132 kV line-1 | 2018-07-21 08:21 | 2018-07-21 18:36 | 10:15 | S/O | Due to project work | 0 | 0 | No interruption
| Khulna(S)-Gallamari132 kV line-1 | 2018-07-22 08:27 | 2018-07-22 18:40 | 10:13 | S/O | Due to project work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari132 kV line-1 | 2018-07-24 08:16 | 2018-07-24 18:03 | 9:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-07-24 09:41 | 2018-07-24 16:29 | 6:48 | S/O | Due to project work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari132 kV line-1 | 2018-07-25 09:11 | 2018-07-25 19:29 | 10:18 | S/O | Due to project work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Gallamari 132 kV line-1 | 2018-07-27 07:32 | 2018-07-27 17:33 | 10:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2018-07-31 08:04 | 2018-07-31 09:09 | 1:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 & 2 | 2018-07-20 09:28 | 2018-07-20 18:27 | 8:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Bheramara-Ishurdi 230 kV line-2 | 2018-07-28 11:34 | 2018-07-28 14:44 | 3:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 12:09 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-07-06 06:49 | 2018-07-06 19:58 | 13:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-07-06 07:34 | 2018-07-06 09:04 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2018-07-06 09:06 | 2018-07-06 12:37 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-07-07 06:53 | 2018-07-07 11:48 | 4:55 | S/O | Due to D/W work | 10 | 49.1667 | Power interruption
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2018-07-13 06:40 | 2018-07-13 10:09 | 3:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| Palashbari-Rangpur 132 kV line-2 | 2018-07-13 10:16 | 2018-07-13 12:07 | 1:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 | 2018-07-20 07:18 | 2018-07-20 17:48 | 10:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sirajganj-Bogra 132 kV line-1 | 2018-07-21 07:42 | 2018-07-21 17:27 | 9:45 | S/O | Due to project work | 0 | 0 | No interruption
| Bogra-Sirajganj 132 kV line-1 | 2018-07-22 08:10 | 2018-07-22 18:00 | 9:50 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-1 | 2018-07-25 04:45 | 2018-07-25 07:05 | 2:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar P/S 132 kV line | 2018-07-28 08:50 | 2018-07-28 10:30 | 1:40 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 132 kV line-1 | 2018-07-29 07:44 | 2018-07-29 16:45 | 9:01 | S/O | Due to project work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 | 2018-07-30 07:20 | 2018-07-30 17:29 | 10:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 81:40 |  | Unserved Energy: |  | 49.1667
Others :
Bangabhban | Babgabhban-Manikngar 132 kV line-1 | 2018-07-06 08:37 | 2018-07-06 12:59 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 4:22 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | #REF! | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July' 2018
| Area | Previous Month (June 2018) |  |  |  | Current Month (July 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 17 | 5 | 26 | 48 | 13 | 1 | 21 | 35
2 | Dhaka (South) Grid Circle. | 16 | 3 | 21 | 40 | 16 | 4 | 25 | 45
3 | Chittagong Grid Circle. | 20 | 9 | 8 | 37 | 4 | 6 | 18 | 28
4 | Comilla Grid Circle. | 21 | 3 | 12 | 36 | 15 | 4 | 13 | 32
5 | Khulna Grid Circle. | 8 | 2 | 7 | 17 | 10 | 4 | 15 | 29
6 | Bheramara HVDC Grid Circle | 4 | 3 | 11 | 18 | 6 | 2 | 4 | 12
7 | Bogra Grid Circle. | 10 | 12 | 17 | 39 | 9 | 5 | 21 | 35
8 | Others | 1 | - | 3 | 4 | - | - | 2 | 2
9 | Total | 97 | 37 | 105 | 239 | 73 | 26 | 119 | 218
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July' 2018
| Area | Previous Month (June 2018) |  |  |  | Current Month (July 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 3 | 42.5 | 702.12 | 747.62 | 134.96 | - | 402.75 | 537.71
2 | Dhaka ( South) grid circle | 18.7 | 30.4 | 221 | 270.1 | 133.67 | 29 | 151 | 313.67
3 | Chittagong grid circle. | 151.16 | 32 | 153.4 | 336.56 | 18.25 | 61.84 | 197.42 | 277.51
4 | Comilla grid circle. | 498.52 | - | - | 498.52 | 244.67 | 590.5 | 63.15 | 898.32
5 | Khulna grid circle. | 17.07 | - | 14 | 31.07 | 106.33 | - | 172.58 | 278.91
6 | Bheramara HVDC grid circle | - | 58.92 | - | 58.92 | 364.58 | 58.92 | - | 423.5
7 | Bogra grid circle. | 60.6 | 22.75 | 269.62 | 352.97 | 51.74 | 283.67 | 526.3 | 861.71
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 749.05 | 186.57 | 1360.14 | 2295.76 | 1054.2 | 1023.93 | 1513.2 | 3591.33
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 3 | 3 | 6 | 3 | - | 3 | 10 | 11
1 | Dhaka (North) | 5308 | 2 | 3 | 5 | 1 | - | 4 | 454.98
2 | Dhaka (South) | 5031.6 | 3 | 3 | 6 | 3 | 1 | 2 | 234.9
3 | Chittagong | 2042 | 4 | 3 | 7 | 2 | 1 | 4 | 264.59
4 | Khulna | 2434 | - | 3 | 3 |  | - | 3 | 172.58
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | - | - | 1 | 58.92
6 | Bogra | 3145.6 | 4 | 1 | 5 | 3 | 1 | 1 | 812.53
7 | Comilla | 2981 | - | 1 | 1 |  | - | 1 | 63.15
| Total | 23365.5 | [6 empty] | 2061.65
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chittagong | 99.97%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.89% | [6 empty] | Executive Engineer
6 | Bogra | 99.92% | [6 empty] | Information Management Division
7 | Comilla | 100% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 3 | - | 3 | 3 | - |  | 82.73
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 1 | - | 2 | 78.77
3 | Chittagong | 917 | 20+9(Partial) | 1 | - | 1 | 1 | - | - | 12.92
4 | Khulna | 1238.4 | 21 | 1 | - | 1 | 1 | - | - | 106.33
5 | Bheramara (HVDC) | 598.7 |  | 1 | - | 1 | 1 | - | - | 364.58
6 | Bogra | 1803.3 | 38 | - | 1 | 1 | 1 | - | 1 | 49.17
7 | Comilla | 1648.16 | 17 | 3 | - | 3 | - | - | 3 | 835.17
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1529.67
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.78%
2 | Dhaka (South) | 99.95%
3 | Chittagong | 99.76%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.86% | [7 empty] | Executive Engineer
6 | Bogra | 99.91% | [7 empty] | Information Management Division
7 | Comilla | 99.76% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
June | 12 | - | 4 | 04hr16 min | 1 | 05hr04 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:July' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Joydevpur | 1 | 0:03 | 26 | 1.3 | Due to tripping of 132/33 kV Transformer T4
Mymensingh | 3 | 0:04 | 176 | 11.7333 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:21 | 112 | 39.2
|  | 0:19 | 200 | 63.3333 | Due to tripping of Mymensingh-Sherpur 132 kV line-1 & 2
Jamalpur | 1 | 0:14 | 26 | 6.0667 | Due to tripping of Jamalpur S/S-Jamalpur P/S 132 kV line-1 & 2
Tongi | 1 | 0:16 | 50 | 13.3333 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
Netrakona | 2 | 1:39 | 15 | 24.75 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 8:24 | 40 | 126
Kishoreganj | 1 | 4:12 | 60 | 252 | Due to S/D of 132 kV Bus-B
Siddhirganj | 1 | 0:22 | 95 | 34.8333 | Due to tripping of 132/33 kV Transformer T1
Moghbazar |  | 0:20 | 134 | 44.6667 | Due to tripping of 132/33 kV Transformers T1 , T2& T3
Munshiganj | 1 | 0:06 | 44 | 4.4 | Due to tripping of 132/33 kV Transformers T2 ,& T3
Rampura | 2 | 2:20 | 20 | 46.6667 | Due to tripping of Rampura-Moghbazar 132 kV line-2 & 1
|  | 2:25 | 12 | 29
Hasnabad | 1 | 0:03 | 62 | 3.1 | Due to tripping of Hasnabad-Kamrangirchar 132 kV line
Siddhirganj | 2 | 2:20 | 40 | 93.3333 | Due to S/D of 132/33 kV Transformer T1
|  | 2:40 | 15 | 40 | Due to S/D of 132/33 kV Transformer T2
Narsinghdi | 1 | 0:53 | 20 | 17.6667 | Due to S/D of 132/33 kV Transformer T2
Madunaghat | 1 | 0:10 | 32 | 5.3333 | Due to tripping of 132/33 kV Transformer T1
Halishahar |  | 0:10 | 10 | 1.6667 | Due to tripping of 132/33 kV Transformers T2
Hathazari |  | 1:58 | 20 | 39.3333 | Due to tripping of 132/33 kV Transformers T3
Khulshi |  | 0:25 | 50 | 20.8333 | Due to tripping of 132/33 kV Transformers T1
Baraulia | 1 | 0:31 | 25 | 12.9167 | Due to tripping of Baraulia-BSRM 132 kV line
Halishahar | 1 | 1:43 | 90 | 154.5 | Due to S/D of 132 kV bus
Dhohazari | 1 | 1:34 | 15 | 17.25 | Due to S/D of 132/33 kV Transformer T1
Bakulia | 1 | 1:17 | 20 | 25.6667 | Due to S/D of 132/33 kV Transformer T2
Comiila(N) | 1 | 6:07 | 40 | 244.6667 | Due to tripping of Comilla(N)-SM nagar 132 kV line-2
Ashuganj | 2 | 8:36 | 30 | 258 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-1
|  | 2:13 | 150 | 332.5 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-2
Sreemongal | 1 | 7:01 | 9 | 63.15 | Due to S/D of 132/33 kV Transformers T1 &T2
Bagerhat | 1 | 0:20 | 319 | 106.3333 | Due to tripping of Bagerhat-Bhandaria 132 kV line
Magura | 1 | 1:56 | 20 | 38.6667 | Due to S/D of 132 kV bus
Mongla | 1 | 7:01 | 15 | 105.25 | Due to S/D of 132/33 kV Transformer T1
Patuakhali | 1 | 1:26 | 20 | 28.6667 | Due to S/D of 132/33 kV Transformer T2
Bheramara | 2 | 1:41 | 35 | 58.9167 | Due to red-hot mainteanance of 132/33 kV Transformer T2
|  | 0:31 | 875 | 364.5833 | Due to tripping of Bheramara-Ishurdi 132 kV line- 1 & 2
Rangpur | 1 | 0:02 | 110 | 3.6667 | Due to tripping of 132/33 kV Transformer T01
Barapukuria | 1 | 0:46 | 370 | 283.6667 | Due to tripping of 230/132 kV Transformer T01
Rangpur | 2 | 0:20 | 110 | 36.6667 | Due to tripping of 132/33 kV Transformer T01
|  | 0:06 | 114 | 11.4 | Due to tripping of 132/33 kV Transformer T02
Natore | 1 | 3:10 | 68 | 477.1333 | Due to S/D of 132 kV bus
Bogra | 1 | 4:55 | 10 | 49.1667 | Due to S/D of Bogra-Palashbari 132 kV line -2
| Total unserved energy : |  |  | 3591.3167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 142 | 19 | 2018-07-01 | 14:00
2 | Munsiganj | 118 | 7 | 2018-07-01 | 21:00
3 | Megnaghat | 153 | 23 | 2018-07-01 | 21:00
4 | Shyampur | 172 | 26 | 2018-07-01 | 10:00
5 | Bhulta | 196 | 15 | 2018-07-01 | 12:00
6 | Madanganj | 61 | 10 | 2018-07-01 | 21:000
7 | Shitalakhya | 120 | 15 | 2018-07-01 | 16:00
8 | Rahim steel | 17 | 28 | 2018-07-01 | 12:00
9 | Matuail | 115 | 16 | 2018-07-01 | 16:00
10 | Ghorasal | 98 | 14 | 2018-07-01 | 21:00
11 | Narsingdi | 126 | 10 | 2018-07-01 | 21:00
12 | Haripur (SBU) | 102 | 30 | 2018-07-01 | 12:00
13 | Ullon | 105 | 19 | 2018-07-01 | 19:00
14 | Hasnabad | 226 | 19 | 2018-07-01 | 21:00
15 | Magbazar | 162 | 19 | 2018-07-01 | 15:00
16 | Maniknagar | 108 | 19 | 2018-07-01 | 12:00
17 | Bangabhaban | 44 | 19 | 2018-07-01 | 13:00
18 | Narinda | 100 | 12 | 2018-07-01 | 16:00
19 | Dhanmondi | 151 | 19 | 2018-07-01 | 13:00
20 | Lalbag | 94 | 10 | 2018-07-01 | 21:00
21 | Madartek | 63 | 9 | 2018-07-01 | 19:30
22 | Mirpur | 113 | 19 | 2018-07-01 | 19:30
23 | Kalyanpur | 130 | 14 | 2018-07-01 | 12:00
24 | Gulshan | 166 | 19 | 2018-07-01 | 13:00
25 | Uttara | 99 | 19 | 2018-07-01 | 1:00
26 | Kamrangirchar | 91 | 4 | 2018-07-01 | 12:00
27 | Savar | 164 | 16 | 2018-07-01 | 21:00
28 | Bhasantec | 177 | 19 | 2018-07-01 | 15:00
29 | Agargaon | 59 | 12 | 2018-07-01 | 20:00
30 | Satmosjid | 111 | 19 | 2018-07-01 | 15:00
31 | Tongi | 153 | 22 | 2018-07-01 | 19:30
32 | Kabirpur | 217 | 22 | 2018-07-01 | 14:00
33 | Basundhara | 132 | 15 | 2018-07-01 | 21:00
34 | Manikganj | 115 | 19 | 2018-07-01 | 20:00
35 | Joydevpur | 243 | 9 | 2018-07-01 | 11:00
36 | New Tongi | 130 | 31 | 2018-07-01 | 20:00
37 | Kodda | 271 | 31 | 2018-07-01 | 19:30
38 | Dhamrai | 124 | 11 | 2018-07-01 | 23:00
39 | Tangail | 187 | 20 | 2018-07-01 | 1:00
40 | Mymensing | 260 | 19 | 2018-07-01 | 21:00
41 | Kishorganj | 108 | 25 | 2018-07-01 | 21:00
42 | Netrokona | 87 | 9 | 2018-07-01 | 19:30
43 | Jamalpur | 116 | 5 | 2018-07-01 | 22:00
44 | Sherpur | 86 | 6 | 2018-07-01 | 21:00
45 | Srimongal | 43 | 28 | 2018-07-01 | 22:00
46 | Shahjibazar | 113 | 19 | 2018-07-01 | 22:00
47 | Fenchuganj | 52 | 19 | 2018-07-01 | 20:00
48 | Kulawara | 47 | 14 | 2018-07-01 | 22:00
49 | Sylhet | 160 | 19 | 2018-07-01 | 18:30
50 | Chatak | 30 | 19 | 2018-07-01 | 20:00
51 | Sunamganj | 134 | 29 | 2018-07-01 | 21:00
52 | Bianibazar | 49 | 19 | 2018-07-01 | 21:00
53 | Cumilla (S) | 172 | 25 | 2018-07-01 | 21:00
54 | Cumilla(N) | 147 | 19 | 2018-07-01 | 19:30
55 | Chandpur | 120 | 6 | 2018-07-01 | 22:00
56 | Feni | 133 | 18 | 2018-07-01 | 22:00
57 | Chowmuhani | 188 | 14 | 2018-07-01 | 20:00
58 | Ashuganj | 65 | 18 | 2018-07-01 | 23:00
59 | Daudkandi | 116 | 9 | 2018-07-01 | 20:00
60 | B.Baria | 156 | 27 | 2018-07-01 | 21:00
61 | Ramganj | 140 | 27 | 2018-07-01 | 21:00
62 | Madanhat | 63 | 1 | 2018-07-01 | 19:30
63 | Hathazari | 96 | 19 | 2018-07-01 | 20:00
64 | Khulshi | 208 | 19 | 2018-07-01 | 15:00
65 | Halishahar | 142 | 15 | 2018-07-01 | 14:00
66 | Baraulia | 176 | 12 | 2018-07-01 | 2:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Sikalbaha | 39 | 1 | 2018-07-01 | 21:00
68 | Dohazari | 92 | 6 | 2018-07-01 | 21:00
69 | Cox'sbazar | 96 | 2 | 2018-07-01 | 20:00
70 | Chandraghona | 35 | 1 | 2018-07-01 | 21:00
71 | Kaptai | 4 | 1 | 2018-07-01 | 21:00
72 | A. Khaer Stl. | 21 | 1 | 2018-07-01 | 23:00
73 | Bakulia | 114 | 19 | 2018-07-01 | 20:00
74 | Julda | 22 | 21 | 2018-07-01 | 13:00
75 | TK chemical | 7 | 4 | 2018-07-01 | 01:00
76 | Modern Steel | 14 | 9 | 2018-07-01 | 17:00
77 | Shahmirpur | 30 | 10 | 2018-07-01 | 21:00
78 | Abul Khair 230 | 199 | 31 | 2018-07-01 | 5:00
79 | BSRM | 120 | 25 | 2018-07-01 | 20:00
80 | Khagrachhari | 18 | 19 | 2018-07-01 | 19:00
81 | Goalpara | 45 | 1 | 2018-07-01 | 20:00
82 | Central s/s | 96 | 21 | 2018-07-01 | 21:00
83 | Noapara | 93 | 2 | 2018-07-01 | 19:30
84 | Jashore | 152 | 1 | 2018-07-01 | 21:00
85 | Jhenida | 102 | 7 | 2018-07-01 | 20:00
86 | Bottail | 134 | 15 | 2018-07-01 | 21:00
87 | G.K Project | 56 | 18 | 2018-07-01 | 21:00
88 | Faridpur | 155 | 30 | 2018-07-01 | 21:00
89 | Madaripur | 152 | 22 | 2018-07-01 | 22:00
90 | Gopalganj | 86 | 19 | 2018-07-01 | 22:00
91 | Bagerhat | 86 | 23 | 2018-07-01 | 21:00
92 | Mongla | 38 | 7 | 2018-07-01 | 20:00
93 | Satkhira | 103 | 19 | 2018-07-01 | 21:00
94 | Gallamari | 52 | 14 | 2018-07-01 | 13:00
95 | Magura | 56 | 1 | 2018-07-01 | 20:00
96 | Chuadanga | 115 | 31 | 2018-07-01 | 20:00
97 | Barishal | 124 | 12 | 2018-07-01 | 19:30
98 | Patuakhali | 92 | 18 | 2018-07-01 | 21:00
99 | Bhandaria | 55 | 30 | 2018-07-01 | 22:00
100 | Ishurdi | 58 | 9 | 2018-07-01 | 1:00
101 | Ruppur Paromanobik | 2 | 8 | 2018-07-01 | 9:00
102 | Natore | 120 | 7 | 2018-07-01 | 20:00
103 | Bogura | 255 | 4 | 2018-07-01 | 20:00
104 | Noagaon | 112 | 20 | 2018-07-01 | 19:30
105 | Rajshahi | 161 | 19 | 2018-07-01 | 20:00
106 | C.Nawabganj | 77 | 19 | 2018-07-01 | 21:00
107 | Amnura | 49 | 20 | 2018-07-01 | 1:00
108 | Pabna | 122 | 18 | 2018-07-01 | 20:00
109 | Shahjadpur | 100 | 19 | 2018-07-01 | 21:00
110 | Serajganj | 98 | 18 | 2018-07-01 | 20:00
111 | Niyamatpur | 66 | 20 | 2018-07-01 | 19:30
112 | Joypurhat | 45 | 1 | 2018-07-01 | 21:00
113 | Rangpur | 130 | 28 | 2018-07-01 | 20:00
114 | Lalmonirhat | 85 | 2 | 2018-07-01 | 20:00
115 | Saidpur | 114 | 21 | 2018-07-01 | 21:00
116 | Purbasadipur | 97 | 12 | 2018-07-01 | 20:00
117 | Thakurgaon | 76 | 19 | 2018-07-01 | 21:00
118 | Palashbari | 104 | 7 | 2018-07-01 | 20:00
119 | Barapukuria | 98 | 18 | 2018-07-01 | 19:30
120 | Panchagar | 40 | 18 | 2018-07-01 | 19:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:July' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 4288 | 19.07.18 | 16:00
Chittagong | 1262 | 18.07.18 | 23:00
Khulna | 1363 | 15.07.18 | 21:00
Rajshahi | 1175 | 20.07.18 | 20:00
Comilla | 1018 | 14.07.18 | 20:00
Mymensingh | 782 | 06.07.18 | 22:00
Sylhet | 509 | 19.07.18 | 19:30
Barisal | 283 | 22.07.18 | 21:00
Rangpur | 643 | 03.07.18 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 406 | 7 | 2018-07-01 | 06:00 | 362 | 13 | 2018-06-01 | 20:00
2 | Bheramara | 400 | 411 | 4 | 2018-07-01 | 6:00 | 382 | 19 | 2018-06-01 | 12:00
3 | Ashuganj(N) | 400 | 395 | 28 | 2018-07-01 | 6:00 | 361 | 21 | 2018-06-01 | 12:00
4 | Kaliakoir | 400 | 397 | 27 | 2018-07-01 | 17:00 | 358 | 22 | 2018-06-01 | 15:00
5 | Bhulta | 400 | 398 | 27 | 2018-07-01 | 15:00 | 369 | 22 | 2018-06-01 | 16:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 235 | 16 | 2018-07-01 | 18:30 | 218 | 13 | 2018-07-01 | 1:00
2 | Ishurdi | 230 | 236 | 1 | 2018-07-01 | 13:00 | 212 | 25 | 2018-07-01 | 21:00
3 | Ashuganj | 230 | 240 | 26 | 2018-07-01 | 7:00 | 199 | 25 | 2018-07-01 | 22:00
4 | Serajganj | 230 | 240 | 25 | 2018-07-01 | 23:00 | 210 | 12 | 2018-07-01 | 22:00
5 | Baghabari | 230 | 233 | 16 | 2018-07-01 | 18:30 | 205 | 31 | 2018-07-01 | 19:30
6 | Barapukuria | 230 | 237 | 1 | 2018-07-01 | 15:00 | 194 | 16 | 2018-07-01 | 21:00
7 | Bogra | 230 | 241 | 31 | 2018-07-01 | 18:30 | 195 | 23 | 2018-07-01 | 19:00
8 | Khulna South | 230 | 243 | 26 | 2018-07-01 | 06'00 | 215 | 16 | 2018-07-01 | 14:00
9 | Rampura | 230 | 226 | 27 | 2018-07-01 | 04:00 | 214 | 22 | 2018-07-01 | 16:00
10 | Haripur | 230 | 232 | 25 | 2018-07-01 | 7:00 | 214 | 22 | 2018-07-01 | 11:00
11 | Hasnabad | 230 | 227 | 12 | 2018-07-01 | 1:00 | 211 | 13 | 2018-07-01 | 24:00
12 | Aminbazar | 230 | 228 | 25 | 2018-07-01 | 06:00 | 213 | 22 | 2018-07-01 | 15:00
13 | Tongi | 230 | 239 | 25 | 2018-07-01 | 24:00 | 210 | 22 | 2018-07-01 | 15:00
14 | Comilla (N) | 230 | 236 | 27 | 2018-07-01 | 19:30 | 211 | 31 | 2018-07-01 | 15:00
15 | Hathazari | 230 | 228 | 31 | 2018-07-01 | 1:00 | 207 | 12 | 2018-07-01 | 10:00
16 | Megnaghat | 230 | 239 | 31 | 2018-07-01 | 3:00 | 217 | 13 | 2018-07-01 | 11:00
17 | Fenchuganj | 230 | 241 | 27 | 2018-07-01 | 7:00 | 208 | 13 | 2018-07-01 | 15:00
18 | Siddhirganj | 230 | 229 | 27 | 2018-07-01 | 19:30 | 209 | 13 | 2018-07-01 | 16:00
19 | Maniknagar | 230 | 226 | 27 | 2018-07-01 | 19:00 | 212 | 22 | 2018-07-01 | 17:00
20 | Old Airport | 230 | 237 | 25 | 2018-07-01 | 07:00 | 211 | 22 | 2018-07-01 | 16:00
21 | Barisal | 230 | 242 | 6 | 2018-07-01 | 10:00 | 206 | 31 | 2018-07-01 | 10:00
22 | AKSML | 230 | 235 | 25 | 2018-07-01 | 01:00 | 204 | 12 | 2018-07-01 | 19:30
23 | BSRM | 230 | 236 | 21 | 2018-07-01 | 07:00 | 207 | 12 | 2018-07-01 | 10:00
24 | Bibiyana | 230 | 239 | 28 | 2018-07-01 | 07:00 | 209 | 13 | 2018-07-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 139 | 27 | 2018-07-01 | 19:30 | 128 | 3 | 2018-07-01 | 10:00
2 | Munsiganj | 132 | 140 | 27 | 2018-07-01 | 19:30 | 128 | 8 | 2018-07-01 | 8:00
3 | Megnaghat | 132 | 136 | 29 | 2018-07-01 | 19:30 | 125 | 22 | 2018-07-01 | 16:00
4 | Shyampur | 132 | 136 | 29 | 2018-07-01 | 20:00 | 122 | 3 | 2018-07-01 | 10:00
5 | Bhulta | 132 | 132 | 13 | 2018-07-01 | 18:00 | 120 | 3 | 2018-07-01 | 10:00
6 | Madanganj | 132 | 140 | 29 | 2018-07-01 | 19:30 | 124 | 22 | 2018-07-01 | 17:00
7 | Shitalakhya | 132 | 141 | 18 | 2018-07-01 | 24:00 | 124 | 22 | 2018-07-01 | 17:00
8 | Rahim Steal | 132 | 140 | 27 | 2018-07-01 | 19:30 | 128 | 22 | 2018-07-01 | 10:00
9 | Matuail | 132 | 138 | 27 | 2018-07-01 | 20:00 | 127 | 3 | 2018-07-01 | 12:00
10 | Ghorasal | 132 | 140 | 2 | 2018-07-01 | 23:00 | 130 | 16 | 2018-07-01 | 14:00
11 | Narsinghdi | 132 | 137 | 28 | 2018-07-01 | 18:30 | 122 | 21 | 2018-07-01 | 12:00
12 | Haripur (SBU) | 132 | 139 | 27 | 2018-07-01 | 19:30 | 128 | 16 | 2018-07-01 | 12:00
13 | Ullon | 132 | 138 | 27 | 2018-07-01 | 6:00 | 126 | 5 | 2018-07-01 | 12:00
14 | Hasnabad | 132 | 140 | 18 | 2018-07-01 | 24:00 | 121 | 24 | 2018-07-01 | 11:00
15 | Magbazar | 132 | 140 | 27 | 2018-07-01 | 5:00 | 124 | 19 | 2018-07-01 | 16:00
16 | Maniknagar | 132 | 143 | 27 | 2018-07-01 | 19:30 | 125 | 21 | 2018-07-01 | 12:00
17 | Bangabhaban | 132 | 143 | 27 | 2018-07-01 | 19:30 | 125 | 21 | 2018-07-01 | 12:00
18 | Narinda | 132 | 143 | 27 | 2018-07-01 | 19:30 | 125 | 21 | 2018-07-01 | 12:00
19 | Dhanmondi | 132 | 141 | 28 | 2018-07-01 | 6:00 | 126 | 16 | 2018-07-01 | 12:00
20 | Lalbag | 132 | 138 | 1 | 2018-07-01 | 22:00 | 121 | 3 | 2018-07-01 | 10:00
21 | Madartek | 132 | 140 | 27 | 2018-07-01 | 5:00 | 124 | 19 | 2018-07-01 | 16:00
22 | Mirpur | 132 | 138 | 28 | 2018-07-01 | 4:00 | 126 | 1 | 2018-07-01 | 18:00
23 | Kalyanpur | 132 | 137 | 11 | 2018-07-01 | 6:00 | 124 | 7 | 2018-07-01 | 17:00
24 | Gulshan | 132 | 138 | 27 | 2018-07-01 | 4:00 | 124 | 19 | 2018-07-01 | 16:00
25 | Uttara | 132 | 137 | 19 | 2018-07-01 | 1:00 | 122 | 16 | 2018-07-01 | 12:00
26 | Kamrangirchar | 132 | 138 | 29 | 2018-07-01 | 19:30 | 122 | 19 | 2018-07-01 | 15:00
27 | Savar | 132 | 136 | 4 | 2018-07-01 | 2:00 | 118 | 2 | 2018-07-01 | 14:00
28 | Bhasantec | 132 | 136 | 12 | 2018-07-01 | 3:00 | 122 | 22 | 2018-07-01 | 16:00
29 | Agargaon | 132 | 135 | 27 | 2018-07-01 | 5:00 | 124 | 16 | 2018-07-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 135 | 28 | 2018-07-01 | 2:00 | 124 | 3 | 2018-07-01 | 10:00
31 | Tongi | 132 | 138 | 8 | 2018-07-01 | 02:00 | 125 | 7 | 2018-07-01 | 16:00
32 | Kabirpur | 132 | 138 | 27 | 2018-07-01 | 16:00 | 122 | 2 | 2018-07-01 | 11:00
33 | Basundhara | 132 | 135 | 28 | 2018-07-01 | 2:00 | 124 | 7 | 2018-07-01 | 21:00
34 | Manikganj | 132 | 141 | 28 | 2018-07-01 | 3:00 | 129 | 7 | 2018-07-01 | 19:30
35 | Joydevpur | 132 | 141 | 8 | 2018-07-01 | 14:00 | 126 | 12 | 2018-07-01 | 8:00
36 | New Tongi | 132 | 138 | 18 | 2018-07-01 | 18:00 | 126 | 3 | 2018-07-01 | 10:00
37 | Kodda | 132 | 140 | 8 | 2018-07-01 | 18:00 | 123 | 4 | 2018-07-01 | 24:00
38 | Dhamrai | 132 | 138 | 28 | 2018-07-01 | 01:00 | 124 | 7 | 2018-07-01 | 20:00
39 | Tangail | 132 | 140 | 28 | 2018-07-01 | 05:00 | 122 | 7 | 2018-07-01 | 20:00
40 | Mymensing | 132 | 135 | 28 | 2018-07-01 | 11:00 | 113 | 4 | 2018-07-01 | 1:00
41 | Kishorganj | 132 | 135 | 19 | 2018-07-01 | 15:00 | 117 | 22 | 2018-07-01 | 21:00
42 | Netrokona | 132 | 135 | 28 | 2018-07-01 | 17:00 | 115 | 15 | 2018-07-01 | 21:00
43 | Jamalpur | 132 | 138 | 1 | 2018-07-01 | 17:00 | 111 | 4 | 2018-07-01 | 1:00
44 | Sherpur | 132 | 138 | 1 | 2018-07-01 | 17:00 | 110 | 4 | 2018-07-01 | 1:00
45 | Srimongal | 132 | 141 | 28 | 2018-07-01 | 6:00 | 130 | 7 | 2018-07-01 | 21:00
46 | Shahjibazar | 132 | 140 | 29 | 2018-07-01 | 08:00 | 130 | 10 | 2018-07-01 | 19:00
47 | Fenchuganj | 132 | 138 | 28 | 2018-07-01 | 07:00 | 129 | 7 | 2018-07-01 | 19:00
48 | Khulawara | 132 | 137 | 18 | 2018-07-01 | 10:00 | 128 | 6 | 2018-07-01 | 21:00
49 | Sylhet | 132 | 137 | 28 | 2018-07-01 | 7:00 | 125 | 7 | 2018-07-01 | 20:00
50 | Chattak | 132 | 137 | 15 | 2018-07-01 | 6:00 | 122 | 7 | 2018-07-01 | 21:00
51 | Sunamganj | 132 | 135 | 14 | 2018-07-01 | 13:00 | 122 | 5 | 2018-07-01 | 21:00
52 | Biani Bazar | 132 | 137 | 16 | 2018-07-01 | 08:00 | 123 | 7 | 2018-07-01 | 21:00
53 | Comilla(South) | 132 | 129 | 2 | 2018-07-01 | 6:00 | 116 | 30 | 2018-07-01 | 20:00
54 | Comilla (North) | 132 | 138 | 19 | 2018-07-01 | 10:00 | 130 | 6 | 2018-07-01 | 23:00
55 | Chandpur | 132 | 140 | 27 | 2018-07-01 | 8:00 | 120 | 7 | 2018-07-01 | 19:30
56 | Feni | 132 | 125 | 25 | 2018-07-01 | 7:00 | 112 | 14 | 2018-07-01 | 23:00
57 | Chowmuhani | 132 | 129 | 25 | 2018-07-01 | 8:00 | 111 | 14 | 2018-07-01 | 21:00
58 | Ashuganj | 132 | 140 | 2 | 2018-07-01 | 7:00 | 130 | 10 | 2018-07-01 | 17:00
59 | Daudkandi | 132 | 140 | 17 | 2018-07-01 | 23:00 | 124 | 17 | 2018-07-01 | 8:00
60 | Brahminbaria | 132 | 140 | 28 | 2018-07-01 | 10:00 | 128 | 10 | 2018-07-01 | 19:00
61 | Ramganj | 132 | 132 | 26 | 2018-07-01 | 7:00 | 112 | 15 | 2018-07-01 | 22:00
62 | Madanhat | 132 | 136 | 19 | 2018-07-01 | 17:00 | 126 | 12 | 2018-07-01 | 16:00
63 | Hathazari | 132 | 132 | 22 | 2018-07-01 | 05:00 | 123 | 12 | 2018-07-01 | 10:00
64 | Khulshi | 132 | 130 | 28 | 2018-07-01 | 7:00 | 120 | 8 | 2018-07-01 | 15:00
65 | Halishahar | 132 | 132 | 13 | 2018-07-01 | 8:00 | 123 | 12 | 2018-07-01 | 15:00
66 | Baraulia | 132 | 130 | 3 | 2018-07-01 | 3:00 | 122 | 12 | 2018-07-01 | 11:00
67 | Sikalbaha | 132 | 132 | 6 | 2018-07-01 | 8:00 | 120 | 8 | 2018-07-01 | 14:00
68 | Dohazari | 132 | 130 | 3 | 2018-07-01 | 6:00 | 123 | 9 | 2018-07-01 | 15:00
69 | Cox'sbazar | 132 | 128 | 6 | 2018-07-01 | 8:00 | 110 | 19 | 2018-07-01 | 9:00
70 | Chandraghona | 132 | 133 | 2 | 2018-07-01 | 21:00 | 120 | 20 | 2018-07-01 | 3:00
71 | Kaptai | 132 | 132 | 1 | 2018-07-01 | 21:00 | 125 | 2 | 2018-07-01 | 12:00
72 | A. Khaer Stl. | 132 | 130 | 26 | 2018-07-01 | 15:00 | 123 | 2 | 2018-07-01 | 16:00
73 | Bakulia | 132 | 130 | 6 | 2018-07-01 | 7:00 | 122 | 12 | 2018-07-01 | 12:00
74 | Julda | 132 | 133 | 6 | 2018-07-01 | 7:00 | 124 | 2 | 2018-07-01 | 12:00
75 | TK Chemical | 132 | 134 | 6 | 2018-07-01 | 7:00 | 127 | 2 | 2018-07-01 | 12:00
76 | Modern Steel | 132 | 131 | 6 | 2018-07-01 | 7:00 | 123 | 2 | 2018-07-01 | 12:00
77 | Shahmirpur | 132 | 131 | 4 | 2018-07-01 | 02:00 | 124 | 2 | 2018-07-01 | 11:00
78 | Khagrachhari | 132 | 132 | 6 | 2018-07-01 | 5:00 | 118 | 12 | 2018-07-01 | 3:00
79 | Goalpara | 132 | 138 | 1 | 2018-07-01 | 21:00 | 125 | 16 | 2018-07-01 | 12:00
80 | Khulna Central | 132 | 142 | 26 | 2018-07-01 | 13:00 | 121 | 10 | 2018-07-01 | 5:00
81 | Noapara | 132 | 140 | 26 | 2018-07-01 | 13:00 | 122 | 16 | 2018-07-01 | 21:00
82 | Jessore | 132 | 132 | 21 | 2018-07-01 | 14:00 | 118 | 7 | 2018-07-01 | 21:00
83 | Jhenida | 132 | 139 | 26 | 2018-07-01 | 13:00 | 112 | 16 | 2018-07-01 | 21:00
84 | Bottail | 132 | 139 | 26 | 2018-07-01 | 13:00 | 124 | 16 | 2018-07-01 | 21:00
85 | G.K.Project | 132 | 143 | 16 | 2018-07-01 | 18:00 | 132 | 16 | 2018-07-01 | 21:00
86 | Faridpur | 132 | 137 | 13 | 2018-07-01 | 20:00 | 118 | 4 | 2018-07-01 | 23:00
87 | Madaripur | 132 | 136 | 3 | 2018-07-01 | 18:30 | 120 | 14 | 2018-07-01 | 21:00
88 | Gopalganj | 132 | 141 | 13 | 2018-07-01 | 20:00 | 118 | 5 | 2018-07-01 | 21:00
89 | Bagerhat | 132 | 137 | 21 | 2018-07-01 | 15:00 | 122 | 16 | 2018-07-01 | 21:00
90 | Mongla | 132 | 135 | 4 | 2018-07-01 | 5:00 | 120 | 16 | 2018-07-01 | 21:00
91 | Satkhira | 132 | 137 | 17 | 2018-07-01 | 19:00 | 120 | 16 | 2018-07-01 | 21:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
92 | Gallamari | 132 | 138 | 1 | 2018-07-01 | 22:00 | 122 | 16 | 2018-07-01 | 10:00
93 | Magura | 132 | 140 | 26 | 2018-07-01 | 13:00 | 110 | 7 | 2018-07-01 | 21:00
94 | Chuadanga | 132 | 135 | 26 | 2018-07-01 | 14:00 | 103 | 16 | 2018-07-01 | 21:00
95 | Barisal | 132 | 140 | 6 | 2018-07-01 | 9:00 | 123 | 13 | 2018-07-01 | 19:00:
96 | Patuakhali | 132 | 138 | 6 | 2018-07-01 | 9:00 | 123 | 13 | 2018-07-01 | 21:00
97 | Bhandaria | 132 | 138 | 2 | 2018-07-01 | 17:00 | 120 | 13 | 2018-07-01 | 19:00
98 | Ishurdi | 132 | 142 | 6 | 2018-07-01 | 18:00 | 130 | 14 | 2018-07-01 | 19:30
99 | Ruppur Paromanobik | 132 | 141 | 6 | 2018-07-01 | 1:00 | 130 | 10 | 2018-07-01 | 13:00
100 | Natore | 132 | 140 | 8 | 2018-07-01 | 18:30 | 122 | 16 | 2018-07-01 | 21:00
101 | Bogra | 132 | 137 | 2 | 2018-07-01 | 18:00 | 114 | 31 | 2018-07-01 | 19:30
102 | Noagaon | 132 | 131 | 1 | 2018-07-01 | 15:00 | 105 | 16 | 2018-07-01 | 21:00
103 | Rajshahi | 132 | 138 | 16 | 2018-07-01 | 18:30 | 122 | 15 | 2018-07-01 | 20:00
104 | C.Nawabganj | 132 | 138 | 5 | 2018-07-01 | 18:30 | 122 | 15 | 2018-07-01 | 20:00
105 | Amnura | 132 | 147 | 13 | 2018-07-01 | 7:00 | 122 | 16 | 2018-07-01 | 21:00
106 | Pabna | 132 | 135 | 1 | 2018-07-01 | 17:00 | 122 | 14 | 2018-07-01 | 20:00
107 | Shahjadpur | 132 | 140 | 1 | 2018-07-01 | 14:00 | 127 | 16 | 2018-07-01 | 21:00
108 | Serajganj | 132 | 135 | 1 | 2018-07-01 | 17:00 | 119 | 16 | 2018-07-01 | 21:00
109 | Niyamatpur | 132 | 135 | 1 | 2018-07-01 | 14:00 | 99 | 16 | 2018-07-01 | 21:00
110 | Joypurhat | 132 | 134 | 1 | 2018-07-01 | 14:00 | 101 | 16 | 2018-07-01 | 21:00
111 | Rangpur | 132 | 132 | 1 | 2018-07-01 | 14:00 | 94 | 16 | 2018-07-01 | 21:00
112 | Lalmonirhat | 132 | 130 | 1 | 2018-07-01 | 15:00 | 83 | 16 | 2018-07-01 | 21:00
113 | Saidpur | 132 | 131 | 1 | 2018-07-01 | 14:00 | 93 | 15 | 2018-07-01 | 21:00
114 | Purbasadipur | 132 | 135 | 1 | 2018-07-01 | 12:00 | 100 | 14 | 2018-07-01 | 20:00
115 | Thakurgaon | 132 | 130 | 1 | 2018-07-01 | 13:00 | 90 | 23 | 2018-07-01 | 19:30
116 | Palashbari | 132 | 131 | 1 | 2018-07-01 | 15:00 | 95 | 16 | 2018-07-01 | 21:00
117 | Barapukuria | 132 | 144 | 24 | 2018-07-01 | 6:00 | 104 | 23 | 2018-07-01 | 19:30
118 | Panchagar | 132 | 140 | 16 | 2018-07-01 | 7:00 | 86 | 23 | 2018-07-01 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:July' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 140 | 420
IP-299421 | Hasnabad | TR2 | 225 | 120 | 420 | 21.07.18 | 17:00
|  | TR3 | 225 | 120 | 400
|  | TR1 | 225 | 160 | 500
IP-299866 | Tongi | TR2 | 225 | 160 | 500 | 18.07.18 | 15:00
|  | TR3 | 225 | 160 | 500
|  | TR1 | 225 | 119 | 345
IP-299427 | Haripur | TR2 | 225 | 119 | 345 | 04.07.18 | 08:00
|  | TR3 | 225 | 119 | 345
|  | TR1 | 225 | 175 | 575
IP-299728 | Rampura | TR2 | 225 | 175 | 575 | 19.07.18 | 16:00
|  | TR3 | 225 | 175 | 575
|  | TR1 | 225 | 145 | 436
IP-299264 | Aminbazar | TR2 | 225 | 145 | 436 | 19.07.18 | 17:00
|  | TR3 | 225 | 151 | 455
| Maniknagar | TR1 | 300 | 125 | 400 | 19.07.18 | 16:00
|  | TR2 | 300 | 125 | 400
IP-399266 | Comilla (N) | TR1 | 225 | 160 | 500 | 14.07.18 | 23:00
|  | TR2 | 225 | 161 | 506
| Fenchuganj | TR1 | 300 | 173 | 443 | 15.07.18 | 24':00
|  | TR1 | 150 | 80 | 220
IP-399428 | Hathazari | TR3 | 150 | 80 | 220 | 21.07.18 | 12:00
|  | TR4 | 150 | 80 | 220
|  | TR1 | 225 | 140 | 430
| Ishurdi | TR2 | 225 | 140 | 430 | 18.07.18 | 21:00
IP-499474 |  | TR3 | 225 | 140 | 430
| Khulna(S) | TR1 | 225 | 171 | 437
IP-58001/58002 |  | TR2 | 225 | 171 | 437 | 19.07.18 | 4:00
| Bogra | TR1 | 225 | 127 | 419 | 11.07.18 | 21:00
|  | TR2 | 225 | 127 | 419
IP-43002/499264 |  | TR3 | 225 | 170 | 554
IP-499224 | Baghabari | TR1 | 225 | 160 | 475 | 18.07.18 | 22:00
| Barapukuria | TR1 | 225 | 196 | 1000 | 02.07.18 | 20:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 97 | 480 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 124 | 642
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:July' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:July' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-07-18 | 10490 | 10490 | - | - | - | - | - | - | - | - | - | - | - | - | 01-07-18 | 8702 | 8702 | - | - | - | - | - | - | - | - | - | - | - | -
02-07-18 | 10639 | 10639 | - | - | - | - | - | - | - | - | - | - | - | - | 02-07-18 | 8587.3 | 8587.3 | - | - | - | - | - | - | - | - | - | - | - | -
03-07-18 | 10057 | 10057 | - | - | - | - | - | - | - | - | - | - | - | - | 03-07-18 | 7895 | 7895 | - | - | - | - | - | - | - | - | - | - | - | -
04-07-18 | 10046 | 10046 | - | - | - | - | - | - | - | - | - | - | - | - | 04-07-18 | 8241 | 8241 | - | - | - | - | - | - | - | - | - | - | - | -
05-07-18 | 10754 | 10754 | - | - | - | - | - | - | - | - | - | - | - | - | 05-07-18 | 8253.7 | 8253.7 | - | - | - | - | - | - | - | - | - | - | - | -
06-07-18 | 10426 | 10426 | - | - | - | - | - | - | - | - | - | - | - | - | 06-07-18 | 7249.7 | 7249.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-07-18 | 11059 | 11059 | - | - | - | - | - | - | - | - | - | - | - | - | 07-07-18 | 8524 | 8524 | - | - | - | - | - | - | - | - | - | - | - | -
08-07-18 | 10791 | 10791 | - | - | - | - | - | - | - | - | - | - | - | - | 08-07-18 | 9009.8 | 9009.8 | - | - | - | - | - | - | - | - | - | - | - | -
09-07-18 | 10966 | 10966 | - | - | - | - | - | - | - | - | - | - | - | - | 09-07-18 | 8946.9 | 8946.9 | - | - | - | - | - | - | - | - | - | - | - | -
10-07-18 | 10975 | 10975 | - | - | - | - | - | - | - | - | - | - | - | - | 10-07-18 | 8979 | 8979 | - | - | - | - | - | - | - | - | - | - | - | -
11-07-18 | 11210 | 11210 | - | - | - | - | - | - | - | - | - | - | - | - | 11-07-18 | 9119 | 9119 | - | - | - | - | - | - | - | - | - | - | - | -
12-07-18 | 11149 | 11149 | - | - | - | - | - | - | - | - | - | - | - | - | 12-07-18 | 9458 | 9458 | - | - | - | - | - | - | - | - | - | - | - | -
13-07-18 | 10304 | 10304 | - | - | - | - | - | - | - | - | - | - | - | - | 13-07-18 | 7810.4 | 7810.4 | - | - | - | - | - | - | - | - | - | - | - | -
14-07-18 | 11306 | 11306 | - | - | - | - | - | - | - | - | - | - | - | - | 14-07-18 | 8783.2 | 8783.2 | - | - | - | - | - | - | - | - | - | - | - | -
15-07-18 | 11113 | 11113 | - | - | - | - | - | - | - | - | - | - | - | - | 15-07-18 | 9267.9 | 9267.9 | - | - | - | - | - | - | - | - | - | - | - | -
16-07-18 | 10978 | 10978 | - | - | - | - | - | - | - | - | - | - | - | - | 16-07-18 | 8838.1 | 8838.1 | - | - | - | - | - | - | - | - | - | - | - | -
17-07-18 | 10928 | 10928 | - | - | - | - | - | - | - | - | - | - | - | - | 17-07-18 | 8971 | 8971 | - | - | - | - | - | - | - | - | - | - | - | -
18-07-18 | 11184 | 11184 | - | - | - | - | - | - | - | - | - | - | - | - | 18-07-18 | 9516.9 | 9516.9 | - | - | - | - | - | - | - | - | - | - | - | -
19-07-18 | 11144 | 11144 | - | - | - | - | - | - | - | - | - | - | - | - | 19-07-18 | 9735.4 | 9735.4 | - | - | - | - | - | - | - | - | - | - | - | -
20-07-18 | 10357 | 10357 | - | - | - | - | - | - | - | - | - | - | - | - | 20-07-18 | 8463.8 | 8463.8 | - | - | - | - | - | - | - | - | - | - | - | -
21-07-18 | 10621 | 10621 | - | - | - | - | - | - | - | - | - | - | - | - | 21-07-18 | 7876 | 7876 | - | - | - | - | - | - | - | - | - | - | - | -
22-07-18 | 10670 | 10670 | - | - | - | - | - | - | - | - | - | - | - | - | 22-07-18 | 8186.4 | 8186.4 | - | - | - | - | - | - | - | - | - | - | - | -
23-07-18 | 10271 | 10271 | - | - | - | - | - | - | - | - | - | - | - | - | 23-07-18 | 8713.5 | 8713.5 | - | - | - | - | - | - | - | - | - | - | - | -
24-07-19 | 9945 | 9945 | - | - | - | - | - | - | - | - | - | - | - | - | 24-07-19 | 8203 | 8203 | - | - | - | - | - | - | - | - | - | - | - | -
25-07-20 | 10340 | 10340 | - | - | - | - | - | - | - | - | - | - | - | - | 25-07-20 | 8224.7 | 8224.7 | - | - | - | - | - | - | - | - | - | - | - | -
26-07-18 | 10256 | 10256 | - | - | - | - | - | - | - | - | - | - | - | - | 26-07-18 | 8326.7 | 8326.7 | - | - | - | - | - | - | - | - | - | - | - | -
27-07-18 | 9613 | 9613 | - | - | - | - | - | - | - | - | - | - | - | - | 27-07-18 | 7091.9 | 7091.9 | - | - | - | - | - | - | - | - | - | - | - | -
28-07-18 | 10263 | 10263 | - | - | - | - | - | - | - | - | - | - | - | - | 28-07-18 | 7817 | 7817 | - | - | - | - | - | - | - | - | - | - | - | -
29-07-18 | 10552 | 10552 | - | - | - | - | - | - | - | - | - | - | - | - | 29-07-18 | 8436.8 | 8436.8 | - | - | - | - | - | - | - | - | - | - | - | -
30-07-18 | 10538 | 10538 | - | - | - | - | - | - | - | - | - | - | - | - | 30-07-18 | 8744.4 | 8744.4 | - | - | - | - | - | - | - | - | - | - | - | -
31-07-18 | 10651 | 10651 | - | - | - | - | - | - | - | - | - | - | - | - | 31-07-18 | 8962 | 8962 | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:July' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11387 | 18/07/18 | 22:00
2 | Maximum day peak Genaration | MW | 9735.4 | 19/07/18 | 11:00
3 | Maximum Evening Peak Demand | MW | 11306 | 14/07/18 | 21:00
4 | Minimum Generation | MW | 6777 | 03/07/18 | 7:00
5 | Average of the daily evening peak Genaration | MW | 10632.129
6 | Average of the daily day peak Genaration | MW | 8546.2742
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6678.3538
12 | Total Generation by IPP | MKWH | 2013.1225 | % of total Gen. | 30.14%
13 | Total Generation by BPDB | MKWH | 3249.9156 | " | 48.66%
14 | A) Total Generation by RPCL | MKWH | 41.5429 | '' | 0.6221%
| B) Total Generation by REB | MKWH | 145.5424 | " | 2.179%
| C) Total Generation by RENTAL | MKWH | 793.0297 | " | 11.87%
| D) Total Imported from India (HVDC) | MKWH | 340.7484 | " | 5.102%
| E) Total Imported from Tripura, India (A.C) | MKWH | 94.4525 | " | 1.414%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3894.5643 | % of total Gen. | 58.32%
| B) Oil | MKWH | 2150.0567 | '' | 32.19%
| C) Hydro | MKWH | 118.2449 | '' | 1.771%
| D) Solar | MKWH | 0.25555 | '' | 0.003827%
| E) Coal | MKWH | 80.0316 | '' | 1.198%
| F) HVDC (Import from India) | MKWH | 340.7484 | '' | 5.102%
| G) A.C (Import from Tripura, India) | MKWH | 94.4525 | '' | 1.414%
16 | Maximun of the daily total Generation . | MKWH | 240.6369 | 19/07/18
17 | Monthly Load factor | % | 78.8292
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 21600.9675
| A) Gas | M.Taka | 2716.5008
| B) Liquid fuel | M.Taka | 18506.318
| C) Coal | M.Taka | 378.1488
| D) HVDC (Import from India) | M.Taka | 1737.8166
| E) Tripura(Import from India) | M.Taka | 646.0548
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1019.2848 | 19/07/18
| A) Gas | M.Taka | 105.1931 | 23/07/18
| B) Liquid fuel | M.Taka | 913.4036 | 19/07/18
| C) Coal | M.Taka | 95.5144 | 30/07/18
| D) HVDC (Import from India) | M.Taka | 59.0005 | 28-07-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 4.225
| B) Excluding Hydro & Solar | Taka/KWHR | 4.3013
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/18 | 06:00
b) | Actual | FT (MSL) | 102.96 | 31/07/18 | 06:00
22 | Peak Genaration of July 2017 | MW | 9334 | 16/07/17 | 21:00
23 | Peak Demand of July 2017 | MW | 9334 | 16/07/17 | 21:00
24 | Maximum peak Generation recorded upto 31/07/18 | MW | 11387 | 18/07/18 | 22:00
25 | Maximum peak Demand recorded upto 31/07/18 | MW | 11306 | 14/07/18 | 21:00
26 | Maximum load shed recorded upto 31/07/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.