## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:June' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | June 2018 |  | May 2018 |  | June 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10949 | 06/06/18 | 10958 | 28/05/18 | 9479 | 07/06/17 | 10958 | 28/05/18
|  |  | 22:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 4876 | 16/06/18 | 4453.1 | 01/05/18 | 4931 | 12/06/17 | - | -
|  |  | 17:00 |  | 7:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10948 | 06/06/18 | 10958 | 28/05/18 | 9479 | 07/06/17 | 10958 | 28/05/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9178.2 | 07/06/18 | 9123.3 | 30/05/2018 | 8743 | 07/06/2017 | 9123.3 | 30/05/18
|  |  | 12:00 |  | 12:00 |  | 11:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10948 | 06/06/18 | 10958 | 28/05/2018 | 9479 | 07/06/17 | 10958 | 28/05/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9879.5 |  | 9278.4 |  | 8545.53 |  | 9296.54 | March -18
7 | Average Generation (MW) at Day Peak | 7768.9767 |  | 7343.17 |  | 7069.87 |  | 7779.98 | March -18
8 | Maximum Power Import from India (MW) | 481 | 17/06/18 | 493 | 12/05/18 | 502 | 05/06/17 | 509 | 2017-07-03
|  |  | 12:00 |  | 8:00 |  | 1:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 186 | 06/06/18 | 188 | 29/05/18 | 158 | 07/06/17 | 188 | 29/05/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3122.9495 |  | 2983.89 |  | 2767.58
21 | Station Use of BPDB (MKWH) | 101.4481 |  | 99.22 |  | 98.67
22 | Net Generation of BPDB (MKWH) | 3021.5015 |  | 2884.67 |  | 2668.91
23 | Net Generation of IPP & RPCL (MKWH) | 1704.9514 |  | 1500.97 |  | 1222.58
24 | Net Generation of REB (MKWH) | 132.5074 |  | 139.44 |  | 101.68
24 | Net Generation of Rental Power Plant (MKWH) | 634.2874 |  | 661.35 |  | 889.09
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5493.2477 |  | 5186.44 |  | 4882.27 |  | 5677.06 | June-18
26 | Energy Generation by Gas (MKWH) | 3635.45 |  | 3455.5 |  | 3489.81 |  | 3749.7 | June-18
27 | Energy Generation by Diesel (MKWH) | 538.4746 |  | 444.89 |  | 317.76 |  | 557.37 | June-18
28 | Energy Generation by Furnace Oil (MKWH) | 1128.8208 |  | 1095.13 |  | 996.68 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 99.1335 |  | 61.25 |  | 87.62 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.31596 |  | 0.34 |  |  |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 192.501 |  | 228.54 |  | 89.08 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 419.7293 |  | 428.88 |  | 427.08 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 76.2934 |  | 70.09 |  | 77.88 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:June' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10949 | 06/06/18 | 21:00
Generation Period
| Dhaka | MW | 3986
| Chittagong | MW | 1072
| Comilla | MW | 961
| Mymensingh | MW | 625
| Sylhet | MW | 424
a) | Total supply in East zone | MW | 7068
| Khulna | MW | 1337
| Barisal | MW | 274
| Rajshahi | MW | 1115
| Rangpur | MW | 620
b) | Total supply in West zone | MW | 3346
c) | Total supply in both zone ( a+b) | MW | 10414
Ref: | 27.21.0603.2604.16.084.18.86 | Date: 18/07/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1080 | 15/06/18 | 13:00
| b) Ishurdi end | MW | - | - | -
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | - | - | -
| b) Ishurdi end | MW | 490 | 15/06/18 | 13:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 7.392 | 21/06/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 7.0924 | 21/06/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 160.0766
| b) Ishurdi end | MKWH | 0.050182
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.048676
| b) Ishurdi end | MKWH | 156.0145
23 | Transmission loss of EWI/ NO-1 | % | 2.53
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 600 | 02/06/18 | 20:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 580 | 02/06/18 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 10.444 | 12/06/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 10.096 | 12/06/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 252.842
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 248.882
30 | Transmission loss of EWI /NO-2 | % | 1.566
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400/230 kV Transformer-T1 | 2018-06-06 00:20 | 2018-06-06 01:36 | 1:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T1, T2 & T3 | 2018-06-08 18:50 | 2018-06-08 18:52 | 0:02 | T | Tripped showing O/C relay | 90 | 3 | Power interruption
Netrakona | 132/33 kV Transformer-T2 | 2018-06-14 10:30 | 2018-06-14 11:50 | 1:07 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformers-T1, & T2 | 2018-06-23 09:05 | 2018-06-23 10:30 | 1:25 | E/O | Due to red hot maintenance | 30 | 42.5 | Power interruption
|  |  | Total : | 3:50 |  | Unserved Energy: |  | 45.5
Dhaka (South) Grid Circle :
Siddhirganj | 132/33 kV Transformer-T1 | 2018-06-08 15:13 | 2018-06-08 16:20 | 1:07 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ghorashal | 230 kV Bus-3&4 | 2018-06-12 13:59 | 2018-06-12 15:28 | 1:29 | T | Tripped showing CB933 & CB943 | 0 | 0 | No interruption
|  |  | Total : | 2:36 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
BSRM | 230/132 kV Transformer-TR-1 | 2018-06-02 09:19 | 2018-06-02 11:57 | 2:38 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Sikalbaha | 132 kV bus-2 | 2018-06-03 08:30 | 2018-06-03 10:50 | 2:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2018-06-08 10:10 | 2018-06-08 10:47 | 0:37 | E/O | Due to Oil filling | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T3 | 2018-06-24 16:52 | 2018-06-24 18:57 | 2:05 | T | Tripped showing PRD realy | 24 | 133.3333 | Power interruption
Cox'sbazar | 132/33 kV Transformer-T2 | 2018-06-28 21:19 | 2018-06-28 22:55 | 1:36 | E/O | Due to red hot maintenance | 20 | 32 | Power interruption
|  |  | Total : | 2:38 |  | Unserved Energy: |  | 165.3333
Comilla Grid Circle :
Sylhet | 132/33 kV Transformer-T4 | 2018-06-03 21:51 | 2018-06-03 22:40 | 0:49 | T | Tripped showing winding temperature high | 64 | 52.2667 | Power interruption
Sylhet | 132/33 kV Transformer-T1 | 2018-06-06 08:40 | 2018-06-06 12:40 | 4:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Comiila(N) | 132/33 kV Transformer-T4 | 2018-06-07 06:27 | 2018-06-07 07:37 | 1:10 | T | Tripped showing Bus protection failure | 20 | 23.3333 | Power interruption
Shahjibazar | 132/33 kV Transformers-T4 & T6 | 2018-06-21 04:30 | 2018-06-21 04:45 | 0:15 | T | Tripped showing E/F relay | 32 | 8 | Power interruption
|  |  | Total : | 6:14 |  | Unserved Energy: |  | 83.6
Khulna Grid Circle :
Noapara | 132/33 kV Transformer-T-4 | 2018-06-01 09:37 | 2018-06-01 09:58 | 0:21 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformers-T-1 & T2 | 2018-06-18 14:10 | 2018-06-18 14:18 | 0:08 | T | Tripped showing O/C relay | 96 | 12.8 | Power interruption
Faridpur | 132/33 kV Transformers-T-1 & T2 | 2018-06-20 23:04 | 2018-06-20 23:10 | 0:06 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Mongla | 132/33 kV Transformers-T-1 & T2 | 2018-06-21 11:17 | 2018-06-21 11:25 | 0:08 | T | Tripped showing E/F relay | 32 | 4.2667 | Power interruption
Bhandaria | 132/33 kV Transformer-T-1 | 2018-06-22 19:27 | 2018-06-22 20:05 | 0:38 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
|  |  | Total : | 0:35 |  | Unserved Energy: |  | 17.0667
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T-2 | 2018-07-20 07:07 | 2018-07-20 08:48 | 1:41 | E/O | Due to red hot maintenance | 35 | 58.9167 | Power interruption
Bheramara | 230/132 kV Transformer-T1 | 2018-06-26 03:07 | 2018-06-26 06:39 | 3:32 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Jessore | 132 kV capacitor bank | 2018-06-27 11:35 | 2018-06-27 13:16 | 1:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 6:54 |  | Unserved Energy: |  | 58.9167
Bogra Grid Circle:
Amnura | 132/33 kV Transformer-T-1 | 2018-06-02 12:35 | 2018-06-02 12:40 | 0:05 | T | Tripped showing Over Voltage | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-T1 | 2018-06-02 10:21 | 2018-06-02 11:06 | 0:45 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-T1 | 2018-06-10 15:42 | 2018-06-10 16:45 | 1:03 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-3 | 2018-06-12 07:15 | 2018-06-12 08:15 | 1:00 | E/O | Due to red hot maintenance | 5 | 5 | Power interruption
Amnura | 132/33 kV Transformer-T-1 | 2018-06-13 10:18 | 2018-06-13 11:02 | 0:44 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T-2 | 2018-06-17 21:46 | 2018-06-18 11:20 | 13:34 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T-6 | 2018-06-20 10:20 | 2018-06-20 11:55 | 1:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T-1 | 2018-06-23 18:34 | 2018-06-23 18:39 | 0:05 | T | Tripped showing O/C relay | 8 | 0.66667 | Power interruption
Saidpur | 132/33 kV Transformer-T-4 | 2018-06-29 11:20 | 2018-06-29 11:35 | 0:15 | E/O | Due to Oil leakage | 9 | 2.25 | Power interruption
Palashbari | 132/33 kV Transformer-T-2 | 2018-06-29 10:38 | 2018-06-29 11:18 | 0:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 19:46 |  | Unserved Energy: |  | 7.9167
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 42:33 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | Tangail-Mymensingh 132 kV line-1 | 2018-06-02 13:11 | 2018-06-02 16:16 | 3:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakor 230 kV line-1 | 2018-06-06 00:20 | 2018-06-07 17:08 | 40:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2018-06-06 13:41 | 2018-06-06 16:59 | 3:18 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2018-06-07 09:59 | 2018-06-07 10:04 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 | 2018-06-08 02:33 | 2018-06-08 02:42 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-06-09 14:28 | 2018-06-09 14:47 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2018-06-10 15:50 | 2018-06-10 17:25 | 1:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2018-06-12 14:07 | 2018-06-12 14:32 | 0:25 | T | Tripped showing CSW,CAT, CD, & CE signal | 0 | 0 | No interruption
| Kabirpur-Tongi 132 kV line-2 | 2018-06-12 14:07 | 2018-06-12 16:27 | 2:20 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 & 2 | 2018-06-15 23:22 | 2018-06-16 13:38 | 14:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh RPCL | Mymensingh RPCL-Mymensingh S/S 132 kV line-1 & 2 | 2018-06-17 23:58 | 2018-06-18 00:09 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh RPCL-Mymensingh S/S 132 kV line-1 | 2018-06-20 21:15 | 2018-06-20 21:38 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-06-23 11:40 | 2018-06-23 11:50 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-06-28 08:43 | 2018-06-28 09:02 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-2 | 2018-06-28 08:43 | 2018-06-28 09:09 | 0:26 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2018-06-28 09:57 | 2018-06-28 17:27 | 7:30 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-06-29 14:34 | 2018-06-29 14:56 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-2 | 2018-06-29 14:34 | 2018-06-29 14:58 | 0:24 | T
|  |  | Total : | 76:05 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj Dutch Bangla 132 kV line | 2018-06-01 16:35 | 2018-06-01 21:35 | 5:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2018-06-03 10:01 | 2018-06-03 10:44 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-06-04 11:55 | 2018-06-04 11:58 | 0:03 | T | Tripped showing dist. relay | 70 | 3.5 | Power interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-1 | 2018-06-04 11:55 | 2018-06-04 12:14 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-APR 230 kV line | 2018-06-06 13:02 | 2018-06-06 13:30 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2018-06-07 21:03 | 2018-06-07 21:25 | 0:22 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-2 | 2018-06-07 21:03 | 2018-06-07 21:29 | 0:26 | T |  | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2018-06-09 18:45 | 2018-06-09 19:25 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Ullon 132 kV line-2 | 2018-06-09 23:31 | 2018-06-09 23:59 | 0:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Siddhirganj -Ullon 132 kV line-2 | 2018-06-10 05:47 | 2018-06-10 12:22 | 6:35 |  |  | 0 | 0 | No interruption
| Siddhirganj -Haripur 132 kV line-1 & 2 | 2018-06-11 12:16 | 2018-06-11 12:22 | 0:06 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Rahim Steel 132 kV line | 2018-06-11 12:16 | 2018-06-11 17:20 | 5:04 | E/O | Due to bursting of lightning arrester | 6 | 30.4 | Power interruption
| Haripur-Bhulta 230 kV line | 2018-06-12 15:20 | 2018-06-12 15:38 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-06-12 16:06 | 2018-06-12 20:20 | 4:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2018-06-16 04:57 | 2018-06-16 06:26 | 1:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2018-06-24 15:38 | 2018-06-24 15:52 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2018-06-24 17:21 | 2018-06-24 17:30 | 0:09 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-06-29 09:21 | 2018-06-29 09:33 | 0:12 | T | Tripped showing dist. relay | 76 | 15.2 | Power interruption
|  |  | Total : | 26:50 |  | Unserved Energy: |  | 49.1
Chittagong Grid Circle :
Baraulia | Baraulia-Hathazari 132 kV line-1 | 2018-06-04 17:32 | 2018-06-04 17:48 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Baraulia-Hathazari 132 kV line-2 | 2018-06-04 17:32 | 2018-06-04 17:56 | 0:24 | T |  | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV line-1 | 2018-06-05 14:54 | 2018-06-05 18:36 | 3:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khagrachori | Khagrachori-Chanraghona 132 kV line-1 | 2018-06-06 17:42 | 2018-06-07 09:55 | 16:13 | E/O | Due to Breaker problem | 0 | 0 | No interruption
Hathazari | Hathazari-Feni 132 kV line-1 | 2018-06-08 22:17 | 2018-06-08 22:24 | 0:07 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV line-1 | 2018-06-09 17:08 | 2018-06-09 17:27 | 0:19 | T | Tripped showing dist.& E/F relay | 8 | 2.5333 | Power interruption 17:08 to 17:27
| Hathazari-Kaptai 132 kV line-2 | 2018-06-09 17:08 | 2018-06-09 17:32 | 0:24 | T
Madunagaht | Madunagaht-TK. Chemical 132 kV line | 2018-06-10 23:08 | 2018-06-10 23:43 | 0:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Modern steel 132 kV line | 2018-06-10 22:45 | 2018-06-10 23:36 | 0:51 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-1 | 2018-06-11 11:18 | 2018-06-11 11:40 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV line-2 | 2018-06-11 11:18 | 2018-06-11 11:51 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madunagaht | Madunagaht-Chandraghona 132 kV line-1 | 2018-06-11 11:18 | 2018-06-11 11:45 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Madunagaht-Khulshi 132 kV line | 2018-06-11 11:18 | 2018-06-11 11:45 | 0:27 | T |  | 34 | 15.3 | Power interruption 11:18 to 11:45
Sikalbaha | Sikalbaha-Madunagaht 132 kV line | 2018-06-11 15:44 | 2018-06-11 16:08 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2018-06-14 12:57 | 2018-06-14 13:10 | 0:13 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV line-2 | 2018-06-14 12:57 | 2018-06-14 13:12 | 0:15 | T |  | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 | 2018-06-14 12:57 | 2018-06-14 13:24 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Chandraghona-Kaptai 132 kV line-2 | 2018-06-14 12:57 | 2018-06-14 13:25 | 0:28 | T |  | 0 | 0 | No interruption
Madunagaht | Madunagaht-Chandraghona 132 kV line-1 | 2018-06-19 08:56 | 2018-06-19 10:17 | 1:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV line-1 | 2018-06-19 10:33 | 2018-06-19 10:48 | 0:15 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Khagrachori 132 kV line-1 | 2018-06-20 14:56 | 2018-06-20 15:26 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2018-06-26 09:51 | 2018-06-26 11:39 | 1:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2018-06-27 08:17 | 2018-06-27 09:27 | 1:10 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 31:31 |  | Unserved Energy: |  | 17.8333
Comilla Grid Circle :
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-2 | 2018-06-02 16:58 | 2018-06-02 17:37 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-06-02 16:46 | 2018-06-02 17:26 | 0:40 | T | Tripped showing dist. relay | 292 | 194.6667 | Power interruption
Comiila(N) | Comiila(N)-Feni 132 kV line | 2018-06-07 07:52 | 2018-06-07 09:56 | 2:04 | T | Tripped showing O/C realy | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line | 2018-06-08 11:50 | 2018-06-08 12:35 | 0:45 | T | Tripped showing O/C & E/F realy | 15 | 36.25 | Power interruption 10:10 to 12:35
Daudkandi | Daudkandi-Comiila(N) 132 kV line-1 | 2018-06-08 16:20 | 2018-06-08 16:45 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Daudkandi-Sonargaon 132 kV line-1 | 2018-06-08 16:43 | 2018-06-08 22:38 | 5:55 | T |  | 0 | 0 | No interruption
| Daudkandi-Sonargaon 132 kV line-2 | 2018-06-08 16:43 | 2018-06-08 22:33 | 5:50 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2018-06-09 21:08 | 2018-06-09 21:22 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Ramganj 132 kV line | 2018-06-10 21:40 | 2018-06-10 22:14 | 0:34 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 line-1 | 2018-06-17 15:28 | 2018-06-17 15:38 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 line-2 | 2018-06-17 23:58 | 2018-06-18 00:03 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV line | 2018-06-18 01:21 | 2018-06-18 01:35 | 0:14 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Feni 132 kV line-2 | 2018-06-18 01:21 | 2018-06-18 02:07 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comiila(S) | Comiila(S)-Sujonagar 132 kV line-1 | 2018-06-18 02:10 | 2018-06-18 03:42 | 1:32 | T | Tripped showing dist. relay | 120 | 184 | Power interruption 02:10 to 03:42
| Comiila(S)-Sujonagar 132 kV line-2 | 2018-06-18 02:10 | 2018-06-18 04:09 | 1:59 | T
Comiila(S) | Comiila(S)-Tripura 132 kV line-2 | 2018-06-19 07:07 | 2018-06-19 08:13 | 1:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV line | 2018-06-22 00:13 | 2018-06-22 22:30 | 22:17 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2018-06-22 12:10 | 2018-06-22 12:21 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-06-24 22:59 | 2018-06-24 23:30 | 0:31 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line | 2018-06-24 22:59 | 2018-06-24 23:40 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 46:38 |  | Unserved Energy: |  | 414.9167
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Goalpara | Goalpara-Khulna© 132 kV line | 2018-06-05 07:27 | 2018-06-05 10:39 | 3:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-06-08 07:06 | 2018-06-08 08:55 | 1:49 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-06-11 16:40 | 2018-06-11 16:46 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line2 | 2018-06-20 12:07 | 2018-06-20 12:47 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-06-20 22:12 | 2018-06-20 22:17 | 0:05 | T | Tripped showing O/C realy | 0 | 0 | No interruption
|  |  |  | 5:52 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2018-06-02 11:40 | 2018-06-02 12:34 | 0:54 | T | Tripped showing PD3,PTAW,RST ,D2H,Z2 signal | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-1 | 2018-06-02 13:23 | 2018-06-02 13:27 | 0:04 | T |  | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2018-06-02 23:02 | 2018-06-03 04:10 | 5:08 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bhearamara | Bhearamara-Faridpur 132 kV line-2 | 2018-06-18 14:10 | 2018-06-18 14:31 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bhearamara 132 kV line-1 | 2018-06-25 03:47 | 2018-06-25 05:26 | 1:39 | E/O | Due to bursting of PT | 0 | 0 | No interruption
|  |  | Total : | 8:06 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-06-06 20:36 | 2018-06-06 20:48 | 0:12 | T | Tripped showing O/C. relay | 200 | 40 | Power interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2018-06-06 20:36 | 2018-06-06 20:49 | 0:13 | T
Thakurgaon | Thakurgaon-Panchuagar 132 kV line | 2018-06-10 12:50 | 2018-06-10 16:09 | 3:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-06-11 19:49 | 2018-06-11 19:53 | 0:04 | T | Tripped showing O/C. relay | 200 | 13.3333 | Power interruption 19:49 to 93
| Saidpur-Purbasadipur 132 kV line-2 | 2018-06-11 19:49 | 2018-06-11 19:54 | 0:05 | T
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-06-14 10:25 | 2018-06-14 14:57 | 4:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-1 | 2018-06-16 17:33 | 2018-06-16 17:39 | 0:06 | E/O | Due to bursting of R-phase CT | 155 | 15.5 | Power interruption 17:33 to 17:39
| Rajshahi-Natore 132 kV line-2 | 2018-06-16 17:33 | 2018-06-17 05:58 | 12:25 | T
Barapukuria | Barapukuria-Rangpur 132 kV line-2 | 2018-06-20 10:20 | 2018-06-20 11:55 | 1:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra-Sirajganj 230 kV line-2 | 2018-06-20 11:18 | 2018-06-20 16:01 | 4:43 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-2 | 2018-06-26 06:06 | 2018-06-26 06:17 | 0:11 | T | Tripped showing main protection relay | 36 | 6.6 | Power interruption
|  |  | Total : | 27:25 |  | Unserved Energy: |  | 75.4333
Others :
Bangabhaban | Bangabhaban-Maniknagar 132 kV line-1 | 2018-05-02 07:50 | 2018-05-02 17:50 | 10:00 | T | Tripped showing pilot wire protection relay | 0 | 0 | No interruption
|  |  | Total : | 10:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 232:27 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: June 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 132/33 kV Transformer-T-2 | 2018-06-02 15:30 | 2018-06-02 16:32 | 1:02 | S/O | Due to maintenance work | 14 | 14.4667 | Power interruption
Netrakona | 132/33 kV Transformer-T3 | 2018-06-08 06:55 | 2018-06-08 08:46 | 1:51 | S/O | Due to C/M work | 17 | 31.45 | Power interruption
Kadda | 132 kV bus-2 | 2018-06-08 07:40 | 2018-06-08 16:32 | 8:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T5 | 2018-06-09 06:40 | 2018-06-09 07:50 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2018-06-14 09:22 | 2018-06-14 17:47 | 8:25 | S/O | Due to painting work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2018-06-18 08:01 | 2018-06-18 17:38 | 9:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kodda | 132 kV bus-1 | 2018-06-29 06:11 | 2018-06-29 12:02 | 5:51 | S/O | Due to project work | 154 | 508.2 | Power interruption 06:11 to 09:29
| 132 kV bus-2 | 2018-06-29 06:11 | 2018-06-29 09:29 | 3:18 | S/O
Mymensingh | 132/33 kV Transformer-T1 | 2018-06-30 09:45 | 2018-06-30 11:24 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2018-06-30 13:12 | 2018-06-30 15:24 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 43:57 |  | Unserved Energy: |  | 554.1167
Dhaka (South) Grid Circle :
Gulshan | 132/33 kV Transformer-T-2 | 2018-06-01 07:01 | 2018-06-01 07:58 | 0:57 | S/O | Due to maintenance work | 0 | 0 | No interruption
Matuail | 132/33 kV Transformer-T2 | 2018-06-02 10:10 | 2018-06-02 11:35 | 1:25 | S/O | Due to relay change | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR2 | 2018-06-07 10:30 | 2018-06-07 11:39 | 1:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-TR1 | 2018-06-08 07:27 | 2018-06-08 10:15 | 2:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-TR1 | 2018-06-12 05:06 | 2018-06-12 07:42 | 2:36 | S/O | Due to C/M work | 85 | 221 | Power interruption
Lalbagh | 132/33 kV Transformers-T1 | 2018-06-22 08:58 | 2018-06-22 12:04 | 3:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-06-22 12:07 | 2018-06-22 12:29 | 0:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sitalakhya | 132 kV bus-2 | 2018-06-24 10:10 | 2018-06-24 21:17 | 11:07 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformers-T1 | 2018-06-25 11:56 | 2018-06-25 17:43 | 5:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-06-25 09:20 | 2018-06-25 11:55 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 31:52 |  | Unserved Energy: |  | 221
Chittagong Grid Circle :
Sikalbaha | 132 kV bus-A | 2018-06-25 07:58 | 2018-06-25 08:40 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformers-T1 & T2 | 2018-06-26 04:20 | 2018-06-26 05:28 | 1:08 | S/O | Due to maintenance work | 52 | 58.9333 | Power interruption
Halishahar | 132/33 kV Transformers-T1 & T2 | 2018-06-29 06:09 | 2018-06-29 07:58 | 1:49 | S/O | Due to maintenance work | 40 | 94.4667 | Power interruption
Bakulia | 132/33 kV Transformer-T3 | 2018-06-30 06:16 | 2018-06-30 12:37 | 6:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformers-T1 | 2018-06-30 09:55 | 2018-06-30 11:45 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 11:08 |  | Unserved Energy: |  | 153.4
Page:2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Sunamganj | 132/33 kV Transformer-T1 | 2018-06-10 09:20 | 2018-06-10 17:15 | 7:55 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2018-06-27 21:53 | 2018-06-27 23:16 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 9:18 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-T2 | 2018-06-06 06:14 | 2018-06-06 15:31 | 9:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2018-06-12 07:15 | 2018-07-11 15:45 | 704:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 | 2018-06-15 07:25 | 2018-06-15 07:57 | 0:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T1 | 2018-06-19 12:50 | 2018-06-19 13:28 | 0:38 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T-3 | 2018-06-25 06:17 | 2018-06-25 07:41 | 1:24 | S/O | Due to maintenance work | 10 | 14 | Power interruption
Gopalganj | 132/33 kV Transformer-T1 | 2018-06-30 07:20 | 2018-06-30 14:24 | 7:04 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 714:08 |  | Unserved Energy : |  | 14
HVDC Grid Circle :
Jhenidah | 132 kV bus-B | 2018-06-10 10:56 | 2018-06-11 10:34 | 23:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132 kV bus-1 & 2 | 2018-06-11 10:30 | 2018-06-11 12:02 | 1:32 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 25:10 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Ishurdi | 230 kV bus-2 | 2018-06-02 09:35 | 2018-06-10 15:32 | 197:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T3 | 2018-06-15 06:30 | 2018-06-15 06:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T01 | 2018-06-22 06:40 | 2018-06-22 08:25 | 1:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T3 | 2018-06-25 08:05 | 2018-06-25 09:25 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T5 | 2018-06-25 11:30 | 2018-06-25 11:38 | 0:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T4 | 2018-06-30 08:05 | 2018-06-30 08:05 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2018-06-30 10:25 | 2018-06-30 16:30 | 6:05 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 207:15 |  | Unserved Energy : |  | 0
Others :
Ghorashal | 230/132 kV Transformer-AT-2 | 2018-06-12 13:59 | 2018-06-13 09:50 | 19:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 19:51 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 1062:39 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: June 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-06-02 08:04 | 2018-06-02 14:37 | 6:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-06-02 08:40 | 2018-06-02 14:37 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Summit Gazipur 230 kV line | 2018-06-05 07:58 | 2018-06-05 17:27 | 9:29 | S/O | Due to project work | 0 | 0 | No interruption
| Tongi-Kaliakoir 230 kV line-2 | 2018-06-05 07:28 | 2018-06-05 21:36 | 14:08 | S/O | Due to project work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Summit Gazipur 230 kV line | 2018-06-05 07:54 | 2018-06-05 07:54 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV line-1 | 2018-06-05 07:35 | 2018-06-05 21:14 | 13:39 | S/O | Due to project work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2018-06-06 07:37 | 2018-06-06 15:01 | 7:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-2 | 2018-06-06 10:15 | 2018-06-07 15:14 | 28:59 | S/O | Due to project work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2018-06-07 07:02 | 2018-06-07 09:02 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Sherpur 132 kV line-2 | 2018-06-07 07:08 | 2018-06-08 03:39 | 20:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Sherpur 132 kV line-1 | 2018-06-09 05:41 | 2018-06-09 14:47 | 9:06 | S/O | Due to D/W work | 40 | 148 | Power interruption 05:51 to 09:33
| Jamalpur-Sherpur 132 kV line-2 | 2018-06-09 05:51 | 2018-06-09 09:33 | 3:42 | S/O
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2018-06-10 09:42 | 2018-06-10 11:54 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2018-06-11 11:03 | 2018-06-11 18:31 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur132 kV line-2 | 2018-06-15 10:06 | 2018-06-15 11:33 | 1:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2018-06-26 12:14 | 2018-06-26 13:02 | 0:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 133:23 |  | Unserved Energy: |  | 148
Page: 2/7 | [8 empty] | QF-LDC-26
Dhaka (South) Grid Circle :
Sonargaon | Sonargaon-Haripur 132 kV line-2 | 2018-06-05 09:37 | 2018-06-12 14:52 | 173:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2018-06-06 07:34 | 2018-06-06 08:15 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2018-06-08 07:32 | 2018-06-08 11:06 | 3:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2018-06-08 10:50 | 2018-06-08 17:52 | 7:02 | S/O | Due to replacement work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-06-10 09:49 | 2018-06-10 11:42 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2018-06-11 10:37 | 2018-06-11 11:57 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2018-06-12 07:57 | 2018-06-12 21:28 | 13:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Ashuganj (S) 230 kV line-1 | 2018-06-12 15:25 | 2018-06-14 09:10 | 41:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV liner-1 | 2018-06-14 13:31 | 2018-06-14 16:41 | 3:10 | S/O | Due to replacement work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-06-27 10:04 | 2018-06-27 15:33 | 5:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-06-30 07:27 | 2018-06-30 20:56 | 13:29 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 265:09 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2018-06-14 10:10 | 2018-06-14 13:12 | 3:02 | S/O | Due to maintenance work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-1 | 2018-06-28 07:19 | 2018-06-28 15:46 | 8:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-2 | 2018-06-28 10:10 | 2018-06-28 13:45 | 3:35 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 15:04 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Ashuganj | Ashuganj-Kishoreganj 132 line-2 | 2018-06-03 07:06 | 2018-06-03 13:47 | 6:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 line-2 | 2018-06-04 07:15 | 2018-06-04 16:08 | 8:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 line-2 | 2018-06-05 07:45 | 2018-06-05 15:13 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line-2 | 2018-06-09 05:30 | 2018-06-10 20:25 | 38:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line-2 | 2018-06-09 10:09 | 2018-06-09 17:37 | 7:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashyuganj | Ashyuganj-Bhulta 400 kV line-2 | 2018-06-18 10:57 | 2018-06-18 14:43 | 3:46 | S/O | Due to project work | 0 | 0 | No interruption
Ashyuganj | Ashuganj-Kishoreganj 132 line-2 | 2018-06-20 09:35 | 2018-06-20 14:22 | 4:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashyuganj | Ashyuganj-Kishoreganj 132 kV line-2 | 2018-06-21 07:43 | 2018-06-21 12:24 | 4:41 | S/O | Due to project work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV line-1 | 2018-06-26 11:19 | 2018-06-26 23:23 | 12:04 | S/O | Due to project work | 0 | 0 | No interruption
| Comilla(N)-Shahjibazar 230 kV line-1 | 2018-06-27 15:40 | 2018-06-27 17:52 | 2:12 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 96:55 |  | Unserved Energy: |  | 0
Page: 6/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: May 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2018-06-02 12:43 | 2018-06-02 13:35 | 0:52 | S/O | Due to tree trimming | 0 | 0 | No interruption
|  |  | Total : | 0:52 |  | Unserved Energy: |  | 0
Page: 7/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: June 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2018-06-02 10:59 | 2018-06-02 15:39 | 4:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Baharampur 400 kV line-1 | 2018-06-06 07:28 | 2018-06-06 14:34 | 7:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Baharampur 400 kV line-2 | 2018-06-06 07:29 | 2018-06-06 14:36 | 7:07 | S/O |  | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line | 2018-06-09 07:10 | 2018-06-09 08:53 | 1:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-2 | 2018-06-10 08:12 | 2018-06-10 10:12 | 2:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Magura 132 kV line-2 | 2018-06-11 10:18 | 2018-06-11 10:44 | 0:26 | S/O | Due to project work | 0 | 0 | No interruption
Bheramara | Bheramara-Baharampur 400 kV line-2 | 2018-06-12 10:50 | 2018-06-12 14:15 | 3:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Bheramara-Baharampur 400 kV line-2 | 2018-06-13 12:50 | 2018-06-13 15:12 | 2:22 | S/O |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2018-06-14 10:40 | 2018-06-14 12:27 | 1:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 30:36 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Natore 132 kV line-2 | 2018-05-05 10:12 | 2018-05-05 11:33 | 1:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-06-22 08:44 | 2018-06-22 11:54 | 3:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Amnura-Rajshahi 132 kV line | 2018-06-21 08:53 | 2018-06-21 11:46 | 2:53 | S/O | Due to project work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-1 | 2018-06-25 14:22 | 2018-06-25 15:13 | 0:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-06-26 15:14 | 2018-06-26 16:03 | 0:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Panchagar 132 kV line | 2018-06-29 05:35 | 2018-06-29 07:18 | 1:43 | S/O | Due to maintenance work | 30 | 51.5 | Power interruption
Saidpur | Thakurgaon-Purbasadipur 132 kV line-2 | 2018-06-29 05:36 | 2018-06-29 09:55 | 4:19 | S/O | Due to maintenance work | 43 | 185.6167 | Power interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-06-29 09:15 | 2018-06-29 10:20 | 1:05 | S/O | Due to maintenance work | 60 | 32.5 | Power interruption
Bogra | Bogra-Bogra(new) 132 kV line-2 | 2018-06-29 10:40 | 2018-06-29 12:30 | 1:50 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-2 | 2018-06-29 09:52 | 2018-06-29 10:32 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 18:41 |  | Unserved Energy: |  | 269.6167
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-1 | 2018-06-20 10:43 | 2018-06-20 17:50 | 7:07 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Maniknagar-Narinda 132 kV line-2 | 2018-06-21 09:10 | 2018-06-21 16:16 | 1:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 8:28 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 444:13 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June' 2018
| Area | Previous Month (May 2018) |  |  |  | Current Month (June 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 22 | 8 | 24 | 54 | 17 | 5 | 26 | 48
2 | Dhaka (South) Grid Circle. | 18 | 2 | 44 | 64 | 16 | 3 | 21 | 40
3 | Chittagong Grid Circle. | 11 | 2 | 9 | 22 | 20 | 9 | 8 | 37
4 | Comilla Grid Circle. | 24 | 3 | 17 | 44 | 21 | 3 | 12 | 36
5 | Khulna Grid Circle. | 19 | 6 | 10 | 35 | 8 | 2 | 7 | 17
6 | Bheramara HVDC Grid Circle | 8 | - | 6 | 14 | 4 | 3 | 11 | 18
7 | Bogra Grid Circle. | 9 | 4 | 10 | 23 | 10 | 12 | 17 | 39
8 | Others | 1 | 1 | 1 | 3 | 1 | - | 3 | 4
9 | Total | 112 | 26 | 121 | 259 | 97 | 37 | 105 | 239
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June' 2018
| Area | Previous Month (May 2018) |  |  |  | Current Month (June 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | - | 796.27 | - | 796.27 | 3 | 42.5 | 702.12 | 747.62
2 | Dhaka ( South) grid circle | 50 | - | - | 50 | 18.7 | 30.4 | 221 | 270.1
3 | Chittagong grid circle. | 3 | - | 87.5 | 90.5 | 151.16 | 32 | 153.4 | 336.56
4 | Comilla grid circle. | 36.6 | 133.37 | 59.5 | 229.47 | 498.52 | - | - | 498.52
5 | Khulna grid circle. | 64.05 | 62.93 | 43.67 | 170.65 | 17.07 | - | 14 | 31.07
6 | Bheramara HVDC grid circle | 26.07 | - | - | 26.07 | - | 58.92 | - | 58.92
7 | Bogra grid circle. | 102.5 | - | 29.95 | 132.45 | 60.6 | 22.75 | 269.62 | 352.97
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 282.22 | 992.57 | 220.62 | 1495.41 | 749.05 | 186.57 | 1360.14 | 2295.76
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 2 | 3 | 5 | 1 | - | 4 | 599.62
2 | Dhaka (South) | 5031.6 | - | 1 | 1 | - | - | 1 | 221
3 | Chittagong | 2042 | 2 | 2 | 4 | - | - | 4 | 318.73
4 | Khulna | 2434 | 2 | 1 | 3 | 2 | - | 1 | 31.07
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | - | - | 1 | 58.92
6 | Bogra | 3145.6 | 3 | - | 3 | 1 | 1 | 1 | 7.92
7 | Comilla | 2981 | 3 | - | 3 | 1 | 1 | 1 | 83.6
| Total | 23365.5 | [6 empty] | 1320.86
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chittagong | 99.97%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.89% | [6 empty] | Executive Engineer
6 | Bogra | 99.92% | [6 empty] | Information Management Division
7 | Comilla | 100% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | - | - | 1 | - | - | 1 | 148
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 2 | - | 1 | 49.1
3 | Chittagong | 917 | 20+9(Partial) | 2 | - | 2 | 2 | - | - | 17.83
4 | Khulna | 1238.4 | 21 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogra | 1803.3 | 38 | 3 | 3 | 7 | 3 | - | 3 | 345.05
7 | Comilla | 1648.16 | 17 | 3 | - | 3 | 1 | - | 2 | 414.92
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 974.9
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.78%
2 | Dhaka (South) | 99.95%
3 | Chittagong | 99.76%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.86% | [7 empty] | Executive Engineer
6 | Bogra | 99.91% | [7 empty] | Information Management Division
7 | Comilla | 99.76% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
June | 12 | - | 4 | 04hr16 min | 1 | 05hr04 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:June' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishoreganj | 1 | 0:02 | 90 | 3 | Due to tripping of 132/33 kV Transformers T1 ,T2 & T3
Jamalpur | 1 | 1:25 | 30 | 42.5 | Due to tripping of 132/33 kV Transformers T1 & T2
Tongi | 1 | 1:02 | 14 | 14.4667 | Due to S/D of 132/33 kV Transformer T2
Netrakona | 1 | 1:51 | 17 | 31.45 | Due to S/D of 132/33 kV Transformer T3
Kadda | 1 | 3:18 | 154 | 508.2 | Due to S/D of 132 kV bus-1 & 2
Jamalpur | 1 | 3:42 | 40 | 148 | Due to tripping of Jamalpur-Serpur 132 kV line-1 & 2
Hasnabad | 1 | 0:03 | 70 | 3.5 | Due to tripping of Hasnabad-Kamrangirchar 132 kV line-1
Haripur | 2 | 5:04 | 6 | 30.4 | Due to bursting of L/A at Haripur-Rahim steel 32 kV line
|  | 0:12 | 76 | 15.2 | Due to tripping of Haripur-Shyampur 132 kV line
Rampura | 1 | 2:36 | 85 | 221 | Due to S/D of 230/132 kV Transformer TR1
Bakulia | 1 | 2:05 | 24 | 133.3333 | Due to tripping of 132/33 kV Transformer T3
Cox'sbazar | 1 | 1:36 | 20 | 32 | Due to tripping of 132/33 kV Transformer T2
Hathazari | 1 | 0:19 | 8 | 2.5333 | Due to tripping of Hathazari-Kaptai 132 kV line-1
Madunaghat | 1 | 0:27 | 34 | 15.3 | Due to tripping of Madunaghat-Kulshi 132 kV line-1 & 2
Bakulia | 1 | 1:08 | 52 | 58.9333 | Due to S/D of 132/33 kV Transformers T1 & T2
Halishahar | 1 | 1:49 | 40 | 94.4667 | Due to S/D of 132/33 kV Transformers T1 & T2
Sylhet | 1 | 0:49 | 64 | 52.2667 | Due to tripping of 132/33 kV Transformer T4
Comilla(N) | 1 | 1:10 | 20 | 23.3333 | Due to tripping of 132/33 kV Transformer T4
Shahjibazar | 1 | 0:15 | 32 | 8 | Due to tripping of 132/33 kV Transformer T4 & T6
Ashuganj | 1 | 0:40 | 292 | 194.6667 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-1
Chatak | 1 | 2:25 | 15 | 36.25 | Due to tripping of Chatak-Sunamganj 132 kV line-1
Comilla(S) | 1 | 1:32 | 120 | 184 | Due to tripping of Comiila(S)-Surjonagar 132 kV line-1 & 2
Faridpur | 1 | 0:08 | 96 | 12.8 | Due to tripping of 132/33 kV Transformer T1 & T2
Mongla | 1 | 0:08 | 32 | 4.2667 | Due to tripping of 132/33 kV Transformers T1 & T2
Khulna© | 1 | 1:24 | 10 | 14 | Due to tripping of 132/33 kV Transformer T3
Botail | 1 | 1:41 | 35 | 58.9167 | Due to red-hot maintenance of 132/33 kV Transformer T2
Saidpur | 2 | 0:01 | 5 | 5 | Due to red-hot maintenance 132/33 kV Transfomer T3
|  | 0:15 | 9 | 2.25 | Due to oil leakage of 132/33 kV Transfomer T4
Amnura | 1 | 0:05 | 8 | 0.66667 | Due to tripping of 132/33 kV Transformer T1
Saidpur | 2 | 0:12 | 200 | 40 | Due to tripping of Saidpur-Purbasadipur 132 kV line-1
|  | 0:04 | 200 | 13.3333 | Due to tripping of Saidpur-Purbasadipur 132 kV line-1 & 2
Rajshahi | 1 | 0:06 | 155 | 15.5 | Due to tripping of Rajshahi-Natore 132 kV line-1 & 2
Thakurgaon | 3 | 0:11 | 36 | 6.6 | Due to tripping of Thakurgaon-Purbasadipur 132 kV line-2
|  | 1:43 | 30 | 51.5 | Due to S/D of Thakurgaon-Panchuga132 kV liner
|  | 4:19 | 43 | 185.6167 | Due to S/D of Thakurgaon -Purbasadipur 132 kV line
Bogra | 1 | 1:05 | 60 | 32.5 | Due to S/D of Bogra-Palshbari 132 kV line-1
| Total unserved energy : |  |  | 2295.75 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 142 | 7 | 2018-06-01 | 12:00
2 | Munsiganj | 124 | 11 | 2018-06-01 | 21:00
3 | Megnaghat | 55 | 3 | 2018-06-01 | 12:00
4 | Shyampur | 170 | 6 | 2018-06-01 | 13:00
5 | Bhulta | 195 | 7 | 2018-06-01 | 21:00
6 | Madanganj | 55 | 4 | 2018-06-01 | 19:30
7 | Shitalakhya | 121 | 9 | 2018-06-01 | 15:00
8 | Rahim steel | 13 | 10 | 2018-06-01 | 14:00
9 | Matuail | 98 | 9 | 2018-06-01 | 9:00
10 | Ghorasal | 83 | 30 | 2018-06-01 | 21:00
11 | Narsingdi | 187 | 8 | 2018-06-01 | 22:00
12 | Haripur (SBU) | 101 | 7 | 2018-06-01 | 09:00
13 | Ullon | 107 | 7 | 2018-06-01 | 23:00
14 | Hasnabad | 214 | 4 | 2018-06-01 | 21:00
15 | Magbazar | 141 | 7 | 2018-06-01 | 14:00
16 | Maniknagar | 100 | 6 | 2018-06-01 | 14:00
17 | Bangabhaban | 40 | 6 | 2018-06-01 | 12:00
18 | Narinda | 92 | 9 | 2018-06-01 | 11:00
19 | Dhanmondi | 133 | 10 | 2018-06-01 | 12:00
20 | Lalbag | 98 | 9 | 2018-06-01 | 13:00
21 | Madartek | 105 | 26 | 2018-06-01 | 19:00
22 | Mirpur | 117 | 14 | 2018-06-01 | 19:30
23 | Kalyanpur | 140 | 26 | 2018-06-01 | 13:00
24 | Gulshan | 152 | 10 | 2018-06-01 | 14:00
25 | Uttara | 96 | 7 | 2018-06-01 | 20:00
26 | Kamrangirchar | 145 | 26 | 2018-06-01 | 21:00
27 | Savar | 161 | 9 | 2018-06-01 | 15:00
28 | Bhasantec | 165 | 7 | 2018-06-01 | 20:00
29 | Agargaon | 130 | 14 | 2018-06-01 | 20:00
30 | Satmosjid | 130 | 24 | 2018-06-01 | 16:00
31 | Tongi | 186 | 25 | 2018-06-01 | 16:00
32 | Kabirpur | 221 | 5 | 2018-06-01 | 14:00
33 | Basundhara | 137 | 10 | 2018-06-01 | 15:00
34 | Manikganj | 224 | 27 | 2018-06-01 | 19:30
35 | Joydevpur | 237 | 30 | 2018-06-01 | 15:00
36 | New Tongi | 230 | 27 | 2018-06-01 | 21:00
37 | Kodda | 236 | 30 | 2018-06-01 | 21:00
38 | Dhamrai | 19 | 29 | 2018-06-01 | 21:00
39 | Tangail | 195 | 13 | 2018-06-01 | 19:30
40 | Mymensing | 236 | 23 | 2018-06-01 | 21:00
41 | Kishorganj | 96 | 18 | 2018-06-01 | 20:00
42 | Netrokona | 89 | 22 | 2018-06-01 | 23:00
43 | Jamalpur | 119 | 21 | 2018-06-01 | 20:00
44 | Sherpur | 91 | 11 | 2018-06-01 | 22:00
45 | Srimongal | 48 | 6 | 2018-06-01 | 21:00
46 | Shahjibazar | 114 | 27 | 2018-06-01 | 19:00
47 | Fenchuganj | 57 | 9 | 2018-06-01 | 21:00
48 | Kulawara | 42 | 3 | 2018-06-01 | 19:00
49 | Sylhet | 165 | 5 | 2018-06-01 | 22:00
50 | Chatak | 31 | 18 | 2018-06-01 | 19:30
51 | Sunamganj | 34 | 20 | 2018-06-01 | 21:00
52 | Binibazar | 44 | 20 | 2018-06-01 | 21:00
53 | Cumilla (S) | 186 | 6 | 2018-06-01 | 20:00
54 | Cumilla(N) | 122 | 7 | 2018-06-01 | 19:00
55 | Chandpur | 130 | 14 | 2018-06-01 | 21:00
56 | Feni | 124 | 6 | 2018-06-01 | 21:00
57 | Chowmuhani | 204 | 5 | 2018-06-01 | 23:00
58 | Ashuganj | 63 | 4 | 2018-06-01 | 21:00
59 | Daudkandi | 112 | 30 | 2018-06-01 | 21:00
60 | B.Baria | 134 | 4 | 2018-06-01 | 22:00
61 | Ramganj | 34 | 20 | 2018-06-01 | 20:00
62 | Madanhat | 62 | 13 | 2018-06-01 | 19:30
63 | Hathazari | 97 | 3 | 2018-06-01 | 13:00
64 | Khulshi | 198 | 28 | 2018-06-01 | 14:00
65 | Halishahar | 152 | 7 | 2018-06-01 | 10:00
66 | Baraulia | 167 | 9 | 2018-06-01 | 19:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
67 | Sikalbaha | 44 | 2 | 2018-06-01 | 20:00
68 | Dohazari | 92 | 18 | 2018-06-01 | 20:00
69 | Cox'sbazar | 96 | 4 | 2018-06-01 | 20:00
70 | Chandraghona | 36 | 18 | 2018-06-01 | 19:00
71 | Kaptai | 5 | 2 | 2018-06-01 | 14:00
72 | A. Khaer Stl. | 29 | 22 | 2018-06-01 | 23:00
73 | Bakulia | 112 | 7 | 2018-06-01 | 15:00
74 | Julda | 22 | 2 | 2018-06-01 | 13:00
75 | TK chemical | 6 | 2 | 2018-06-01 | 24:00
76 | Modern Steel | 18 | 7 | 2018-06-01 | 01:00
77 | Shahmirpur | 128 | 4 | 2018-06-01 | 16:00
78 | Abul Khair 230 | 201 | 2 | 2018-06-01 | 11:00
79 | BSRM | 116 | 28 | 2018-06-01 | 20:00
80 | Khagrachhari | 114 | 9 | 2018-06-01 | 20:00
81 | Goalpara | 64 | 17 | 2018-06-01 | 21:00
82 | Central s/s | 76 | 5 | 2018-06-01 | 22:00
83 | Noapara | 101 | 9 | 2018-06-01 | 19:00
84 | Jashore | 149 | 7 | 2018-06-01 | 20:00
85 | Jhenida | 104 | 9 | 2018-06-01 | 21:00
86 | Bottail | 132 | 9 | 2018-06-01 | 21:00
87 | G.K Project | 58 | 8 | 2018-06-01 | 20:00
88 | Faridpur | 160 | 4 | 2018-06-01 | 21:00
89 | Madaripur | 148 | 30 | 2018-06-01 | 21:00
90 | Gopalganj | 88 | 7 | 2018-06-01 | 19:30
91 | Bagerhat | 87 | 7 | 2018-06-01 | 10:00
92 | Mongla | 38 | 3 | 2018-06-01 | 21:00
93 | Satkhira | 101 | 15 | 2018-06-01 | 23:00
94 | Gallamari | 53 | 4 | 2018-06-01 | 20:00
95 | Magura | 54 | 17 | 2018-06-01 | 20:00
96 | Chuadanga | 120 | 1 | 2018-06-01 | 19:00
97 | Barishal | 118 | 7 | 2018-06-01 | 21:00
98 | Patuakhali | 98 | 14 | 2018-06-01 | 21:00
99 | Bhandaria | 51 | 17 | 2018-06-01 | 21:00
100 | Ishurdi | 56 | 10 | 2018-06-01 | 1:00
101 | Ruppur Paromanobik | 2 | 11 | 2018-06-01 | 21:00
102 | Natore | 122 | 14 | 2018-06-01 | 21:00
103 | Bogura | 244 | 26 | 2018-06-01 | 12:00
104 | Noagaon | 112 | 11 | 2018-06-01 | 21:00
105 | Rajshahi | 150 | 6 | 2018-06-01 | 20:00
106 | C.Nawabganj | 71 | 24 | 2018-06-01 | 3:00
107 | Amnura | 39 | 10 | 2018-06-01 | 21:00
108 | Pabna | 117 | 26 | 2018-06-01 | 20:00
109 | Shahjadpur | 92 | 28 | 2018-06-01 | 20:00
110 | Serajganj | 99 | 14 | 2018-06-01 | 21:00
111 | Niyamatpur | 57 | 14 | 2018-06-01 | 20:00
112 | Joypurhat | 50 | 25 | 2018-06-01 | 21:00
113 | Rangpur | 126 | 23 | 2018-06-01 | 19:30
114 | Lalmonirhat | 88 | 20 | 2018-06-01 | 20:00
115 | Saidpur | 114 | 3 | 2018-06-01 | 20:00
116 | Purbasadipur | 101 | 9 | 2018-06-01 | 20:00
117 | Thakurgaon | 72 | 5 | 2018-06-01 | 21:00
118 | Palashbari | 106 | 30 | 2018-06-01 | 21:00
119 | Barapukuria | 110 | 18 | 2018-06-01 | 21:00
120 | Panchagar | 42 | 11 | 2018-06-01 | 21:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:June' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 4118 | 07.06.18 | 21:00
Chittagong | 1256 | 60.06.18 | 23:00
Khulna | 1353 | 05.06.18 | 21:00
Rajshahi | 1171 | 14.06.18 | 1:00
Comilla | 1005 | 05.06.18 | 22:00
Mymensingh | 795 | 13.01.18 | 21:00
Sylhet | 459 | 07.06.18 | 21:00
Barisal | 289 | 14.06.18 | 21:00
Rangpur | 654 | 12.06.18 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 397 | 16 | 2018-06-01 | 05:00 | 376 | 5 | 2018-06-01 | 23:00
2 | Bheramara | 400 | 495 | 30 | 2018-06-01 | 15:00 | 384 | 15 | 2018-06-01 | 23:00
3 | Kaliakoir | 400 | 384 | 19 | 2018-06-01 | 08:00 | 353 | 5 | 2018-06-01 | 12:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 1 | 2018-06-01 | 01:00 | 222 | 5 | 2018-06-01 | 1:00
2 | Ishurdi | 230 | 237 | 1 | 2018-06-01 | 13:00 | 210 | 7 | 2018-06-01 | 19:00
3 | Ashuganj | 230 | 238 | 28 | 2018-06-01 | 5:00 | 228 | 2 | 2018-06-01 | 21:00
4 | Serajganj | 230 | 229 | 1 | 2018-06-01 | 12:00 | 202 | 2 | 2018-06-01 | 19:30
5 | Baghabari | 230 | 232 | 19 | 2018-06-01 | 10:00 | 208 | 2 | 2018-06-01 | 19:30
6 | Barapukuria | 230 | 240 | 1 | 2018-06-01 | 7:00 | 215 | 30 | 2018-06-01 | 20:00
7 | Bogra | 230 | 232 | 1 | 2018-06-01 | 08':00 | 196 | 30 | 2018-06-01 | 21:00
8 | Khulna South | 230 | 244 | 22 | 2018-06-01 | 18'30 | 212 | 7 | 2018-06-01 | 19:00
9 | Rampura | 230 | 226 | 16 | 2018-06-01 | 07:00 | 200 | 29 | 2018-06-01 | 19:00
10 | Haripur | 230 | 228 | 16 | 2018-06-01 | 6:00 | 215 | 5 | 2018-06-01 | 12:00
11 | Hasnabad | 230 | 230 | 16 | 2018-06-01 | 6:00 | 215 | 2 | 2018-06-01 | 11:00
12 | Aminbazar | 230 | 229 | 19 | 2018-06-01 | 08:00 | 214 | 5 | 2018-06-01 | 12:00
13 | Tongi | 230 | 230 | 4 | 2018-06-01 | 1:00 | 206 | 5 | 2018-06-01 | 9:00
14 | Comilla (N) | 230 | 235 | 19 | 2018-06-01 | 11:00 | 220 | 5 | 2018-06-01 | 15:00
15 | Hathazari | 230 | 226 | 15 | 2018-06-01 | 19:00 | 206 | 5 | 2018-06-01 | 24:00
16 | Megnaghat | 230 | 232 | 15 | 2018-06-01 | 19:30 | 220 | 5 | 2018-06-01 | 11:00
17 | Fenchuganj | 230 | 239 | 7 | 2018-06-01 | 6:00 | 229 | 8 | 2018-06-01 | 04:00
18 | Siddhirganj | 230 | 228 | 1 | 2018-06-01 | 18:30 | 217 | 5 | 2018-06-01 | 12:00
19 | Maniknagar | 230 | 227 | 1 | 2018-06-01 | 19:00 | 214 | 30 | 2018-06-01 | 9:00
20 | Old Airport | 230 | 227 | 16 | 2018-06-01 | 05:00 | 212 | 5 | 2018-06-01 | 12:00
21 | Barisal | 230 | 242 | 19 | 2018-06-01 | 14:00 | 210 | 19 | 2018-06-01 | 10:00
22 | AKSML | 230 | 224 | 10 | 2018-06-01 | 17:00 | 201 | 3 | 2018-06-01 | 19:00
23 | BSRM | 230 | 228 | 25 | 2018-06-01 | 21:00 | 205 | 3 | 2018-06-01 | 14:00
24 | Bibiyana | 230 | 238 | 19 | 2018-06-01 | 09:00 | 226 | 5 | 2018-06-01 | 13:00
132 kV Substation
1 | Siddhirganj | 132 | 138 | 16 | 2018-06-01 | 05:00 | 128 | 30 | 2018-06-01 | 9:00
2 | Munsiganj | 132 | 138 | 4 | 2018-06-01 | 18:30 | 127 | 30 | 2018-06-01 | 9:00
3 | Megnaghat | 132 | 136 | 16 | 2018-06-01 | 6:00 | 127 | 30 | 2018-06-01 | 10:00
4 | Shyampur | 132 | 137 | 17 | 2018-06-01 | 20:00 | 121 | 12 | 2018-06-01 | 11:00
5 | Bhulta | 132 | 138 | 1 | 2018-06-01 | 2:00 | 114 | 6 | 2018-06-01 | 9:00
6 | Madanganj | 132 | 139 | 19 | 2018-06-01 | 9:00 | 124 | 3 | 2018-06-01 | 16:00
7 | Shitalakhya | 132 | 140 | 20 | 2018-06-01 | 20:00 | 125 | 2 | 2018-06-01 | 11:00
8 | Rahim Steal | 132 | 138 | 16 | 2018-06-01 | 06:00 | 128 | 12 | 2018-06-01 | 9:00
9 | Matuail | 132 | 138 | 16 | 2018-06-01 | 5:00 | 127 | 12 | 2018-06-01 | 11:00
10 | Ghorasal | 132 | 138 | 1 | 2018-06-01 | 16:00 | 130 | 5 | 2018-06-01 | 21:00
11 | Narsinghdi | 132 | 137 | 1 | 2018-06-01 | 5:00 | 122 | 12 | 2018-06-01 | 11:00
12 | Haripur (SBU) | 132 | 138 | 16 | 2018-06-01 | 5:00 | 128 | 30 | 2018-06-01 | 9:00
13 | Ullon | 132 | 138 | 1 | 2018-06-01 | 6:00 | 123 | 28 | 2018-06-01 | 13:00
14 | Hasnabad | 132 | 138 | 16 | 2018-06-01 | 6:00 | 127 | 2 | 2018-06-01 | 11:00
15 | Magbazar | 132 | 140 | 1 | 2018-06-01 | 6:00 | 125 | 10 | 2018-06-01 | 12:00
16 | Maniknagar | 132 | 139 | 16 | 2018-06-01 | 6:00 | 129 | 5 | 2018-06-01 | 12:00
17 | Bangabhaban | 132 | 139 | 16 | 2018-06-01 | 6:00 | 129 | 5 | 2018-06-01 | 11:00
18 | Narinda | 132 | 139 | 16 | 2018-06-01 | 6:00 | 129 | 5 | 2018-06-01 | 12:00
19 | Dhanmondi | 132 | 138 | 1 | 2018-06-01 | 6:00 | 123 | 28 | 2018-06-01 | 13:00
20 | Lalbag | 132 | 141 | 26 | 2018-06-01 | 6:00 | 122 | 2 | 2018-06-01 | 10:00
21 | Madartek | 132 | 138 | 16 | 2018-06-01 | 6:00 | 126 | 10 | 2018-06-01 | 12:00
22 | Mirpur | 132 | 138 | 29 | 2018-06-01 | 1:00 | 126 | 30 | 2018-06-01 | 17:00
23 | Kalyanpur | 132 | 138 | 20 | 2018-06-01 | 6:00 | 120 | 10 | 2018-06-01 | 11:00
24 | Gulshan | 132 | 138 | 2 | 2018-06-01 | 5:00 | 108 | 26 | 2018-06-01 | 11:00
25 | Uttara | 132 | 136 | 17 | 2018-06-01 | 6:00 | 120 | 7 | 2018-06-01 | 9:00
26 | Kamrangirchar | 132 | 138 | 16 | 2018-06-01 | 5:00 | 123 | 2 | 2018-06-01 | 15:00
27 | Savar | 132 | 137 | 17 | 2018-06-01 | 2:00 | 120 | 29 | 2018-06-01 | 12:00
28 | Bhasantec | 132 | 136 | 19 | 2018-06-01 | 8:00 | 120 | 5 | 2018-06-01 | 12:00
29 | Agargaon | 132 | 136 | 16 | 2018-06-01 | 5:00 | 121 | 5 | 2018-06-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 136 | 20 | 2018-06-01 | 4:00 | 121 | 5 | 2018-06-01 | 20:00
31 | Tongi | 132 | 139 | 16 | 2018-06-01 | 15:00 | 124 | 5 | 2018-06-01 | 15:00
32 | Kabirpur | 132 | 137 | 19 | 2018-06-01 | 8:00 | 118 | 2 | 2018-06-01 | 12:00
33 | Basundhara | 132 | 135 | 16 | 2018-06-01 | 16:00 | 120 | 28 | 2018-06-01 | 10:00
34 | Manikganj | 132 | 142 | 19 | 2018-06-01 | 8:00 | 130 | 2 | 2018-06-01 | 12:00
35 | Joydevpur | 132 | 143 | 13 | 2018-06-01 | 18:30 | 128 | 5 | 2018-06-01 | 7:00
36 | New Tongi | 132 | 140 | 19 | 2018-06-01 | 08:00 | 123 | 5 | 2018-06-01 | 15:00
37 | Kodda | 132 | 140 | 12 | 2018-06-01 | 18:30 | 125 | 2 | 2018-06-01 | 9:00
38 | Dhamrai | 132 | 133 | 29 | 2018-06-01 | 05:00 | 125 | 30 | 2018-06-01 | 21:00
39 | Tangail | 132 | 140 | 19 | 2018-06-01 | 07:00 | 120 | 4 | 2018-06-01 | 15:00
40 | Mymensing | 132 | 139 | 19 | 2018-06-01 | 07:00 | 106 | 7 | 2018-06-01 | 19:00
41 | Kishorganj | 132 | 136 | 15 | 2018-06-01 | 06:00 | 115 | 8 | 2018-06-01 | 19:00
42 | Netrokona | 132 | 139 | 19 | 2018-06-01 | 06:00 | 105 | 5 | 2018-06-01 | 14:00
43 | Jamalpur | 132 | 137 | 19 | 2018-06-01 | 04:00 | 109 | 9 | 2018-06-01 | 19:00
44 | Sherpur | 132 | 138 | 21 | 2018-06-01 | 23:00 | 102 | 9 | 2018-06-01 | 19:30
45 | Srimongal | 132 | 140 | 19 | 2018-06-01 | 6:00 | 129 | 12 | 2018-06-01 | 11:00
46 | Shahjibazar | 132 | 139 | 19 | 2018-06-01 | 06:00 | 128 | 12 | 2018-06-01 | 10:00
47 | Fenchuganj | 132 | 137 | 26 | 2018-06-01 | 05:00 | 128 | 2 | 2018-06-01 | 9:00
48 | Khulawara | 132 | 137 | 15 | 2018-06-01 | 06:00 | 121 | 12 | 2018-06-01 | 11:00
49 | Sylhet | 132 | 138 | 1 | 2018-06-01 | 2:00 | 121 | 12 | 2018-06-01 | 12:00
50 | Chattak | 132 | 137 | 14 | 2018-06-01 | 10:00 | 124 | 3 | 2018-06-01 | 16:00
51 | Sunamganj | 132 | 139 | 12 | 2018-06-01 | 19:00 | 125 | 2 | 2018-06-01 | 11:00
52 | Biani Bazar | 132 | 137 | 14 | 2018-06-01 | 10:00 | 129 | 22 | 2018-06-01 | 21:00
53 | Comilla(South) | 132 | 131 | 1 | 2018-06-01 | 7:00 | 117 | 6 | 2018-06-01 | 21:00
54 | Comilla (North) | 132 | 140 | 19 | 2018-06-01 | 12:00 | 124 | 28 | 2018-06-01 | 15:00
55 | Chandpur | 132 | 139 | 16 | 2018-06-01 | 7:00 | 110 | 7 | 2018-06-01 | 3:00
56 | Feni | 132 | 127 | 16 | 2018-06-01 | 6:00 | 110 | 18 | 2018-06-01 | 22:00
57 | Chowmuhani | 132 | 133 | 1 | 2018-06-01 | 17:00 | 106 | 22 | 2018-06-01 | 19:30
58 | Ashuganj | 132 | 140 | 19 | 2018-06-01 | 4:00 | 130 | 4 | 2018-06-01 | 21:00
59 | Daudkandi | 132 | 141 | 9 | 2018-06-01 | 20:00 | 124 | 30 | 2018-06-01 | 9:00
60 | Brahminbaria | 132 | 138 | 18 | 2018-06-01 | 10:00 | 126 | 7 | 2018-06-01 | 21:00
61 | Ramganj | 132 | 140 | 16 | 2018-06-01 | 7:00 | 108 | 20 | 2018-06-01 | 21:00
62 | Madanhat | 132 | 135 | 1 | 2018-06-01 | 06:00 | 126 | 2 | 2018-06-01 | 15:00
63 | Hathazari | 132 | 136 | 22 | 2018-06-01 | 18:30 | 124 | 6 | 2018-06-01 | 11:00
64 | Khulshi | 132 | 132 | 10 | 2018-06-01 | 21:00 | 120 | 3 | 2018-06-01 | 14:00
65 | Halishahar | 132 | 135 | 10 | 2018-06-01 | 21:00 | 121 | 4 | 2018-06-01 | 12:00
66 | Baraulia | 132 | 132 | 10 | 2018-06-01 | 21:00 | 120 | 3 | 2018-06-01 | 12:00
67 | Sikalbaha | 132 | 135 | 10 | 2018-06-01 | 21:00 | 123 | 3 | 2018-06-01 | 10:00
68 | Dohazari | 132 | 134 | 10 | 2018-06-01 | 21:00 | 121 | 6 | 2018-06-01 | 1:00
69 | Cox'sbazar | 132 | 133 | 24 | 2018-06-01 | 11:00 | 111 | 7 | 2018-06-01 | 21:00
70 | Chandraghona | 132 | 134 | 10 | 2018-06-01 | 11:00 | 125 | 3 | 2018-06-01 | 14:00
71 | Kaptai | 132 | 135 | 25 | 2018-06-01 | 21:00 | 125 | 3 | 2018-06-01 | 12:00
72 | A. Khaer Stl. | 132 | 132 | 15 | 2018-06-01 | 18:00 | 122 | 3 | 2018-06-01 | 14:00
73 | Bakulia | 132 | 132 | 10 | 2018-06-01 | 22:00 | 121 | 3 | 2018-06-01 | 14:00
74 | Julda | 132 | 134 | 10 | 2018-06-01 | 21:00 | 122 | 3 | 2018-06-01 | 11:00
75 | TK Chemical | 132 | 137 | 10 | 2018-06-01 | 21:00 | 125 | 7 | 2018-06-01 | 14:00
76 | Modern Steel | 132 | 134 | 14 | 2018-06-01 | 16:00 | 121 | 3 | 2018-06-01 | 11:00
77 | Shahmirpur | 132 | 133 | 10 | 2018-06-01 | 21:00 | 122 | 4 | 2018-06-01 | 12:00
78 | Khagrachhari | 132 | 134 | 10 | 2018-06-01 | 21:00 | 124 | 4 | 2018-06-01 | 19:00
79 | Goalpara | 132 | 139 | 7 | 2018-06-01 | 17:00 | 126 | 10 | 2018-06-01 | 12:00
80 | Khulna Central | 132 | 139 | 6 | 2018-06-01 | 10:00 | 127 | 10 | 2018-06-01 | 12:00
81 | Noapara | 132 | 137 | 6 | 2018-06-01 | 12:00 | 123 | 7 | 2018-06-01 | 19:00
82 | Jessore | 132 | 135 | 29 | 2018-06-01 | 15:00 | 116 | 7 | 2018-06-01 | 19:00
83 | Jhenida | 132 | 137 | 1 | 2018-06-01 | 13:00 | 110 | 8 | 2018-06-01 | 21:00
84 | Bottail | 132 | 140 | 26 | 2018-06-01 | 05:00 | 119 | 13 | 2018-06-01 | 21:00
85 | G.K.Project | 132 | 142 | 1 | 2018-06-01 | 13:00 | 125 | 7 | 2018-06-01 | 21:00
86 | Faridpur | 132 | 138 | 16 | 2018-06-01 | 17:00 | 116 | 9 | 2018-06-01 | 19:00
87 | Madaripur | 132 | 140 | 16 | 2018-06-01 | 15:00 | 117 | 9 | 2018-06-01 | 19:00
88 | Gopalganj | 132 | 144 | 16 | 2018-06-01 | 15:00 | 116 | 13 | 2018-06-01 | 19:00
89 | Bagerhat | 132 | 138 | 2 | 2018-06-01 | 12:00 | 122 | 7 | 2018-06-01 | 19:00
90 | Mongla | 132 | 136 | 10 | 2018-06-01 | 7:00 | 122 | 10 | 2018-06-01 | 12:00
91 | Satkhira | 132 | 137 | 2 | 2018-06-01 | 12:00 | 124 | 13 | 2018-06-01 | 21:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
92 | Gallamari | 132 | 139 | 6 | 2018-06-01 | 13:00 | 127 | 17 | 2018-06-01 | 2:00
93 | Magura | 132 | 138 | 1 | 2018-06-01 | 14:00 | 106 | 7 | 2018-06-01 | 19:00
94 | Chuadanga | 132 | 136 | 1 | 2018-06-01 | 14:00 | 101 | 18 | 2018-06-01 | 21:00
95 | Barisal | 132 | 142 | 16 | 2018-06-01 | 15:00 | 128 | 16 | 2018-06-01 | 24:00:
96 | Patuakhali | 132 | 142 | 25 | 2018-06-01 | 5:00 | 122 | 17 | 2018-06-01 | 1:00
97 | Bhandaria | 132 | 140 | 16 | 2018-06-01 | 16:00 | 121 | 9 | 2018-06-01 | 19:00
98 | Ishurdi | 132 | 142 | 1 | 2018-06-01 | 13:00 | 121 | 9 | 2018-06-01 | 1:00
99 | Ruppur Paromanobik | 132 | 142 | 1 | 2018-06-01 | 13:00 | 122 | 7 | 2018-06-01 | 1:00
100 | Natore | 132 | 139 | 6 | 2018-06-01 | 13:00 | 119 | 13 | 2018-06-01 | 2:00
101 | Bogra | 132 | 139 | 1 | 2018-06-01 | 9:00 | 113 | 30 | 2018-06-01 | 21:00
102 | Noagaon | 132 | 137 | 1 | 2018-06-01 | 10:00 | 110 | 30 | 2018-06-01 | 21:00
103 | Rajshahi | 132 | 138 | 27 | 2018-06-01 | 17:00 | 118 | 13 | 2018-06-01 | 20:00
104 | C.Nawabganj | 132 | 137 | 13 | 2018-06-01 | 18:30 | 118 | 22 | 2018-06-01 | 13:00
105 | Amnura | 132 | 140 | 3 | 2018-06-01 | 17:00 | 116 | 22 | 2018-06-01 | 13:00
106 | Pabna | 132 | 137 | 16 | 2018-06-01 | 16:00 | 119 | 13 | 2018-06-01 | 3:00
107 | Shahjadpur | 132 | 144 | 1 | 2018-06-01 | 13:00 | 128 | 12 | 2018-06-01 | 20:00
108 | Serajganj | 132 | 140 | 1 | 2018-06-01 | 13:00 | 119 | 30 | 2018-06-01 | 21:00
109 | Niyamatpur | 132 | 137 | 1 | 2018-06-01 | 11:00 | 105 | 30 | 2018-06-01 | 20:00
110 | Joypurhat | 132 | 140 | 1 | 2018-06-01 | 9:00 | 105 | 30 | 2018-06-01 | 21:00
111 | Rangpur | 132 | 134 | 1 | 2018-06-01 | 8:00 | 97 | 30 | 2018-06-01 | 20:00
112 | Lalmonirhat | 132 | 137 | 16 | 2018-06-01 | 6:00 | 93 | 21 | 2018-06-01 | 20:00
113 | Saidpur | 132 | 134 | 1 | 2018-06-01 | 11:00 | 97 | 30 | 2018-06-01 | 21:00
114 | Purbasadipur | 132 | 140 | 8 | 2018-06-01 | 7:00 | 110 | 30 | 2018-06-01 | 20:00
115 | Thakurgaon | 132 | 138 | 17 | 2018-06-01 | 5:00 | 102 | 30 | 2018-06-01 | 20:00
116 | Palashbari | 132 | 135 | 1 | 2018-06-01 | 7:00 | 105 | 23 | 2018-06-01 | 1:00
117 | Barapukuria | 132 | 140 | 1 | 2018-06-01 | 17:00 | 115 | 30 | 2018-06-01 | 20:00
118 | Panchagar | 132 | 135 | 16 | 2018-06-01 | 6:00 | 96 | 30 | 2018-06-01 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:June' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 130 | 400
IP-299421 | Hasnabad | TR2 | 225 | 120 | 400 | 01.06.18 | 12:00
|  | TR3 | 225 | 120 | 380
|  | TR1 | 225 | 170 | 565
IP-299866 | Tongi | TR2 | 225 | 170 | 565 | 07.06.18 | 08:00
|  | TR3 | 225 | 170 | 565
|  | TR1 | 225 | 116 | 315
IP-299427 | Haripur | TR2 | 225 | 116 | 315 | 30.06.18 | 09:00
|  | TR3 | 225 | 116 | 315
|  | TR1 | 225 | 200 | 610
IP-299728 | Rampura | TR2 | 225 | 200 | 610 | 10.06.18 | 12:00
|  | TR3 | 225 | 200 | 610
|  | TR1 | 225 | 128 | 376
IP-299264 | Aminbazar | TR2 | 225 | 128 | 376 | 23.06.18 | 12:00
|  | TR3 | 225 | 134 | 392
| Maniknagar | TR1 | 300 | 122 | 380 | 06.06.18 | 14:00
|  | TR2 | 300 | 122 | 380
IP-399266 | Comilla (N) | TR1 | 225 | 185 | 590 | 26.06.18 | 01:00
|  | TR2 | 225 | 183 | 562
| Fenchuganj | TR1 | 300 | 178 | 448 | 06.06.18 | 6:00
|  | TR1 | 150 | 68 | 200
IP-399428 | Hathazari | TR3 | 150 | 68 | 200 | 09.06.18 | 12:00
|  | TR4 | 150 | 68 | 200
|  | TR1 | 225 | 160 | 520
| Ishurdi | TR2 | 225 | 160 | 520 | 15.06.18 | 2:00
IP-499474 |  | TR3 | 225 | 160 | 520
| Khulna(S) | TR1 | 225 | 148 | 373
IP-58001/58002 |  | TR2 | 225 | 148 | 373 | 16.06.18 | 3:00
| Bogra | TR1 | 225 | 129 | 395 | 14.06.18 | 22:00
|  | TR2 | 225 | 129 | 395
IP-43002/499264 |  | TR3 | 225 | 171 | 522
IP-499224 | Baghabari | TR1 | 225 | 183 | 550 | 23.06.18 | 22:00
| Barapukuria | TR1 | 225 | 184 | 1080 | 06.06.18 | 21:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 117 | 580 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 153 | 764
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:June' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:June' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-06-18 | 9198 | 9198 | - | - | - | - | - | - | - | - | - | - | - | - | 01-06-18 | 6607 | 6607 | - | - | - | - | - | - | - | - | - | - | - | -
02-06-18 | 10364 | 10364 | - | - | - | - | - | - | - | - | - | - | - | - | 02-06-18 | 7861.4 | 7861.4 | - | - | - | - | - | - | - | - | - | - | - | -
03-06-18 | 10602 | 10602 | - | - | - | - | - | - | - | - | - | - | - | - | 03-06-18 | 8703.2 | 8703.2 | - | - | - | - | - | - | - | - | - | - | - | -
04-06-18 | 10716 | 10716 | - | - | - | - | - | - | - | - | - | - | - | - | 04-06-18 | 8886.3 | 8886.3 | - | - | - | - | - | - | - | - | - | - | - | -
05-06-18 | 10903 | 10903 | - | - | - | - | - | - | - | - | - | - | - | - | 05-06-18 | 8864 | 8864 | - | - | - | - | - | - | - | - | - | - | - | -
06-06-18 | 10948 | 10948 | - | - | - | - | - | - | - | - | - | - | - | - | 06-06-18 | 9023.2 | 9023 | - | - | - | - | - | - | - | - | - | - | - | -
07-06-18 | 10909 | 10909 | - | - | - | - | - | - | - | - | - | - | - | - | 07-06-18 | 9178.2 | 9178 | - | - | - | - | - | - | - | - | - | - | - | -
08-06-18 | 10561 | 10561 | - | - | - | - | - | - | - | - | - | - | - | - | 08-06-18 | 7958.2 | 7958.2 | - | - | - | - | - | - | - | - | - | - | - | -
09-06-18 | 10249 | 10249 | - | - | - | - | - | - | - | - | - | - | - | - | 09-06-18 | 9043 | 9043 | - | - | - | - | - | - | - | - | - | - | - | -
10-06-18 | 10044 | 10044 | - | - | - | - | - | - | - | - | - | - | - | - | 10-06-18 | 8718.6 | 8718.6 | - | - | - | - | - | - | - | - | - | - | - | -
11-06-18 | 10480 | 10480 | - | - | - | - | - | - | - | - | - | - | - | - | 11-06-18 | 8523.6 | 8523.6 | - | - | - | - | - | - | - | - | - | - | - | -
12-06-18 | 9286 | 9286 | - | - | - | - | - | - | - | - | - | - | - | - | 12-06-18 | 8881.2 | 8881.2 | - | - | - | - | - | - | - | - | - | - | - | -
13-06-18 | 10263 | 10263 | - | - | - | - | - | - | - | - | - | - | - | - | 13-06-18 | 7608.4 | 7608.4 | - | - | - | - | - | - | - | - | - | - | - | -
14-06-18 | 9944 | 9944 | - | - | - | - | - | - | - | - | - | - | - | - | 14-06-18 | 8150.2 | 8150.2 | - | - | - | - | - | - | - | - | - | - | - | -
15-06-18 | 8616 | 8616 | - | - | - | - | - | - | - | - | - | - | - | - | 15-06-18 | 6515.3 | 6515.3 | - | - | - | - | - | - | - | - | - | - | - | -
16-06-18 | 7749 | 7749 | - | - | - | - | - | - | - | - | - | - | - | - | 16-06-18 | 5387.9 | 5387.9 | - | - | - | - | - | - | - | - | - | - | - | -
17-06-18 | 8503 | 8503 | - | - | - | - | - | - | - | - | - | - | - | - | 17-06-18 | 5801.1 | 5801.1 | - | - | - | - | - | - | - | - | - | - | - | -
18-06-18 | 9132 | 9132 | - | - | - | - | - | - | - | - | - | - | - | - | 18-06-18 | 6436.7 | 6436.7 | - | - | - | - | - | - | - | - | - | - | - | -
19-06-18 | 8229 | 8229 | - | - | - | - | - | - | - | - | - | - | - | - | 19-06-18 | 5470.1 | 5470.1 | - | - | - | - | - | - | - | - | - | - | - | -
20-06-18 | 9186 | 9186 | - | - | - | - | - | - | - | - | - | - | - | - | 20-06-18 | 7000.3 | 7000.3 | - | - | - | - | - | - | - | - | - | - | - | -
21-06-18 | 9641 | 9641 | - | - | - | - | - | - | - | - | - | - | - | - | 21-06-18 | 7678.9 | 7678.9 | - | - | - | - | - | - | - | - | - | - | - | -
22-06-18 | 9651 | 9651 | - | - | - | - | - | - | - | - | - | - | - | - | 22-06-18 | 7221 | 7221 | - | - | - | - | - | - | - | - | - | - | - | -
23-06-18 | 10021 | 10021 | - | - | - | - | - | - | - | - | - | - | - | - | 23-06-18 | 7590.8 | 7590.8 | - | - | - | - | - | - | - | - | - | - | - | -
24-06-19 | 9839 | 9839 | - | - | - | - | - | - | - | - | - | - | - | - | 24-06-19 | 8179.5 | 8179.5 | - | - | - | - | - | - | - | - | - | - | - | -
25-06-20 | 10094 | 10094 | - | - | - | - | - | - | - | - | - | - | - | - | 25-06-20 | 8081.5 | 8081.5 | - | - | - | - | - | - | - | - | - | - | - | -
26-06-18 | 10337 | 10337 | - | - | - | - | - | - | - | - | - | - | - | - | 26-06-18 | 8115.9 | 8115.9 | - | - | - | - | - | - | - | - | - | - | - | -
27-06-18 | 10426 | 10426 | - | - | - | - | - | - | - | - | - | - | - | - | 27-06-18 | 8107.9 | 8107.9 | - | - | - | - | - | - | - | - | - | - | - | -
28-06-18 | 10359 | 10359 | - | - | - | - | - | - | - | - | - | - | - | - | 28-06-18 | 8287.9 | 8287.9 | - | - | - | - | - | - | - | - | - | - | - | -
29-06-18 | 9456 | 9456 | - | - | - | - | - | - | - | - | - | - | - | - | 29-06-18 | 7051.7 | 7051.7 | - | - | - | - | - | - | - | - | - | - | - | -
30-06-18 | 10679 | 10679 | - | - | - | - | - | - | - | - | - | - | - | - | 30-06-18 | 8136.3 | 8136.3 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:June' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10949 | 06/06/18 | 22:00
2 | Maximum day peak Genaration | MW | 9178.2 | 07/06/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 10948 | 06/06/18 | 21:00
4 | Minimum Generation | MW | 4876 | 16/06/18 | 17:00
5 | Average of the daily evening peak Genaration | MW | 9879.5
6 | Average of the daily day peak Genaration | MW | 7768.9767
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6014.4251
12 | Total Generation by IPP | MKWH | 1627.6053 | % of total Gen. | 27.06%
13 | Total Generation by BPDB | MKWH | 3122.9495 | " | 51.92%
14 | A) Total Generation by RPCL | MKWH | 77.3461 | '' | 1.286%
| B) Total Generation by REB | MKWH | 132.5074 | " | 2.203%
| C) Total Generation by RENTAL | MKWH | 634.2874 | " | 10.55%
| D) Total Imported from India (HVDC) | MKWH | 321.0787 | " | 5.338%
| E) Total Imported from Tripura, India (A.C) | MKWH | 98.6506 | " | 1.64%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3635.45 | % of total Gen. | 60.45%
| B) Oil | MKWH | 1667.2953 | '' | 27.72%
| C) Hydro | MKWH | 99.1335 | '' | 1.648%
| D) Solar | MKWH | 0.31596 | '' | 0.005253%
| E) Coal | MKWH | 192.501 | '' | 3.201%
| F) HVDC (Import from India) | MKWH | 321.0787 | '' | 5.338%
| G) A.C (Import from Tripura, India) | MKWH | 98.6506 | '' | 1.64%
16 | Maximun of the daily total Generation . | MKWH | 233.988 | 07/06/18
17 | Monthly Load factor | % | 76.2934
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 17313.7404
| A) Gas | M.Taka | 2704.8328
| B) Liquid fuel | M.Taka | 14336.7138
| C) Coal | M.Taka | 272.1938
| D) HVDC (Import from India) | M.Taka | 1637.5015
| E) Tripura(Import from India) | M.Taka | 674.7698
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 890.1145 | 07/06/18
| A) Gas | M.Taka | 100.1187 | 04/06/18
| B) Liquid fuel | M.Taka | 796.4875 | 07/06/18
| C) Coal | M.Taka | 12.1841 | 20/06/18
| D) HVDC (Import from India) | M.Taka | 59.9426 | 18-06-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.9006
| B) Excluding Hydro & Solar | Taka/KWHR | 3.9662
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/06/18 | 06:00
b) | Actual | FT (MSL) | 102.25 | 30/06/18 | 06:00
22 | Peak Genaration of June 2017 | MW | 9479 | 07/06/17 | 21:00
23 | Peak Demand of June 2017 | MW | 9479 | 07/06/17 | 21:00
24 | Maximum peak Generation recorded upto 30/06/18 | MW | 10958 | 28/05/18 | 21:00
25 | Maximum peak Demand recorded upto 30/06/18 | MW | 10958 | 28/05/18 | 21:00
26 | Maximum load shed recorded upto 30/06/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.