## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:May' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | May 2018 |  | April 2018 |  | May 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10958 | 28/05/18 | 10137 | 24/04/18 | 9471 | 27/05/17 | 10958 | 28/05/18
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 21:00
2 | Minimum Generation (MW) | 4453.1 | 01/05/18 | 4376 | 18/04/18 | 3393 | 16/05/17 | - | -
|  |  | 7:00 |  | 4:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10958 | 28/05/18 | 10137 | 24/04/18 | 9356 | 27/05/17 | 10958 | 28/05/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9123.3 | 30/05/18 | 8526.2 | 24/04/2018 | 8571 | 29/05/2017 | 9123.3 | 30/05/18
|  |  | 12:00 |  | 12:00 |  | 11:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10958 | 28/05/18 | 10137 | 24/04/2018 | 9356 | 27/05/17 | 10958 | 28/05/18
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9278.4 |  | 8951.2 |  | 8379.77 |  | 9296.54 | March -18
7 | Average Generation (MW) at Day Peak | 7343.1667 |  | 7375.85 |  | 7259.71 |  | 7779.98 | March -18
8 | Maximum Power Import from India (MW) | 493 | 12/05/18 | 486 | 28/04/18 | 505 | 24/05/17 | 509 | 2017-07-03
|  |  | 8:00 |  | 14:00 |  | 2:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 188 | 29/05/18 | 176 | 05/04/18 | 162 | 13/05/17 | 188 | 29/05/18
|  |  | 21:00 |  | 18:30 |  | 21:00 |  | 21:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2983.8892 |  | 2819.51 |  | 2360.83
21 | Station Use of BPDB (MKWH) | 99.2172 |  | 81.19 |  | 111.17
22 | Net Generation of BPDB (MKWH) | 2884.6721 |  | 2738.32 |  | 2249.66
23 | Net Generation of IPP & RPCL (MKWH) | 1500.9682 |  | 1495.62 |  | 1380.24
24 | Net Generation of REB (MKWH) | 139.4421 |  | 119.68 |  | 112.32
24 | Net Generation of Rental Power Plant (MKWH) | 661.3537 |  | 631.84 |  | 1197.44
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5186.4361 |  | 4985.46 |  | 4939.65 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3455.5029 |  | 3261.2 |  | 3269.66 |  | 3545.44 | March-18
27 | Energy Generation by Diesel (MKWH) | 444.8904 |  | 465.99 |  | 424.76 |  | 465.99 | April-18
28 | Energy Generation by Furnace Oil (MKWH) | 1095.1285 |  | 1060.14 |  | 1205.97 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 61.2514 |  | 64.49 |  | 57.21 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.33688 |  | 0.36 |  |  |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 228.5432 |  | 214.46 |  | 93.21 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 428.8754 |  | 280.62 |  | 436.84 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 70.0932 |  | 73.26 |  | 77.88 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:May' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10958 | 28/05/18 | 21:00
Generation Period
| Dhaka | MW | 4005
| Chittagong | MW | 1119
| Comilla | MW | 984
| Mymensingh | MW | 666
| Sylhet | MW | 423
a) | Total supply in East zone | MW | 7197
| Khulna | MW | 1384
| Barisal | MW | 267
| Rajshahi | MW | 1042
| Rangpur | MW | 434
b) | Total supply in West zone | MW | 3127
c) | Total supply in both zone ( a+b) | MW | 10324
Ref: | 27.21.0603.2604.16.084.18.83 | Date: 20/06/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 900 | 30/05/18 | 20:00
| b) Ishurdi end | MW | 140 | 16/05/18 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 410 | 16/05/18 | 10:00
| b) Ishurdi end | MW | 400 | 30/05/18 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 4.3065 | 22/05/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 4.1818 | 22/05/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 100.1471
| b) Ishurdi end | MKWH | 2.3585
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 2.2878
| b) Ishurdi end | MKWH | 97.6013
23 | Transmission loss of EWI/ NO-1 | % | 2.54
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 500 | 20/05/18 | 21:00
| b)Serajganj end | MW | 80 | 16/05/18 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 70 | 16/05/18 | 9:00
| b)Sirajganj end | MW | 480 | 20/05/18 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 8.52 | 22/05/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 8.43 | 22/05/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 187.62
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 185.484
30 | Transmission loss of EWI /NO-2 | % | 1.138
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
*** The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kallyanpur | 132/33 kV Transformer-T3 | 2018-05-01 11:17 | 2018-05-01 12:15 | 0:58 | E/O | Due toOil leakage | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T4 | 2018-05-08 03:30 | 2018-05-08 03:48 | 0:18 | T | Tripped showing differential relay | 0 | 0 | No interruption
Aminbazar | 132 kV bus-B | 2018-05-15 11:58 | 2018-05-15 13:42 | 1:44 | E/O | Due to bursting of PT | 389 | 674.2667 | Power interruption
Gulshan | 132/33 kV Transformer-T2 | 2018-05-22 03:27 | 2018-05-22 08:00 | 4:33 | T | Tripped showing differential relay | 0 | 0 | No interruption
Tongi | 230/132 kV Transformers-TR-2 | 2018-05-24 07:32 | 2018-05-24 16:20 | 8:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-05-27 12:55 | 2018-05-27 13:40 | 0:45 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2018-05-27 12:55 | 2018-05-27 13:40 | 0:45 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformers-TR-1 | 2018-05-27 22:17 | 2018-05-28 12:58 | 14:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 32:32 |  | Unserved Energy: |  | 674.2667
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-T2 | 2018-05-02 19:48 | 2018-05-02 23:17 | 3:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformers-T-1 & T2 | 2018-05-05 15:19 | 2018-05-05 15:35 | 0:16 | T | Tripped showing differential relay | 40 | 10.6667 | Power interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2018-05-13 05:47 | 2018-05-13 06:10 | 0:23 | T | Tripped showing inst.E/F relay | 60 | 23 | Power interruption
|  |  | Total : | 4:08 |  | Unserved Energy: |  | 33.6667
Chittagong Grid Circle :
Madunaghat | 132/33 kV Transformer-T1 | 2018-05-30 22:22 | 2018-05-30 22:28 | 0:06 | T | Tripped showing O/C relay | 30 | 3 | Power interruption
|  |  | Total : | 0:06 |  | Unserved Energy: |  | 3
Comilla Grid Circle :
Shahjibazar | 132/33 kV Transformer-T-2 | 2018-05-10 17:48 | 2018-05-10 17:55 | 0:07 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformers-T1 | 2018-05-15 18:51 | 2018-05-15 19:29 | 0:38 | E/O | Due to over Voltage during bad weather | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-05-15 18:51 | 2018-05-15 19:26 | 0:35 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2018-05-15 18:51 | 2018-05-15 19:25 | 0:34 | T |  | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-TR2 | 2018-05-19 09:18 | 2018-05-19 12:04 | 2:46 | E/O | Due to red hot maintenance | 7 | 19.3667 | Power interruption
Sylhet | 132/33 kV Transformer-T4 | 2018-05-23 05:58 | 2018-05-23 08:22 | 2:24 | E/O | Due to red hot maintenance | 35 | 84 | Power interruption
Comilla(N) | 132/33 kV Transformer-T4 | 2018-05-24 09:33 | 2018-05-24 11:03 | 1:30 | E/O | Due to red hot maintenance | 20 | 30 | Power interruption
Sunamganj | 132/33 kV Transformer-T2 | 2018-05-29 09:20 | 2018-05-29 09:20 | 0:00 | T | Tripped showing differential relay | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformer-T4 | 2018-05-30 09:52 | 2018-05-30 10:15 | 0:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2018-05-30 22:01 | 2018-05-30 22:03 | 0:02 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Sylhet | 132 kV Bus Section-4 | 2018-05-30 23:50 | 2018-05-31 07:55 | 8:05 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 17:04 |  | Unserved Energy: |  | 133.3667
Khulna Grid Circle :
Khulna© | 132/33 kV Transformer-T-3 | 2018-05-01 07:36 | 2018-05-01 10:31 | 2:55 | E/O | Due toOil leakage | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T-1 & T2 | 2018-05-02 16:29 | 2018-05-02 18:03 | 1:34 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T-1 | 2018-05-02 16:30 | 2018-05-02 18:22 | 1:52 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T-2 | 2018-05-11 17:13 | 2018-05-11 18:19 | 1:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T-2 | 2018-05-16 10:35 | 2018-05-16 10:38 | 0:03 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T-2 | 2018-05-16 21:36 | 2018-05-16 22:08 | 0:32 | E/O | Due to red hot maintenance | 22 | 11.7333 | Power interruption
Faridpur | 132/33 kV Transformer-T-1 | 2018-05-24 11:51 | 2018-05-24 12:52 | 1:01 | E/O | Due toOil leakage | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T-2 | 2018-05-28 09:39 | 2018-05-28 16:03 | 6:24 | E/O | Due to Oil leakage | 8 | 51.2 | Power interruption
| 132/33 kV Transformer-T-1 | 2018-05-29 01:01 | 2018-05-29 01:17 | 0:16 | T | Tripped showing Over Voltage | 140 | 37.3333 | Power interruption
Satkhira | 132/33 kV Transformer-T-1 | 2018-05-29 15:04 | 2018-05-29 15:08 | 0:04 | T | Tripped showing O/C relay | 64 | 4.2667 | Power interruption
|  |  | Total : | 4:29 |  | Unserved Energy: |  | 104.5333
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T2 | 2018-05-29 09:58 | 2018-05-29 11:10 | 1:12 | T | Tripped showing Bushing temperature high | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1 | 2018-05-31 05:49 | 2018-05-31 05:56 | 0:07 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 1:19 |  | Unserved Energy: |  | 0
Bogra Grid Circle:
Palashbari | 132/33 kV Transformer-T-2 | 2018-05-02 12:10 | 2018-05-02 13:22 | 1:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T2 | 2018-05-24 12:10 | 2018-05-24 13:10 | 1:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-TR-1 | 2018-05-24 14:44 | 2018-05-24 17:17 | 2:33 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T01 | 2018-05-25 14:54 | 2018-05-25 16:12 | 1:18 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-TR-1 | 2018-05-28 21:33 | 2018-05-28 22:27 | 0:54 | E/O | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:57 |  | Unserved Energy: |  | 0
Others :
Ashuganj | 132/6.6 kV Transformer-OAT02 | 2018-05-30 19:45 | 2018-05-31 04:09 | 8:24 | E/O | Due to bursting of lightning arrester | 0 | 0 | No interruption
|  |  | Total : | 8:24 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 74:59 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-05-04 10:57 | 2018-05-04 11:37 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-2 | 2018-05-04 12:46 | 2018-05-04 13:10 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-05-07 05:01 | 2018-05-07 05:48 | 0:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2018-05-07 02:33 | 2018-05-07 02:53 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2018-05-07 02:33 | 2018-05-07 02:58 | 0:25 | T |  | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 | 2018-05-07 04:45 | 2018-05-07 04:58 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-05-07 16:26 | 2018-05-07 17:42 | 1:16 | E/O | Due to Breaker mainteanance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-05-09 10:35 | 2018-05-09 12:50 | 2:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2018-05-09 11:10 | 2018-05-09 11:26 | 0:16 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakor 230 kV line-1 | 2018-05-09 13:30 | 2018-05-09 14:03 | 0:33 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Agarogon | Agarogon-Aminbazar 230 kV line-1 | 2018-05-10 11:00 | 2018-05-10 11:33 | 0:33 | T | Tripped showing differential .relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2018-05-10 11:11 | 2018-05-11 00:55 | 13:44 | T | Tripped showing differential .relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2018-05-22 06:35 | 2018-05-22 06:51 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2018-05-23 09:53 | 2018-05-23 10:21 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 | 2018-05-25 20:30 | 2018-05-25 21:40 | 1:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tangail-Mymensingh RPCL 132 kV line-2 | 2018-05-25 20:42 | 2018-05-25 21:36 | 0:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-05-28 23:48 | 2018-05-29 01:50 | 2:02 | E/O | Due to red hot maintenance | 50 | 122 | Power interruption
| Tongi-Uttara 132 kV line | 2018-05-29 01:59 | 2018-05-29 02:45 | 0:46 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-1 | 2018-05-29 00:59 | 2018-05-29 02:17 | 1:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2018-05-30 16:50 | 2018-05-30 16:56 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-05-31 06:47 | 2018-05-31 14:25 | 7:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 36:04 |  | Unserved Energy: |  | 122
Dhaka (South) Grid Circle :
Haripur | Haripur-Siddhirganj 132 kV line-4 | 2018-05-03 16:09 | 2018-05-03 16:17 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 & 2 | 2018-05-04 10:57 | 2018-05-04 12:55 | 1:58 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2018-05-04 20:41 | 2018-05-04 22:48 | 2:07 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Keraniganj P/S 230 kV line | 2018-05-05 09:06 | 2018-05-05 16:48 | 7:42 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-4 | 2018-05-05 15:20 | 2018-05-05 16:39 | 1:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundahara 132 kV line-1 | 2018-05-06 09:12 | 2018-05-06 09:33 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-05-07 05:20 | 2018-05-07 06:09 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line-1 | 2018-05-10 11:16 | 2018-05-10 11:47 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-4 | 2018-05-10 18:23 | 2018-05-10 18:39 | 0:16 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Siddhirganj-Haripur 132 kV line-1 | 2018-05-10 18:23 | 2018-05-10 18:36 | 0:13 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 132 kV line-1 | 2018-05-10 11:44 | 2018-05-10 12:40 | 0:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2018-05-12 17:56 | 2018-05-13 16:00 | 22:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-05-16 04:14 | 2018-05-16 04:50 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Haripur-Shyampur 132 kV line | 2018-05-16 05:30 | 2018-05-16 05:50 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line | 2018-05-22 01:14 | 2018-05-22 01:22 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-05-29 12:33 | 2018-05-29 12:43 | 0:10 | T | Tripped showing dist. relay | 98 | 16.3333 | Power interruption
Madanganj | Madanganj-Munsiganj 132 kV line-1 | 2018-05-31 08:10 | 2018-05-31 09:30 | 1:20 | T | Tripped showing differential relay | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakhya 132 kV line | 2018-05-31 08:04 | 2018-05-31 08:56 | 0:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 41:50 |  | Unserved Energy: |  | 16.3333
Chittagong Grid Circle :
Khulshi | Khulshi-Bakulia 132 kV line-1 | 2018-05-03 02:28 | 2018-05-03 11:39 | 9:11 | E/O | Due to breaker problem | 0 | 0 | No interruption
BSRM | BSRM-Hathazari 230 kV line | 2018-05-04 04:07 | 2018-05-04 04:16 | 0:09 | T | Tripped showing E/F realy | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line | 2018-05-04 05:12 | 2018-05-04 05:44 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2018-05-05 10:01 | 2018-05-05 10:39 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bakulia-Sikalbaha 132 kV line-1 | 2018-05-05 10:01 | 2018-05-05 10:36 | 0:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line | 2018-05-07 07:08 | 2018-05-07 07:15 | 0:07 | T | Tripped showing E/F realy | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 line-1 | 2018-05-11 17:45 | 2018-05-11 17:56 | 0:11 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 | 2018-05-17 11:55 | 2018-05-17 12:02 | 0:07 | T | Tripped showing E/F realy | 0 | 0 | No interruption
Hathazari | Hathazari-Feni 132 kV line-1 | 2018-05-24 12:53 | 2018-05-24 12:59 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2018-05-28 23:32 | 2018-05-29 02:42 | 3:10 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Tk.chemical -Sikalbaha 132 kV line | 2018-05-29 12:10 | 2018-05-29 13:01 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line | 2018-05-31 01:56 | 2018-05-31 03:01 | 1:05 | T | Tripped showing E/F realy | 0 | 0 | No interruption
|  |  | Total : | 16:42 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Ashuganj(N) | Ashuganj(N)-Bhulta 400 kV line-1 | 2018-05-02 15:58 | 2018-05-03 11:27 | 19:29 | E/O | Due to heavy spriking at R-phase isolator | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Feni 132 kV line-1 | 2018-05-02 17:02 | 2018-05-02 17:08 | 0:06 | T | Tripped showing E/F realy | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2018-05-03 00:21 | 2018-05-03 00:50 | 0:29 | E/O | Due to heavy spriking at R-phase isolator | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Feni 132 kV line-2 | 2018-05-04 12:17 | 2018-05-04 12:29 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
B.baria | B.baria-Shahjibazar 132 kV line-1 | 2018-05-07 00:48 | 2018-05-07 00:51 | 0:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-05-07 02:50 | 2018-05-07 03:47 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
B.baria | B.baria-Shahjibazar 132 kV line-2 | 2018-05-07 03:25 | 2018-05-07 04:15 | 0:50 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-05-09 12:24 | 2018-05-09 12:30 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 & 2 | 2018-05-09 13:18 | 2018-05-09 13:34 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Comiila(N) 132 kV line-2 | 2018-05-10 11:54 | 2018-05-10 12:47 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-05-10 12:07 | 2018-05-10 12:11 | 0:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line1 | 2018-05-10 12:32 | 2018-05-10 12:44 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Comilla(N) 132 kV line | 2018-05-11 16:52 | 2018-05-11 21:17 | 4:25 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-05-18 06:42 | 2018-05-18 06:54 | 0:12 | T | Tripped showing dist. relay | 183 | 36.6 | Power interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-2 | 2018-05-24 12:53 | 2018-05-24 13:00 | 0:07 | T | Tripped showing E/F realy | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 line-1 & 2 | 2018-05-24 14:27 | 2018-05-24 14:41 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 line-2 | 2018-05-25 06:52 | 2018-05-25 15:45 | 8:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2018-05-26 06:41 | 2018-05-26 07:01 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2018-05-30 19:44 | 2018-05-30 21:30 | 1:46 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2018-05-30 19:44 | 2018-05-30 21:33 | 1:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2018-05-30 21:56 | 2018-05-30 22:13 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 41:40 |  | Unserved Energy: |  | 36.6
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line | 2018-05-02 13:15 | 2018-05-02 13:36 | 0:21 | T | Tripped showing dist. relay | 39 | 13.65 | Power interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2018-05-10 10:36 | 2018-05-10 13:13 | 2:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-1 | 2018-05-10 11:04 | 2018-05-10 16:17 | 5:13 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
| Khulna©-Noapara 132 kV line-2 | 2018-05-10 11:04 | 2018-05-10 17:34 | 6:30 | T |  | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-1 | 2018-05-11 17:13 | 2018-05-11 17:38 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Khulna©-Noapara 132 kV line-2 | 2018-05-11 17:13 | 2018-05-11 18:17 | 1:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Khulna©-Goalpara 132 kV line-1 | 2018-05-11 17:07 | 2018-05-11 18:23 | 1:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2018-05-11 17:01 | 2018-05-11 18:10 | 1:09 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line-1 | 2018-05-11 18:54 | 2018-05-11 19:27 | 0:33 | T | Tripped showing O/C. relay | 16 | 8.8 | Power interruption
Barisal | Barisal-Bhandaria 132 kV line1 | 2018-05-15 10:26 | 2018-05-15 11:24 | 0:58 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-1 | 2018-05-16 06:31 | 2018-05-16 07:35 | 1:04 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2018-05-16 06:31 | 2018-05-16 07:37 | 1:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna© 132 kV line-1 | 2018-05-22 14:22 | 2018-05-22 20:23 | 6:01 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line2 | 2018-05-25 21:03 | 2018-05-25 21:23 | 0:20 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-2 | 2018-05-27 16:18 | 2018-05-27 17:15 | 0:57 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  |  | 29:34 |  | Unserved Energy: |  | 22.45
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 & 2 | 2018-05-05 05:09 | 2018-05-05 06:28 | 1:19 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Jhenidah | Jhenidah-Bottail 132 kV line-1 | 2018-05-05 01:39 | 2018-05-05 02:15 | 0:36 | T | Tripped showing E/F relay | 23 | 13.8 | Power interruption 01:39 to 02:16
| Jhenidah-Bottail 132 kV line-2 | 2018-05-05 01:39 | 2018-05-05 02:16 | 0:37 | T
| Jhenidah-Jessore 132 kV line-1 | 2018-05-05 01:39 | 2018-05-05 02:11 | 0:32 | T | Tripped showing dist. relay | 23 | 12.2667 | Power interruption 01:39 to 02:11
| Jhenidah-Jessore 132 kV line-2 | 2018-05-05 01:39 | 2018-05-05 02:12 | 0:33 | T
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-05-06 01:39 | 2018-05-06 02:07 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 4:05 |  | Unserved Energy: |  | 26.0667
Bogra Grid Circle :
Naogaon | Naogaon-Niyamatpur 132 kV line | 2018-05-16 00:27 | 2018-05-16 00:47 | 0:20 | T | Tripped showing dist. relay | 30 | 10 | Power interruption
| Naogaon-Niyamatpur 132 kV line | 2018-05-16 00:58 | 2018-05-16 02:12 | 1:14 | T |  | 30 | 32 | Power interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-05-17 16:27 | 2018-05-17 16:46 | 0:19 | T | Tripped showing dist. relay | 110 | 23.8333 | Power interruption 16:27 to 16:40
| Saidpur-Purbasadipur 132 kV line-2 | 2018-05-17 16:27 | 2018-05-17 16:40 | 0:13 | T
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-2 | 2018-05-25 04:20 | 2018-05-25 04:38 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Palshbari 132 kV line-1 | 2018-05-28 21:33 | 2018-05-28 22:23 | 0:50 | T | Tripped showing O/C relay | 200 | 36.6667 | Power interruption 21:33 to 21:44
| Rangpur-Palshbari 132 kV line-2 | 2018-05-28 21:33 | 2018-05-28 21:44 | 0:11 | T
Barapukuria | Barapukuria-Rangpur 132 kV line-2 | 2018-05-28 21:33 | 2018-05-28 22:32 | 0:59 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 4:24 |  | Unserved Energy: |  | 102.5
Others :
Bangabhaban | Bangabhaban-Maniknagar 132 kV line-1 | 2018-05-02 07:50 | 2018-05-02 17:50 | 10:00 | T | Tripped showing pilot wire protection relay | 0 | 0 | No interruption
|  |  | Total : | 10:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 184:19 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-T-2 | 2018-05-06 09:38 | 2018-05-06 12:33 | 2:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T1 | 2018-05-08 07:15 | 2018-05-08 08:30 | 1:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2018-05-12 07:12 | 2018-05-12 14:19 | 7:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2018-05-17 08:20 | 2018-05-17 10:52 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargon | 230/132 kV Transformer-Tr-1 | 2018-05-19 08:39 | 2018-05-19 15:09 | 6:30 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 20:19 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Savar | 132 kV main bus | 2018-05-01 06:50 | 2018-05-01 08:18 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2018-05-10 22:22 | 2018-05-14 17:57 | 91:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2018-05-15 08:03 | 2018-05-15 15:12 | 7:09 | S/O | Due to delta test | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-05-15 15:23 | 2018-05-15 18:46 | 3:23 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 103:35 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Chandraghona | 132/33 kV Transformers-T-1 | 2018-05-05 06:03 | 2018-05-05 12:45 | 6:42 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV Transformers-T-2 | 2018-05-05 06:03 | 2018-05-05 12:46 | 6:43 | S/O |  | 0 | 0 | No interruption
Cox'sbazar | 230/132 kV Transformer-T3 | 2018-05-14 10:02 | 2018-05-14 12:35 | 2:33 | S/O | Due to cable change | 14 | 35.7 | Power interruption
Cox'sbazar | 132/33 kV Transformer-T3 | 2018-05-27 09:38 | 2018-05-27 13:20 | 3:42 | S/O | Due to maintenance work | 19 | 51.8 | Power interruption
|  |  | Total : | 19:40 |  | Unserved Energy: |  | 87.5
Page:2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
B.baria | 132/33 kV Transformer-T2 | 2018-05-09 12:12 | 2018-05-09 16:01 | 3:49 | S/O | Due to delta test | 0 | 0 | No interruption
Bibiyana | 400/230 kV Transformer-T1 | 2018-05-16 08:45 | 2018-05-16 16:25 | 7:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformer-T4 | 2018-05-16 14:10 | 2018-05-16 15:10 | 1:00 | S/O | Due to replacement work | 30 | 30 | Power interruption
| 132/33 kV Transformer-T3 | 2018-05-16 14:26 | 2018-05-16 15:25 | 0:59 | S/O |  | 30 | 29.5 | Power interruption
Ashuganj | 230 kV Bus-2 | 2018-05-24 09:40 | 2018-05-24 18:01 | 8:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total | 21:49 |  | Unserved Energy : |  | 59.5
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformer-T2 | 2018-05-05 16:57 | 2018-05-05 17:17 | 0:20 | S/O | Due to replacement work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2018-05-11 07:14 | 2018-05-11 12:41 | 5:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2018-05-11 09:25 | 2018-05-11 10:29 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2018-05-21 09:38 | 2018-05-21 19:27 | 9:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T5 | 2018-05-29 09:18 | 2018-05-29 18:18 | 9:00 | S/O | Due to painting work | 0 | 0 | No interruption
|  |  | Total : | 25:40 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
Bheramara | 400 kV Bus-1 | 2018-05-16 08:45 | 2018-05-16 16:25 | 7:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 7:40 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Saidpur | 132/33 kV Transformer-T5 | 2018-05-04 11:05 | 2018-05-04 11:31 | 0:26 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-05-04 11:44 | 2018-05-04 12:13 | 0:29 | S/O | Due to maintenance work | 9 | 4.35 | Power interruption
Rangpur | 132/33 kV Transformer-T1 | 2018-05-09 12:20 | 2018-05-09 13:50 | 1:30 | S/O | Due to feeder problem | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2018-05-09 15:40 | 2018-05-09 16:28 | 0:48 | S/O | Due to maintenance work | 32 | 25.6 | Power interruption
Bogra | 132/33 kV Transformer-T4 | 2018-05-10 08:05 | 2018-05-10 09:40 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 | 2018-05-11 09:30 | 2018-05-11 12:05 | 2:35 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 7:23 |  | Unserved Energy : |  | 29.95
Others :
Ghorashal | 230/132 kV Transformer-AT-2 | 2018-05-01 04:41 | 2018-05-02 18:12 | 37:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 37:31 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 243:37 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: May 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kallyanpur | Kallyanpur-Lalbagh 132 kV line | 2018-05-01 07:32 | 2018-05-01 11:17 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kodda 230 kV line | 2018-05-05 12:36 | 2018-05-05 13:13 | 0:37 | S/O | Due to CB test | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-2 | 2018-05-10 13:28 | 2018-05-11 00:55 | 11:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-05-11 18:10 | 2018-05-11 20:29 | 2:19 | S/O | Due to tree trimming | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2018-05-13 06:45 | 2018-05-13 07:55 | 1:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-2 | 2018-05-13 08:53 | 2018-05-13 18:35 | 9:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-05-13 07:06 | 2018-05-13 17:06 | 10:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2018-05-14 07:46 | 2018-05-14 16:27 | 8:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-17 08:35 | 2018-05-17 10:39 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 & 2 | 2018-05-18 09:34 | 2018-05-18 16:38 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2018-05-19 06:01 | 2018-05-19 06:55 | 0:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-19 08:39 | 2018-05-19 15:09 | 6:30 | S/O | Due to project work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 122 kV line-1 | 2018-05-20 07:41 | 2018-05-20 16:19 | 8:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-24 10:22 | 2018-05-24 17:09 | 6:47 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-26 07:23 | 2018-05-26 16:05 | 8:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-27 06:26 | 2018-05-27 11:57 | 5:31 | S/O | Due to project work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-29 07:26 | 2018-05-29 16:38 | 9:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-05-30 06:46 | 2018-05-30 17:24 | 10:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2018-05-31 09:17 | 2018-05-31 16:24 | 7:07 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 120:48 |  | Unserved Energy: |  | 0
Page: 2/7 | [8 empty] | QF-LDC-26
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad -Meghnaghat 230 kV line-2 | 2018-05-05 09:06 | 2018-05-05 16:48 | 7:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV line | 2018-05-03 10:36 | 2018-05-03 13:31 | 2:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-05-04 06:13 | 2018-05-04 16:10 | 9:57 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Syampur 132 kV line | 2018-05-05 06:13 | 2018-05-05 20:12 | 13:59 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 line | 2018-05-05 06:45 | 2018-05-05 20:20 | 13:35 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Syampur 132 kV line | 2018-05-07 11:54 | 2018-05-07 17:10 | 5:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| Haripur-Madanganj 132 line | 2018-05-07 10:56 | 2018-05-07 17:03 | 6:07 | S/O |  | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-2 | 2018-05-10 06:39 | 2018-05-10 18:39 | 12:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2018-05-10 12:54 | 2018-05-10 16:49 | 3:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-2 | 2018-05-11 06:44 | 2018-05-11 15:53 | 9:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj Desh 132 kV line | 2018-05-11 06:44 | 2018-05-11 17:50 | 11:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-2 | 2018-05-11 08:22 | 2018-05-11 12:05 | 3:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-1 | 2018-05-11 16:03 | 2018-05-11 17:47 | 1:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2018-05-12 07:20 | 2018-05-12 19:12 | 11:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-05-12 07:30 | 2018-05-12 18:32 | 11:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-4 | 2018-05-12 09:38 | 2018-05-12 13:36 | 3:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalakyha | Sitalakyha -Hasnabad 132 kV line | 2018-05-13 08:25 | 2018-05-13 22:23 | 13:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 132 kV line | 2018-05-13 08:02 | 2018-05-14 00:05 | 16:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Sitalakyha | Sitalakyha -Hasnabad 132 kV line | 2018-05-13 08:25 | 2018-05-13 22:23 | 13:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2018-05-14 05:58 | 2018-05-14 18:15 | 12:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2018-05-14 05:50 | 2018-05-14 17:36 | 11:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj Desh 132 kV line | 2018-05-14 06:14 | 2018-05-14 18:15 | 12:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| Siddhirganj-Haripur 132 kV line-2 | 2018-05-15 06:08 | 2018-05-15 19:39 | 13:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj Desh 132 kV line | 2018-05-15 06:13 | 2018-05-15 19:31 | 13:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-1 | 2018-05-15 09:12 | 2018-05-15 16:02 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Sitalakhya 132 kV line-1 | 2018-05-15 08:44 | 2018-05-15 16:54 | 8:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Shyampur 132 kV line | 2018-05-15 09:22 | 2018-05-15 16:08 | 6:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-05-16 09:47 | 2018-05-16 18:17 | 8:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2018-05-16 12:12 | 2018-05-16 19:40 | 7:28 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Comilla(N) 230 kV line-1 | 2018-05-17 09:15 | 2018-05-17 13:52 | 4:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR Energy P/P 230 kV line | 2018-05-17 09:25 | 2018-05-17 22:46 | 13:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2018-05-17 10:28 | 2018-05-17 20:20 | 9:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line-1 | 2018-05-17 16:22 | 2018-05-17 16:37 | 0:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line-2 | 2018-05-19 09:03 | 2018-05-19 10:38 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 230 kV line-1 | 2018-05-23 10:38 | 2018-05-23 15:21 | 4:43 | S/O | Due to project work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-1 | 2018-05-24 13:40 | 2018-05-24 16:03 | 2:23 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2018-05-24 16:04 | 2018-05-24 20:59 | 4:55 | S/O | Due to project work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 230 kV line-1 | 2018-05-27 09:37 | 2018-05-27 15:35 | 5:58 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2018-05-28 10:33 | 2018-05-28 14:34 | 4:01 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-05-30 10:13 | 2018-05-30 16:01 | 5:48 | S/O | Due to line checking | 0 | 0 | No interruption
|  |  | Total : | 330:04 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2018-05-13 10:50 | 2018-05-13 12:35 | 1:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV line | 2018-05-14 08:54 | 2018-05-14 17:04 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-05-22 08:02 | 2018-05-22 16:59 | 8:57 | S/O | Due to project work | 0 | 0 | No interruption
Khagrachhori | Khagrachhori -Changraghona 132 kV line-1 | 2018-05-26 10:38 | 2018-05-26 13:54 | 3:16 | S/O | Due to Breaker problem | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2018-05-29 10:45 | 2018-05-29 13:09 | 2:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 24:32 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Comilla(N) | Comilla(N)-Feni 132 kV line-1 | 2018-05-04 05:32 | 2018-05-04 10:56 | 5:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 & 2 | 2018-05-07 09:52 | 2018-05-07 19:03 | 9:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 line-1 | 2018-05-12 08:47 | 2018-05-12 14:42 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Comiila(N) 132 kV line-1 | 2018-05-12 09:32 | 2018-05-12 11:12 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Feni 132 kV line-2 | 2018-05-12 16:35 | 2018-05-12 18:52 | 2:17 | S/O | Due to replacement work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj 230 kV diameter -3 | 2018-05-14 10:02 | 2018-05-14 21:32 | 11:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 & 2 | 2018-05-15 07:31 | 2018-05-15 19:50 | 12:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV line-1 & 2 | 2018-05-16 08:38 | 2018-05-16 19:10 | 10:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2018-05-16 11:08 | 2018-05-16 12:32 | 1:24 | S/O | Due to replacement work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 line-1 | 2018-05-16 12:18 | 2018-05-16 15:24 | 3:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 line-1 | 2018-05-21 14:20 | 2018-05-21 16:47 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Chandpur 132 kV line-2 | 2018-05-24 09:11 | 2018-05-24 13:44 | 4:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 70:18 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Goalpara | Goalpara-Khulna P/S 132 kV line | 2018-05-09 20:46 | 2018-05-09 20:52 | 0:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
Goalpara | Goalpara-Khuilna P/S 132 kV line | 2018-05-10 10:46 | 2018-05-10 14:33 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna©-KPCL P/S 132 kV line | 2018-05-11 17:09 | 2018-05-11 18:10 | 1:01 | S/O | Due to maintenance work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna© 132 kV line-1 | 2018-05-22 08:40 | 2018-05-22 13:34 | 4:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barisal | Barisal-Patuakahli 132 kV line | 2018-05-24 14:59 | 2018-05-24 17:10 | 2:11 | S/O | Due to maintenance work | 20 | 43.6667 | Power interruption
|  |  | Total : | 11:59 |  | Unserved Energy: |  | 43.6667
HVDC Grid Circle :
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2018-05-03 09:13 | 2018-05-03 10:45 | 1:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 & 2 | 2018-05-07 07:32 | 2018-05-07 15:31 | 7:59 | S/O | Due to project work | 0 | 0 | No interruption
Bheramara | Bheramara-Bheramara 400 kV line-1 | 2018-05-17 08:51 | 2018-05-17 13:16 | 4:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara -Bottail 132 kV line-2 | 2018-05-19 09:03 | 2018-05-19 10:38 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Bheramara 400 kV line-2 | 2018-05-23 09:32 | 2018-05-23 17:26 | 7:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 23:25 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Natore 132 kV line-2 | 2018-05-05 10:12 | 2018-05-05 11:33 | 1:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2018-05-10 11:02 | 2018-05-10 12:42 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-2 | 2018-05-10 10:16 | 2018-05-10 12:50 | 2:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Thakurgaon 132 kV line | 2018-05-19 08:35 | 2018-05-19 09:55 | 1:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 6:55 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 467:13 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May' 2018
| Area | Previous Month (April 2018) |  |  |  | Current Month (May 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 24 | 2 | 15 | 41 | 22 | 8 | 24 | 54
2 | Dhaka (South) Grid Circle. | 33 | 5 | 34 | 72 | 18 | 2 | 44 | 64
3 | Chittagong Grid Circle. | 5 | 6 | 9 | 20 | 11 | 2 | 9 | 22
4 | Comilla Grid Circle. | 32 | - | 16 | 48 | 24 | 3 | 17 | 44
5 | Khulna Grid Circle. | 27 | 3 | 8 | 38 | 19 | 6 | 10 | 35
6 | Bheramara HVDC Grid Circle | 14 | 2 | 3 | 19 | 8 | - | 6 | 14
7 | Bogra Grid Circle. | 24 | 5 | 24 | 53 | 9 | 4 | 10 | 23
8 | Others | 3 | 1 | 1 | 5 | 1 | 1 | 1 | 3
9 | Total | 162 | 24 | 110 | 296 | 112 | 26 | 121 | 259
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May' 2018
| Area | Previous Month (April 2018) |  |  |  | Current Month (May 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 27.42 | - | - | 27.42 | - | 796.27 | - | 796.27
2 | Dhaka ( South) grid circle | 19.33 | 63.5 | - | 82.83 | 50 | - | - | 50
3 | Chittagong grid circle. | - | - | 29.7 | 29.7 | 3 | - | 87.5 | 90.5
4 | Comilla grid circle. | 206.08 | - | 145.6 | 351.68 | 36.6 | 133.37 | 59.5 | 229.47
5 | Khulna grid circle. | 246.02 | 29.33 |  | 275.35 | 64.05 | 62.93 | 43.67 | 170.65
6 | Bheramara HVDC grid circle | 7.83 | 20.5 | 231 | 259.33 | 26.07 | - | - | 26.07
7 | Bogra grid circle. | 181.97 | 14.73 | - | 196.7 | 102.5 | - | 29.95 | 132.45
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 688.65 | 128.06 | 406.3 | 1223.01 | 282.22 | 992.57 | 220.62 | 1495.41
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 | 1 | 1 | - | - | 1 | 674.27
2 | Dhaka (South) | 5031.6 | 2 |  | 2 | 1 | - | - | 33.67
3 | Chittagong | 2042 | 1 | 2 | 3 | 1 | - | 2 | 90.5
4 | Khulna | 2434 | 4 | - | 4 | 3 |  | 1 | 104.53
5 | Bheramara (HVDC) | 2423.3 | - | - | - | - | - | - | -
6 | Bogra | 3145.6 | 2 | - | 2 | 1 |  | 1 | 29.95
7 | Comilla | 2981 | 3 | 2 | 5 | - | 2 | 3 | 192.87
| Total | 23365.5 | [6 empty] | 1125.79
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.88%
2 | Dhaka (South) | 99.97%
3 | Chittagong | 99.99%
4 | Khulna | 99.94%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.96% | [6 empty] | Information Management Division
7 | Comilla | 99.98% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 | - | - | 1 | 122
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | 1 | - | - | 16.33
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 2 | 1 | 3 | 1 | 1 | 1 | 66.12
5 | Bheramara (HVDC) | 598.7 |  | 2 | - | 2 | - | 2 | - | 26.07
6 | Bogra | 1803.3 | 38 | 3 | - | 3 | 2 | 1 | - | 102.5
7 | Comilla | 1648.16 | 17 | 1 | - | 1 | 1 | - | - | 36.6
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 369.62
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.89%
2 | Dhaka (South) | 99.9%
3 | Chittagong | 99.97%
4 | Khulna | 99.91%
5 | Bheramara (HVDC) | 99.97% | [7 empty] | Executive Engineer
6 | Bogra | 99.98% | [7 empty] | Information Management Division
7 | Comilla | 99.77% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
May | 14 | - | 6 | 14hr40 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:May' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Aminbazar | 1 | 1:44 | 389 | 674.2667 | Due to bursting of PT
Tongi | 1 | 2:02 | 50 | 122 | Due to red-hot maintenance of Tongi-Kabirpur 132 kV line
Kamrangirchar | 1 | 0:16 | 40 | 10.6667 | Due to tripping of 132/33 kV Transformers T1 & T2
Siddhirganj | 1 | 0:23 | 60 | 23 | Due to tripping of 132/33 kV Transformer T1
Haripur | 1 | 0:10 | 98 | 16.3333 | Due to tripping of Haripur-Siddhirganj 132 kV line
Madunaghat | 1 | 0:06 | 30 | 3 | Due to tripping of 132/33 kV Transformer T1
Cox'sbazar | 2 | 2:33 | 14 | 35.7 | Due to S/D of 132/33 kV Transformer T3
|  | 3:42 | 19 | 51.8
Fenchuganj | 1 | 2:46 | 7 | 19.3667 | Due to red-hot maintenance of 132/33 kV Transformer TR2
Sylhet | 1 | 2:24 | 35 | 84 | Due to red-hot maintenance of 132/33 kV Transformer T4
Comiila(N) | 1 | 1:30 | 20 | 30 | Due to red-hot maintenance of 132/33 kV Transformer T4
Ashuganj | 1 | 0:12 | 183 | 36.6 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-2
Comiila(N) | 2 | 1:00 | 30 | 30 | Due to S/D of 132/33 kV Transformer T4
|  | 0:59 | 30 | 29.5 | Due to S/D of 132/33 kV Transformer T3
Bagerhat | 1 | 0:32 | 22 | 11.7333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Faridpur | 2 | 6:24 | 8 | 51.2 | Due to Oil leakage of 132/33 kV Transformer T2
|  | 0:16 | 140 | 37.3333
Satkhira | 1 | 0:04 | 64 | 4.2667 | Due to tripping of 132/33 kV Transformer T1
Madaripur | 1 | 0:21 | 39 | 13.65 | Due to tripping of Madaripur-Gopalganj 132 kV line
Barisal | 1 | 0:33 | 16 | 8.8 | Due to tripping of Barisal-Patuakahli 132 kV line
| 1 | 2:11 | 20 | 43.6667 | Due to S/D of Barisal-Patuakhali 132 kV line
Jhenidah | 2 | 0:36 | 23 | 13.8 | Due to tripping of Jhenidah-Bottail 132 kV line-1 & 2
|  | 0:32 | 23 | 12.2667
Naogaon | 2 | 0:20 | 30 | 10 | Due to tripping of Naogaon-Niyamatpur 132 kV line
|  | 1:14 | 30 | 32
Saidpur | 1 | 0:13 | 110 | 23.8333 | Due to tripping of Saidpur-Purbasadipur 132 kV line-1 & 2
Rangpur | 1 | 0:11 | 200 | 36.6667 | Due to tripping of Rangpur-Palashbari 132 kV line-1 & 2
Saidpur | 1 | 0:29 | 9 | 4.35 | Due to S/D of 132/33 kV Transformer T4
Ishurdi | 1 | 0:48 | 32 | 25.6
| Total unserved energy : |  |  | 1495.4 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:May'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 140 | 28 | 2018-05-01 | 15:00
2 | Munsiganj | 120 | 29 | 2018-05-01 | 21:00
3 | Megnaghat | 58 | 29 | 2018-05-01 | 21:00
4 | Shyampur | 184 | 10 | 2018-05-01 | 12:00
5 | Bhulta | 184 | 8 | 2018-05-01 | 19:30
6 | Madanganj | 58 | 26 | 2018-05-01 | 21:00
7 | Shitalakhya | 117 | 12 | 2018-05-01 | 16:00
8 | Rahim steel | 18 | 16 | 2018-05-01 | 6:00
9 | Matuail | 98 | 30 | 2018-05-01 | 10:00
10 | Ghorasal | 84 | 28 | 2018-05-01 | 21:00
11 | Narsingdi | 123 | 26 | 2018-05-01 | 21:00
12 | Haripur (SBU) | 100 | 16 | 2018-05-01 | 21:00
13 | Ullon | 105 | 27 | 2018-05-01 | 19:30
14 | Hasnabad | 211 | 27 | 2018-05-01 | 20:00
15 | Magbazar | 132 | 30 | 2018-05-01 | 15:00
16 | Maniknagar | 96 | 28 | 2018-05-01 | 12:00
17 | Bangabhaban | 38 | 30 | 2018-05-01 | 12:00
18 | Narinda | 84 | 15 | 2018-05-01 | 16:00
19 | Dhanmondi | 170 | 27 | 2018-05-01 | 12:00
20 | Lalbag | 94 | 30 | 2018-05-01 | 13:00
21 | Madartek | 64 | 21 | 2018-05-01 | 1:00
22 | Mirpur | 116 | 13 | 2018-05-01 | 19:00
23 | Kalyanpur | 135 | 28 | 2018-05-01 | 20:00
24 | Gulshan | 142 | 30 | 2018-05-01 | 13:00
25 | Uttara | 96 | 27 | 2018-05-01 | 21:00
26 | Kamrangirchar | 99 | 7 | 2018-05-01 | 19:00
27 | Savar | 161 | 15 | 2018-05-01 | 20:00
28 | Bhasantec | 170 | 27 | 2018-05-01 | 16:00
29 | Agargaon | 142 | 22 | 2018-05-01 | 18:30
30 | Satmosjid | 103 | 28 | 2018-05-01 | 19:00
31 | Tongi | 144 | 30 | 2018-05-01 | 9:00
32 | Kabirpur | 214 | 30 | 2018-05-01 | 14:00
33 | Basundhara | 134 | 29 | 2018-05-01 | 21:00
34 | Manikganj | 112 | 28 | 2018-05-01 | 21:00
35 | Joydevpur | 229 | 13 | 2018-05-01 | 19:30
36 | New Tongi | 119 | 8 | 2018-05-01 | 12:00
37 | Kodda | 212 | 1 | 2018-05-01 | 1:00
38 | Tangail | 168 | 30 | 2018-05-01 | 21:00
39 | Mymensing | 220 | 6 | 2018-05-01 | 20:00
40 | Kishorganj | 92 | 29 | 2018-05-01 | 21:00
41 | Netrokona | 76 | 19 | 2018-05-01 | 19:30
42 | Jamalpur | 100 | 26 | 2018-05-01 | 20:00
43 | Sherpur | 77 | 27 | 2018-05-01 | 23:00
44 | Srimongal | 43 | 28 | 2018-05-01 | 20:00
45 | Shahjibazar | 105 | 28 | 2018-05-01 | 22:00
46 | Fenchuganj | 52 | 27 | 2018-05-01 | 20:00
47 | Khulawara | 42 | 27 | 2018-05-01 | 19:00
48 | Sylhet | 155 | 29 | 2018-05-01 | 21:00
49 | Chatak | 43 | 1 | 2018-05-01 | 19:00
50 | Sunamganj | 40 | 17 | 2018-05-01 | 21:00
51 | Comilla (S) | 188 | 29 | 2018-05-01 | 21:00
52 | Comilla(N) | 111 | 24 | 2018-05-01 | 19:00
53 | Chandpur | 129 | 28 | 2018-05-01 | 19:30
54 | Feni | 123 | 30 | 2018-05-01 | 22:00
55 | Chowmuhani | 204 | 27 | 2018-05-01 | 21:00
56 | Ashuganj | 59 | 28 | 2018-05-01 | 23:00
57 | Daudkandi | 108 | 27 | 2018-05-01 | 21:00
58 | B.Baria | 140 | 28 | 2018-05-01 | 21:00
59 | Madanhat | 71 | 29 | 2018-05-01 | 20:00
60 | Hathazari | 96 | 30 | 2018-05-01 | 21:00
61 | Khulshi | 200 | 8 | 2018-05-01 | 15:00
62 | Halishahar | 143 | 30 | 2018-05-01 | 15:00
63 | Baraulia | 152 | 23 | 2018-05-01 | 14:00
64 | Sikalbaha | 131 | 13 | 2018-05-01 | 9:00
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:May'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
65 | Dohazari | 94 | 27 | 2018-05-01 | 21:00
66 | Cox'sbazar | 100 | 28 | 2018-05-01 | 21:00
67 | Chandraghona | 36 | 22 | 2018-05-01 | 19:00
68 | Kaptai | 5 | 20 | 2018-05-01 | 12:00
69 | A. Khaer Stl. | 12 | 15 | 2018-05-01 | 09:00
70 | Bakulia | 206 | 9 | 2018-05-01 | 19:30
71 | Julda | 23 | 27 | 2018-05-01 | 11:00
72 | TK chemical | 7.4 | 17 | 2018-05-01 | 16:00
73 | Modern Steel | 16 | 6 | 2018-05-01 | 6:00
74 | Shahmirpur | 30 | 9 | 2018-05-01 | 19:00
75 | Abul Khair 230 | 202 | 4 | 2018-05-01 | 4:00
76 | BSRM | 115 | 24 | 2018-05-01 | 18:00
77 | Khagrachhari | 18 | 29 | 2018-05-01 | 22:00
78 | Goalpara | 49 | 30 | 2018-05-01 | 22:00
79 | Central s/s | 96 | 24 | 2018-05-01 | 21:00
80 | Noapara | 95 | 29 | 2018-05-01 | 19:30
81 | Jessore | 152 | 30 | 2018-05-01 | 20:00
82 | Jhenida | 92 | 29 | 2018-05-01 | 21:00
83 | Bottail | 128 | 27 | 2018-05-01 | 21:00
84 | G.K Project | 58 | 28 | 2018-05-01 | 21:00
85 | Faridpur | 150 | 26 | 2018-05-01 | 20:00
86 | Madaripur | 134 | 28 | 2018-05-01 | 21:00
87 | Gopalganj | 182 | 27 | 2018-05-01 | 19:30
88 | Bagerhat | 87 | 30 | 2018-05-01 | 19:30
89 | Mongla | 40 | 23 | 2018-05-01 | 10:00
90 | Satkhira | 95 | 26 | 2018-05-01 | 21:00
91 | Gallamari | 60 | 28 | 2018-05-01 | 20:00
92 | Magura | 54 | 27 | 2018-05-01 | 21:00
93 | Chuadanga | 82 | 26 | 2018-05-01 | 21:00
94 | Barisal | 120 | 30 | 2018-05-01 | 20:00
95 | Patuakhali | 97 | 30 | 2018-05-01 | 20:00
96 | Bhandaria | 86 | 26 | 2018-05-01 | 21:00
97 | Ishurdi | 55 | 23 | 2018-05-01 | 21:00
98 | Ruppur Paromanobik | 1 | 1 | 2018-05-01 | 1:00
99 | Natore | 114 | 26 | 2018-05-01 | 21:00
100 | Bogra | 236 | 27 | 2018-05-01 | 21:00
101 | Noagaon | 102 | 28 | 2018-05-01 | 3:00
102 | Rajshahi | 145 | 27 | 2018-05-01 | 21:00
103 | C.Nawabganj | 69 | 24 | 2018-05-01 | 2:00
104 | Amnura | 35 | 23 | 2018-05-01 | 21:00
105 | Pabna | 110 | 27 | 2018-05-01 | 21:00
106 | Shahjadpur | 91 | 28 | 2018-05-01 | 20:00
107 | Serajganj | 91 | 27 | 2018-05-01 | 20:00
108 | Niyamatpur | 58 | 9 | 2018-05-01 | 21:00
109 | Joypurhat | 52 | 28 | 2018-05-01 | 20:00
110 | Rangpur | 121 | 26 | 2018-05-01 | 19:30
111 | Lalmonirhat | 89 | 31 | 2018-05-01 | 20:00
112 | Saidpur | 119 | 22 | 2018-05-01 | 21:00
113 | Purbasadipur | 101 | 24 | 2018-05-01 | 20:00
114 | Thakurgaon | 71 | 22 | 2018-05-01 | 20:00
115 | Palashbari | 104 | 28 | 2018-05-01 | 19:00
116 | Barapukuria | 51 | 30 | 2018-05-01 | 21:00
117 | Panchagar | 38 | 18 | 2018-05-01 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:May' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 4005 | 28.05.18 | 21:00
Chittagong | 1266 | 30.05.18 | 24:00
Khulna | 1384 | 28.05.18 | 21:00
Rajshahi | 1108 | 26.05.18 | 21:00
Comilla | 995 | 26.05.18 | 4:00
Mymensingh | 675 | 29.05.18 | 21:00
Sylhet | 428 | 27.05.18 | 22:00
Barisal | 269 | 27.05.18 | 20:00
Rangpur | 664 | 22.05.18 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 416 | 3 | 2018-05-01 | 01:00 | 380 | 7 | 2018-05-01 | 19:30
2 | Bheramara | 400 | 419 | 14 | 2018-05-01 | 4:00 | 388 | 2 | 2018-05-01 | 24:00
3 | Kaliakoir | 400 | 416 | 3 | 2018-05-01 | 01:00 | 353 | 6 | 2018-05-01 | 19:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 235 | 1 | 2018-05-01 | 01:00 | 222 | 28 | 2018-05-01 | 11:00
2 | Ishurdi | 230 | 238 | 16 | 2018-05-01 | 4:00 | 220 | 7 | 2018-05-01 | 21:00
3 | Ashuganj | 230 | 240 | 11 | 2018-05-01 | 7:00 | 225 | 29 | 2018-05-01 | 11:00
4 | Serajganj | 230 | 232 | 4 | 2018-05-01 | 9:00 | 210 | 30 | 2018-05-01 | 11:00
5 | Baghabari | 230 | 232 | 10 | 2018-05-01 | 11:00 | 200 | 1 | 2018-05-01 | 20:00
6 | Barapukuria | 230 | 246 | 16 | 2018-05-01 | 5:00 | 220 | 5 | 2018-05-01 | 19:30
7 | Bogra | 230 | 237 | 4 | 2018-05-01 | 08':00 | 207 | 27 | 2018-05-01 | 21:00
8 | Khulna South | 230 | 239 | 2 | 2018-05-01 | 16'00 | 206 | 10 | 2018-05-01 | 5:00
9 | Rampura | 230 | 228 | 1 | 2018-05-01 | 07:00 | 216 | 28 | 2018-05-01 | 12:00
10 | Haripur | 230 | 228 | 1 | 2018-05-01 | 9:00 | 215 | 28 | 2018-05-01 | 11:00
11 | Hasnabad | 230 | 232 | 11 | 2018-05-01 | 8:00 | 212 | 29 | 2018-05-01 | 12:00
12 | Aminbazar | 230 | 231 | 1 | 2018-05-01 | 04:00 | 213 | 29 | 2018-05-01 | 11:00
13 | Tongi | 230 | 230 | 7 | 2018-05-01 | 7:00 | 205 | 28 | 2018-05-01 | 10:00
14 | Comilla (N) | 230 | 235 | 11 | 2018-05-01 | 7:00 | 220 | 28 | 2018-05-01 | 09:00
15 | Hathazari | 230 | 230 | 19 | 2018-05-01 | 22:00 | 202 | 8 | 2018-05-01 | 16:00
16 | Megnaghat | 230 | 232 | 1 | 2018-05-01 | 1:00 | 219 | 29 | 2018-05-01 | 12:00
17 | Fenchuganj | 230 | 240 | 1 | 2018-05-01 | 4:00 | 225 | 6 | 2018-05-01 | 18:00
18 | Siddhirganj | 230 | 228 | 10 | 2018-05-01 | 19:00 | 207 | 6 | 2018-05-01 | 11:00
19 | Maniknagar | 230 | 230 | 16 | 2018-05-01 | 4:00 | 205 | 6 | 2018-05-01 | 11:00
20 | Old Airport | 230 | 231 | 1 | 2018-05-01 | 05:00 | 210 | 29 | 2018-05-01 | 12:00
21 | Barisal | 230 | 244 | 11 | 2018-05-01 | 18:30 | 218 | 29 | 2018-05-01 | 01:00
22 | AKSML | 230 | 227 | 7 | 2018-05-01 | 08:00 | 202 | 28 | 2018-05-01 | 24:00
23 | BSRM | 230 | 232 | 7 | 2018-05-01 | 08:00 | 206 | 8 | 2018-05-01 | 16:00
24 | Bibiyana | 230 | 238 | 2 | 2018-05-01 | 03:00 | 223 | 3 | 2018-05-01 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 139 | 21 | 2018-05-01 | 18:30 | 125 | 6 | 2018-05-01 | 11:00
2 | Munsiganj | 132 | 140 | 19 | 2018-05-01 | 18:30 | 126 | 6 | 2018-05-01 | 10:00
3 | Megnaghat | 132 | 138 | 21 | 2018-05-01 | 18:30 | 126 | 29 | 2018-05-01 | 12:00
4 | Shyampur | 132 | 136 | 21 | 2018-05-01 | 7:00 | 120 | 6 | 2018-05-01 | 11:00
5 | Bhulta | 132 | 142 | 31 | 2018-05-01 | 4:00 | 118 | 6 | 2018-05-01 | 11:00
6 | Madanganj | 132 | 139 | 1 | 2018-05-01 | 7:00 | 124 | 28 | 2018-05-01 | 10:00
7 | Shitalakhya | 132 | 140 | 2 | 2018-05-01 | 16:00 | 125 | 19 | 2018-05-01 | 11:00
8 | Rahim Steal | 132 | 138 | 16 | 2018-05-01 | 04:00 | 126 | 6 | 2018-05-01 | 10:00
9 | Matuail | 132 | 137 | 16 | 2018-05-01 | 5:00 | 124 | 6 | 2018-05-01 | 10:00
10 | Ghorasal | 132 | 145 | 4 | 2018-05-01 | 13:00 | 130 | 28 | 2018-05-01 | 11:00
11 | Narsinghdi | 132 | 136 | 18 | 2018-05-01 | 13:00 | 122 | 6 | 2018-05-01 | 9:00
12 | Haripur (SBU) | 132 | 138 | 8 | 2018-05-01 | 21:00 | 125 | 6 | 2018-05-01 | 11:00
13 | Ullon | 132 | 140 | 16 | 2018-05-01 | 5:00 | 126 | 27 | 2018-05-01 | 12:00
14 | Hasnabad | 132 | 138 | 1 | 2018-05-01 | 8:00 | 126 | 28 | 2018-05-01 | 10:00
15 | Magbazar | 132 | 141 | 16 | 2018-05-01 | 6:00 | 125 | 27 | 2018-05-01 | 12:00
16 | Maniknagar | 132 | 139 | 10 | 2018-05-01 | 19:00 | 123 | 6 | 2018-05-01 | 11:00
17 | Bangabhaban | 132 | 140 | 2 | 2018-05-01 | 5:00 | 123 | 6 | 2018-05-01 | 11:00
18 | Narinda | 132 | 141 | 16 | 2018-05-01 | 5:00 | 128 | 5 | 2018-05-01 | 10:00
19 | Dhanmondi | 132 | 140 | 16 | 2018-05-01 | 05:00 | 126 | 27 | 2018-05-01 | 12:00
20 | Lalbag | 132 | 140 | 2 | 2018-05-01 | 5:00 | 119 | 29 | 2018-05-01 | 12:00
21 | Madartek | 132 | 141 | 16 | 2018-05-01 | 5:00 | 126 | 27 | 2018-05-01 | 12:00
22 | Mirpur | 132 | 138 | 16 | 2018-05-01 | 4:00 | 123 | 27 | 2018-05-01 | 11:00
23 | Kalyanpur | 132 | 137 | 16 | 2018-05-01 | 5:00 | 125 | 5 | 2018-05-01 | 11:00
24 | Gulshan | 132 | 140 | 16 | 2018-05-01 | 4:00 | 119 | 22 | 2018-05-01 | 11:00
25 | Uttara | 132 | 136 | 16 | 2018-05-01 | 6:00 | 113 | 28 | 2018-05-01 | 12:00
26 | Kamrangirchar | 132 | 138 | 2 | 2018-05-01 | 5:00 | 123 | 19 | 2018-05-01 | 11:00
27 | Savar | 132 | 136 | 16 | 2018-05-01 | 4:00 | 119 | 27 | 2018-05-01 | 12:00
28 | Bhasantec | 132 | 136 | 23 | 2018-05-01 | 18:30 | 118 | 29 | 2018-05-01 | 12:00
29 | Agargaon | 132 | 135 | 1 | 2018-05-01 | 5:00 | 120 | 29 | 2018-05-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 134 | 1 | 2018-05-01 | 4:00 | 119 | 29 | 2018-05-01 | 12:00
31 | Tongi | 132 | 142 | 7 | 2018-05-01 | 05:00 | 122 | 28 | 2018-05-01 | 10:00
32 | Kabirpur | 132 | 142 | 7 | 2018-05-01 | 5:00 | 120 | 16 | 2018-05-01 | 17:00
33 | Basundhara | 132 | 137 | 7 | 2018-05-01 | 5:00 | 120 | 28 | 2018-05-01 | 14:00
34 | Manikganj | 132 | 144 | 7 | 2018-05-01 | 5:00 | 126 | 20 | 2018-05-01 | 15:00
35 | Joydevpur | 132 | 144 | 16 | 2018-05-01 | 5:00 | 125 | 24 | 2018-05-01 | 9:00
36 | New Tongi | 132 | 142 | 7 | 2018-05-01 | 04:00 | 121 | 28 | 2018-05-01 | 14:00
37 | Kodda | 132 | 144 | 29 | 2018-05-01 | 02:00 | 126 | 31 | 2018-05-01 | 14:00
38 | Tangail | 132 | 145 | 7 | 2018-05-01 | 05:00 | 120 | 28 | 2018-05-01 | 19:30
39 | Mymensing | 132 | 142 | 9 | 2018-05-01 | 12:00 | 107 | 20 | 2018-05-01 | 19:00
40 | Kishorganj | 132 | 140 | 7 | 2018-05-01 | 04:00 | 113 | 21 | 2018-05-01 | 21:00
41 | Netrokona | 132 | 140 | 8 | 2018-05-01 | 05:00 | 105 | 22 | 2018-05-01 | 19:30
42 | Jamalpur | 132 | 142 | 9 | 2018-05-01 | 12:00 | 108 | 21 | 2018-05-01 | 22:00
43 | Sherpur | 132 | 143 | 9 | 2018-05-01 | 11:00 | 107 | 21 | 2018-05-01 | 22:00
44 | Srimongal | 132 | 142 | 7 | 2018-05-01 | 17:00 | 127 | 29 | 2018-05-01 | 12:00
45 | Shahjibazar | 132 | 141 | 8 | 2018-05-01 | 09:00 | 127 | 29 | 2018-05-01 | 11:00
46 | Fenchuganj | 132 | 138 | 1 | 2018-05-01 | 05:00 | 126 | 29 | 2018-05-01 | 12:00
47 | Khulawara | 132 | 136 | 1 | 2018-05-01 | 01:00 | 122 | 29 | 2018-05-01 | 12:00
48 | Sylhet | 132 | 142 | 31 | 2018-05-01 | 19:00 | 120 | 18 | 2018-05-01 | 10:00
49 | Chattak | 132 | 139 | 18 | 2018-05-01 | 19:00 | 124 | 28 | 2018-05-01 | 10:00
50 | Sunamganj | 132 | 140 | 18 | 2018-05-01 | 03:00 | 125 | 19 | 2018-05-01 | 11:00
51 | Comilla(South) | 132 | 139 | 7 | 2018-05-01 | 6:00 | 117 | 27 | 2018-05-01 | 21:00
52 | Comilla (North) | 132 | 140 | 1 | 2018-05-01 | 18:00 | 125 | 25 | 2018-05-01 | 11:00
53 | Chandpur | 132 | 138 | 7 | 2018-05-01 | 7:00 | 119 | 6 | 2018-05-01 | 15:00
54 | Feni | 132 | 130 | 7 | 2018-05-01 | 8:00 | 113 | 7 | 2018-05-01 | 1:00
55 | Chowmuhani | 132 | 137 | 16 | 2018-05-01 | 7:00 | 116 | 28 | 2018-05-01 | 10:00
56 | Ashuganj | 132 | 143 | 15 | 2018-05-01 | 18:00 | 125 | 21 | 2018-05-01 | 22:00
57 | Daudkandi | 132 | 142 | 8 | 2018-05-01 | 8:00 | 125 | 28 | 2018-05-01 | 10:00
58 | Brahminbaria | 132 | 142 | 15 | 2018-05-01 | 19:30 | 123 | 20 | 2018-05-01 | 21:00
59 | Madanhat | 132 | 141 | 7 | 2018-05-01 | 08:00 | 123 | 28 | 2018-05-01 | 10:00
60 | Hathazari | 132 | 134 | 2 | 2018-05-01 | 19:00 | 120 | 31 | 2018-05-01 | 10:00
61 | Khulshi | 132 | 137 | 9 | 2018-05-01 | 6:00 | 118 | 28 | 2018-05-01 | 11:00
62 | Halishahar | 132 | 140 | 7 | 2018-05-01 | 08:00 | 121 | 9 | 2018-05-01 | 15:00
63 | Baraulia | 132 | 133 | 13 | 2018-05-01 | 13:00 | 107 | 14 | 2018-05-01 | 11:00
64 | Sikalbaha | 132 | 138 | 13 | 2018-05-01 | 13:00 | 122 | 8 | 2018-05-01 | 16:00
65 | Dohazari | 132 | 135 | 4 | 2018-05-01 | 12:00 | 118 | 30 | 2018-05-01 | 15:00
66 | Cox'sbazar | 132 | 135 | 4 | 2018-05-01 | 12:00 | 111 | 30 | 2018-05-01 | 15:00
67 | Chandraghona | 132 | 139 | 7 | 2018-05-01 | 8:00 | 115 | 5 | 2018-05-01 | 15:00
68 | Kaptai | 132 | 135 | 2 | 2018-05-01 | 19:30 | 122 | 8 | 2018-05-01 | 15:00
69 | A. Khaer Stl. | 132 | 133 | 7 | 2018-05-01 | 08:00 | 120 | 28 | 2018-05-01 | 12:00
70 | Bakulia | 132 | 137 | 7 | 2018-05-01 | 08:00 | 120 | 28 | 2018-05-01 | 12:00
71 | Julda | 132 | 135 | 7 | 2018-05-01 | 07:00 | 120 | 6 | 2018-05-01 | 20:00
72 | TK Chemical | 132 | 137 | 20 | 2018-05-01 | 14:00 | 124 | 28 | 2018-05-01 | 12:00
73 | Modern Steel | 132 | 133 | 7 | 2018-05-01 | 08:00 | 119 | 28 | 2018-05-01 | 10:00
74 | Shahmirpur | 132 | 134 | 19 | 2018-05-01 | 08:00 | 121 | 28 | 2018-05-01 | 12:00
75 | Khagrachhari | 132 | 134 | 19 | 2018-05-01 | 18:30 | 119 | 28 | 2018-05-01 | 12:00
76 | Goalpara | 132 | 141 | 2 | 2018-05-01 | 16:00 | 118 | 10 | 2018-05-01 | 5:00
77 | Khulna Central | 132 | 139 | 2 | 2018-05-01 | 16:00 | 120 | 10 | 2018-05-01 | 5:00
78 | Noapara | 132 | 139 | 2 | 2018-05-01 | 16:00 | 118 | 10 | 2018-05-01 | 4:00
79 | Jessore | 132 | 136 | 4 | 2018-05-01 | 18:30 | 117 | 10 | 2018-05-01 | 16:00
80 | Jhenida | 132 | 139 | 2 | 2018-05-01 | 16:00 | 109 | 19 | 2018-05-01 | 13:00
81 | Bottail | 132 | 144 | 10 | 2018-05-01 | 10:00 | 120 | 6 | 2018-05-01 | 21:00
82 | G.K.Project | 132 | 144 | 17 | 2018-05-01 | 09:00 | 130 | 9 | 2018-05-01 | 2:00
83 | Faridpur | 132 | 141 | 2 | 2018-05-01 | 17:00 | 120 | 12 | 2018-05-01 | 23:00
84 | Madaripur | 132 | 142 | 2 | 2018-05-01 | 17:00 | 122 | 10 | 2018-05-01 | 3:00
85 | Gopalganj | 132 | 146 | 2 | 2018-05-01 | 17:00 | 118 | 10 | 2018-05-01 | 5:00
86 | Bagerhat | 132 | 141 | 11 | 2018-05-01 | 18:30 | 120 | 2 | 2018-05-01 | 12:00
87 | Mongla | 132 | 138 | 16 | 2018-05-01 | 21:00 | 113 | 10 | 2018-05-01 | 5:00
88 | Satkhira | 132 | 141 | 2 | 2018-05-01 | 16:00 | 121 | 12 | 2018-05-01 | 14:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
89 | Gallamari | 132 | 141 | 11 | 2018-05-01 | 18:30 | 122 | 10 | 2018-05-01 | 5:00
90 | Magura | 132 | 140 | 6 | 2018-05-01 | 3:00 | 107 | 19 | 2018-05-01 | 13:00
91 | Chuadanga | 132 | 139 | 10 | 2018-05-01 | 10:00 | 105 | 19 | 2018-05-01 | 13:00
92 | Barisal | 132 | 142 | 2 | 2018-05-01 | 17:00 | 126 | 12 | 2018-05-01 | 14:00
93 | Patuakhali | 132 | 142 | 2 | 2018-05-01 | 17:00 | 126 | 12 | 2018-05-01 | 14:00
94 | Bhandaria | 132 | 140 | 13 | 2018-05-01 | 10:00 | 120 | 12 | 2018-05-01 | 14:00
95 | Ishurdi | 132 | 145 | 7 | 2018-05-01 | 9:00 | 130 | 9 | 2018-05-01 | 4:00
96 | Ruppur Paromanobik | 132 | 142 | 16 | 2018-05-01 | 10:00 | 131 | 28 | 2018-05-01 | 1:00
97 | Natore | 132 | 141 | 16 | 2018-05-01 | 20:00 | 126 | 28 | 2018-05-01 | 3:00
98 | Bogra | 132 | 143 | 16 | 2018-05-01 | 3:00 | 119 | 30 | 2018-05-01 | 21:00
99 | Noagaon | 132 | 146 | 10 | 2018-05-01 | 11:00 | 115 | 27 | 2018-05-01 | 21:00
100 | Rajshahi | 132 | 138 | 16 | 2018-05-01 | 2:00 | 125 | 10 | 2018-05-01 | 12:00
101 | C.Nawabganj | 132 | 138 | 14 | 2018-05-01 | 18:00 | 120 | 10 | 2018-05-01 | 12:00
102 | Amnura | 132 | 140 | 6 | 2018-05-01 | 19:30 | 118 | 19 | 2018-05-01 | 13:00
103 | Pabna | 132 | 140 | 7 | 2018-05-01 | 9:00 | 124 | 30 | 2018-05-01 | 21:00
104 | Shahjadpur | 132 | 145 | 4 | 2018-05-01 | 11:00 | 131 | 31 | 2018-05-01 | 18:30
105 | Serajganj | 132 | 142 | 16 | 2018-05-01 | 2:00 | 123 | 22 | 2018-05-01 | 20:00
106 | Niyamatpur | 132 | 142 | 16 | 2018-05-01 | 3:00 | 111 | 27 | 2018-05-01 | 21:00
107 | Joypurhat | 132 | 144 | 4 | 2018-05-01 | 8:00 | 111 | 30 | 2018-05-01 | 21:00
108 | Rangpur | 132 | 138 | 4 | 2018-05-01 | 7:00 | 108 | 27 | 2018-05-01 | 21:00
109 | Lalmonirhat | 132 | 143 | 16 | 2018-05-01 | 20:00 | 100 | 22 | 2018-05-01 | 21:00
110 | Saidpur | 132 | 140 | 4 | 2018-05-01 | 7:00 | 104 | 30 | 2018-05-01 | 21:00
111 | Purbasadipur | 132 | 145 | 16 | 2018-05-01 | 5:00 | 112 | 30 | 2018-05-01 | 20:00
112 | Thakurgaon | 132 | 145 | 16 | 2018-05-01 | 5:00 | 105 | 19 | 2018-05-01 | 21:00
113 | Palashbari | 132 | 140 | 4 | 2018-05-01 | 7:00 | 110 | 27 | 2018-05-01 | 21:00
114 | Barapukuria | 132 | 146 | 16 | 2018-05-01 | 5:00 | 120 | 5 | 2018-05-01 | 19:30
115 | Panchagar | 132 | 147 | 16 | 2018-05-01 | 5:00 | 98 | 20 | 2018-05-01 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:May' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 135 | 400
IP-299421 | Hasnabad | TR2 | 225 | 125 | 390 | 12.05.18 | 23:00
|  | TR3 | 225 | 125 | 370
|  | TR1 | 225 | 180 | 570
IP-299866 | Tongi | TR2 | 225 | 180 | 570 | 28.05.18 | 21:00
|  | TR3 | 225 | 180 | 570
|  | TR1 | 225 | 103 | 270
IP-299427 | Haripur | TR2 | 225 | 103 | 270 | 10.05.18 | 12:00
|  | TR3 | 225 | 103 | 270
|  | TR1 | 225 | 150 | 600
IP-299728 | Rampura | TR2 | 225 | 150 | 600 | 27.05.18 | 12:00
|  | TR3 | 225 | 150 | 600
|  | TR1 | 225 | 137 | 411
IP-299264 | Aminbazar | TR2 | 225 | 137 | 411 | 27.05.18 | 21:00
|  | TR3 | 225 | 143 | 429
| Maniknagar | TR1 | 300 | 115 | 360 | 28.05.18 | 14:00
|  | TR2 | 300 | 115 | 360
IP-399266 | Comilla (N) | TR1 | 225 | 160 | 480 | 06.05.18 | 24:00
|  | TR2 | 225 | 160 | 480
| Fenchuganj | TR1 | 300 | 264 | 680 | 09.05.18 | 15:00
|  | TR1 | 150 | 85 | 205
IP-399428 | Hathazari | TR3 | 150 | 85 | 205 | 20.05.18 | 7:00
|  | TR4 | 150 | 85 | 205
|  | TR1 | 225 | 150 | 540
| Ishurdi | TR2 | 225 | 150 | 540 | 09.05.18 | 2:00
IP-499474 |  | TR3 | 225 | 150 | 540
| Khulna(S) | TR1 | 225 | 148 | 399
IP-58001/58002 |  | TR2 | 225 | 148 | 399 | 19.05.18 | 12:00
| Bogra | TR1 | 225 | 116 | 350 | 20.05.18 | 21:00
|  | TR2 | 225 | 116 | 350
IP-43002/499264 |  | TR3 | 225 | 155 | 458
IP-499224 | Baghabari | TR1 | 225 | 140 | 430 | 21.05.18 | 21:00
| Barapukuria | TR1 | 225 | 190 | 950 | 27.05.18 | 20:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 300 | 110 | 570 |  |  | 132 kV current is being provided
|  | TR6 | 225 | 146 | 743
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:May' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-05-18 | 7710 | 7710 | - | - | - | - | - | - | - | - | - | - | - | - | 01-05-18 | 5578 | 5578 | - | - | - | - | - | - | - | - | - | - | - | -
02-05-18 | 6579 | 6579 | - | - | - | - | - | - | - | - | - | - | - | - | 02-05-18 | 5636.6 | 5636 | - | - | - | - | - | - | - | - | - | - | - | -
03-05-18 | 9091 | 9091 | - | - | - | - | - | - | - | - | - | - | - | - | 03-05-18 | 7342.8 | 7342.8 | - | - | - | - | - | - | - | - | - | - | - | -
04-05-18 | 8024 | 8024 | - | - | - | - | - | - | - | - | - | - | - | - | 04-05-18 | 5661.1 | 5661.1 | - | - | - | - | - | - | - | - | - | - | - | -
05-05-18 | 8883 | 8883 | - | - | - | - | - | - | - | - | - | - | - | - | 05-05-18 | 7201 | 7201 | - | - | - | - | - | - | - | - | - | - | - | -
06-05-18 | 9758 | 9758 | - | - | - | - | - | - | - | - | - | - | - | - | 06-05-18 | 7898 | 7898 | - | - | - | - | - | - | - | - | - | - | - | -
07-05-18 | 9641 | 9641 | - | - | - | - | - | - | - | - | - | - | - | - | 07-05-18 | 7083.3 | 7083.3 | - | - | - | - | - | - | - | - | - | - | - | -
08-05-18 | 9566 | 9566 | - | - | - | - | - | - | - | - | - | - | - | - | 08-05-18 | 7628.1 | 7628.1 | - | - | - | - | - | - | - | - | - | - | - | -
09-05-18 | 9446 | 9446 | - | - | - | - | - | - | - | - | - | - | - | - | 09-05-18 | 7650.3 | 7650.3 | - | - | - | - | - | - | - | - | - | - | - | -
10-05-18 | 8033 | 8033 | - | - | - | - | - | - | - | - | - | - | - | - | 10-05-18 | 7342.4 | 7342.4 | - | - | - | - | - | - | - | - | - | - | - | -
11-05-18 | 6549 | 6549 | - | - | - | - | - | - | - | - | - | - | - | - | 11-05-18 | 5767.7 | 5767.7 | - | - | - | - | - | - | - | - | - | - | - | -
12-05-18 | 9449 | 9449 | - | - | - | - | - | - | - | - | - | - | - | - | 12-05-18 | 6988 | 6988 | - | - | - | - | - | - | - | - | - | - | - | -
13-05-18 | 9160 | 9160 | - | - | - | - | - | - | - | - | - | - | - | - | 13-05-18 | 7537.1 | 7537.1 | - | - | - | - | - | - | - | - | - | - | - | -
14-05-18 | 9464 | 9464 | - | - | - | - | - | - | - | - | - | - | - | - | 14-05-18 | 7619 | 7619 | - | - | - | - | - | - | - | - | - | - | - | -
15-05-18 | 9313 | 9313 | - | - | - | - | - | - | - | - | - | - | - | - | 15-05-18 | 7952 | 7952 | - | - | - | - | - | - | - | - | - | - | - | -
16-05-18 | 8753 | 8753 | - | - | - | - | - | - | - | - | - | - | - | - | 16-05-18 | 6623.3 | 6623.3 | - | - | - | - | - | - | - | - | - | - | - | -
17-05-18 | 9703 | 9703 | - | - | - | - | - | - | - | - | - | - | - | - | 17-05-18 | 7620.3 | 7620.3 | - | - | - | - | - | - | - | - | - | - | - | -
18-05-18 | 8668 | 8668 | - | - | - | - | - | - | - | - | - | - | - | - | 18-05-18 | 5664.6 | 5664.5 | - | - | - | - | - | - | - | - | - | - | - | -
19-05-18 | 9917 | 9917 | - | - | - | - | - | - | - | - | - | - | - | - | 19-05-18 | 7219.7 | 7219.7 | - | - | - | - | - | - | - | - | - | - | - | -
20-05-18 | 9715 | 9715 | - | - | - | - | - | - | - | - | - | - | - | - | 20-05-18 | 7472.4 | 7472.4 | - | - | - | - | - | - | - | - | - | - | - | -
21-05-18 | 9663 | 9663 | - | - | - | - | - | - | - | - | - | - | - | - | 21-05-18 | 7460.2 | 7460.2 | - | - | - | - | - | - | - | - | - | - | - | -
22-05-18 | 10147 | 10147 | - | - | - | - | - | - | - | - | - | - | - | - | 22-05-18 | 7877.3 | 7877.3 | - | - | - | - | - | - | - | - | - | - | - | -
23-05-18 | 9004 | 9004 | - | - | - | - | - | - | - | - | - | - | - | - | 23-05-18 | 7694.9 | 7694.9 | - | - | - | - | - | - | - | - | - | - | - | -
24-05-19 | 10130 | 10130 | - | - | - | - | - | - | - | - | - | - | - | - | 24-05-19 | 7976.2 | 7976.2 | - | - | - | - | - | - | - | - | - | - | - | -
25-05-20 | 8960 | 8960 | - | - | - | - | - | - | - | - | - | - | - | - | 25-05-20 | 6999 | 6999 | - | - | - | - | - | - | - | - | - | - | - | -
26-05-18 | 10699 | 10699 | - | - | - | - | - | - | - | - | - | - | - | - | 26-05-18 | 8129 | 8129 | - | - | - | - | - | - | - | - | - | - | - | -
27-05-18 | 10825 | 10825 | - | - | - | - | - | - | - | - | - | - | - | - | 27-05-18 | 8732.9 | 8732.9 | - | - | - | - | - | - | - | - | - | - | - | -
28-05-18 | 10958 | 10958 | - | - | - | - | - | - | - | - | - | - | - | - | 28-05-18 | 8783.2 | 8783.2 | - | - | - | - | - | - | - | - | - | - | - | -
29-05-18 | 10875 | 10875 | - | - | - | - | - | - | - | - | - | - | - | - | 29-05-18 | 8033.3 | 8033.3 | - | - | - | - | - | - | - | - | - | - | - | -
30-05-18 | 9869 | 9869 | - | - | - | - | - | - | - | - | - | - | - | - | 30-05-18 | 9123.3 | 9123.3 | - | - | - | - | - | - | - | - | - | - | - | -
31-05-18 | 9887 | 9887 | - | - | - | - | - | - | - | - | - | - | - | - | 31-05-18 | 7365.5 | 7365.5 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:May' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10958 | 28/05/18 | 21:00
2 | Maximum day peak Genaration | MW | 9123.3 | 30/05/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 10958 | 28/05/18 | 21:00
4 | Minimum Generation | MW | 4453.1 | 01/05/18 | 7:00
5 | Average of the daily evening peak Genaration | MW | 9298.0323
6 | Average of the daily day peak Genaration | MW | 7343.1667
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5714.5287
12 | Total Generation by IPP | MKWH | 1433.9889 | % of total Gen. | 25.0937
13 | Total Generation by BPDB | MKWH | 2983.8892 | " | 52.2158
14 | A) Total Generation by RPCL | MKWH | 66.9793 | '' | 1.1721
| B) Total Generation by REB | MKWH | 139.4421 | " | 2.4401
| C) Total Generation by RENTAL | MKWH | 661.3537 | " | 11.5732
| D) Total Imported from India (HVDC) | MKWH | 339.7433 | " | 5.9453
| E) Total Imported from Tripura, India (A.C) | MKWH | 89.1322 | " | 1.5597
15 | Fuel wise Generation.
| A) Gas | MKWH | 3455.5029 | % of total Gen. | 60.47%
| B) Oil | MKWH | 1540.0188 | '' | 26.95%
| C) Hydro | MKWH | 61.2514 | '' | 1.072%
| D) Solar | MKWH | 0.33688 | '' | 0.005895%
| E) Coal | MKWH | 228.5432 | '' | 3.999%
| F) HVDC (Import from India) | MKWH | 339.7433 | '' | 5.945%
| G) A.C (Import from Tripura, India) | MKWH | 89.1322 | '' | 1.56%
16 | Maximun of the daily total Generation . | MKWH | 223.9926 | 27/05/18
17 | Monthly Load factor | % | 70.0932
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 14917.6026
| A) Gas | M.Taka | 2655.4331
| B) Liquid fuel | M.Taka | 12057.6776
| C) Coal | M.Taka | 204.4919
| D) HVDC (Import from India) | M.Taka | 1732.6907
| E) Tripura(Import from India) | M.Taka | 609.664
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 731.9929 | 27/05/18
| A) Gas | M.Taka | 94.2116 | 27/05/18
| B) Liquid fuel | M.Taka | 626.6328 | 27/05/18
| C) Coal | M.Taka | 11.2703 | 31/05/18
| D) HVDC (Import from India) | M.Taka | 62.2571 | 2018-11-05
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.8174
| B) Excluding Hydro & Solar | Taka/KWHR | 3.859
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/18 | 06:00
b) | Actual | FT (MSL) | 74.91 | 31/05/18 | 06:00
22 | Peak Genaration of May 2017 | MW | 9356 | 27/05/17 | 21:00
23 | Peak Demand of May 2017 | MW | 9356 | 27/05/17 | 21:00
24 | Maximum peak Generation recorded upto 31/05/18 | MW | 10958 | 28/05/18 | 21:00
25 | Maximum peak Demand recorded upto 31/05/18 | MW | 10958 | 28/05/18 | 21:00
26 | Maximum load shed recorded upto 31/05/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.