## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:April' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | April 2018 |  | March 2018 |  | April 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10137 | 24/04/18 | 10084 | 19/03/18 | 9212 | 18/04/17 | 10137 | 24/04/18
|  |  | 21:00 |  | 19:30 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 4376 | 18/04/18 | 1774 | 31/03/18 | 3695 | 22/04/17 | - | -
|  |  | 4:00 |  | 7:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10137 | 24/04/18 | 10084 | 19/03/18 | 9212 | 18/04/17 | 10137 | 24/04/18
|  |  | 21:00 |  | 19:30 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 8526.2 | 24/04/18 | 8476.9 | 22/03/2018 | 8081 | 13/04/2017 | 8743 | 07/6/17
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10137 | 24/04/18 | 10084 | 19/03/18 | 9212 | 18/04/17 | 10137 | 24/04/18
|  |  | 21:00 |  | 19:30 |  | 20:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 8951.2 |  | 9296.54 |  | 8081.68 |  | 9296.54 | March -18
7 | Average Generation (MW) at Day Peak | 7375.8533 |  | 7779.98 |  | 6906.82 |  | 7779.98 | March -18
8 | Maximum Power Import from India (MW) | 486 | 28/04/18 | 488 | 03/03/18 | 500 | 02/04/17 | 509 | 2017-07-03
|  |  | 14:00 |  | 10:00 |  | 14:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 176 | 05/04/18 | 174 | 27/03/18 | 164 | 13/04/17 | 176 | 05/04/18
|  |  | 18:30 |  | 18:30 |  | 21:00 |  | 18:30
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2819.5077 |  | 2868.69 |  | 2210.58
21 | Station Use of BPDB (MKWH) | 81.1889 |  | 94.27 |  | 120.39
22 | Net Generation of BPDB (MKWH) | 2738.3188 |  | 2774.42 |  | 2090.19
23 | Net Generation of IPP & RPCL (MKWH) | 1495.6209 |  | 1603.06 |  | 1334.95
24 | Net Generation of REB (MKWH) | 119.679 |  | 143.12 |  | 102.3
24 | Net Generation of Rental Power Plant (MKWH) | 631.8383 |  | 700.15 |  | 924.23
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4985.4569 |  | 5220.75 |  | 4451.67 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3261.1999 |  | 3545 |  | 3229.55 |  | 3545.44 | March-18
27 | Energy Generation by Diesel (MKWH) | 465.9897 |  | 298.94 |  | 263.19 |  | 465.99 | April-18
28 | Energy Generation by Furnace Oil (MKWH) | 1060.1386 |  | 1180.53 |  | 925.72 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 64.4935 |  | 53.53 |  | 75.66 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.36478 |  | 0.38 |  |  |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 214.4594 |  | 236.64 |  | 77.94 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 280.6211 |  | 423.51 |  | 411.13 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 73.2639 |  | 76.49 |  | 72.83 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:April' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10137 | 24/04/18 | 21:00
Generation Period
| Dhaka | MW | 3704
| Chittagong | MW | 1035
| Comilla | MW | 868
| Mymensingh | MW | 493
| Sylhet | MW | 385
a) | Total supply in East zone | MW | 6485
| Khulna | MW | 1197
| Barisal | MW | 256
| Rajshahi | MW | 1070
| Rangpur | MW | 618
b) | Total supply in West zone | MW | 3141
c) | Total supply in both zone ( a+b) | MW | 9626
Ref: | 27.21.2604.603.16.084.18.80 | Date: 22 /05/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1160 | 08/04/18 | 20:00
| b) Ishurdi end | MW | 100 | 05/04/18 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 300 | 05/04/18 | 17:00
| b) Ishurdi end | MW | 460 | 08/04/18 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 7.5735 | 09/04/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 6.8916 | 09/04/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 137.4304
| b) Ishurdi end | MKWH | 1.5055
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 1.4603
| b) Ishurdi end | MKWH | 134.0383
23 | Transmission loss of EWI/ NO-1 | % | 2.46
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 610 | 08/04/18 | 20:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 600 | 08/04/18 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 11.07 | 04/04/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 10.73 | 04/04/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 241.366
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 237.774
30 | Transmission loss of EWI /NO-2 | % | 1.488
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV Transformer-T-1 | 2018-04-30 08:43 | 2018-04-30 15:59 | 7:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 7:16 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-TR-2 | 2018-04-11 20:14 | 2018-04-11 22:09 | 1:55 | T | Tripped showing master protection relay | 0 | 0 | No interruption
| 230/132 kV Transformer-TR-3 | 2018-04-11 17:59 | 2018-04-11 21:18 | 3:19 | T |  | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-3 | 2018-04-19 01:44 | 2018-04-19 08:14 | 6:30 | T | Tripped showing master protection relay | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-3 | 2018-04-20 19:22 | 2018-04-20 23:08 | 3:46 | T | Tripped showing master protection relay | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T1 | 2018-04-21 17:03 | 2018-04-21 17:41 | 0:38 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Ghorashal | 230 kV bus-2 | 2018-04-21 17:03 | 2018-04-21 17:45 | 0:42 | T | Due to failure of CB | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-3 | 2018-04-25 22:46 | 2018-04-25 23:18 | 0:32 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
|  |  | Total : | 17:22 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Hathazari | 132/33 kV Transformer-T1 | 2018-04-11 08:18 | 2018-04-11 11:20 | 3:02 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T2 | 2018-04-13 09:25 | 2018-04-13 11:28 | 2:03 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T-2 | 2018-04-17 08:13 | 2018-04-17 09:21 | 1:08 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khagrachori | 132/33 kV Transformer-T1 | 2018-04-19 18:02 | 2018-04-19 19:31 | 1:29 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 7:42 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Fenchuganj | 132/33 kV Transformer-T-2 | 2018-04-13 02:17 | 2018-04-14 11:01 | 32:44 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 32:44 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gallamari | 132/33 kV Transformers-T-1 & T2 | 2018-04-07 22:13 | 2018-04-07 22:31 | 0:18 | T | Tripped showing dist. E/F relay | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformers-T-1 & T2 | 2018-04-12 01:25 | 2018-04-12 01:36 | 0:11 | T | Tripped showing O/C relay | 12 | 2.2 | Power interruption
Madaripur | 132/33 kV Transformers-T-1 | 2018-04-12 00:26 | 2018-04-12 02:04 | 1:38 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformers-T-1 | 2018-04-17 11:18 | 2018-04-17 13:40 | 2:22 | E/O | Due toOil leakage | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T-1 | 2018-04-18 01:27 | 2018-04-18 05:43 | 4:16 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T-1 | 2018-04-18 02:01 | 2018-04-18 02:43 | 0:42 | T | Tripped showing O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T-2 | 2018-04-18 02:01 | 2018-04-18 02:47 | 0:46 | T |  | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformers-T-2 | 2018-04-18 14:22 | 2018-04-18 14:26 | 0:04 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T-1 | 2018-04-18 20:26 | 2018-04-18 21:10 | 0:44 | E/O | Due to red hot maintenance | 40 | 29.3333 | Power interruption
Bottail | 132/33 kV Transformer-T-2 | 2018-04-19 00:43 | 2018-04-19 01:00 | 0:17 | T | Tripped showing O/C relay | 25 | 7.0833 | Power interruption
Gallamari | 132/33 kV Transformers-T1 | 2018-04-23 08:26 | 2018-04-23 08:31 | 0:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-04-23 08:26 | 2018-04-23 08:34 | 0:08 | T |  | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T-1 | 2018-04-23 18:56 | 2018-04-23 19:10 | 0:14 | T | Tripped showing O/C relay | 60 | 14 | Power interruption
|  |  | Total : | 0:29 |  | Unserved Energy: |  | 52.6167
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara | 230/132 kV Transformer-TR-1 | 2018-04-07 20:47 | 2018-04-07 23:19 | 2:32 | T | Tripped showing differential relay | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T2 | 2018-04-07 22:21 | 2018-04-07 22:27 | 0:06 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bheramara | 230/132 kV Transformer-TR-1 | 2018-04-11 19:34 | 2018-04-11 21:09 | 1:35 | T | Tripped showing differential relay | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2018-04-17 05:52 | 2018-04-17 05:55 | 0:03 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T1 | 2018-04-18 15:48 | 2018-04-18 15:51 | 0:03 | T | Tripped showing E/F relay | 55 | 2.75 | Power interruption 07:36 to 07:45
Bottail | 132/33 kV Transformer-T2 | 2018-04-24 06:29 | 2018-04-24 07:10 | 0:41 | E/O | Due to red hot maintenance | 30 | 20.5 | Power interruption 07:36 to 07:45
Ishurdi | 132/33 kV Transformer-T1 | 2018-04-24 09:28 | 2018-04-24 10:29 | 1:01 | E/O | Due to red hot maintenance | 5 | 5.0833 | Power interruption 07:36 to 07:45
Bheramara | 230/132 kV Transformers-TR-1 | 2018-04-30 00:04 | 2018-04-30 01:07 | 1:03 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| 230/132 kV Transformers-TR-2 | 2018-04-30 00:04 | 2018-04-30 13:53 | 13:49 | T |  | 0 | 0 | No interruption
|  |  | Total : | 20:53 |  | Unserved Energy: |  | 28.3333
Bogra Grid Circle:
Amnura | 132/33 kV Transformers-T-1 | 2018-04-01 21:13 | 2018-04-01 21:23 | 0:10 | T | Tripped showing O/V relay | 10 | 2 | Power interruption 07:36 to 07:45
Baghabari | 230/132 kV Transformer-TR-2 | 2018-04-11 19:35 | 2018-04-17 17:40 | 142:05 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2018-04-17 11:36 | 2018-04-17 13:27 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2018-04-20 07:03 | 2018-04-20 08:11 | 1:08 | E/O | Due to red hot maintenance | 13 | 14.7333 | Power interruption 07:36 to 07:45
Bogra | 132/33 kV Transformer-T1 | 2018-04-20 12:01 | 2018-04-20 16:52 | 4:51 | E/O | Due toOil leakage | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-TR-2 | 2018-04-21 06:25 | 2018-04-21 11:29 | 5:04 | T | Tripped showing differential relay | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-TR-2 | 2018-04-21 07:30 | 2018-04-21 09:58 | 2:28 | T | Tripped showing Bus protection & Lockout relay | 0 | 0 | No interruption
| 230/132 kV Transformer-TR-3 | 2018-04-21 07:30 | 2018-04-21 10:03 | 2:33 | T |  | 0 | 0 | No interruption
| 230/132 kV Transformer-TR-6 | 2018-04-21 07:30 | 2018-04-21 10:04 | 2:34 | T |  | 0 | 0 | No interruption
| 230/132 kV Transformer-TR-6 | 2018-04-21 07:30 | 2018-04-21 10:25 | 2:55 | T |  | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-TR-1 | 2018-04-25 13:34 | 2018-04-25 13:43 | 0:09 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-1 | 2018-04-29 06:06 | 2018-04-29 06:22 | 0:16 | T | Tripped showing main protection relay | 0 | 0 | No interruption
|  |  | Total : | 166:04 |  | Unserved Energy: |  | 16.7333
Others :
Ghorashal | 230/132 kV Transformer-AT1 | 2018-04-21 17:03 | 2018-04-23 21:32 | 52:29 | E/O | Due to air pressure drop | 0 | 0 | No interruption
|  |  | Total : | 52:29 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 304:59 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC24
Page: 1/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Tangail 132 kV line-1 | 2018-04-11 23:53 | 2018-04-12 00:07 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Kabirpur-Tangail 132 kV line-2 | 2018-04-11 23:53 | 2018-04-12 00:58 | 1:05 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-04-12 08:04 | 2018-04-12 08:19 | 0:15 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2018-04-12 20:58 | 2018-04-13 10:14 | 13:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mirpur | Mirpur-Aminabazar 132 kV line | 2018-04-13 06:20 | 2018-04-13 10:10 | 3:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tangail | Tangail-Kaliakori 132 kV line-1 | 2018-04-17 12:12 | 2018-04-17 12:36 | 0:24 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-04-17 23:35 | 2018-04-17 23:57 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 & 2 | 2018-04-21 09:57 | 2018-04-21 10:21 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Mirpur 132 kV line | 2018-04-21 10:00 | 2018-04-21 18:16 | 8:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2018-04-21 09:58 | 2018-04-21 10:59 | 1:01 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
| Joydevpur-Ghorashal 132 kV line-2 | 2018-04-21 09:58 | 2018-04-21 16:01 | 6:03 | T |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-04-25 19:10 | 2018-04-25 19:51 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-1 | 2018-04-27 01:10 | 2018-04-27 02:34 | 1:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 & 2 | 2018-04-28 08:50 | 2018-04-28 08:57 | 0:07 | T | Tripped showing main protcetion relay | 235 | 27.4167 | Power interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2018-04-29 07:55 | 2018-04-29 09:15 | 1:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tangail-Kaliakoir 132 kV line-2 | 2018-04-29 07:55 | 2018-04-29 09:16 | 1:21 | T |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakor 132 kV line-1 | 2018-04-29 08:30 | 2018-04-29 20:38 | 12:08 | T | Tripped showing general trip | 0 | 0 | No interruption
| Aminbazar-Kaliakor 132 kV line-2 | 2018-04-29 08:30 | 2018-04-29 09:57 | 1:27 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-04-29 08:01 | 2018-04-29 09:18 | 1:17 | T | Tripped showing CSW,CAT,CD & CE singnal | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2018-04-29 08:02 | 2018-04-29 09:06 | 1:04 | T | Tripped showing E/F.relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2018-04-29 08:23 | 2018-04-29 17:10 | 8:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2018-04-29 08:23 | 2018-04-29 10:11 | 1:48 | T |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 & 2 | 2018-04-29 08:30 | 2018-04-29 09:32 | 1:02 | T | Tripped showing dist.3-phase relay | 0 | 0 | No interruption
Kadda | Kadda-Joydevpur 132 kV line-1 & 2 | 2018-04-30 00:28 | 2018-04-30 00:45 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2018-04-30 11:40 | 2018-04-30 12:38 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 68:51 |  | Unserved Energy: |  | 27.4167
Dhaka (South) Grid Circle :
Madanganj | Madanganj-Sitalakhya 132 kV line | 2018-04-01 10:18 | 2018-04-01 13:08 | 2:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bashundahara 132 kV line-1 | 2018-04-05 18:29 | 2018-04-05 19:13 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-04-11 19:08 | 2018-04-11 19:34 | 0:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hahsnabad 230 kV line-2 | 2018-04-12 22:45 | 2018-04-13 02:58 | 4:13 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-04-14 18:29 | 2018-04-15 15:05 | 20:36 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Madanganj | Madanganj-Sitalakya 132 kV line | 2018-04-17 12:38 | 2018-04-17 13:07 | 0:29 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2018-04-17 23:35 | 2018-04-18 00:26 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-04-17 23:56 | 2018-04-18 00:28 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-2 | 2018-04-19 08:50 | 2018-04-19 10:14 | 1:24 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2018-04-19 20:05 | 2018-04-19 20:33 | 0:28 | T | Tripped showing PTAW,PD3 signal | 0 | 0 | No interruption
Page: 2/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-04-20 19:12 | 2018-04-20 19:42 | 0:30 | T | Tripped showing dist. relay | 10 | 5 | Power interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 | 2018-04-20 19:14 | 2018-04-20 19:51 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2018-04-21 17:03 | 2018-04-21 17:30 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2018-04-21 17:03 | 2018-04-21 19:07 | 2:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-2 | 2018-04-21 17:03 | 2018-04-21 17:58 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2018-04-22 18:15 | 2018-04-22 18:26 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundahara 132 kV line-1 | 2018-04-22 18:17 | 2018-04-22 18:44 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-4 | 2018-04-22 18:13 | 2018-04-22 18:54 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-2 | 2018-04-22 18:15 | 2018-04-22 18:52 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2018-04-23 19:02 | 2018-04-23 19:07 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bashundahara | Bashundahara -Rampura 132 kV line-1 | 2018-04-24 08:36 | 2018-04-24 09:05 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundahara 132 kV line-1 | 2018-04-25 04:57 | 2018-04-25 05:13 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bashundahara | Bashundahara -Tongi 132 kV line-1 | 2018-04-25 19:19 | 2018-04-25 20:30 | 1:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2018-04-25 20:03 | 2018-04-25 20:08 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-2 | 2018-04-25 20:03 | 2018-04-25 20:09 | 0:06 | T |  | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorasal 132 kV line-2 | 2018-04-25 19:50 | 2018-04-25 20:39 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-4 | 2018-04-25 19:23 | 2018-04-25 21:02 | 1:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-04-27 01:26 | 2018-04-27 02:26 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line-1 | 2018-04-27 01:29 | 2018-04-27 02:09 | 0:40 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2018-04-29 02:48 | 2018-04-29 11:25 | 8:37 | E/O | Due to bursting of L/A | 50 | 10.8333 | Power interruption 02:48 to 3:01
Haripur | Haripur-Shyampur 132 kV line | 2018-04-29 09:02 | 2018-04-29 09:08 | 0:06 | T | Tripped showing dist. relay | 35 | 3.5 | Power interruption
|  |  | Total : | 54:05 |  | Unserved Energy: |  | 19.3333
Chittagong Grid Circle :
Madunaghat | Meghanaghat-Chandraghona 132 kV line-2 | 2018-04-05 20:46 | 2018-04-05 20:58 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 12 kV line | 2018-04-12 10:55 | 2018-04-12 12:22 | 1:27 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 12 kV line | 2018-04-13 06:01 | 2018-04-13 07:54 | 1:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 12 kV line-1 | 2018-04-13 10:08 | 2018-04-13 10:14 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2018-04-13 17:40 | 2018-04-13 20:38 | 2:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Khgachori 132 kV line-2 | 2018-04-18 08:55 | 2018-04-18 13:06 | 4:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaptai | Kaptai-Hathazari 132 kV line-1 | 2018-04-30 14:06 | 2018-04-30 14:29 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 11:10 |  | Unserved Energy: |  | 0
Page: 3/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Fenchuganj | Fenchuganj-Sylhet S/S 132 kV line | 2018-04-03 14:56 | 2018-04-03 17:57 | 3:01 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-04-03 02:15 | 2018-04-03 07:56 | 5:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal -Fenchuganj 132 kV line-1 | 2018-04-05 14:24 | 2018-04-05 15:29 | 1:05 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Sreemongal -Fenchuganj 132 kV line-2 | 2018-04-05 14:24 | 2018-04-05 17:08 | 2:44 | T |  | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2018-04-05 14:24 | 2018-04-05 15:25 | 1:01 | T | Tripped showing O/C & E/F relay | 20 | 20.3333 | Power interruption 14:24 to 15:25
| Sreemongal-Shahjibazar 132 kV line-2 | 2018-04-05 14:24 | 2018-04-05 16:21 | 1:57 | T |  | 0 | 0
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-04-05 19:18 | 2018-04-05 20:09 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-04-06 08:11 | 2018-04-06 08:17 | 0:06 | T | Tripped showing dist. relay | 160 | 16 | Power interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2018-04-06 10:28 | 2018-04-06 14:05 | 3:37 | T | Tripped showing E/F realy | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-BSRM 230 kV line-1 | 2018-04-07 12:14 | 2018-04-07 12:24 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Comiila(N)-BSRM 230 kV line-2 | 2018-04-07 12:14 | 2018-04-07 12:18 | 0:04 | T |  | 0 | 0 | No interruption
Feni | Feni-Comilla(N) 132 kV line-1 | 2018-04-12 23:19 | 2018-04-13 10:37 | 11:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-04-17 13:40 | 2018-04-17 13:51 | 0:11 | T | Tripped showing dist. relay | 105 | 19.25 | Power interruption
Comiila(N) | Comiila(N)-Feni 132 kV line-1 | 2018-04-20 14:59 | 2018-04-20 15:23 | 0:24 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line-2 | 2018-04-20 15:01 | 2018-04-20 15:08 | 0:07 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Comiila(N) 132 kV line-2 | 2018-04-24 11:03 | 2018-04-24 11:23 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Chandpur 132 kV line-2 | 2018-04-24 14:40 | 2018-04-24 15:02 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2018-04-25 20:02 | 2018-04-25 20:24 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comiila(N) 230 kV line-1 | 2018-04-25 20:33 | 2018-04-25 22:36 | 2:03 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 & 2 | 2018-04-28 08:50 | 2018-04-28 09:12 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-04-28 22:33 | 2018-04-28 23:22 | 0:49 | T | Tripped showing dist.(C-phase) relay | 20 | 16.3333 | Power interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 & 2 | 2018-04-28 22:40 | 2018-04-28 23:03 | 0:23 | T | Tripped showing dist. relay | 350 | 134.1667 | Power interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-1 | 2018-04-28 23:09 | 2018-04-29 00:37 | 1:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2018-04-29 00:29 | 2018-04-29 00:51 | 0:22 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal P/S 132 kV line-1 & 2 | 2018-04-29 08:41 | 2018-04-29 09:22 | 0:41 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV line-1 & 2 | 2018-04-29 08:41 | 2018-04-29 09:39 | 0:58 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-1 | 2018-04-29 08:41 | 2018-04-29 09:31 | 0:50 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Fenchuganj S/S-Fenchuganj P/S 132 kV line-3 | 2018-04-29 08:41 | 2018-04-29 09:34 | 0:53 | T |  | 0 | 0 | No interruption
Feni | Feni-Comilla(N) 132 kV line-1 | 2018-04-30 12:19 | 2018-04-30 12:27 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-04-30 12:25 | 2018-04-30 12:32 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comilla(N) 230 kV line-1 | 2018-04-30 12:29 | 2018-04-30 13:25 | 0:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comiila(S) | Comiila(S)-Tripura 132 kV line-2 | 2018-04-30 12:51 | 2018-04-30 13:28 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-2 | 2018-04-30 13:53 | 2018-04-30 14:26 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 44:31 |  | Unserved Energy: |  | 206.0833
Page: 4/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Noapara | Noapara-Khulna© 132 kV line-1 | 2018-04-05 14:20 | 2018-04-05 14:52 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line-1 | 2018-04-05 14:20 | 2018-04-05 14:49 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna© | Khulna©-Goalpara 132 kV line-1 | 2018-04-05 14:20 | 2018-04-05 18:07 | 3:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna© | Khulna©-Noapara 132 kV line-1 | 2018-04-07 12:45 | 2018-04-07 13:05 | 0:20 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| Khulna©-Noapara 132 kV line-2 | 2018-04-07 12:45 | 2018-04-07 13:01 | 0:16 | T |  | 285 | 76 | Power interruption
Barisal | Barisal-Madaripur 132 kV line-1 | 2018-04-07 22:48 | 2018-04-07 23:48 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2018-04-12 00:37 | 2018-04-12 01:43 | 1:06 | T | Tripped showing dist. relay | 40 | 44 | Power interruption
Gopalganj | Gopalganj-Madaripur 132 kV line | 2018-04-14 20:46 | 2018-04-14 21:26 | 0:40 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-04-14 23:50 | 2018-04-15 06:40 | 6:50 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur P/S | Faridpur P/S -Faridpur S/S 132 kV line | 2018-04-17 00:35 | 2018-04-17 13:14 | 12:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-2 | 2018-04-17 00:58 | 2018-04-17 16:21 | 15:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Barisal-Patuakhali 132 kV line | 2018-04-17 13:13 | 2018-04-17 17:41 | 4:28 | T | Tripped showing dist. & E/F relay | 23 | 102.7333 | Power interruption
Barisal(N) | Barisal-Madaripur 132 kV line-1 | 2018-04-17 14:16 | 2018-04-17 16:44 | 2:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2018-04-17 14:21 | 2018-04-17 14:50 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-04-18 10:56 | 2018-04-18 12:19 | 1:23 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulna© | Khulna©-Goalpara 132 kV line-2 | 2018-04-27 23:58 | 2018-04-28 01:06 | 1:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-04-29 14:31 | 2018-04-29 18:52 | 4:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  |  | 57:19 |  | Unserved Energy: |  | 222.7333
HVDC Grid Circle :
Jhenidah | Jhenidah -Bottail 132 kV line-1 | 2018-04-07 20:48 | 2018-04-07 22:35 | 1:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
HVDC | HVDC-Bheramara 230 kV line-2 | 2018-04-14 14:03 | 2018-04-14 14:47 | 0:44 | T | Tripped showing directional relay | 0 | 0 | No interruption
| HVDC -Ishurdi 230 kV line-2 | 2018-04-14 14:03 | 2018-04-14 14:15 | 0:12 | T | Tripped showing REL 316 DTT2 signal | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2018-04-16 07:59 | 2018-04-17 00:28 | 16:29 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 230 kV line-1 | 2018-04-19 19:20 | 2018-04-19 20:53 | 1:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2018-04-21 10:03 | 2018-04-21 10:56 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2018-04-28 08:50 | 2018-04-28 08:59 | 0:09 | T | Tripped showing L96, DST2 signal | 0 | 0 | No interruption
Jhenidah | Jhenidah-Chuadanga 132 kV line | 2018-04-30 09:47 | 2018-04-30 09:52 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 21:52 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-04-01 10:57 | 2018-04-01 11:15 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogra | Bogra-Natore 132 kV line-1 | 2018-04-06 00:54 | 2018-04-06 02:56 | 2:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV lkine-1 | 2018-04-08 12:10 | 2018-04-08 12:19 | 0:09 | T | Tripped showing dist. relay | 160 | 24 | Power interruption
| Saidpur-Purbasadipur 132 kV lkine-2 | 2018-04-08 12:10 | 2018-04-08 12:32 | 0:22 | T | Tripped showing dist. relay
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2018-04-11 12:05 | 2018-04-11 14:40 | 2:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rajsahai | Rajsahai-Natore 132 kV line-1 | 2018-04-17 22:32 | 2018-04-17 22:40 | 0:08 | T | Tripped showing dist. relay | 90 | 12 | Power interruption 22:32 to 22:40
| Rajsahai-Natore 132 kV line-2 | 2018-04-17 22:32 | 2018-04-17 22:48 | 0:16 | T
Barapukuria | Barapukuria-Rangpur 132 kV line-1 | 2018-04-19 20:19 | 2018-04-19 20:49 | 0:30 | T | Tripped showing E/F. relay | 245 | 118.4167 | Power interruption 20:19 to 20:48
| Barapukuria-Rangpur 132 kV line-2 | 2018-04-19 20:19 | 2018-04-19 20:48 | 0:29 | T
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2018-04-19 20:19 | 2018-04-19 20:59 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Palashbari-Rangpur 132 kV line-2 | 2018-04-19 20:19 | 2018-04-19 20:55 | 0:36 | T |  | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-1 | 2018-04-20 06:59 | 2018-04-20 07:47 | 0:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bogra-Naogaon 132 kV line-2 | 2018-04-20 06:59 | 2018-04-20 07:56 | 0:57 | T |  | 0 | 0 | No interruption
Naogaon | Naogaon-Niamatpur 132 kV line | 2018-04-26 13:13 | 2018-04-26 13:27 | 0:14 | T | Tripped showing dist. relay | 12 | 2.8 | Power interruption
Palashbari | Palashbari-Rangpur 132 kV line-2 | 2018-04-29 06:06 | 2018-04-29 06:19 | 0:13 | T | Tripped showing dist. relay | 105 | 22.75 | Power interruption
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2018-04-29 06:06 | 2018-04-29 10:01 | 3:55 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
|  |  | Total : | 14:12 |  | Unserved Energy: |  | 179.9667
Others :
Maniknagar | Maniknagar-Matuail 132 kV line | 2018-04-11 19:01 | 2018-04-11 21:17 | 2:16 | T | Tripped showing pilot wire protection relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matuial 132 kV line | 2018-04-14 17:28 | 2018-04-14 18:38 | 1:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matuial 132 kV line | 2018-04-20 19:13 | 2018-04-20 20:15 | 1:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 4:28 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 276:28 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC25
Page: 1/1 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | 132/33 kV Transformer-T-1 | 2018-04-10 10:27 | 2018-04-10 16:37 | 6:10 | S/O | Due to C/M work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T2 | 2018-04-20 08:10 | 2018-04-20 21:02 | 12:52 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2018-04-22 09:33 | 2018-04-22 11:16 | 1:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-TR-1 | 2018-04-28 10:36 | 2018-04-28 13:10 | 2:34 | S/O | Due to Oil shortage | 0 | 0 | No interruption
|  |  | Total : | 23:19 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-T2 | 2018-04-06 09:11 | 2018-04-06 16:47 | 7:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 132 kV bus section -3 | 2018-04-07 08:04 | 2018-04-07 17:41 | 9:37 | S/O | Due to project work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T1 | 2018-04-13 08:54 | 2018-04-13 14:16 | 5:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T3 | 2018-04-23 10:45 | 2018-04-23 16:50 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T-1 | 2018-04-29 06:07 | 2018-04-29 08:14 | 2:07 | S/O | Due to maintenance work | 30 | 63.5 | Power interruption
|  |  | Total : | 30:47 |  | Unserved Energy: |  | 63.5
Chittagong Grid Circle :
Sikalbaha | 132/33 kV Transformer-T3 | 2018-04-06 07:51 | 2018-04-06 09:30 | 1:39 | S/O | Due to D/W work | 18 | 29.7 | Power interruption
Madunaghat | 132/33 kV Transformer-T-2 | 2018-04-12 07:50 | 2018-04-12 09:38 | 1:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT-3 | 2018-04-21 10:30 | 2018-04-21 14:10 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 37:54 |  | Unserved Energy: |  | 29.7
Comilla Grid Circle :
Daudkandi | 132 kV bus | 2018-04-06 06:35 | 2018-04-06 10:12 | 3:37 | S/O | Due to D/W work | 40 | 144.6667 | Power interruption
B.baria | 132/33 kV Transformer-T1 | 2018-04-15 19:16 | 2018-04-15 20:30 | 1:14 | S/O | Due to removing nest | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-TR-1 | 2018-04-28 11:37 | 2018-04-28 15:10 | 3:33 | S/O | Due to Oil shortage | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2018-04-30 14:07 | 2018-04-30 14:15 | 0:08 | S/O | Due to maintenance work | 7 | 0.93333 | Power interruption
|  |  | Total | 8:32 |  | Unserved Energy : |  | 145.6
Khulna Grid Circle :
Noapara | 132 kV bus | 2018-04-03 06:10 | 2018-04-03 16:15 | 10:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 & T2 | 2018-04-06 06:21 | 2018-04-06 08:36 | 2:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T5 | 2018-04-17 10:15 | 2018-04-20 14:35 | 76:20 | S/O | Due to replacement work | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-TR-1 | 2018-04-22 10:16 | 2018-04-22 12:49 | 2:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barisal | 230/132 kV Transformer-TR-2 | 2018-04-25 08:20 | 2018-04-25 11:59 | 3:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 94:52 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
Bottail | 132 kV Bus-1 & 2 | 2018-04-06 07:09 | 2018-04-06 12:17 | 5:08 | S/O | Due to D/W work | 45 | 231 | Power interruption
|  |  | Total : | 5:08 |  | Unserved Energy : |  | 231
Bogra Grid Circle:
Amnura | 132/33 kV Transformer-T1 | 2018-04-07 10:10 | 2018-04-07 14:13 | 4:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramgpur | 132 kV bus-B | 2018-04-11 09:45 | 2018-04-11 10:50 | 1:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T5 | 2018-04-18 07:10 | 2018-04-18 09:05 | 1:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T3 | 2018-04-19 08:22 | 2018-04-19 14:48 | 6:26 | S/O | Due to project work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T3 | 2018-04-20 06:14 | 2018-04-20 12:49 | 6:35 | S/O | Due to project work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2018-04-20 06:04 | 2018-04-20 12:52 | 6:48 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T2 | 2018-04-21 13:48 | 2018-04-21 15:05 | 1:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T2 | 2018-04-21 13:48 | 2018-04-21 15:05 | 1:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siragjanj | 132/33 kV Transformer-T1 | 2018-04-21 06:30 | 2018-04-21 16:22 | 9:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogra | 230/132 kV Transformer-TR2 | 2018-04-23 08:42 | 2018-04-23 20:01 | 11:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T2 | 2018-04-24 12:30 | 2018-04-27 01:47 | 61:17 | S/O | Due to replecment work | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T4 | 2018-04-25 10:16 | 2018-04-25 11:28 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-TR-1 | 2018-04-27 07:35 | 2018-04-27 14:35 | 7:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T2 | 2018-04-28 08:07 | 2018-04-29 15:36 | 31:29 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 151:35 |  | Unserved Energy : |  | 0
Others :
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 352:07 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | Mirpur-Uttara 132 kV line-1 | 2018-04-10 09:55 | 2018-04-10 11:35 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamari 132 kV line-2 | 2018-04-10 10:50 | 2018-04-10 18:00 | 7:10 | S/O | Due to project work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2018-04-13 06:06 | 2018-04-13 08:02 | 1:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamari 132 kV line-1 & 2 | 2018-04-19 11:04 | 2018-04-19 18:07 | 7:03 | S/O | Due to project work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-1 | 2018-04-20 07:23 | 2018-04-20 18:32 | 11:09 | S/O | Due to project work | 0 | 0 | No interruption
| Kaliakoir-Tongi 230 kV line-2 | 2018-04-20 07:24 | 2018-04-20 18:33 | 11:09 | S/O | Due to project work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV line-2 | 2018-04-20 07:37 | 2018-04-20 18:04 | 10:27 | S/O | Due to project work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyna 400 kV line-2 | 2018-04-24 11:19 | 2018-04-24 18:30 | 7:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2018-04-26 09:22 | 2018-04-26 11:07 | 1:45 | S/O | Due to relay changing | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2018-04-29 08:30 | 2018-04-29 13:58 | 5:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2018-04-29 13:45 | 2018-04-29 13:58 | 0:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 65:11 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj P/S 132 kV line | 2018-04-04 10:12 | 2018-04-04 15:06 | 4:54 | S/O | Due to painting work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2018-04-05 08:28 | 2018-04-05 10:53 | 2:25 | S/O | Due to DS temp.high | 0 | 0 | No interruption
| Meghnaghat-Hasnabad 230 kV line-2 | 2018-04-06 09:17 | 2018-04-06 17:53 | 8:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2018-04-11 10:10 | 2018-04-11 11:14 | 1:04 | S/O | Due to project work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-2 | 2018-04-11 11:17 | 2018-04-11 12:03 | 0:46 | S/O | Due to project work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-3 | 2018-04-11 12:04 | 2018-04-11 12:47 | 0:43 | S/O | Due to project work | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-4 | 2018-04-11 12:48 | 2018-04-11 13:18 | 0:30 | S/O | Due to project work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV line-1 | 2018-04-11 13:25 | 2018-04-11 13:42 | 0:17 | S/O | Due to project work | 0 | 0 | No interruption
| Bhulta-Haripur 230 kV line-2 | 2018-04-11 13:45 | 2018-04-11 14:04 | 0:19 | S/O |  | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 20 kV line-1 & 2 | 2018-04-13 05:05 | 2018-04-13 18:18 | 13:13 | S/O | Due to project work | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV line-1 | 2018-04-13 08:22 | 2018-04-13 09:56 | 1:34 | S/O | Due to project work | 0 | 0 | No interruption
| Bhulta-Ghorashal 230 kV line-2 | 2018-04-13 09:57 | 2018-04-13 10:50 | 0:53 | S/O |  | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Haripur 132 kV line-2 | 2018-04-13 07:39 | 2018-04-13 20:20 | 12:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-2 | 2018-04-14 06:36 | 2018-04-14 17:07 | 10:31 | S/O | Due to project work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj Desh 132 kV line | 2018-04-14 06:59 | 2018-04-14 17:08 | 10:09 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2018-04-16 06:25 | 2018-04-16 08:29 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-04-16 08:31 | 2018-04-18 18:56 | 58:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2018-04-16 10:47 | 2018-04-16 15:14 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2018-04-18 07:05 | 2018-04-18 08:05 | 1:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-2 | 2018-04-19 14:08 | 2018-04-19 14:33 | 0:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2018-04-20 06:33 | 2018-04-20 18:40 | 12:07 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2018-04-20 06:11 | 2018-04-20 16:05 | 9:54 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat -Hasnabad230 kV line-2 | 2018-04-21 07:18 | 2018-04-23 18:05 | 58:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-1 | 2018-04-22 06:03 | 2018-04-22 14:47 | 8:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Maniknagar-Siddhirganj-Ullon 132 kV line-2 | 2018-04-23 08:38 | 2018-04-23 13:29 | 4:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Siddhirganj P/S 132 kV line | 2018-04-24 06:59 | 2018-04-24 17:24 | 10:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Ullon-Maniknagar 132 kV line | 2018-04-24 08:20 | 2018-04-24 14:39 | 6:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj Desh 132 kV line | 2018-04-25 06:56 | 2018-04-25 18:38 | 11:42 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-4 | 2018-04-28 08:33 | 2018-04-28 15:32 | 6:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 264:44 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2018-04-01 09:07 | 2018-04-01 09:55 | 0:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line | 2018-04-13 08:40 | 2018-04-13 12:34 | 3:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hathazari | Hathazari-Barauila 132 kV line-1 | 2018-04-17 11:10 | 2018-04-17 11:59 | 0:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Khgachori 132 kV line-1 | 2018-04-17 10:23 | 2018-04-17 13:44 | 3:21 | S/O | Due to maintenance work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Khgachori 132 kV line-2 | 2018-04-18 08:55 | 2018-04-18 13:06 | 4:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Dohazari | Dohazari-CoX'sbazar 132 kV line-1 | 2018-04-28 07:58 | 2018-04-28 15:50 | 7:52 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 20:55 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Comilla(N) | Comilla(N)-BSRM 230 kV line-2 | 2018-04-06 09:05 | 2018-04-06 14:38 | 5:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line | 2018-04-06 10:39 | 2018-04-06 13:18 | 2:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-04-08 09:26 | 2018-04-08 18:50 | 9:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-04-19 05:32 | 2018-04-19 17:27 | 11:55 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2018-04-19 05:33 | 2018-04-19 17:39 | 12:06 | S/O |  | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 | 2018-04-19 05:40 | 2018-04-19 17:31 | 11:51 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-2 | 2018-04-19 05:55 | 2018-04-19 17:33 | 11:38 | S/O |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 & 2 | 2018-04-21 05:12 | 2018-04-21 15:58 | 10:46 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 & 2 | 2018-04-21 05:35 | 2018-04-21 16:21 | 10:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-1 & 2 | 2018-04-23 05:05 | 2018-04-23 16:15 | 11:10 | S/O | Due to project work | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line-1 & 2 | 2018-04-25 10:02 | 2018-04-25 18:50 | 8:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2018-04-27 08:25 | 2018-04-27 18:24 | 9:59 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 111:02 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-04-16 11:27 | 2018-04-16 11:35 | 0:08 | S/O | Due to maintenance work
Barisal | Barisal-Bhandaria 132 kV line | 2018-04-20 10:12 | 2018-04-20 10:58 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-1 | 2018-04-24 09:52 | 2018-04-24 12:31 | 2:39 | S/O | Due to tree trimming | 0 | 0 | No interruption
|  |  | Total : | 3:33 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Bottail 132 kV line-1 | 2018-04-07 08:16 | 2018-04-07 17:54 | 9:38 | S/O | Due to project work | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2018-04-11 09:47 | 2018-04-11 12:22 | 2:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 12:13 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-04-02 15:49 | 2018-04-02 17:28 | 1:39 | S/O | Due to project work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-1 | 2018-04-10 10:21 | 2018-04-10 12:06 | 1:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-04-21 08:10 | 2018-04-21 17:53 | 9:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-04-21 07:19 | 2018-04-21 16:56 | 9:37 | S/O | Due to D/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line | 2018-04-24 07:17 | 2018-04-24 16:50 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-04-26 07:30 | 2018-04-26 17:03 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-04-27 08:20 | 2018-04-27 16:38 | 8:18 | S/O | Due to project work | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-04-28 08:14 | 2018-04-28 16:58 | 8:44 | S/O | Due to project work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2018-04-29 08:30 | 2018-04-29 13:40 | 5:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-04-30 15:05 | 2018-04-30 16:54 | 1:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 65:51 |  | Unserved Energy: |  | 0
Others :
Manikinagar | Manikinagar-Baghabhaban 132 kV line-2 | 2018-04-20 09:43 | 2018-04-20 17:57 | 8:14 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 8:14 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 494:46 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April' 2018
| Area | Previous Month (March 2018) |  |  |  | Current Month (April 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 16 | 2 | 13 | 31 | 24 | 2 | 15 | 41
2 | Dhaka (South) Grid Circle. | 13 | 6 | 42 | 61 | 33 | 5 | 34 | 72
3 | Chittagong Grid Circle. | 9 | 3 | 12 | 24 | 5 | 6 | 9 | 20
4 | Comilla Grid Circle. | 24 | - | 12 | 36 | 32 | - | 16 | 48
5 | Khulna Grid Circle. | 11 | 1 | 16 | 28 | 27 | 3 | 8 | 38
6 | Bheramara HVDC Grid Circle | 7 |  | 8 | 15 | 14 | 2 | 3 | 19
7 | Bogra Grid Circle. | 3 | 4 | 13 | 20 | 24 | 5 | 24 | 53
8 | Others | 2 | - | 2 | 4 | 3 | 1 | 1 | 5
9 | Total | 85 | 16 | 118 | 219 | 162 | 24 | 110 | 296
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April' 2018
| Area | Previous Month (March 2018) |  |  |  | Current Month (April 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 161.66 | - | 1145.33 | 1306.99 | 27.42 | - | - | 27.42
2 | Dhaka ( South) grid circle | 349.85 | - | 72.34 | 422.19 | 19.33 | 63.5 | - | 82.83
3 | Chittagong grid circle. | 182.03 | - | - | 182.03 | - | - | 29.7 | 29.7
4 | Comilla grid circle. | 96.23 | - | 42 | 138.23 | 206.08 | - | 145.6 | 351.68
5 | Khulna grid circle. | 28.63 | - | 588.8 | 617.43 | 246.02 | 29.33 |  | 275.35
6 | Bheramara HVDC grid circle | 1993.68 | - | - | 1993.68 | 7.83 | 20.5 | 231 | 259.33
7 | Bogra grid circle. | 4 | 34.67 | 177.33 | 216 | 181.97 | 14.73 | - | 196.7
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 2816.08 | 34.67 | 2025.8 | 4876.55 | 688.65 | 128.06 | 406.3 | 1223.01
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | - | - | - | - | - | - | -
2 | Dhaka (South) | 5031.6 | - | 1 | 1 | - | - | 1 | 63.5
3 | Chittagong | 2042 | - | 1 | 1 | - | - | 1 | 29.7
4 | Khulna | 2434 | 4 | - | 4 | 3 | 1 | - | 52.62
5 | Bheramara (HVDC) | 2423.3 | 3 | 1 | 4 | 1 | 1 | 2 | 259.33
6 | Bogra | 3145.6 | 2 | - | 2 | 1 |  | 1 | 16.73
7 | Comilla | 2981 | - | 2 | 2 | 1 | - | 1 | 145.6
| Total | 23365.5 | [6 empty] | 567.48
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.9%
3 | Chittagong | 99.96%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.75% | [6 empty] | Executive Engineer
6 | Bogra | 98.4% | [6 empty] | Information Management Division
7 | Comilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 | 1 | - | - | 27.42
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 2 | - | 1 | 19.33
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 3 | - | 3 | 1 | - | 2 | 222.73
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogra | 1803.3 | 38 | 4 | - | 4 | 4 | - | - | 179.97
7 | Comilla | 1648.16 | 17 | 5 | - | 5 | 5 | - | - | 206.08
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 655.53
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.92%
2 | Dhaka (South) | 99.81%
3 | Chittagong | 99.97%
4 | Khulna | 99.77%
5 | Bheramara (HVDC) | 99.94% | [7 empty] | Executive Engineer
6 | Bogra | 99.9% | [7 empty] | Information Management Division
7 | Comilla | 99.81% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
April | 16 | - | 4 | 3hr34 min | 1 | 13min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:April' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Joydevpur | 1 | 0:07 | 235 | 27.4167 | Due to tripping of Joydevpur-Ghorashal 132 kV line-1 & 2
Hasnabad | 1 | 0:30 | 10 | 5 | Due to tripping of Hasnabad -Shyampur 132 kV line
Haripur | 2 | 0:13 | 50 | 10.8333 | Due to tripping of Haripur-Narsinghdi 132kV line
|  | 0:06 | 35 | 3.5 | Due to tripping of Haripur -Shyampur 132 kV line
Siddhirganj | 1 | 2:07 | 30 | 63.5 | Due to S/D of 132/33 kV Transformer T2
Sikalbaha | 1 | 1:39 | 18 | 29.7 | Due to S/D of 132/33 kV Transformer T3
Sreemingal | 1 | 1:01 | 20 | 20.3333 | Due to tripping of Sreemongal-Shahjibazar 132 kV line
Ashuganj | 3 | 0:06 | 160 | 16 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-2
|  | 0:11 | 105 | 19.25 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-2
|  | 0:49 | 20 | 16.3333 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-2
Shahjibazar | 1 | 0:23 | 350 | 134.1667 | Due to tripping of Shahjibazar-Sreemongal 132 kV line-1 & 2
Daudkandi | 1 | 3:37 | 40 | 144.6667 | Due to S/D of 132 kV bus
Shahjibazar | 1 | 0:08 | 7 | 0.93333 | Due to S/D of 132/33 kV Transformer T4
Faridpur | 1 | 0:11 | 12 | 2.2 | Due to tripping of 132/33 kV Transformers T1 & T2
Gopalganj | 1 | 0:44 | 40 | 29.3333 | Due to tripping of 132/33 kV Transformer T1
Bagerhat | 1 | 0:14 | 60 | 14 | Due to tripping of 132/33 kV Transformer T1
Khulna© | 1 | 0:16 | 285 | 76 | Due to tripping of Khulna(C)-Noapara 132 kV line-1 & 2
Madaripur | 1 | 1:06 | 40 | 44 | Due to tripping of Madaripur-Gopalganj 132 kV line
Barisal | 1 | 4:28 | 23 | 102.7333 | Due to tripping of Barisal-Patuakhali 132 kV line
Jessore | 1 | 0:03 | 55 | 2.75 | Due to tripping of 132/33 kV Transformer T1
Bottail | 3 | 0:17 | 25 | 7.0833 | Due to tripping of 132/33 kV Transformer T2
|  | 0:41 | 30 | 20.5 | Due to red-hot mainteanance of 132 /33 kV X-former T2
|  | 5:08 | 45 | 231 | Due to S/D of 132 kV bus- 1 & 2
Ishurdi | 1 | 1:01 | 5 | 5.0833 | Due to red-hot mainteanance of 132 /33 kV X-former T1
Amnura | 1 | 0:10 | 10 | 2 | Due to tripping of 132/33 kV Transformer T1
Natore | 1 | 1:08 | 13 | 14.7333 | Due to red-hot mainteanance of 132 /33 kV X-former T3
Saidpur | 1 | 0:09 | 160 | 24 | Due to tripping of Saidpur-Purbasadipur 132 kV line
Rajshahi | 1 | 0:08 | 90 | 12 | Due to tripping of Rajshahi-Natore 132 kV line
Barapukuria |  | 0:29 | 245 | 118.4167 | Due to tripping of Barapukuria-Rangpur 132 kV line-1 &2
Naogaon | 1 | 0:14 | 12 | 2.8 | Due to tripping of Naogaon-Niyamatpur 132 kV line
Palashbari | 1 | 0:13 | 105 | 22.75 | Due to tripping of Palashbari-Rangpur 132 kV line-2
| Total unserved energy : |  |  | 1223.0167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 129 | 11 | 2018-04-01 | 16:00
2 | Munsiganj | 114 | 23 | 2018-04-01 | 19:30
3 | Megnaghat | 58 | 7 | 2018-04-01 | 19:00
4 | Shyampur | 162 | 22 | 2018-04-01 | 12:00
5 | Bhulta | 171 | 22 | 2018-04-01 | 14:00
6 | Madanganj | 59 | 24 | 2018-04-01 | 14:00
7 | Shitalakhya | 114 | 5 | 2018-04-01 | 10:00
8 | Rahim steel | 15 | 29 | 2018-04-01 | 13:00
9 | Matuail | 96 | 9 | 2018-04-01 | 10:00
10 | Ghorasal | 80 | 4 | 2018-04-01 | 7:00
11 | Narsingdi | 192 | 29 | 2018-04-01 | 21:00
12 | Haripur (SBU) | 129 | 1 | 2018-04-01 | 15:00
13 | Ullon | 99 | 23 | 2018-04-01 | 13:00
14 | Hasnabad | 197 | 24 | 2018-04-01 | 21:00
15 | Magbazar | 128 | 25 | 2018-04-01 | 15:00
16 | Maniknagar | 92 | 24 | 2018-04-01 | 16:00
17 | Bangabhaban | 38 | 24 | 2018-04-01 | 11:00
18 | Narinda | 74 | 3 | 2018-04-01 | 18:30
19 | Dhanmondi | 151 | 16 | 2018-04-01 | 12:00
20 | Lalbag | 87 | 23 | 2018-04-01 | 20:00
21 | Madartek | 50 | 24 | 2018-04-01 | 22:00
22 | Mirpur | 101 | 28 | 2018-04-01 | 19:00
23 | Kalyanpur | 123 | 11 | 2018-04-01 | 18:30
24 | Gulshan | 130 | 23 | 2018-04-01 | 16:00
25 | Uttara | 103 | 14 | 2018-04-01 | 13:00
26 | Kamrangirchar | 86 | 4 | 2018-04-01 | 19:00
27 | Savar | 159 | 18 | 2018-04-01 | 20:00
28 | Bhasantec | 167 | 24 | 2018-04-01 | 17:00
29 | Agargaon | 130 | 29 | 2018-04-01 | 13:00
30 | Satmosjid | 95 | 16 | 2018-04-01 | 19:00
31 | Tongi | 137 | 12 | 2018-04-01 | 16:00
32 | Kabirpur | 199 | 25 | 2018-04-01 | 16:00
33 | Basundhara | 130 | 25 | 2018-04-01 | 19:00
34 | Manikganj | 109 | 23 | 2018-04-01 | 21:00
35 | Joydevpur | 216 | 24 | 2018-04-01 | 19:00
36 | New Tongi | 119 | 11 | 2018-04-01 | 16:00
37 | Kodda | 212 | 1 | 2018-04-01 | 18:30
38 | Tangail | 167 | 15 | 2018-04-01 | 19:30
39 | Mymensing | 204 | 13 | 2018-04-01 | 20:00
40 | Kishorganj | 88 | 15 | 2018-04-01 | 22:00
41 | Netrokona | 76 | 13 | 2018-04-01 | 19:30
42 | Jamalpur | 96 | 11 | 2018-04-01 | 23:00
43 | Sherpur | 70 | 11 | 2018-04-01 | 21:00
44 | Srimongal | 33 | 3 | 2018-04-01 | 19:00
45 | Shahjibazar | 99 | 15 | 2018-04-01 | 21:00
46 | Fenchuganj | 48 | 9 | 2018-04-01 | 18:30
47 | Khulawara | 37 | 16 | 2018-04-01 | 19:30
48 | Sylhet | 145 | 23 | 2018-04-01 | 19:30
49 | Chatak | 51 | 12 | 2018-04-01 | 20:00
50 | Comilla (S) | 176 | 5 | 2018-04-01 | 23:00
51 | Comilla(N) | 97 | 15 | 2018-04-01 | 22:00
52 | Chandpur | 118 | 28 | 2018-04-01 | 21:00
53 | Feni | 108 | 5 | 2018-04-01 | 19:00
54 | Chowmuhani | 184 | 23 | 2018-04-01 | 22:00
55 | Ashuganj | 57 | 10 | 2018-04-01 | 19:00
56 | Daudkandi | 100 | 16 | 2018-04-01 | 21:00
57 | B.Baria | 124 | 28 | 2018-04-01 | 21:00
58 | Madanhat | 65.5 | 24 | 2018-04-01 | 19:00
59 | Hathazari | 102 | 1 | 2018-04-01 | 19:00
60 | Khulshi | 198 | 28 | 2018-04-01 | 18:30
61 | Halishahar | 144 | 3 | 2018-04-01 | 15:00
62 | Baraulia | 157 | 11 | 2018-04-01 | 23:00
63 | Sikalbaha | 36 | 18 | 2018-04-01 | 18:30
Page: 2/2
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
64 | Dohazari | 88 | 2 | 2018-04-01 | 18:30
65 | Cox'sbazar | 90 | 21 | 2018-04-01 | 19:00
66 | Chandraghona | 34 | 14 | 2018-04-01 | 19:00
67 | Kaptai | 5 | 21 | 2018-04-01 | 19:30
68 | A. Khaer Stl. | 25 | 10 | 2018-04-01 | 10:00
69 | Bakulia | 115 | 12 | 2018-04-01 | 18:30
70 | Julda | 23 | 7 | 2018-04-01 | 19:00
71 | TK chemical | 2 | 25 | 2018-04-01 | 20:00
72 | Modern Steel | 17 | 1 | 2018-04-01 | 24:00
73 | Shahmirpur | 30.5 | 16 | 2018-04-01 | 18:30
74 | Abul Khair 230 | 202 | 25 | 2018-04-01 | 17:00
75 | BSRM | 116 | 8 | 2018-04-01 | 13:00
76 | Khagrachhari | 17 | 24 | 2018-04-01 | 21:00
77 | Goalpara | 43 | 11 | 2018-04-01 | 21:00
78 | Central s/s | 93 | 19 | 2018-04-01 | 19:00
79 | Noapara | 88 | 15 | 2018-04-01 | 19:00
80 | Jessore | 142 | 23 | 2018-04-01 | 19:30
81 | Jhenida | 88 | 23 | 2018-04-01 | 20:00
82 | Bottail | 118 | 24 | 2018-04-01 | 20:00
83 | G.K Project | 86 | 28 | 2018-04-01 | 19:30
84 | Faridpur | 144 | 23 | 2018-04-01 | 22:00
85 | Madaripur | 118 | 24 | 2018-04-01 | 22:00
86 | Gopalganj | 168 | 7 | 2018-04-01 | 21:00
87 | Bagerhat | 75 | 15 | 2018-04-01 | 22:00
88 | Mongla | 41 | 19 | 2018-04-01 | 12:00
89 | Satkhira | 86 | 18 | 2018-04-01 | 22:00
90 | Gallamari | 48 | 9 | 2018-04-01 | 20:00
91 | Magura | 50 | 16 | 2018-04-01 | 21:00
92 | Chuadanga | 110 | 20 | 2018-04-01 | 21:00
93 | Barisal | 118 | 24 | 2018-04-01 | 21:00
94 | Patuakhali | 81 | 23 | 2018-04-01 | 22:00
95 | Bhandaria | 46 | 13 | 2018-04-01 | 21:00
96 | Ishurdi | 52 | 19 | 2018-04-01 | 19:30
97 | Ruppur Paromanobik | 1 | 1 | 2018-04-01 | 1:00
98 | Natore | 107 | 16 | 2018-04-01 | 21:00
99 | Bogra | 221 | 24 | 2018-04-01 | 20:00
100 | Noagaon | 114 | 17 | 2018-04-01 | 21:00
101 | Rajshahi | 155 | 24 | 2018-04-01 | 21:00
102 | C.Nawabganj | 63 | 23 | 2018-04-01 | 20:00
103 | Amnura | 34 | 17 | 2018-04-01 | 20:00
104 | Pabna | 109 | 23 | 2018-04-01 | 19:30
105 | Shahjadpur | 93 | 16 | 2018-04-01 | 21:00
106 | Serajganj | 89 | 16 | 2018-04-01 | 10:00
107 | Niyamatpur | 77 | 15 | 2018-04-01 | 20:00
108 | Joypurhat | 51 | 7 | 2018-04-01 | 21:00
109 | Rangpur | 124 | 23 | 2018-04-01 | 19:30
110 | Lalmonirhat | 83 | 7 | 2018-04-01 | 21:00
111 | Saidpur | 114 | 24 | 2018-04-01 | 19:30
112 | Purbasadipur | 91 | 24 | 2018-04-01 | 20:00
113 | Thakurgaon | 66 | 8 | 2018-04-01 | 19:30
114 | Palashbari | 90 | 8 | 2018-04-01 | 19:30
115 | Barapukuria | 52 | 4 | 2018-04-01 | 19:30
116 | Panchagar | 40 | 8 | 2018-04-01 | 19:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 3721 | 25.04.18 | 16:00
Chittagong | 1201 | 23.04.18 | 23:00
Khulna | 1197 | 24.04.18 | 21:00
Rajshahi | 1070 | 24.04.18 | 21:00
Comilla | 1061 | 17.04.18 | 20:00
Mymensingh | 653 | 13.04.18 | 21:00
Sylhet | 389 | 16.04.18 | 21:00
Barisal | 263 | 23.04.18 | 22:00
Rangpur | 627 | 24.04.18 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 425 | 17 | 2018-04-01 | 24:00 | 374 | 16 | 2018-04-01 | 16:00
2 | Bheramara | 400 | 418 | 8 | 2018-04-01 | 18:00 | 379 | 10 | 2018-04-01 | 16:00
3 | Kaliakoir | 400 | 428 | 29 | 2018-04-01 | 09:00 | 340 | 24 | 2018-04-01 | 16:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 232 | 6 | 2018-04-01 | 07:00 | 220 | 28 | 2018-04-01 | 14:00
2 | Ishurdi | 230 | 237 | 1 | 2018-04-01 | 8:00 | 211 | 16 | 2018-04-01 | 21:00
3 | Ashuganj | 230 | 240 | 13 | 2018-04-01 | 18:00 | 214 | 10 | 2018-04-01 | 21:00
4 | Serajganj | 230 | 234 | 30 | 2018-04-01 | 12:00 | 208 | 16 | 2018-04-01 | 21:00
5 | Baghabari | 230 | 239 | 10 | 2018-04-01 | 4:00 | 202 | 4 | 2018-04-01 | 19:30
6 | Barapukuria | 230 | 245 | 30 | 2018-04-01 | 10:00 | 214 | 10 | 2018-04-01 | 21:00
7 | Bogra | 230 | 240 | 12 | 2018-04-01 | 23':00 | 203 | 3 | 2018-04-01 | 20:00
8 | Khulna South | 230 | 241 | 30 | 2018-04-01 | 12'00 | 215 | 9 | 2018-04-01 | 7:00
9 | Rampura | 230 | 228 | 30 | 2018-04-01 | 12:00 | 205 | 4 | 2018-04-01 | 7:00
10 | Haripur | 230 | 230 | 25 | 2018-04-01 | 19:30 | 215 | 24 | 2018-04-01 | 17:00
11 | Hasnabad | 230 | 233 | 7 | 2018-04-01 | 7:00 | 215 | 24 | 2018-04-01 | 16:00
12 | Aminbazar | 230 | 234 | 14 | 2018-04-01 | 17:00 | 210 | 10 | 2018-04-01 | 15:00
13 | Tongi | 230 | 233 | 21 | 2018-04-01 | 10:00 | 204 | 24 | 2018-04-01 | 15:00
14 | Comilla (N) | 230 | 236 | 3 | 2018-04-01 | 4:00 | 215 | 10 | 2018-04-01 | 15:00
15 | Hathazari | 230 | 230 | 10 | 2018-04-01 | 19:00 | 205 | 25 | 2018-04-01 | 11:00
16 | Megnaghat | 230 | 235 | 10 | 2018-04-01 | 6:00 | 220 | 20 | 2018-04-01 | 18:00
17 | Fenchuganj | 230 | 248 | 17 | 2018-04-01 | 24:00 | 211 | 10 | 2018-04-01 | 15:00
18 | Siddhirganj | 230 | 237 | 25 | 2018-04-01 | 20:00 | 208 | 10 | 2018-04-01 | 16:00
19 | Maniknagar | 230 | 236 | 30 | 2018-04-01 | 12:00 | 208 | 5 | 2018-04-01 | 12:00
20 | Old Airport | 230 | 240 | 17 | 2018-04-01 | 18:00 | 212 | 24 | 2018-04-01 | 16:00
21 | Barisal | 230 | 243 | 7 | 2018-04-01 | 11:00 | 213 | 10 | 2018-04-01 | 09:00
22 | AKSML | 230 | 227 | 27 | 2018-04-01 | 03:00 | 203 | 25 | 2018-04-01 | 04:00
23 | BSRM | 230 | 235 | 10 | 2018-04-01 | 07:00 | 206 | 25 | 2018-04-01 | 12:00
24 | Bibiyana | 230 | 247 | 17 | 2018-04-01 | 24:00 | 218 | 15 | 2018-04-01 | 22:00
132 kV Substation
1 | Siddhirganj | 132 | 138 | 30 | 2018-04-01 | 12:00 | 123 | 26 | 2018-04-01 | 12:00
2 | Munsiganj | 132 | 138 | 30 | 2018-04-01 | 12:00 | 124 | 26 | 2018-04-01 | 12:00
3 | Megnaghat | 132 | 134 | 14 | 2018-04-01 | 18:00 | 122 | 28 | 2018-04-01 | 11:00
4 | Shyampur | 132 | 137 | 11 | 2018-04-01 | 19:30 | 119 | 19 | 2018-04-01 | 10:00
5 | Bhulta | 132 | 140 | 30 | 2018-04-01 | 12:00 | 124 | 15 | 2018-04-01 | 12:00
6 | Madanganj | 132 | 142 | 14 | 2018-04-01 | 18:00 | 125 | 4 | 2018-04-01 | 10:00
7 | Shitalakhya | 132 | 144 | 30 | 2018-04-01 | 12:00 | 126 | 30 | 2018-04-01 | 10:00
8 | Rahim Steal | 132 | 138 | 30 | 2018-04-01 | 12:00 | 123 | 22 | 2018-04-01 | 13:00
9 | Matuail | 132 | 138 | 30 | 2018-04-01 | 12:00 | 122 | 25 | 2018-04-01 | 10:00
10 | Ghorasal | 132 | 144 | 30 | 2018-04-01 | 12:00 | 130 | 9 | 2018-04-01 | 15:00
11 | Narsinghdi | 132 | 141 | 29 | 2018-04-01 | 9:00 | 119 | 28 | 2018-04-01 | 11:00
12 | Haripur (SBU) | 132 | 137 | 28 | 2018-04-01 | 7:00 | 124 | 26 | 2018-04-01 | 12:00
13 | Ullon | 132 | 139 | 25 | 2018-04-01 | 19:30 | 120 | 5 | 2018-04-01 | 12:00
14 | Hasnabad | 132 | 140 | 7 | 2018-04-01 | 6:00 | 127 | 28 | 2018-04-01 | 10:00
15 | Magbazar | 132 | 149 | 25 | 2018-04-01 | 19:30 | 120 | 5 | 2018-04-01 | 11:00
16 | Maniknagar | 132 | 144 | 30 | 2018-04-01 | 12:00 | 125 | 5 | 2018-04-01 | 12:00
17 | Bangabhaban | 132 | 140 | 15 | 2018-04-01 | 6:00 | 125 | 5 | 2018-04-01 | 12:00
18 | Narinda | 132 | 139 | 22 | 2018-04-01 | 6:00 | 125 | 5 | 2018-04-01 | 13:00
19 | Dhanmondi | 132 | 144 | 30 | 2018-04-01 | 12:00 | 120 | 8 | 2018-04-01 | 15:00
20 | Lalbag | 132 | 140 | 15 | 2018-04-01 | 6:00 | 124 | 24 | 2018-04-01 | 17:00
21 | Madartek | 132 | 139 | 22 | 2018-04-01 | 6:00 | 121 | 1 | 2018-04-01 | 16:00
22 | Mirpur | 132 | 141 | 25 | 2018-04-01 | 19:30 | 122 | 21 | 2018-04-01 | 11:00
23 | Kalyanpur | 132 | 141 | 25 | 2018-04-01 | 19:30 | 123 | 10 | 2018-04-01 | 16:00
24 | Gulshan | 132 | 139 | 25 | 2018-04-01 | 19:30 | 120 | 5 | 2018-04-01 | 11:00
25 | Uttara | 132 | 138 | 25 | 2018-04-01 | 19:30 | 120 | 11 | 2018-04-01 | 15:00
26 | Kamrangirchar | 132 | 141 | 25 | 2018-04-01 | 19:30 | 121 | 22 | 2018-04-01 | 12:00
27 | Savar | 132 | 139 | 25 | 2018-04-01 | 19:30 | 120 | 24 | 2018-04-01 | 15:00
28 | Bhasantec | 132 | 136 | 7 | 2018-04-01 | 5:00 | 121 | 19 | 2018-04-01 | 12:00
29 | Agargaon | 132 | 137 | 7 | 2018-04-01 | 5:00 | 119 | 7 | 2018-04-01 | 13:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 136 | 7 | 2018-04-01 | 6:00 | 120 | 24 | 2018-04-01 | 15:00
31 | Tongi | 132 | 146 | 25 | 2018-04-01 | 19:30 | 124 | 4 | 2018-04-01 | 15:00
32 | Kabirpur | 132 | 139 | 29 | 2018-04-01 | 9:00 | 120 | 24 | 2018-04-01 | 16:00
33 | Basundhara | 132 | 135 | 18 | 2018-04-01 | 1:00 | 117 | 11 | 2018-04-01 | 13:00
34 | Manikganj | 132 | 145 | 12 | 2018-04-01 | 1:00 | 128 | 16 | 2018-04-01 | 16:00
35 | Joydevpur | 132 | 145 | 20 | 2018-04-01 | 12:00 | 124 | 15 | 2018-04-01 | 9:00
36 | New Tongi | 132 | 140 | 25 | 2018-04-01 | 19:30 | 123 | 4 | 2018-04-01 | 15:00
37 | Kodda | 132 | 144 | 21 | 2018-04-01 | 14:00 | 121 | 15 | 2018-04-01 | 15:00
38 | Tangail | 132 | 145 | 18 | 2018-04-01 | 24:00 | 118 | 19 | 2018-04-01 | 18:00
39 | Mymensing | 132 | 140 | 28 | 2018-04-01 | 22:00 | 111 | 24 | 2018-04-01 | 22:00
40 | Kishorganj | 132 | 142 | 21 | 2018-04-01 | 17:00 | 115 | 24 | 2018-04-01 | 22:00
41 | Netrokona | 132 | 144 | 18 | 2018-04-01 | 24:00 | 110 | 22 | 2018-04-01 | 20:00
42 | Jamalpur | 132 | 138 | 28 | 2018-04-01 | 22:00 | 107 | 15 | 2018-04-01 | 14:00
43 | Sherpur | 132 | 140 | 30 | 2018-04-01 | 22:00 | 110 | 15 | 2018-04-01 | 14:00
44 | Srimongal | 132 | 145 | 29 | 2018-04-01 | 2:00 | 129 | 25 | 2018-04-01 | 1:00
45 | Shahjibazar | 132 | 140 | 21 | 2018-04-01 | 14:00 | 127 | 24 | 2018-04-01 | 22:00
46 | Fenchuganj | 132 | 141 | 3 | 2018-04-01 | 17:00 | 126 | 18 | 2018-04-01 | 19:30
47 | Khulawara | 132 | 140 | 1 | 2018-04-01 | 05:00 | 125 | 18 | 2018-04-01 | 20:00
48 | Sylhet | 132 | 140 | 6 | 2018-04-01 | 5:00 | 123 | 18 | 2018-04-01 | 18:30
49 | Chattak | 132 | 139 | 30 | 2018-04-01 | 06:00 | 122 | 7 | 2018-04-01 | 20:00
50 | Comilla(South) | 132 | 138 | 25 | 2018-04-01 | 21:00 | 119 | 10 | 2018-04-01 | 19:30
51 | Comilla (North) | 132 | 142 | 22 | 2018-04-01 | 20:00 | 120 | 25 | 2018-04-01 | 17:00
52 | Chandpur | 132 | 142 | 30 | 2018-04-01 | 17:00 | 116 | 24 | 2018-04-01 | 23:00
53 | Feni | 132 | 135 | 25 | 2018-04-01 | 21:00 | 113 | 24 | 2018-04-01 | 23:00
54 | Chowmuhani | 132 | 136 | 30 | 2018-04-01 | 18:30 | 111 | 24 | 2018-04-01 | 22:00
55 | Ashuganj | 132 | 142 | 29 | 2018-04-01 | 1:00 | 127 | 24 | 2018-04-01 | 17:00
56 | Daudkandi | 132 | 141 | 12 | 2018-04-01 | 19:00 | 126 | 26 | 2018-04-01 | 14:00
57 | Brahminbaria | 132 | 142 | 25 | 2018-04-01 | 19:00 | 127 | 12 | 2018-04-01 | 19:00
58 | Madanhat | 132 | 136 | 6 | 2018-04-01 | 18:30 | 126 | 25 | 2018-04-01 | 12:00
59 | Hathazari | 132 | 135 | 27 | 2018-04-01 | 03:00 | 107 | 20 | 2018-04-01 | 11:00
60 | Khulshi | 132 | 134 | 27 | 2018-04-01 | 3:00 | 120 | 25 | 2018-04-01 | 12:00
61 | Halishahar | 132 | 136 | 27 | 2018-04-01 | 03:00 | 122 | 25 | 2018-04-01 | 12:00
62 | Baraulia | 132 | 133 | 17 | 2018-04-01 | 16:00 | 115 | 6 | 2018-04-01 | 11:00
63 | Sikalbaha | 132 | 134 | 17 | 2018-04-01 | 16:00 | 123 | 25 | 2018-04-01 | 11:00
64 | Dohazari | 132 | 136 | 27 | 2018-04-01 | 3:00 | 115 | 22 | 2018-04-01 | 9:00
65 | Cox'sbazar | 132 | 132 | 17 | 2018-04-01 | 18:00 | 110 | 28 | 2018-04-01 | 13:00
66 | Chandraghona | 132 | 135 | 17 | 2018-04-01 | 16:00 | 107 | 14 | 2018-04-01 | 18:30
67 | Kaptai | 132 | 136 | 17 | 2018-04-01 | 16:00 | 125 | 23 | 2018-04-01 | 15:00
68 | A. Khaer Stl. | 132 | 136 | 29 | 2018-04-01 | 20:00 | 121 | 25 | 2018-04-01 | 12:00
69 | Bakulia | 132 | 134 | 17 | 2018-04-01 | 16:00 | 121 | 25 | 2018-04-01 | 12:00
70 | Julda | 132 | 133 | 27 | 2018-04-01 | 03:00 | 122 | 18 | 2018-04-01 | 12:00
71 | TK Chemical | 132 | 138 | 27 | 2018-04-01 | 03:00 | 123 | 23 | 2018-04-01 | 15:00
72 | Modern Steel | 132 | 134 | 17 | 2018-04-01 | 16:00 | 120 | 25 | 2018-04-01 | 12:00
73 | Shahmirpur | 132 | 135 | 27 | 2018-04-01 | 03:00 | 122 | 25 | 2018-04-01 | 12:00
74 | Khagrachhari | 132 | 134 | 17 | 2018-04-01 | 16:00 | 124 | 12 | 2018-04-01 | 11:00
75 | Goalpara | 132 | 140 | 12 | 2018-04-01 | 20:00 | 120 | 3 | 2018-04-01 | 6:00
76 | Khulna Central | 132 | 140 | 12 | 2018-04-01 | 21:00 | 125 | 8 | 2018-04-01 | 19:30
77 | Noapara | 132 | 140 | 12 | 2018-04-01 | 19:30 | 120 | 8 | 2018-04-01 | 19:30
78 | Jessore | 132 | 138 | 30 | 2018-04-01 | 11:00 | 117 | 7 | 2018-04-01 | 11:00
79 | Jhenida | 132 | 140 | 30 | 2018-04-01 | 12:00 | 110 | 7 | 2018-04-01 | 10:00
80 | Bottail | 132 | 142 | 30 | 2018-04-01 | 11:00 | 112 | 14 | 2018-04-01 | 13:00
81 | G.K.Project | 132 | 144 | 30 | 2018-04-01 | 12:00 | 122 | 14 | 2018-04-01 | 13:00
82 | Faridpur | 132 | 140 | 12 | 2018-04-01 | 22:00 | 121 | 14 | 2018-04-01 | 13:00
83 | Madaripur | 132 | 142 | 22 | 2018-04-01 | 18:00 | 120 | 3 | 2018-04-01 | 20:00
84 | Gopalganj | 132 | 146 | 22 | 2018-04-01 | 9:00 | 118 | 14 | 2018-04-01 | 13:00
85 | Bagerhat | 132 | 141 | 1 | 2018-04-01 | 17:00 | 122 | 8 | 2018-04-01 | 19:30
86 | Mongla | 132 | 140 | 30 | 2018-04-01 | 22:00 | 120 | 3 | 2018-04-01 | 21:00
87 | Satkhira | 132 | 141 | 30 | 2018-04-01 | 22:00 | 122 | 3 | 2018-04-01 | 20:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
88 | Gallamari | 132 | 141 | 30 | 2018-04-01 | 12:00 | 122 | 28 | 2018-04-01 | 21:00
89 | Magura | 132 | 142 | 30 | 2018-04-01 | 13:00 | 108 | 7 | 2018-04-01 | 11:00
90 | Chuadanga | 132 | 138 | 1 | 2018-04-01 | 23:00 | 104 | 3 | 2018-04-01 | 20:00
91 | Barisal | 132 | 142 | 12 | 2018-04-01 | 22:00 | 125 | 26 | 2018-04-01 | 11:00
92 | Patuakhali | 132 | 142 | 12 | 2018-04-01 | 22:00 | 125 | 26 | 2018-04-01 | 11:00
93 | Bhandaria | 132 | 140 | 8 | 2018-04-01 | 8:00 | 120 | 28 | 2018-04-01 | 11:00
94 | Ishurdi | 132 | 144 | 30 | 2018-04-01 | 10:00 | 122 | 4 | 2018-04-01 | 13:00
95 | Ruppur Paromanobik | 132 | 141 | 29 | 2018-04-01 | 9:00 | 121 | 14 | 2018-04-01 | 13:00
96 | Natore | 132 | 144 | 30 | 2018-04-01 | 10:00 | 121 | 15 | 2018-04-01 | 14:00
97 | Bogra | 132 | 142 | 30 | 2018-04-01 | 10:00 | 106 | 16 | 2018-04-01 | 12:00
98 | Noagaon | 132 | 140 | 29 | 2018-04-01 | 9:00 | 113 | 16 | 2018-04-01 | 20:00
99 | Rajshahi | 132 | 142 | 30 | 2018-04-01 | 10:00 | 121 | 3 | 2018-04-01 | 20:00
100 | C.Nawabganj | 132 | 140 | 30 | 2018-04-01 | 10:00 | 118 | 14 | 2018-04-01 | 13:00
101 | Amnura | 132 | 142 | 30 | 2018-04-01 | 11:00 | 115 | 11 | 2018-04-01 | 4:00
102 | Pabna | 132 | 140 | 30 | 2018-04-01 | 11:00 | 118 | 14 | 2018-04-01 | 15:00
103 | Shahjadpur | 132 | 145 | 30 | 2018-04-01 | 10:00 | 115 | 16 | 2018-04-01 | 12:00
104 | Serajganj | 132 | 142 | 30 | 2018-04-01 | 11:00 | 115 | 16 | 2018-04-01 | 21:00
105 | Niyamatpur | 132 | 143 | 30 | 2018-04-01 | 10:00 | 108 | 16 | 2018-04-01 | 21:00
106 | Joypurhat | 132 | 144 | 30 | 2018-04-01 | 10:00 | 110 | 16 | 2018-04-01 | 21:00
107 | Rangpur | 132 | 136 | 30 | 2018-04-01 | 11:00 | 100 | 3 | 2018-04-01 | 20:00
108 | Lalmonirhat | 132 | 141 | 30 | 2018-04-01 | 10:00 | 105 | 15 | 2018-04-01 | 19:00
109 | Saidpur | 132 | 138 | 8 | 2018-04-01 | 12:00 | 108 | 16 | 2018-04-01 | 21:00
110 | Purbasadipur | 132 | 143 | 30 | 2018-04-01 | 10:00 | 118 | 1 | 2018-04-01 | 7:00
111 | Thakurgaon | 132 | 140 | 30 | 2018-04-01 | 9:00 | 103 | 3 | 2018-04-01 | 20:00
112 | Palashbari | 132 | 140 | 17 | 2018-04-01 | 10:00 | 105 | 3 | 2018-04-01 | 20:00
113 | Barapukuria | 132 | 145 | 30 | 2018-04-01 | 10:00 | 122 | 3 | 2018-04-01 | 20:00
114 | Panchagar | 132 | 138 | 30 | 2018-04-01 | 9:00 | 100 | 3 | 2018-04-01 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:April' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 127 | 390
IP-299421 | Hasnabad | TR2 | 225 | 120 | 390 | 28.04.18 | 23:00
|  | TR3 | 225 | 118 | 370
|  | TR1 | 225 | 130 | 420
IP-299866 | Tongi | TR2 | 225 | 130 | 420 | 04.04.18 | 15:00
|  | TR3 | 225 | 130 | 420
|  | TR1 | 225 | 124 | 325
IP-299427 | Haripur | TR2 | 225 | 124 | 325 | 21.04.18 | 09:00
|  | TR3 | 225 | 124 | 325
|  | TR1 | 225 | 190 | 590
IP-299728 | Rampura | TR2 | 225 | 190 | 590 | 08.04.18 | 15:00
|  | TR3 | 225 | 190 | 590
|  | TR1 | 225 | 118 | 325
IP-299264 | Aminbazar | TR2 | 225 | 118 | 325 | 22.04.18 | 17:00
|  | TR3 | 225 | 121 | 336
| Maniknagar | TR1 | 300 | 106 | 350 | 24.04.18 | 7:00
|  | TR2 | 300 | 106 | 350
IP-399266 | Comilla (N) | TR1 | 225 | 140 | 430 | 26.04.18 | 23:00
|  | TR2 | 225 | 138 | 411
| Fenchuganj | TR1 | 300 | 242 | 609 | 21.04.18 | 10:00
|  | TR1 | 150 | 80 | 220
IP-399428 | Hathazari | TR3 | 150 | 80 | 220 | 30.04.18 | 12:00
|  | TR4 | 150 | 80 | 220
|  | TR1 | 225 | 130 | 410
| Ishurdi | TR2 | 225 | 130 | 410 | 21.04.18 | 20:00
IP-499474 |  | TR3 | 225 | 130 | 410
| Khulna(S) | TR1 | 225 | 144 | 380
IP-58001/58002 |  | TR2 | 225 | 144 | 380 | 20.04.18 | 22:00
| Bogra | TR1 | 225 | 135 | 390 | 09.04.18 | 7:00
|  | TR2 | 225 | 135 | 390
IP-43002/499264 |  | TR3 | 300 | 179 | 523
IP-499224 | Baghabari | TR1 | 225 | 150 | 450 | 04.04.18 | 9:00
| Barapukuria | TR2 | 225 | 119 | 575 |  |  | Due to unavailability of 230 kV side meters
|  | TR6 | 300 | 139 | 665 |  |  | 132 kV current is being provided
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:April' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:April' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-04-18 | 9147 | 9147 | - | - | - | - | - | - | - | - | - | - | - | - | 01-04-18 | 7359.1 | 7359.1 | - | - | - | - | - | - | - | - | - | - | - | -
02-04-18 | 9258 | 9258 | - | - | - | - | - | - | - | - | - | - | - | - | 02-04-18 | 7656.5 | 7656.5 | - | - | - | - | - | - | - | - | - | - | - | -
03-04-18 | 9350 | 9350 | - | - | - | - | - | - | - | - | - | - | - | - | 03-04-18 | 8216.2 | 8216.2 | - | - | - | - | - | - | - | - | - | - | - | -
04-04-18 | 9248 | 9248 | - | - | - | - | - | - | - | - | - | - | - | - | 04-04-18 | 7969.2 | 7969.2 | - | - | - | - | - | - | - | - | - | - | - | -
05-04-18 | 7443 | 7443 | - | - | - | - | - | - | - | - | - | - | - | - | 05-04-18 | 8361.2 | 8361.2 | - | - | - | - | - | - | - | - | - | - | - | -
06-04-18 | 8396 | 8396 | - | - | - | - | - | - | - | - | - | - | - | - | 06-04-18 | 5941.9 | 5941.9 | - | - | - | - | - | - | - | - | - | - | - | -
07-04-18 | 9255 | 9255 | - | - | - | - | - | - | - | - | - | - | - | - | 07-04-18 | 7424.3 | 7424.3 | - | - | - | - | - | - | - | - | - | - | - | -
08-04-18 | 9200 | 9200 | - | - | - | - | - | - | - | - | - | - | - | - | 08-04-18 | 7269.5 | 7269.5 | - | - | - | - | - | - | - | - | - | - | - | -
09-04-18 | 9510 | 9510 | - | - | - | - | - | - | - | - | - | - | - | - | 09-04-18 | 8255.1 | 8255.1 | - | - | - | - | - | - | - | - | - | - | - | -
10-04-18 | 9355 | 9355 | - | - | - | - | - | - | - | - | - | - | - | - | 10-04-18 | 7950.4 | 7950.4 | - | - | - | - | - | - | - | - | - | - | - | -
11-04-18 | 8943 | 8943 | - | - | - | - | - | - | - | - | - | - | - | - | 11-04-18 | 6580.6 | 6580.6 | - | - | - | - | - | - | - | - | - | - | - | -
12-04-18 | 8917 | 8917 | - | - | - | - | - | - | - | - | - | - | - | - | 12-04-18 | 7923.3 | 7923.3 | - | - | - | - | - | - | - | - | - | - | - | -
13-04-18 | 9257 | 9257 | - | - | - | - | - | - | - | - | - | - | - | - | 13-04-18 | 6363.3 | 6363.3 | - | - | - | - | - | - | - | - | - | - | - | -
14-04-18 | 7614 | 7614 | - | - | - | - | - | - | - | - | - | - | - | - | 14-04-18 | 7522.3 | 7522.3 | - | - | - | - | - | - | - | - | - | - | - | -
15-04-18 | 9961 | 9961 | - | - | - | - | - | - | - | - | - | - | - | - | 15-04-18 | 8044 | 8044 | - | - | - | - | - | - | - | - | - | - | - | -
16-04-18 | 9702 | 9702 | - | - | - | - | - | - | - | - | - | - | - | - | 16-04-18 | 6548 | 6548 | - | - | - | - | - | - | - | - | - | - | - | -
17-04-18 | 8464 | 8464 | - | - | - | - | - | - | - | - | - | - | - | - | 17-04-18 | 7437.1 | 7437.1 | - | - | - | - | - | - | - | - | - | - | - | -
18-04-18 | 9758 | 9758 | - | - | - | - | - | - | - | - | - | - | - | - | 18-04-18 | 7536.3 | 7536.3 | - | - | - | - | - | - | - | - | - | - | - | -
19-04-18 | 9425 | 9425 | - | - | - | - | - | - | - | - | - | - | - | - | 19-04-18 | 7639.7 | 7639.7 | - | - | - | - | - | - | - | - | - | - | - | -
20-04-18 | 8095 | 8095 | - | - | - | - | - | - | - | - | - | - | - | - | 20-04-18 | 6206.6 | 6206.6 | - | - | - | - | - | - | - | - | - | - | - | -
21-04-18 | 8498 | 8498 | - | - | - | - | - | - | - | - | - | - | - | - | 21-04-18 | 7094.3 | 7094.3 | - | - | - | - | - | - | - | - | - | - | - | -
22-04-18 | 8461 | 8461 | - | - | - | - | - | - | - | - | - | - | - | - | 22-04-18 | 7953.8 | 7953.8 | - | - | - | - | - | - | - | - | - | - | - | -
23-04-18 | 9778 | 9778 | - | - | - | - | - | - | - | - | - | - | - | - | 23-04-18 | 8105.4 | 8105.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-04-19 | 10137 | 10137 | - | - | - | - | - | - | - | - | - | - | - | - | 24-04-19 | 8526.2 | 8526.2 | - | - | - | - | - | - | - | - | - | - | - | -
25-04-20 | 8591 | 8591 | - | - | - | - | - | - | - | - | - | - | - | - | 25-04-20 | 8329.3 | 8329.3 | - | - | - | - | - | - | - | - | - | - | - | -
26-03-18 | 9261 | 9261 | - | - | - | - | - | - | - | - | - | - | - | - | 26-03-18 | 7243.4 | 7243.4 | - | - | - | - | - | - | - | - | - | - | - | -
27-04-18 | 8876 | 8876 | - | - | - | - | - | - | - | - | - | - | - | - | 27-04-18 | 6297.3 | 6297.3 | - | - | - | - | - | - | - | - | - | - | - | -
28-04-18 | 9573 | 9573 | - | - | - | - | - | - | - | - | - | - | - | - | 28-04-18 | 7884.3 | 7884.3 | - | - | - | - | - | - | - | - | - | - | - | -
29-04-18 | 7807 | 7807 | - | - | - | - | - | - | - | - | - | - | - | - | 29-04-18 | 5524 | 5524 | - | - | - | - | - | - | - | - | - | - | - | -
30-04-18 | 7256 | 7256 | - | - | - | - | - | - | - | - | - | - | - | - | 30-04-18 | 6113 | 6113 | - | - | - | - | - | - | - | - | - | - | - | -
31-03-18 | 8314 | 8314 | - | - | - | - | - | - | - | - | - | - | - | - | 31-03-18 | 4893.4 | 4893.4 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:April' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10137 | 24/04/18 | 21:00
2 | Maximum day peak Genaration | MW | 8526.2 | 24/04/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 10137 | 24/04/18 | 21:00
4 | Minimum Generation | MW | 4376 | 18/04/18 | 4:00
5 | Average of the daily evening peak Genaration | MW | 8951.2
6 | Average of the daily day peak Genaration | MW | 7375.8533
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5347.2669
12 | Total Generation by IPP | MKWH | 1425.5331 | % of total Gen. | 26.6591
13 | Total Generation by BPDB | MKWH | 2819.5077 | " | 52.728
14 | A) Total Generation by RPCL | MKWH | 70.0878 | '' | 1.3107
| B) Total Generation by REB | MKWH | 119.679 | " | 2.2381
| C) Total Generation by RENTAL | MKWH | 631.8383 | " | 11.8161
| D) Total Imported from India (HVDC) | MKWH | 195.6342 | " | 3.6586
| E) Total Imported from Tripura, India (A.C) | MKWH | 84.9869 | " | 1.5894
15 | Fuel wise Generation.
| A) Gas | MKWH | 3261.1999 | % of total Gen. | 60.99%
| B) Oil | MKWH | 1526.1283 | '' | 28.54%
| C) Hydro | MKWH | 64.4935 | '' | 1.206%
| D) Solar | MKWH | 0.36478 | '' | 0.006822%
| E) Coal | MKWH | 214.4594 | '' | 4.011%
| F) HVDC (Import from India) | MKWH | 195.6342 | '' | 3.659%
| G) A.C (Import from Tripura, India) | MKWH | 84.9869 | '' | 1.589%
16 | Maximun of the daily total Generation . | MKWH | 209.8156 | 24/04/18
17 | Monthly Load factor | % | 73.2639
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 16249.4991
| A) Gas | M.Taka | 2509.4376
| B) Liquid fuel | M.Taka | 13496.7442
| C) Coal | M.Taka | 243.3173
| D) HVDC (Import from India) | M.Taka | 997.7343
| E) Tripura(Import from India) | M.Taka | 581.3103
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 743.2679 | 16/04/18
| A) Gas | M.Taka | 100.6195 | 11/04/18
| B) Liquid fuel | M.Taka | 643.7513 | 16/04/18
| C) Coal | M.Taka | 9.5646 | 06/04/18
| D) HVDC (Import from India) | M.Taka | 59.6088 | 28/04/18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 4.0099
| B) Excluding Hydro & Solar | Taka/KWHR | 4.0592
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.4 | 30/04/18 | 06:00
b) | Actual | FT (MSL) | 81.29 | 30/04/18 | 06:00
22 | Peak Genaration of April 2017 | MW | 9212 | 18/04/17 | 20:00
23 | Peak Demand of April 2017 | MW | 9212 | 18/04/17 | 20:00
24 | Maximum peak Generation recorded upto 30/04/18 | MW | 10137 | 24/04/18 | 21:00
25 | Maximum peak Demand recorded upto 30/04/18 | MW | 10137 | 24/04/18 | 21:00
26 | Maximum load shed recorded upto 30/04/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.