## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | March 2018 |  | February 2018 |  | March 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10084 | 19/03/18 | 8848 | 24/02/18 | 8737 | 28/03/17 | 10084 | 19/03/18
|  |  | 19:30 |  | 19:30 |  | 20:00 |  | 19:30
2 | Minimum Generation (MW) | 1774 | 31/03/18 | 2515 | 26/02/18 | 3614 | 25/03/17 | - | -
|  |  | 7:00 |  | 5:00 |  | 10:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10084 | 19/03/18 | 8848 | 24/02/18 | 8737 | 28/03/17 | 10084 | 19/03/18
|  |  | 19:30 |  | 19:30 |  | 20:00 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 8476.9 | 22/03/18 | 7547.8 | 25/02/2018 | 7059 | 23/03/2017 | 8743 | 07/6/17
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10084 | 19/03/18 | 8848 | 24/02/18 | 8737 | 28/03/17 | 10084 | 19/03/18
|  |  | 19:30 |  | 19:30 |  | 20:00 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 9137.129 |  | 8183.61 |  | 7863.5 |  | 9296.54 | March -18
7 | Average Generation (MW) at Day Peak | 7657.3516 |  | 6720.43 |  | 6280.57 |  | 7779.98 | March -18
8 | Maximum Power Import from India (MW) | 488 | 03/03/18 | 485 | 25/02/18 | 509 | 07/03/17 | 509 | 2017-07-03
|  |  | 10:00 |  | 19:30 |  | 11:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 174 | 27/03/18 | 152 | 28/02/18 | 134 | 25/03/17 | 174 | 27/03/18
|  |  | 18:30 |  | 18:30 |  | 10:00 |  | 18:30
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2868.6919 |  | 2291.72 |  | 2196.32
21 | Station Use of BPDB (MKWH) | 94.272 |  | 77.21 |  | 102.94
22 | Net Generation of BPDB (MKWH) | 2774.42 |  | 2214.52 |  | 2093.38
23 | Net Generation of IPP & RPCL (MKWH) | 1603.063 |  | 1131.29 |  | 1120.95
24 | Net Generation of REB (MKWH) | 143.1202 |  | 129.42 |  | 115.46
24 | Net Generation of Rental Power Plant (MKWH) | 700.15 |  | 494.98 |  | 889.11
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5220.7531 |  | 3970.21 |  | 4218.91 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3545.0029 |  | 3002.47 |  | 3314.55 |  | 3545.44 | March-18
27 | Energy Generation by Diesel (MKWH) | 298.9369 |  | 15.65 |  | 100.94 |  | 424.76 | May-17
28 | Energy Generation by Furnace Oil (MKWH) | 1180.533 |  | 754.47 |  | 733.32 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 53.5263 |  | 52.44 |  | 62.45 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.38342 |  | 0.28 |  | - |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 236.6426 |  | 222.1 |  | 110.59 |  | 236.64 | March-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 423.514 |  | 329.45 |  | 412.16 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 76.4884 |  | 73.61 |  | 72.83 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10084 | 19/03/18 | 19:30
Generation Period
| Dhaka | MW | 3611
| Chittagong | MW | 1062
| Comilla | MW | 861
| Mymensingh | MW | 621
| Sylhet | MW | 363
a) | Total supply in East zone | MW | 6518
| Khulna | MW | 1138
| Barisal | MW | 202
| Rajshahi | MW | 1017
| Rangpur | MW | 591
b) | Total supply in West zone | MW | 2948
c) | Total supply in both zone ( a+b) | MW | 9466
Ref: | 27.21.0603.2604.16.084.18.74 | Date: 16/04/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1150 | 31/03/18 | 13:00
| b) Ishurdi end | MW | 160 | 08/03/18 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 370 | 08/03/18 | 16:00
| b) Ishurdi end | MW | 440 | 31/03/18 | 13:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.5869 | 31/03/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 4.6695 | 31/03/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 82.7828
| b) Ishurdi end | MKWH | 2.7265
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 2.6447
| b) Ishurdi end | MKWH | 80.4059
23 | Transmission loss of EWI/ NO-1 | % | 2.87
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 610 | 31/03/18 | 19:30
| b)Serajganj end | MW | 40 | 06/03/18 | 17:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 25 | 06/03/18 | 17:00
| b)Sirajganj end | MW | 580 | 31/03/18 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 9.27 | 31/03/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 8.828 | 31/03/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 182.876
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 180.8018
30 | Transmission loss of EWI /NO-2 | % | 1.134
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Netrakona | 132/33 kV Transformer-T-2 | 2018-03-10 10:50 | 2018-03-10 11:15 | 0:25 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Savar | 132/33 kV Transformers-T-1 | 2018-03-28 06:17 | 2018-03-28 09:14 | 2:57 | T | Tripped showing O/C relay | 70 | 15.1667 | Power interruption 0617: 06:30
| 132/33 kV Transformer-T-2 | 2018-03-28 06:17 | 2018-03-28 06:30 | 0:13 | T
Savar | 132/33 kV Transformers-T-1 & T2 | 2018-03-29 02:52 | 2018-03-29 03:17 | 0:25 | T | Tripped showing E/F relay | 64 | 26.6667 | Power interruption 0617: 06:30
|  |  | Total : | 4:00 |  | Unserved Energy: |  | 41.8333
Dhaka (South) Grid Circle :
Siddhirganj | 132/33 kV Transformer-T-1 | 2018-03-17 21:21 | 2018-03-17 22:47 | 1:26 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T-1 | 2018-03-24 07:57 | 2018-03-24 09:03 | 1:06 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-3 | 2018-03-26 16:09 | 2018-03-26 19:08 | 2:59 | T | Tripped showing O/C relay | 114 | 340.1 | Power interruption
Madertek | 132/33 kV Transformer-T1 | 2018-03-30 03:41 | 2018-03-30 05:12 | 1:31 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformers-TR-2 | 2018-03-30 17:04 | 2018-03-30 18:49 | 1:45 | T | Tripped showing main protection realy | 0 | 0 | No interruption
|  |  | Total : | 8:47 |  | Unserved Energy: |  | 340.1
Chittagong Grid Circle :
Hathazari | 132/33 kV Transformer-T-1 | 2018-03-02 08:59 | 2018-03-02 09:30 | 0:31 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 0:31 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Chatak | 132/33 kV Transformers-T-1 | 2018-03-04 12:27 | 2018-03-04 12:35 | 0:08 | T | Tripped showing E/F & O/C relay | 7 | 0.93333 | Power interruption
Fenchuganj | 132/33 kV Transformers-T-1 | 2018-03-26 19:47 | 2018-03-26 19:51 | 0:04 | T | Tripped showing backup protection relay | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T-1 | 2018-03-27 09:47 | 2018-03-27 09:55 | 0:08 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T-1 | 2018-03-27 13:32 | 2018-03-27 13:35 | 0:03 | T |  | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T-1 | 2018-03-27 20:28 | 2018-03-28 03:06 | 6:38 | T | Tripped showing O/C relay | 11 | 72.9667 | Power interruption 02:31 to 02:42
Sreemongal | 132/33 kV Transformers-T-1 T2 & T3 | 2018-03-28 14:25 | 2018-03-28 14:37 | 0:12 | T | Tripped showing E/F relay | 20 | 4 | Power interruption 02:31 to 02:42
|  |  | Total : | 7:13 |  | Unserved Energy: |  | 77.9
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T-2 | 2018-03-06 11:54 | 2018-03-06 12:04 | 0:10 | T | Tripped showing directional & Lockout relay | 0 | 0 | No interruption
Noapara | 132/33 kV Transformers-T-4 | 2018-03-13 12:21 | 2018-03-13 13:30 | 1:09 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformers-T-1 | 2018-03-22 02:31 | 2018-03-22 02:42 | 0:11 | T | Tripped showing O/C relay | 34 | 6.2333 | Power interruption 02:31 to 02:42
| 132/33 kV Transformers-T-2 | 2018-03-22 02:31 | 2018-03-22 02:45 | 0:14 | T
| 132/33 kV Transformers-T-1 | 2018-03-22 07:36 | 2018-03-22 07:45 | 0:09 | T | Tripped showing O/C relay | 32 | 4.8 | Power interruption 07:36 to 07:45
| 132/33 kV Transformers-T-2 | 2018-03-22 07:36 | 2018-03-22 07:46 | 0:10 | T
Gallamari | 132/33 kV Transformers-T-1 & T2 | 2018-03-22 14:08 | 2018-03-22 14:30 | 0:22 | T | Tripped showing O/C relay | 39 | 14.3 | Power interruption
Mongla | 132/33 kV Transformers-T-1 & T2 | 2018-03-26 17:06 | 2018-03-26 17:15 | 0:09 | T | Tripped showing dist. relay | 22 | 3.3 | Power interruption
|  |  | Total : | 1:19 |  | Unserved Energy: |  | 28.6333
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T-1 | 2018-03-14 06:18 | 2018-03-14 06:25 | 0:07 | T | Tripped showing E/F relay | 20 | 2.3333 | Power interruption
Jessore | 132/33 kV Transformers-T-1 | 2018-03-23 09:32 | 2018-03-23 09:42 | 0:10 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Jessore | 132/33 kV Transformers-T-3 | 2018-03-23 09:36 | 2018-03-23 09:49 | 0:13 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 0:30 |  | Unserved Energy: |  | 2.3333
Bogra Grid Circle:
Palashbari | 132/33 kV Transformers-T-1 | 2018-03-02 09:08 | 2018-03-02 15:35 | 6:27 | E/O | Due to problem with 132 kV breaker | 5 | 32.25 | Power interruption
Purbasadipur | 132/33 kV Transformers-T-3 | 2018-03-26 09:52 | 2018-03-26 09:58 | 0:06 | T | Tripped showing E/F relay | 40 | 4 | Power interruption
Purbasadipur | 132/33 kV Transformers-T-1 | 2018-03-26 09:52 | 2018-03-26 09:55 | 0:03 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformers-T-2 | 2018-03-31 10:20 | 2018-03-31 13:35 | 3:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 9:51 |  | Unserved Energy: |  | 36.25
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 32:11 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2018-03-02 17:30 | 2018-03-03 16:12 | 22:42 | E/O | Due to CB problem | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-03-03 17:58 | 2018-03-03 18:16 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Basila 108 MW 132 kV line | 2018-03-03 17:58 | 2018-03-03 18:37 | 0:39 | T | Tripped showing dist & E/F. relay | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-1 | 2018-03-19 05:09 | 2018-03-19 05:32 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2018-03-19 08:01 | 2018-03-19 08:26 | 0:25 | T | Tripped showing dist. relay | 54 | 22.5 | Power interruption 08:01 to 8:30
| Tongi-Kabirpur 132 kV line-2 | 2018-03-19 08:01 | 2018-03-19 08:30 | 0:29 | T
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2018-03-25 14:14 | 2018-03-25 14:20 | 0:06 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2018-03-25 14:27 | 2018-03-25 21:43 | 7:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2018-03-26 03:35 | 2018-03-26 04:09 | 0:34 | T | Tripped showing DEF relay | 160 | 90.6667 | Power interruption 03:35 to 04:09
| Joydevpur-Ghorashal 132 kV line-2 | 2018-03-26 03:35 | 2018-03-26 04:11 | 0:36 | T
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-03-26 16:43 | 2018-03-26 17:27 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 & 2 | 2018-03-29 20:12 | 2018-03-29 20:22 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2018-03-30 16:55 | 2018-03-30 17:39 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 & 2 | 2018-03-30 16:32 | 2018-03-30 17:12 | 0:40 | T | Tripped showing dist. relay | 10 | 6.6667 | Power interruption
|  |  | Total : | 35:46 |  | Unserved Energy: |  | 119.8333
Dhaka (South) Grid Circle :
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2018-03-07 20:58 | 2018-03-07 21:58 | 1:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Haripur | Haripur-Sonaragon 132 kV line-1 | 2018-03-18 06:37 | 2018-03-18 12:41 | 6:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2018-03-19 09:36 | 2018-03-19 17:17 | 7:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2018-03-23 16:30 | 2018-03-23 16:40 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2018-03-26 03:35 | 2018-03-26 04:05 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-2 | 2018-03-26 03:35 | 2018-03-26 04:08 | 0:33 | T |  | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2018-03-26 17:13 | 2018-03-26 17:35 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-03-27 16:09 | 2018-03-27 22:22 | 6:13 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Rampura | Rampura-Bashundahara 132 kV line-1 | 2018-03-28 12:36 | 2018-03-28 12:48 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2018-03-29 09:46 | 2018-03-29 10:49 | 1:03 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2018-03-30 17:05 | 2018-03-30 17:18 | 0:13 | T | Tripped showing dist. relay | 45 | 9.75 | Power interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-03-30 17:25 | 2018-03-30 19:26 | 2:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-03-30 17:25 | 2018-03-30 17:57 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-2 | 2018-03-31 13:39 | 2018-03-31 15:33 | 1:54 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 28:28 |  | Unserved Energy: |  | 9.75
Chittagong Grid Circle :
Madunaghat | Meghanaghat-TK.chemical 132 kV line | 2018-03-11 14:13 | 2018-03-11 14:52 | 0:39 | T | Tripped showing O/C.& E/F relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2018-03-11 14:15 | 2018-03-11 14:23 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Halishahar | Halishahar-Juldah 132 kV line | 2018-03-11 14:15 | 2018-03-11 14:35 | 0:20 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2018-03-15 09:48 | 2018-03-15 11:28 | 1:40 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Halishahar | Halishahar-Juldah 132 kV line | 2018-03-15 09:04 | 2018-03-15 10:25 | 1:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-03-15 11:28 | 2018-03-15 12:42 | 1:14 | T | Tripped showing dist. relay | 58 | 86.0333 | Power interruption 12:42 to 12:57
| Dohazari-Cox'sbazar 132 kV line-2 | 2018-03-15 11:28 | 2018-03-15 12:57 | 1:29 | T
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2018-03-15 15:51 | 2018-03-15 16:05 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV line | 2018-03-15 15:51 | 2018-03-15 16:32 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
T.K Chemical | T.K Chemical -Madunaghat 132 kV line | 2018-03-15 15:51 | 2018-03-15 16:35 | 0:44 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazari 132 kV line-2 | 2018-03-24 00:50 | 2018-03-24 03:14 | 2:24 | E/O | Due to red hot maintenance | 40 | 96 | Power interruption
|  |  | Total : | 10:54 |  | Unserved Energy: |  | 182.0333
Comilla Grid Circle :
Chowmuhani | Chowmuhani-Chandpur 132 kV line-1 | 2018-03-03 18:42 | 2018-03-03 18:52 | 0:10 | T | Tripped showing O/C. relay | 140 | 7 | Power interruption
| Chowmuhani-Chandpur 132 kV line-2 | 2018-03-03 18:42 | 2018-03-03 18:45 | 0:03 | T
Sylhet | Sylhet-Fenchuganj S/S 132 kV line | 2018-03-10 11:15 | 2018-03-10 11:32 | 0:17 | T | Tripped showing O/C. relay | 40 | 11.3333 | Power interruption
Fenchuganj | Fenchuganj-Fenchugan P/S 132 kV line | 2018-03-17 02:34 | 2018-03-17 02:50 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2018-03-23 09:50 | 2018-03-23 10:15 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-03-25 10:02 | 2018-03-25 10:17 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2018-03-25 14:25 | 2018-03-25 17:29 | 3:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2018-03-25 14:27 | 2018-03-25 21:43 | 7:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2018-03-26 17:10 | 2018-03-26 17:32 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2018-03-26 17:51 | 2018-03-26 18:40 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(S) | Comilla(S)-Surjanagar 132 kV line-1 & 2 | 2018-03-26 18:18 | 2018-03-26 18:45 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.baria 132 kV line-1 | 2018-03-26 18:18 | 2018-03-26 18:25 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-03-29 01:41 | 2018-03-29 03:03 | 1:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 | 2018-03-29 05:25 | 2018-03-29 05:42 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2018-03-29 09:07 | 2018-03-29 09:19 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comiila(N) 230 kV line-1 | 2018-03-30 16:33 | 2018-03-30 16:40 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Comila(N) 132 kV line-1 | 2018-03-30 17:50 | 2018-03-30 18:12 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Chandpur-Comila(N) 132 kV line-2 | 2018-03-30 17:50 | 2018-03-31 14:38 | 20:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 36:39 |  | Unserved Energy: |  | 18.3333
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Goalpara | Goalpara-Bagerhat 132 kV line-2 | 2018-03-11 07:41 | 2018-03-11 10:30 | 2:49 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-03-11 12:56 | 2018-03-11 13:05 | 0:09 | T | Tripped showing dist.E/F relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-03-22 02:50 | 2018-03-22 03:10 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-03-25 07:28 | 2018-03-25 12:20 | 4:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  |  | 2:49 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jessore | Jessore-Jhenidah 132 kV line-1 | 2018-03-16 06:34 | 2018-03-16 07:02 | 0:28 | T | Tripped showing dist. relay | 109 | 50.8667 | Power interruption 06:34 to 7:02
| Jessore-Jhenidah 132 kV line-2 | 2018-03-16 06:34 | 2018-03-16 07:03 | 0:29 | T
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2018-03-31 05:00 | 2018-03-31 07:52 | 2:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2018-03-31 04:59 | 2018-03-31 07:52 | 2:53 | T | Tripped showing O/V relay | 673 | 1940.4833 | Power interruption
|  |  | Total : | 6:42 |  | Unserved Energy: |  | 1991.35
Bogra Grid Circle :
Barakupuria | Barakupuria-Saidpur 132 kV line-2 | 2018-03-16 08:15 | 2018-03-16 11:31 | 3:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-03-26 09:53 | 2018-03-26 09:54 | 0:01 | E/O | Due to Oil leakage | 145 | 2.4167 | Power interruption
Naogaon | Naogaon-Niamatpur 132 kV line | 2018-03-31 13:58 | 2018-03-31 14:05 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 3:24 |  | Unserved Energy: |  | 2.4167
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2018-03-12 05:34 | 2018-03-12 06:02 | 0:28 | T | Tripped showing pilot wire protection relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2018-03-13 03:07 | 2018-03-13 03:35 | 0:28 | T |  | 0 | 0 | No interruption
|  |  | Total : | 0:28 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 125:10 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV Transformers-T-1 & T2 | 2018-03-02 08:12 | 2018-03-02 18:12 | 10:00 | S/O | Due to replacement work | 90 | 900 | Power interruption 18:12 to 10:00
| 132/33 kV Transformers-T-3 | 2018-03-02 08:12 | 2018-03-02 18:40 | 10:28 | S/O
Bibiyana | 400/230 kV Transformers-T-R-2 | 2018-03-13 10:02 | 2018-03-13 17:15 | 7:13 | S/O | Due to project work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus-A | 2018-03-18 08:30 | 2018-03-18 14:27 | 5:57 | S/O | Due to maintenance work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T-2 | 2018-03-31 08:17 | 2018-03-31 11:50 | 3:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 37:11 |  | Unserved Energy: |  | 900
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformer-T-1 | 2018-03-01 10:52 | 2018-03-01 13:12 | 2:20 | S/O | Due to temperature high | 0 | 0 | No interruption
| 230/132 kV Transformer-T-3 | 2018-03-01 10:54 | 2018-03-01 14:04 | 3:10 | S/O | Due to decrease the bus temp. | 0 | 0 | No interruption
| 132/33 kV Transformer-T-5 | 2018-03-01 13:13 | 2018-03-01 14:17 | 1:04 | S/O | Due to 132 kV side CT temp.high | 0 | 0 | No interruption
Rampura | 230 kV bus-1 | 2018-03-03 08:11 | 2018-03-03 11:19 | 3:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | 230 kV bus--A | 2018-03-07 15:52 | 2018-03-07 20:53 | 5:01 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2018-03-13 06:40 | 2018-03-13 08:12 | 1:32 | S/O | Due to maintenance work | 30 | 7.6667 | Power interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2018-03-13 22:48 | 2018-03-16 21:47 | 70:59 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T-2 | 2018-03-18 11:51 | 2018-03-18 12:49 | 0:58 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shitalakhya | 132/33 kV Transformer-T3 | 2018-03-23 09:19 | 2018-03-23 09:55 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV bus--1 | 2018-03-24 09:04 | 2018-03-24 13:57 | 4:53 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-Tr-1 | 2018-03-25 07:45 | 2018-03-25 11:32 | 3:47 | S/O | Due to 132 kV under ground cable replacement | 0 | 0 | No interruption
| 230/132 kV Transformer-Tr-3 | 2018-03-25 12:45 | 2018-03-25 14:06 | 1:21 | S/O |  | 0 | 0 | No interruption
Meghnaghat | 230 kV bus--1 | 2018-03-25 09:26 | 2018-03-25 14:40 | 5:14 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 132 kV bus | 2018-03-27 10:30 | 2018-03-27 11:02 | 0:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T3 | 2018-03-27 12:08 | 2018-03-27 13:15 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T2 | 2018-03-31 08:47 | 2018-03-31 11:33 | 2:46 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T1 | 2018-03-31 09:43 | 2018-03-31 16:20 | 6:37 | S/O | Due to project work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T1 | 2018-03-31 11:06 | 2018-03-31 15:01 | 3:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 119:00 |  | Unserved Energy: |  | 7.6667
Chittagong Grid Circle :
Chandraghona | 132/33 kV Transformer-T-2 | 2018-03-11 08:02 | 2018-03-16 17:33 | 129:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformers-T1 | 2018-03-16 08:21 | 2018-03-16 10:02 | 1:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-03-16 10:05 | 2018-03-16 11:58 | 1:53 |  |  | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformers-T1 | 2018-03-17 08:10 | 2018-03-19 17:09 | 56:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T2 | 2018-03-23 08:27 | 2018-03-23 10:56 | 2:29 | S/O | Due to D/W work | 0 | 0 | No interruption
BSRM | 230/132 kV Transformer-T2 | 2018-03-27 10:51 | 2018-03-27 13:27 | 2:36 | S/O | Due to annual maintenance work | 0 | 0 | No interruption
|  |  | Total : | 195:09 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Chatak | 132/33 kV Transformer-T3 | 2018-03-01 09:22 | 2018-03-01 15:05 | 5:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla (S) | 132 kV bus | 2018-03-30 06:36 | 2018-03-30 08:00 | 1:24 | S/O | Due to C/M work | 30 | 42 | Power interruption
|  |  | Total | 7:07 |  | Unserved Energy : |  | 42
Khulna Grid Circle :
Khulna(S) | 230/132 kV Transformers-TR1 | 2018-03-06 12:29 | 2018-03-06 13:10 | 0:41 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2018-03-07 09:06 | 2018-03-07 11:50 | 2:44 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2018-03-07 09:16 | 2018-03-07 18:28 | 9:12 | S/O | Due to changing of PRD | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2018-03-08 00:14 | 2018-03-08 03:20 | 3:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 | 2018-03-09 06:16 | 2018-03-09 11:09 | 4:53 | S/O | Due to project work | 30 | 146.5 | Power interruption
| 132/33 kV Transformer-T3 | 2018-03-09 06:16 | 2018-03-09 11:10 | 4:54 | S/O
Madaripur | 132/33 kV Transformer-T2 | 2018-03-10 06:06 | 2018-03-10 12:54 | 6:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2018-03-10 07:14 | 2018-03-10 19:28 | 12:14 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barisal | 230/132 kV Transformer-TR2 | 2018-03-23 08:37 | 2018-03-25 11:04 | 50:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | 132/33 kV Transformers-T1 | 2018-03-23 10:47 | 2018-03-23 10:55 | 0:08 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2018-03-23 10:56 | 2018-03-23 11:31 | 0:35 | S/O |  | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2018-03-24 06:25 | 2018-03-24 12:41 | 6:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 &T2 | 2018-03-25 11:19 | 2018-03-25 12:24 | 1:05 | S/O | Due to replacement work | 0 | 0 | No interruption
Bagerhat | 132 kV bus | 2018-03-27 09:21 | 2018-03-27 11:42 | 2:21 | S/O | Due to D/W work | 60 | 141 | Power interruption
Bagerhat | 132/33 kV Transformers-T1 T 2 | 2018-03-27 09:16 | 2018-03-27 15:49 | 6:33 | S/O | Due to D/W work | 46 | 301.3 | Power interruption
|  |  | Total : | 111:57 |  | Unserved Energy : |  | 588.8
HVDC Grid Circle :
Bheramara | 132 kV Bus-A | 2018-03-09 08:02 | 2018-03-09 11:18 | 3:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ishurdi | 230 kV bus-2 | 2018-03-10 09:25 | 2018-03-10 13:20 | 3:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T-1 | 2018-03-16 07:31 | 2018-03-16 16:20 | 8:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T-1 | 2018-03-27 07:06 | 2018-03-30 22:03 | 86:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformer-T-1 | 2018-03-28 08:18 | 2018-03-28 08:38 | 0:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 103:17 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Barapukuria | 132 kV bus-1 | 2018-03-01 09:00 | 2018-03-01 12:00 | 3:00 | S/O | Due to D/M work | 0 | 0 | No interruption
Bogra | 132 kV main bus | 2018-03-01 10:28 | 2018-03-01 15:58 | 5:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barapukuria | 132 kV bus-2 | 2018-03-01 12:25 | 2018-03-01 15:40 | 3:15 | S/O | Due to D/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2018-03-03 09:49 | 2018-03-07 22:14 | 108:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barakukuria | 132 kV main bus | 2018-03-14 10:05 | 2018-03-14 18:20 | 8:15 | S/O | Due to project work | 0 | 0 | No interruption
Barakukuria | 230/132 kV Transformer-T02 | 2018-03-16 08:30 | 2018-03-16 15:28 | 6:58 | S/O | Due to project work | 0 | 0 | No interruption
Natore | 132 kV main bus | 2018-03-30 07:06 | 2018-03-30 09:38 | 2:32 | S/O | Due to C/M work | 70 | 177.3333 | Power interruption
|  |  | Total : | 137:55 |  | Unserved Energy : |  | 177.3333
Others :
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 711:36 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | Jamalpur-Mymensingh 132 kV line | 2018-03-03 15:55 | 2018-03-03 17:20 | 1:25 | S/O | Due to protection checking | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2018-03-12 10:13 | 2018-03-12 11:41 | 1:28 | S/O | Due to protection test | 0 | 0 | No interruption
| Jamalpur-Mymensingh 132 kV line-2 | 2018-03-12 08:21 | 2018-03-12 10:09 | 1:48 | S/O |  | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-1 | 2018-03-18 08:30 | 2018-03-18 14:44 | 6:14 | S/O | Due to maintenance work | 40 | 245.3333 | Power interruption 8:30 to 14:38
| Kishoreganj-Mymensingh 132 kV line-2 | 2018-03-18 08:30 | 2018-03-18 14:38 | 6:08 | S/O | Due to maintenance work
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2018-03-19 10:13 | 2018-03-19 16:22 | 6:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamari 230 kV line-2 | 2018-03-22 12:20 | 2018-03-22 14:42 | 2:22 | S/O | Due to protection test | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2018-03-28 09:35 | 2018-03-28 13:14 | 3:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 29:13 |  | Unserved Energy: |  | 245.3333
Dhaka (South) Grid Circle :
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-03-01 13:11 | 2018-03-02 12:29 | 23:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | Haripur-Narshingdi 132 kV line | 2018-03-08 07:30 | 2018-03-08 11:16 | 3:46 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Meghanaghat 230 kV line-1 | 2018-03-11 13:22 | 2018-03-11 15:13 | 1:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-03-11 06:42 | 2018-03-11 07:46 | 1:04 | S/O | Due to replacement work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2018-03-12 07:20 | 2018-03-12 08:15 | 0:55 | S/O | Due to temperature at R-phase line insulator | 0 | 0 | No interruption
| Bashundhara-Rampura 132 kV line-2 | 2018-03-12 08:50 | 2018-03-12 09:50 | 1:00 | S/O |  | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2018-03-12 14:55 | 2018-03-12 17:55 | 3:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Sikalbaha 132 kV line-1 | 2018-03-13 08:18 | 2018-03-13 14:55 | 6:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Madanganj | Madanganj-Haripur 132 kV line | 2018-03-15 13:20 | 2018-03-15 16:30 | 3:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 132 kV line-4 | 2018-03-16 06:12 | 2018-03-16 21:37 | 15:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Desh energy 132 kV line | 2018-03-16 08:26 | 2018-03-16 17:32 | 9:06 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 132 kV line-4 | 2018-03-17 06:25 | 2018-03-18 12:32 | 30:07 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2018-03-18 09:52 | 2018-03-18 12:25 | 2:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-03-18 09:52 | 2018-03-18 11:26 | 1:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur S/S-Haripur P/S 132 kV line-1 | 2018-03-19 11:12 | 2018-03-19 17:05 | 5:53 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2018-03-20 07:29 | 2018-03-22 11:52 | 52:23 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2018-03-21 06:22 | 2018-03-21 07:01 | 0:39 | S/O | Due to removing bird nest | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line-2 | 2018-03-21 07:18 | 2018-03-21 08:08 | 0:50 | S/O |  | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 400 kV line-3 | 2018-03-23 06:36 | 2018-03-24 02:34 | 19:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Hasnabad 230 kV line-1 | 2018-03-27 10:57 | 2018-03-27 19:32 | 8:35 | S/O | Due to D/M work | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2018-03-28 10:02 | 2018-03-28 11:14 | 1:12 | S/O | Due to D/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-03-29 07:43 | 2018-03-29 09:42 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2018-03-30 06:30 | 2018-03-30 08:07 | 1:37 | S/O | Due to C/M work | 40 | 64.6667 | Power interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-03-31 08:38 | 2018-03-31 12:33 | 3:55 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 200:27 |  | Unserved Energy: |  | 64.6667
Chittagong Grid Circle :
Halishahar | Halishahar-Juldah 132 kV line | 2018-03-01 08:14 | 2018-03-01 20:30 | 12:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 & 2 | 2018-03-03 05:52 | 2018-03-03 07:12 | 1:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulshi | Khulshi-Modern steel 132 kV line | 2018-03-07 10:10 | 2018-03-07 11:15 | 1:05 | S/O | Due to relay test | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-03-07 08:45 | 2018-03-07 15:22 | 6:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-03-08 09:20 | 2018-03-08 14:21 | 5:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 & 2 | 2018-03-11 13:58 | 2018-03-11 14:35 | 0:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2018-03-14 10:44 | 2018-03-14 10:54 | 0:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 27:06 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Fenchuganj S/S | Fenchuganj S/S-Fenchuganj P/S 132 kV line-2 | 2018-03-05 08:10 | 2018-03-05 14:32 | 6:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-1 | 2018-03-09 10:25 | 2018-03-16 18:04 | 175:39 | S/O | Due to project work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2018-03-12 09:53 | 2018-03-12 23:25 | 13:32 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line | 2018-03-12 15:21 | 2018-03-12 15:33 | 0:12 | S/O | Due to CT ratio checking | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-2 | 2018-03-15 10:29 | 2018-03-15 13:11 | 2:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-03-18 08:30 | 2018-03-18 14:27 | 5:57 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2018-03-23 06:15 | 2018-03-23 19:23 | 13:08 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line-2 | 2018-03-23 06:15 | 2018-03-23 18:50 | 12:35 | S/O |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 | 2018-03-28 06:41 | 2018-03-28 20:06 | 13:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Ashuganj 230 kV line-1 | 2018-03-28 14:40 | 2018-03-29 17:23 | 26:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 270:15 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barisal | Barisal-Barisal P/S 132 kV line | 2018-03-27 12:04 | 2018-03-27 15:10 | 3:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 3:06 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Bottail 132 kV line-1 | 2018-03-09 08:17 | 2018-03-09 12:55 | 4:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-1 | 2018-03-09 07:33 | 2018-03-09 18:01 | 10:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2018-03-25 07:48 | 2018-03-25 21:05 | 13:17 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 28:23 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Natore 132 kV line-2 | 2018-03-01 11:04 | 2018-03-01 15:58 | 4:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Bogra new 132 kV line-1 | 2018-03-03 11:00 | 2018-03-03 14:11 | 3:11 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2018-03-10 10:30 | 2018-03-10 12:55 | 2:25 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-03-16 08:55 | 2018-03-16 12:37 | 3:42 | S/O | Due to project work | 0 | 0 | No interruption
Amnura | Amnura-Cnawabganj 132 kV line | 2018-03-16 14:50 | 2018-03-16 17:04 | 2:14 | S/O | Due to project work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line-1 | 2018-03-19 09:25 | 2018-03-19 12:39 | 3:14 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 19:40 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-1 | 2018-03-23 08:12 | 2018-03-23 09:40 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikinagar | Manikinagar-Baghabhaban 132 kV line-2 | 2018-03-31 09:17 | 2018-03-31 12:58 | 3:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1:28 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 551:53 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March' 2018
| Area | Previous Month (February 2018) |  |  |  | Current Month (March 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 11 | 1 | 21 | 33 | 16 | 2 | 13 | 31
2 | Dhaka (South) Grid Circle. | 18 | 2 | 18 | 38 | 13 | 6 | 42 | 61
3 | Chittagong Grid Circle. | 1 | 3 | 17 | 21 | 9 | 3 | 12 | 24
4 | Comilla Grid Circle. | 15 | 2 | 28 | 45 | 24 | - | 12 | 36
5 | Khulna Grid Circle. | 6 | 2 | 12 | 20 | 11 | 1 | 16 | 28
6 | Bheramara HVDC Grid Circle | 12 | 7 | 5 | 24 | 7 |  | 8 | 15
7 | Bogra Grid Circle. | 3 | 6 | 3 | 12 | 3 | 4 | 13 | 20
8 | Others | 1 | - | 1 | 2 | 2 | - | 2 | 4
9 | Total | 67 | 23 | 105 | 195 | 85 | 16 | 118 | 219
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March' 2018
| Area | Previous Month (February 2018) |  |  |  | Current Month (March 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 476.27 | - | - | 476.27 | 161.66 | - | 1145.33 | 1306.99
2 | Dhaka ( South) grid circle | 603.32 | - | - | 603.32 | 349.85 | - | 72.34 | 422.19
3 | Chittagong grid circle. | - | 36.27 | 9.75 | 46.02 | 182.03 | - | - | 182.03
4 | Comilla grid circle. | 76.33 | - | - | 76.33 | 96.23 | - | 42 | 138.23
5 | Khulna grid circle. | 2.02 | 19.17 | - | 21.19 | 28.63 | - | 588.8 | 617.43
6 | Bheramara HVDC grid circle | 60.6 | 61.33 | - | 121.93 | 1993.68 | - | - | 1993.68
7 | Bogra grid circle. | 14 | 258.34 | - | 272.34 | 4 | 34.67 | 177.33 | 216
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 1232.54 | 375.11 | 9.75 | 1617.4 | 2816.08 | 34.67 | 2025.8 | 4876.55
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 2 | 1 | 3 | 1 | - | 2 | 941.83
2 | Dhaka (South) | 5031.6 | 1 | 1 | 2 | - | - | 2 | 347.77
3 | Chittagong | 2042 | - | - | - | - | - | - | -
4 | Khulna | 2434 | 4 | 3 | 2 | 4 | - | 3 | 617.43
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | 1 | - | - | 2.33
6 | Bogra | 3145.6 | 2 | 1 | 3 | 1 |  | 2 | 213.58
7 | Comilla | 2981 | 3 | 1 | 4 | 2 | - | 2 | 119.9
| Total | 23365.5 | [6 empty] | 2242.84
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chittagong | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.99% | [6 empty] | Information Management Division
7 | Comilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 3 | 1 | 4 | 1 | 2 | 1 | 365.16
2 | Dhaka (South) | 990.29 |  | 1 | 1 | 2 | 1 | - | 1 | 74.42
3 | Chittagong | 917 | 20+9(Partial) | 2 | - | 2 | - | - | 2 | 182.03
4 | Khulna | 1238.4 | 21 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 598.7 |  | 2 |  | 2 | 1 | - | 1 | 1991.35
6 | Bogra | 1803.3 | 38 | 1 | - | 1 | 1 | 1 |  | 2.42
7 | Comilla | 1648.16 | 17 | 2 | - | 2 | 2 | - | - | 18.3333
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 2633.7133
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 9991%
2 | Dhaka (South) | 99.94%
3 | Chittagong | 99.95%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogra | 99.99% | [7 empty] | Information Management Division
7 | Comilla | 99.81% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
March | 25 | - | 1 | 6hr27 min | 1 | 1min | - | - | 1 | 2hr 50 min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:March' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Savar | 1 | 2:57 | 70 | 15.1667 | Due to tripping of 132/33 kV Transformer T1
Mymensingh | 1 | 0:25 | 64 | 26.6667 | Due to tripping of 132/33 kV Transformers T 1 & T2
Tongi | 2 | 0:25 | 54 | 22.5 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
|  | 0:40 | 10 | 6.6667 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
Joydevpur | 1 | 0:34 | 160 | 90.6667 | Due to tripping of Ghorashal-Joydevpur 132 kV line-1 & 2
Kabirpur | 1 | 10:00 | 90 | 900 | Due to S/D of 132/33 kV Transformers T 1 & T2
Kishoreganj | 1 | 6:08 | 40 | 245.3333 | Due to S/D of Kishoreganj-Mymensingh 132 kV line-1 & 2
Shyampur | 1 | 2:59 | 114 | 340.1 | Due to tripping of Haripur-Bhulta 132 kV line
Siddhirganj | 1 | 1:12 | 30 | 7.6667 | Due to S/D of 132/33 kV Transformer T2
Rampura | 1 | 1:37 | 40 | 64.6667 | Due to S/D of Rampura-Ullon 132 kV line-1
Hasnabad | 1 | 0:13 | 45 | 9.75 | Due to tripping of Hasnabad-Lalbagh 132 kV line
Dohazari | 1 | 1:29 | 58 | 86.0333 | Due to tripping of Dohazari-Cox'sbazar 132 kV line-1 & 2
Baraulia | 1 | 2:24 | 40 | 96 | Due to red-hot maintenance of Baraulia-Hathazari 132 kV line-2
Chatak | 2 | 0:08 | 7 | 0.93333 | Due to tripping of 132/33 kV Transformer T1
|  | 6:38 | 11 | 72.9667 | Due to tripping of 132/33 kV Transformer T1
Sreemongal | 1 | 0:12 | 20 | 4 | Due to tripping of 132/33 kV Transformers T1, T2 & T3
Chowmuhani | 1 | 0:03 | 140 | 7 | Due to tripping of Chowmuhani-Chandpur 132 kV line-1 & 2
Sylhet | 1 | 0:17 | 40 | 11.3333 | Due to tripping of Sylhet-Fenchuganj 132 kV line
Comiila(S) | 1 | 1:24 | 30 | 42 | Due to S/D of 132 kV bUs
Gallamari | 3 | 0:11 | 34 | 6.2333 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:09 | 32 | 4.8 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:22 | 39 | 14.3 | Due to tripping of 132/33 kV Transformers T1 & T2
Mongla | 1 | 0:09 | 22 | 3.3 | Due to tripping of 132/33 kV Transformers T1 & T2
Bottail | 1 | 0:07 | 20 | 2.3333 | Due to tripping of 132/33 kV Transformer T1
Ishurdi | 1 | 2:53 | 673 | 1940.4833 | Due to tripping of Ishurdi- Bheramara 132 kV line
Jessore | 1 | 0:28 | 109 | 50.8667 | Due to tripping of Jessore- Jhenidah 132 kV line
Madaripur | 1 | 4:53 | 30 | 146.5 | Due to S/D of 132/33 kV Transformer T1
Bagerhat | 2 | 2:21 | 60 | 141 | Due to S/D of 132 kV Bus
|  | 6:33 | 46 | 301.3 | Due to S/D of 132/33 kV Transformers T1 & T2
Purbasadipur | 1 | 6:27 | 5 | 32.25 | Due to 132/33 kV Breaker problem
Palashabri | 1 | 0:06 | 40 | 4 | Due to tripping of 132/33 kV Transformer T3
Saidpur | 1 | 0:01 | 145 | 2.4167 | Due to Oil leakage of Saidpur-Purbasadipur 132 kV line-1
Natore | 1 | 2:32 | 70 | 177.3333 | Due to S/D of 132 kV Bus
| Total unserved energy : |  |  | 4876.5667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2018
\ | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 125 | 18 | 2018-03-01 | 16:00
2 | Munsiganj | 106 | 25 | 2018-03-01 | 22:00
3 | Megnaghat | 74 | 18 | 2018-03-01 | 19:00
4 | Shyampur | 164 | 21 | 2018-03-01 | 23:00
5 | Bhulta | 169 | 24 | 2018-03-01 | 19:30
6 | Madanganj | 52 | 24 | 2018-03-01 | 20:00
7 | Shitalakhya | 113 | 15 | 2018-03-01 | 18:30
8 | Rahim steel | 22 | 25 | 2018-03-01 | 11:00
9 | Matuail | 94 | 12 | 2018-03-01 | 12:00
10 | Ghorasal | 79 | 21 | 2018-03-01 | 22:00
11 | Narsingdi | 112 | 15 | 2018-03-01 | 19:00
12 | Haripur (SBU) | 97 | 19 | 2018-03-01 | 19:30
13 | Ullon | 84 | 28 | 2018-03-01 | 20:00
14 | Hasnabad | 187 | 15 | 2018-03-01 | 21:00
15 | Magbazar | 121 | 22 | 2018-03-01 | 12:00
16 | Maniknagar | 86 | 12 | 2018-03-01 | 15:00
17 | Bangabhaban | 40 | 25 | 2018-03-01 | 15:00
18 | Narinda | 84 | 14 | 2018-03-01 | 19:30
19 | Dhanmondi | 162 | 25 | 2018-03-01 | 13:00
20 | Lalbag | 91 | 5 | 2018-03-01 | 13:00
21 | Madartek | 46 | 29 | 2018-03-01 | 22:00
22 | Mirpur | 104 | 4 | 2018-03-01 | 19:00
23 | Kalyanpur | 131 | 18 | 2018-03-01 | 18:00
24 | Gulshan | 120 | 25 | 2018-03-01 | 13:00
25 | Uttara | 82 | 6 | 2018-03-01 | 19:00
26 | Kamrangirchar | 76 | 18 | 2018-03-01 | 12:00
27 | Savar | 154 | 25 | 2018-03-01 | 19:30
28 | Bhasantec | 152 | 29 | 2018-03-01 | 18:30
29 | Agargaon | 56 | 9 | 2018-03-01 | 18:30
30 | Satmosjid | 89 | 28 | 2018-03-01 | 19:30
31 | Tongi | 136 | 21 | 2018-03-01 | 15:00
32 | Kabirpur | 205 | 29 | 2018-03-01 | 15:00
33 | Basundhara | 130 | 12 | 2018-03-01 | 18:30
34 | Manikganj | 104 | 24 | 2018-03-01 | 20:00
35 | Joydevpur | 210 | 6 | 2018-03-01 | 18:00
36 | New Tongi | 116 | 15 | 2018-03-01 | 15:00
37 | Kodda | 229 | 19 | 2018-03-01 | 19:30
38 | Tangail | 168 | 16 | 2018-03-01 | 19:00
39 | Mymensing | 207 | 17 | 2018-03-01 | 18:30
40 | Kishorganj | 85 | 15 | 2018-03-01 | 18:30
41 | Netrokona | 84 | 12 | 2018-03-01 | 19:30
42 | Jamalpur | 96 | 9 | 2018-03-01 | 19:00
43 | Sherpur | 78 | 23 | 2018-03-01 | 18:30
44 | Srimongal | 38 | 12 | 2018-03-01 | 19:30
45 | Shahjibazar | 99 | 24 | 2018-03-01 | 19:00
46 | Fenchuganj | 46 | 25 | 2018-03-01 | 20:00
47 | Khulawara | 35 | 24 | 2018-03-01 | 19:30
48 | Sylhet | 146 | 24 | 2018-03-01 | 19:00
49 | Chatak | 50 | 24 | 2018-03-01 | 20:00
50 | Comilla (S) | 172 | 27 | 2018-03-01 | 20:00
51 | Comilla(N) | 93 | 24 | 2018-03-01 | 18:30
52 | Chandpur | 116 | 26 | 2018-03-01 | 18:30
53 | Feni | 197 | 18 | 2018-03-01 | 21:00
54 | Chowmuhani | 178 | 18 | 2018-03-01 | 21:00
55 | Ashuganj | 56 | 24 | 2018-03-01 | 19:30
56 | Daudkandi | 100 | 15 | 2018-03-01 | 21:00
57 | B.Baria | 119 | 27 | 2018-03-01 | 19:30
58 | Madanhat | 66 | 18 | 2018-03-01 | 21:00
59 | Hathazari | 99 | 27 | 2018-03-01 | 21:00
60 | Khulshi | 200 | 6 | 2018-03-01 | 15:00
61 | Halishahar | 143 | 20 | 2018-03-01 | 15:00
62 | Baraulia | 150 | 18 | 2018-03-01 | 01:00
63 | Sikalbaha | 130 | 24 | 2018-03-01 | 18:30
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
64 | Dohazari | 88 | 19 | 2018-03-01 | 20:00
65 | Cox'sbazar | 84 | 18 | 2018-03-01 | 19:00
66 | Chandraghona | 33 | 27 | 2018-03-01 | 20:00
67 | Kaptai | 7.2 | 30 | 2018-03-01 | 20:00
68 | A. Khaer Stl. | 22 | 18 | 2018-03-01 | 22:00
69 | Bakulia | 104 | 18 | 2018-03-01 | 19:00
70 | Julda | 22 | 31 | 2018-03-01 | 21:00
71 | TK chemical | 0 | 1 | 2018-03-01 | 19:30
72 | Modern Steel | 27 | 29 | 2018-03-01 | 20:00
73 | Shahmirpur | 29 | 25 | 2018-03-01 | 02:00
74 | Abul Khair 230 | 212 | 5 | 2018-03-01 | 4:00
75 | BSRM | 111 | 3 | 2018-03-01 | 18:30
76 | Goalpara | 42 | 21 | 2018-03-01 | 19:30
77 | Central s/s | 81 | 14 | 2018-03-01 | 21:00
78 | Noapara | 88 | 19 | 2018-03-01 | 19:00
79 | Jessore | 124 | 29 | 2018-03-01 | 23:00
80 | Jhenida | 88 | 15 | 2018-03-01 | 20:00
81 | Bottail | 110 | 29 | 2018-03-01 | 21:00
82 | G.K Project | 50 | 8 | 2018-03-01 | 19:00
83 | Faridpur | 126 | 15 | 2018-03-01 | 19:30
84 | Madaripur | 116 | 15 | 2018-03-01 | 21:00
85 | Gopalganj | 75 | 15 | 2018-03-01 | 19:00
86 | Bagerhat | 72 | 4 | 2018-03-01 | 19:30
87 | Mongla | 40 | 14 | 2018-03-01 | 12:00
88 | Satkhira | 84 | 18 | 2018-03-01 | 19:30
89 | Gallamari | 48 | 27 | 2018-03-01 | 18:30
90 | Magura | 46 | 15 | 2018-03-01 | 19:30
91 | Chuadanga | 76 | 14 | 2018-03-01 | 19:00
92 | Barisal | 114 | 25 | 2018-03-01 | 18:30
93 | Patuakhali | 76 | 25 | 2018-03-01 | 19:00
94 | Bhandaria | 40 | 15 | 2018-03-01 | 19:00
95 | Ishurdi | 46 | 22 | 2018-03-01 | 19:00
96 | Ruppur Paromanobik | 1 | 1 | 2018-03-01 | 1:00
97 | Natore | 107 | 25 | 2018-03-01 | 20:00
98 | Bogra | 205 | 17 | 2018-03-01 | 19:00
99 | Noagaon | 108 | 28 | 2018-03-01 | 20:00
100 | Rajshahi | 133 | 27 | 2018-03-01 | 21:00
101 | C.Nawabganj | 68 | 23 | 2018-03-01 | 20:00
102 | Amnura | 34 | 16 | 2018-03-01 | 19:00
103 | Pabna | 94 | 13 | 2018-03-01 | 19:00
104 | Shahjadpur | 93 | 29 | 2018-03-01 | 20:00
105 | Serajganj | 84 | 20 | 2018-03-01 | 20:00
106 | Niyamatpur | 93 | 28 | 2018-03-01 | 20:00
107 | Joypurhat | 49 | 28 | 2018-03-01 | 21:00
108 | Rangpur | 119 | 18 | 2018-03-01 | 19:30
109 | Lalmonirhat | 83 | 16 | 2018-03-01 | 19:30
110 | Saidpur | 109 | 14 | 2018-03-01 | 19:00
111 | Purbasadipur | 85 | 26 | 2018-03-01 | 19:30
112 | Thakurgaon | 65 | 22 | 2018-03-01 | 19:00
113 | Palashbari | 93 | 19 | 2018-03-01 | 19:00
114 | Barapukuria | 51 | 28 | 2018-03-01 | 20:00
115 | Panchagar | 39 | 14 | 2018-03-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 3696 | 24.03.18 | 19:00
Chittagong | 1111 | 14.03.18 | 24:00
Khulna | 1157 | 18.03.18 | 20:00
Rajshahi | 1025 | 13.03.18 | 19:30
Comilla | 884 | 15.03.18 | 21:00
Mymensingh | 679 | 11.03.18 | 19:00
Sylhet | 396 | 24.03.18 | 20:00
Barisal | 224 | 25.03.18 | 20:00
Rangpur | 603 | 14.03.18 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 413 | 31 | 2018-03-01 | 07:00 | 368 | 26 | 2018-03-01 | 12:00
2 | Bheramara | 400 | 417 | 3 | 2018-03-01 | 4:00 | 393 | 21 | 2018-03-01 | 19:30
3 | Kaliakoir | 400 | 396 | 31 | 2018-03-01 | 07:00 | 344 | 29 | 2018-03-01 | 18:30
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 31 | 2018-03-01 | 07:00 | 220 | 28 | 2018-03-01 | 9:00
2 | Ishurdi | 230 | 250 | 31 | 2018-03-01 | 4:00 | 213 | 23 | 2018-03-01 | 21:00
3 | Ashuganj | 230 | 244 | 31 | 2018-03-01 | 4:00 | 225 | 24 | 2018-03-01 | 15:00
4 | Serajganj | 230 | 248 | 31 | 2018-03-01 | 6:00 | 202 | 31 | 2018-03-01 | 18:30
5 | Baghabari | 230 | 253 | 31 | 2018-03-01 | 6:00 | 208 | 24 | 2018-03-01 | 16:00
6 | Barapukuria | 230 | 240 | 12 | 2018-03-01 | 23:00 | 220 | 14 | 2018-03-01 | 10:00
7 | Bogra | 230 | 264 | 31 | 2018-03-01 | 06':00 | 200 | 31 | 2018-03-01 | 18:30
8 | Khulna South | 230 | 238 | 23 | 2018-03-01 | 13'00 | 214 | 2 | 2018-03-01 | 7:00
9 | Rampura | 230 | 233 | 31 | 2018-03-01 | 07:00 | 212 | 29 | 2018-03-01 | 16:00
10 | Haripur | 230 | 235 | 31 | 2018-03-01 | 7:00 | 215 | 27 | 2018-03-01 | 11:00
11 | Hasnabad | 230 | 236 | 31 | 2018-03-01 | 7:00 | 214 | 11 | 2018-03-01 | 14:00
12 | Aminbazar | 230 | 242 | 31 | 2018-03-01 | 07:00 | 215 | 29 | 2018-03-01 | 16:00
13 | Tongi | 230 | 232 | 31 | 2018-03-01 | 7:00 | 203 | 29 | 2018-03-01 | 15:00
14 | Comilla (N) | 230 | 236 | 31 | 2018-03-01 | 9:00 | 215 | 29 | 2018-03-01 | 13:00
15 | Hathazari | 230 | 230 | 30 | 2018-03-01 | 20:00 | 203 | 1 | 2018-03-01 | 15:00
16 | Megnaghat | 230 | 242 | 31 | 2018-03-01 | 7:00 | 218 | 25 | 2018-03-01 | 24:00
17 | Fenchuganj | 230 | 240 | 31 | 2018-03-01 | 7:00 | 218 | 5 | 2018-03-01 | 12:00
18 | Siddhirganj | 230 | 240 | 31 | 2018-03-01 | 07:00 | 212 | 29 | 2018-03-01 | 16:00
19 | Maniknagar | 230 | 239 | 31 | 2018-03-01 | 7:00 | 209 | 29 | 2018-03-01 | 16:00
20 | Old Airport | 230 | 241 | 31 | 2018-03-01 | 07:00 | 213 | 29 | 2018-03-01 | 16:00
21 | Barisal | 230 | 248 | 31 | 2018-03-01 | 22:00 | 224 | 28 | 2018-03-01 | 02:00
22 | AKSML | 230 | 228 | 31 | 2018-03-01 | 9:00 | 201 | 15 | 2018-03-01 | 21:00
23 | BSRM | 230 | 230 | 31 | 2018-03-01 | 09:00 | 207 | 4 | 2018-03-01 | 12:00
24 | Bibiyana | 230 | 236 | 31 | 2018-03-01 | 06:00 | 217 | 4 | 2018-03-01 | 18:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 31 | 2018-03-01 | 08:00 | 124 | 19 | 2018-03-01 | 10:00
2 | Munsiganj | 132 | 140 | 31 | 2018-03-01 | 7:00 | 125 | 19 | 2018-03-01 | 10:00
3 | Megnaghat | 132 | 145 | 20 | 2018-03-01 | 13:00 | 125 | 26 | 2018-03-01 | 15:00
4 | Shyampur | 132 | 139 | 30 | 2018-03-01 | 19:00 | 120 | 27 | 2018-03-01 | 9:00
5 | Bhulta | 132 | 145 | 31 | 2018-03-01 | 7:00 | 126 | 11 | 2018-03-01 | 11:00
6 | Madanganj | 132 | 140 | 23 | 2018-03-01 | 13:00 | 125 | 3 | 2018-03-01 | 13:00
7 | Shitalakhya | 132 | 146 | 31 | 2018-03-01 | 7:00 | 126 | 18 | 2018-03-01 | 10:00
8 | Rahim Steal | 132 | 138 | 31 | 2018-03-01 | 07:00 | 125 | 19 | 2018-03-01 | 10:00
9 | Matuail | 132 | 140 | 31 | 2018-03-01 | 7:00 | 123 | 19 | 2018-03-01 | 11:00
10 | Ghorasal | 132 | 145 | 31 | 2018-03-01 | 7:00 | 125 | 25 | 2018-03-01 | 13:00
11 | Narsinghdi | 132 | 138 | 30 | 2018-03-01 | 18:00 | 121 | 19 | 2018-03-01 | 17:00
12 | Haripur (SBU) | 132 | 138 | 31 | 2018-03-01 | 7:00 | 125 | 29 | 2018-03-01 | 16:00
13 | Ullon | 132 | 139 | 31 | 2018-03-01 | 7:00 | 120 | 25 | 2018-03-01 | 16:00
14 | Hasnabad | 132 | 143 | 31 | 2018-03-01 | 8:00 | 124 | 22 | 2018-03-01 | 12:00
15 | Magbazar | 132 | 134 | 2 | 2018-03-01 | 7:00 | 110 | 6 | 2018-03-01 | 5:00
16 | Maniknagar | 132 | 140 | 31 | 2018-03-01 | 7:00 | 124 | 14 | 2018-03-01 | 15:00
17 | Bangabhaban | 132 | 144 | 30 | 2018-03-01 | 18:00 | 124 | 14 | 2018-03-01 | 10:00
18 | Narinda | 132 | 140 | 31 | 2018-03-01 | 7:00 | 126 | 5 | 2018-03-01 | 12:00
19 | Dhanmondi | 132 | 140 | 31 | 2018-03-01 | 07:00 | 120 | 25 | 2018-03-01 | 16:00
20 | Lalbag | 132 | 145 | 30 | 2018-03-01 | 18:00 | 124 | 3 | 2018-03-01 | 12:00
21 | Madartek | 132 | 140 | 31 | 2018-03-01 | 7:00 | 120 | 25 | 2018-03-01 | 12:00
22 | Mirpur | 132 | 140 | 30 | 2018-03-01 | 18:00 | 125 | 3 | 2018-03-01 | 12:00
23 | Kalyanpur | 132 | 142 | 30 | 2018-03-01 | 18:00 | 125 | 4 | 2018-03-01 | 12:00
24 | Gulshan | 132 | 139 | 31 | 2018-03-01 | 7:00 | 120 | 25 | 2018-03-01 | 12:00
25 | Uttara | 132 | 143 | 31 | 2018-03-01 | 7:00 | 118 | 5 | 2018-03-01 | 12:00
26 | Kamrangirchar | 132 | 145 | 31 | 2018-03-01 | 7:00 | 124 | 27 | 2018-03-01 | 11:00
27 | Savar | 132 | 141 | 31 | 2018-03-01 | 7:00 | 121 | 4 | 2018-03-01 | 12:00
28 | Bhasantec | 132 | 144 | 31 | 2018-03-01 | 7:00 | 120 | 4 | 2018-03-01 | 12:00
29 | Agargaon | 132 | 144 | 31 | 2018-03-01 | 7:00 | 121 | 4 | 2018-03-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 144 | 31 | 2018-03-01 | 7:00 | 121 | 4 | 2018-03-01 | 12:00
31 | Tongi | 132 | 142 | 31 | 2018-03-01 | 07:00 | 120 | 5 | 2018-03-01 | 15:00
32 | Kabirpur | 132 | 140 | 30 | 2018-03-01 | 17:00 | 118 | 5 | 2018-03-01 | 12:00
33 | Basundhara | 132 | 138 | 26 | 2018-03-01 | 17:00 | 118 | 5 | 2018-03-01 | 15:00
34 | Manikganj | 132 | 145 | 30 | 2018-03-01 | 17:00 | 123 | 5 | 2018-03-01 | 15:00
35 | Joydevpur | 132 | 145 | 31 | 2018-03-01 | 7:00 | 127 | 19 | 2018-03-01 | 11:00
36 | New Tongi | 132 | 144 | 31 | 2018-03-01 | 07:00 | 118 | 5 | 2018-03-01 | 15:00
37 | Kodda | 132 | 140 | 31 | 2018-03-01 | 10:00 | 124 | 25 | 2018-03-01 | 9:00
38 | Tangail | 132 | 140 | 26 | 2018-03-01 | 24:00 | 112 | 3 | 2018-03-01 | 12:00
39 | Mymensing | 132 | 144 | 30 | 2018-03-01 | 16:00 | 109 | 18 | 2018-03-01 | 16:00
40 | Kishorganj | 132 | 143 | 31 | 2018-03-01 | 09:00 | 114 | 25 | 2018-03-01 | 16:00
41 | Netrokona | 132 | 142 | 30 | 2018-03-01 | 17:00 | 108 | 22 | 2018-03-01 | 12:00
42 | Jamalpur | 132 | 147 | 31 | 2018-03-01 | 07:00 | 108 | 8 | 2018-03-01 | 23:00
43 | Sherpur | 132 | 145 | 30 | 2018-03-01 | 16:00 | 105 | 13 | 2018-03-01 | 6:00
44 | Srimongal | 132 | 143 | 30 | 2018-03-01 | 17:00 | 125 | 25 | 2018-03-01 | 17:00
45 | Shahjibazar | 132 | 144 | 31 | 2018-03-01 | 07:00 | 125 | 25 | 2018-03-01 | 16:00
46 | Fenchuganj | 132 | 141 | 14 | 2018-03-01 | 06:00 | 128 | 25 | 2018-03-01 | 18:30
47 | Khulawara | 132 | 140 | 2 | 2018-03-01 | 05:00 | 127 | 25 | 2018-03-01 | 16:00
48 | Sylhet | 132 | 139 | 14 | 2018-03-01 | 7:00 | 122 | 3 | 2018-03-01 | 16:00
49 | Chattak | 132 | 139 | 29 | 2018-03-01 | 03:00 | 121 | 25 | 2018-03-01 | 16:00
50 | Comilla(South) | 132 | 138 | 30 | 2018-03-01 | 18:30 | 118 | 5 | 2018-03-01 | 18:30
51 | Comilla (North) | 132 | 145 | 31 | 2018-03-01 | 7:00 | 128 | 25 | 2018-03-01 | 22:00
52 | Chandpur | 132 | 139 | 31 | 2018-03-01 | 7:00 | 115 | 24 | 2018-03-01 | 16:00
53 | Feni | 132 | 128 | 31 | 2018-03-01 | 7:00 | 114 | 23 | 2018-03-01 | 18:30
54 | Chowmuhani | 132 | 136 | 31 | 2018-03-01 | 9:00 | 114 | 3 | 2018-03-01 | 20:00
55 | Ashuganj | 132 | 146 | 31 | 2018-03-01 | 7:00 | 121 | 25 | 2018-03-01 | 16:00
56 | Daudkandi | 132 | 141 | 31 | 2018-03-01 | 7:00 | 108 | 15 | 2018-03-01 | 15:00
57 | Brahminbaria | 132 | 146 | 31 | 2018-03-01 | 7:00 | 120 | 26 | 2018-03-01 | 4:00
58 | Madanhat | 132 | 138 | 1 | 2018-03-01 | 17:00 | 120 | 15 | 2018-03-01 | 16:00
59 | Hathazari | 132 | 135 | 30 | 2018-03-01 | 20:00 | 119 | 15 | 2018-03-01 | 16:00
60 | Khulshi | 132 | 133 | 31 | 2018-03-01 | 9:00 | 109 | 15 | 2018-03-01 | 16:00
61 | Halishahar | 132 | 135 | 31 | 2018-03-01 | 09:00 | 110 | 15 | 2018-03-01 | 16:00
62 | Baraulia | 132 | 134 | 30 | 2018-03-01 | 20:00 | 113 | 15 | 2018-03-01 | 16:00
63 | Sikalbaha | 132 | 136 | 3 | 2018-03-01 | 01:00 | 117 | 15 | 2018-03-01 | 16:00
64 | Dohazari | 132 | 134 | 11 | 2018-03-01 | 15:00 | 120 | 1 | 2018-03-01 | 15:00
65 | Cox'sbazar | 132 | 132 | 11 | 2018-03-01 | 15:00 | 112 | 7 | 2018-03-01 | 15:00
66 | Chandraghona | 132 | 134 | 30 | 2018-03-01 | 21:00 | 114 | 15 | 2018-03-01 | 16:00
67 | Kaptai | 132 | 135 | 31 | 2018-03-01 | 08:00 | 125 | 3 | 2018-03-01 | 20:00
68 | A. Khaer Stl. | 132 | 132 | 2 | 2018-03-01 | 08:00 | 116 | 15 | 2018-03-01 | 16:00
69 | Bakulia | 132 | 132 | 2 | 2018-03-01 | 07:00 | 118 | 15 | 2018-03-01 | 16:00
70 | Julda | 132 | 133 | 14 | 2018-03-01 | 05:00 | 110 | 15 | 2018-03-01 | 16:00
71 | TK Chemical | 132 | 137 | 31 | 2018-03-01 | 09:00 | 125 | 1 | 2018-03-01 | 15:00
72 | Modern Steel | 132 | 132 | 2 | 2018-03-01 | 08:00 | 115 | 15 | 2018-03-01 | 16:00
73 | Shahmirpur | 132 | 132 | 11 | 2018-03-01 | 15:00 | 115 | 15 | 2018-03-01 | 16:00
74 | Goalpara | 132 | 140 | 5 | 2018-03-01 | 24:00 | 124 | 2 | 2018-03-01 | 7:00
75 | Khulna Central | 132 | 140 | 5 | 2018-03-01 | 14:00 | 125 | 1 | 2018-03-01 | 8:00
76 | Noapara | 132 | 137 | 2 | 2018-03-01 | 23:00 | 121 | 2 | 2018-03-01 | 11:00
77 | Jessore | 132 | 134 | 30 | 2018-03-01 | 17:00 | 114 | 2 | 2018-03-01 | 11:00
78 | Jhenida | 132 | 139 | 30 | 2018-03-01 | 18:00 | 113 | 2 | 2018-03-01 | 11:00
79 | Bottail | 132 | 141 | 30 | 2018-03-01 | 18:00 | 120 | 23 | 2018-03-01 | 19:00
80 | G.K.Project | 132 | 145 | 31 | 2018-03-01 | 04:00 | 116 | 20 | 2018-03-01 | 21:00
81 | Faridpur | 132 | 139 | 30 | 2018-03-01 | 18:00 | 122 | 26 | 2018-03-01 | 11:00
82 | Madaripur | 132 | 142 | 31 | 2018-03-01 | 9:00 | 120 | 25 | 2018-03-01 | 9:00
83 | Gopalganj | 132 | 145 | 31 | 2018-03-01 | 9:00 | 118 | 8 | 2018-03-01 | 19:00
84 | Bagerhat | 132 | 140 | 5 | 2018-03-01 | 17:00 | 121 | 22 | 2018-03-01 | 23:00
85 | Mongla | 132 | 135 | 1 | 2018-03-01 | 22:00 | 121 | 2 | 2018-03-01 | 7:00
86 | Satkhira | 132 | 139 | 2 | 2018-03-01 | 22:00 | 125 | 2 | 2018-03-01 | 10:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
87 | Gallamari | 132 | 140 | 2 | 2018-03-01 | 22:00 | 121 | 4 | 2018-03-01 | 7:00
88 | Magura | 132 | 140 | 30 | 2018-03-01 | 17:00 | 112 | 29 | 2018-03-01 | 21:00
89 | Chuadanga | 132 | 139 | 30 | 2018-03-01 | 18:00 | 106 | 23 | 2018-03-01 | 19:00
90 | Barisal | 132 | 142 | 31 | 2018-03-01 | 22:00 | 127 | 23 | 2018-03-01 | 19:00
91 | Patuakhali | 132 | 142 | 31 | 2018-03-01 | 22:00 | 127 | 23 | 2018-03-01 | 19:00
92 | Bhandaria | 132 | 140 | 30 | 2018-03-01 | 20:00 | 124 | 23 | 2018-03-01 | 18:30
93 | Ishurdi | 132 | 160 | 31 | 2018-03-01 | 6:00 | 124 | 23 | 2018-03-01 | 19:00
94 | Ruppur Paromanobik | 132 | 134 | 1 | 2018-03-01 | 1:00 | 129 | 13 | 2018-03-01 | 9:00
95 | Natore | 132 | 160 | 31 | 2018-03-01 | 6:00 | 120 | 23 | 2018-03-01 | 19:00
96 | Bogra | 132 | 160 | 31 | 2018-03-01 | 5:00 | 111 | 29 | 2018-03-01 | 19:00
97 | Noagaon | 132 | 150 | 31 | 2018-03-01 | 6:00 | 110 | 20 | 2018-03-01 | 7:00
98 | Rajshahi | 132 | 146 | 31 | 2018-03-01 | 4:00 | 119 | 26 | 2018-03-01 | 11:00
99 | C.Nawabganj | 132 | 144 | 31 | 2018-03-01 | 4:00 | 116 | 16 | 2018-03-01 | 14:00
100 | Amnura | 132 | 140 | 29 | 2018-03-01 | 18:00 | 119 | 23 | 2018-03-01 | 19:00
101 | Pabna | 132 | 152 | 31 | 2018-03-01 | 6:00 | 120 | 23 | 2018-03-01 | 19:00
102 | Shahjadpur | 132 | 150 | 31 | 2018-03-01 | 5:00 | 130 | 20 | 2018-03-01 | 7:00
103 | Serajganj | 132 | 150 | 31 | 2018-03-01 | 5:00 | 114 | 5 | 2018-03-01 | 8:00
104 | Niyamatpur | 132 | 150 | 31 | 2018-03-01 | 6:00 | 107 | 25 | 2018-03-01 | 7:00
105 | Joypurhat | 132 | 150 | 31 | 2018-03-01 | 5:00 | 111 | 25 | 2018-03-01 | 7:00
106 | Rangpur | 132 | 141 | 31 | 2018-03-01 | 7:00 | 105 | 26 | 2018-03-01 | 19:00
107 | Lalmonirhat | 132 | 143 | 6 | 2018-03-01 | 15:00 | 104 | 31 | 2018-03-01 | 11:00
108 | Saidpur | 132 | 138 | 6 | 2018-03-01 | 15:00 | 103 | 31 | 2018-03-01 | 10:00
109 | Purbasadipur | 132 | 140 | 6 | 2018-03-01 | 15:00 | 104 | 31 | 2018-03-01 | 11:00
110 | Thakurgaon | 132 | 138 | 30 | 2018-03-01 | 12:00 | 103 | 31 | 2018-03-01 | 19:30
111 | Palashbari | 132 | 142 | 31 | 2018-03-01 | 6:00 | 108 | 2 | 2018-03-01 | 10:00
112 | Barapukuria | 132 | 140 | 30 | 2018-03-01 | 11:00 | 108 | 31 | 2018-03-01 | 11:00
113 | Panchagar | 132 | 137 | 30 | 2018-03-01 | 14:00 | 98 | 31 | 2018-03-01 | 19:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:March' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 126 | 375
IP-299421 | Hasnabad | TR2 | 225 | 116 | 375 | 01.03.18 | 24:00
|  | TR3 | 225 | 118 | 360
|  | TR1 | 225 | 138 | 445
IP-299866 | Tongi | TR2 | 225 | 138 | 445 | 24.03.18 | 18:00
|  | TR3 | 225 | 138 | 445
|  | TR1 | 225 | 160 | 420
IP-299427 | Haripur | TR2 | 225 | 160 | 420 | 09.03.18 | 21:00
|  | TR3 | 225 | 160 | 420
|  | TR1 | 225 | 148 | 560
IP-299728 | Rampura | TR2 | 225 | 148 | 560 | 12.03.18 | 18:00
|  | TR3 | 225 | 148 | 560
|  | TR1 | 225 | 110 | 339
IP-299264 | Aminbazar | TR2 | 225 | 110 | 339 | 24.03.18 | 11:00
|  | TR3 | 225 | 117 | 352
| Maniknagar | TR1 | 300 | 114 | 360 | 25.03.18 | 15:00
|  | TR2 | 300 | 114 | 360
IP-399266 | Comilla (N) | TR1 | 225 | 150 | 480 | 23.03.18 | 22:00
|  | TR2 | 225 | 153 | 520
| Fenchuganj | TR1 | 300 | - | - | - | - | Transformer is unavailable since 12.12.17
|  | TR1 | 150 | 85 | 250
IP-399428 | Hathazari | TR3 | 150 | 85 | 250 | 30.03.18 | 15:00
|  | TR4 | 150 | 85 | 250
|  | TR1 | 225 | 160 | 430
| Ishurdi | TR2 | 225 | 160 | 430 | 01.03.18 | 19:00
IP-499474 |  | TR3 | 225 | 160 | 430
| Khulna(S) | TR1 | 225 | 169 | 461
IP-58001/58002 |  | TR2 | 225 | 169 | 461 | 03.03.18 | 7:00
| Bogra | TR1 | 225 | 110 | 340 | 22.03.18 | 21:00
|  | TR3 | 225 | 110 | 340
IP-43002/499264 |  | TR2 | 225 | 148 | 448
IP-499224 | Baghabari | TR1 | 225 | 175 | 530 | 02.03.18 | 10:00
| Barapukuria | TR1 | 225 | 196 | 980 | 20.03.18 | 20:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 225 | 210 | 1050 |  |  | 132 kV current is being provided
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:March' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-03-18 | 8835 | 8835 | - | - | - | - | - | - | - | - | - | - | - | - | 01-03-18 | 7467 | 7467 | - | - | - | - | - | - | - | - | - | - | - | -
02-03-18 | 8316 | 8316 | - | - | - | - | - | - | - | - | - | - | - | - | 02-03-18 | 6246.6 | 6246.6 | - | - | - | - | - | - | - | - | - | - | - | -
03-03-18 | 9262 | 9262 | - | - | - | - | - | - | - | - | - | - | - | - | 03-03-18 | 6941 | 6941 | - | - | - | - | - | - | - | - | - | - | - | -
04-03-18 | 9032 | 9032 | - | - | - | - | - | - | - | - | - | - | - | - | 04-03-18 | 7838.3 | 7838.3 | - | - | - | - | - | - | - | - | - | - | - | -
05-03-18 | 9015 | 9015 | - | - | - | - | - | - | - | - | - | - | - | - | 05-03-18 | 8116 | 8116 | - | - | - | - | - | - | - | - | - | - | - | -
06-03-18 | 9307 | 9307 | - | - | - | - | - | - | - | - | - | - | - | - | 06-03-18 | 8109.2 | 8109.2 | - | - | - | - | - | - | - | - | - | - | - | -
07-03-18 | 9431 | 9431 | - | - | - | - | - | - | - | - | - | - | - | - | 07-03-18 | 8057.4 | 8057.4 | - | - | - | - | - | - | - | - | - | - | - | -
08-03-18 | 9241 | 9241 | - | - | - | - | - | - | - | - | - | - | - | - | 08-03-18 | 7776 | 7776 | - | - | - | - | - | - | - | - | - | - | - | -
09-03-18 | 8306 | 8306 | - | - | - | - | - | - | - | - | - | - | - | - | 09-03-18 | 6335.1 | 6335.1 | - | - | - | - | - | - | - | - | - | - | - | -
10-03-18 | 9249 | 9249 | - | - | - | - | - | - | - | - | - | - | - | - | 10-03-18 | 7095.2 | 7095.2 | - | - | - | - | - | - | - | - | - | - | - | -
11-03-18 | 9454 | 9454 | - | - | - | - | - | - | - | - | - | - | - | - | 11-03-18 | 7935.9 | 7935.9 | - | - | - | - | - | - | - | - | - | - | - | -
12-03-18 | 9533 | 9533 | - | - | - | - | - | - | - | - | - | - | - | - | 12-03-18 | 7946 | 7946 | - | - | - | - | - | - | - | - | - | - | - | -
13-03-18 | 9616 | 9616 | - | - | - | - | - | - | - | - | - | - | - | - | 13-03-18 | 8237.7 | 8237.7 | - | - | - | - | - | - | - | - | - | - | - | -
14-03-18 | 9494 | 9494 | - | - | - | - | - | - | - | - | - | - | - | - | 14-03-18 | 8080.9 | 8080.9 | - | - | - | - | - | - | - | - | - | - | - | -
15-03-18 | 9715 | 9715 | - | - | - | - | - | - | - | - | - | - | - | - | 15-03-18 | 8200 | 8200 | - | - | - | - | - | - | - | - | - | - | - | -
16-03-18 | 8842 | 8842 | - | - | - | - | - | - | - | - | - | - | - | - | 16-03-18 | 6548 | 6548 | - | - | - | - | - | - | - | - | - | - | - | -
17-03-18 | 9467 | 9467 | - | - | - | - | - | - | - | - | - | - | - | - | 17-03-18 | 8038.2 | 8038 | - | - | - | - | - | - | - | - | - | - | - | -
18-03-18 | 9939 | 9939 | - | - | - | - | - | - | - | - | - | - | - | - | 18-03-18 | 8223.1 | 8223.1 | - | - | - | - | - | - | - | - | - | - | - | -
19-03-18 | 10084 | 10084 | - | - | - | - | - | - | - | - | - | - | - | - | 19-03-18 | 8155.3 | 8155.3 | - | - | - | - | - | - | - | - | - | - | - | -
20-03-18 | 9578 | 9578 | - | - | - | - | - | - | - | - | - | - | - | - | 20-03-18 | 8335 | 8335 | - | - | - | - | - | - | - | - | - | - | - | -
21-03-18 | 9714 | 9714 | - | - | - | - | - | - | - | - | - | - | - | - | 21-03-18 | 8402 | 8402 | - | - | - | - | - | - | - | - | - | - | - | -
22-03-18 | 9819 | 9819 | - | - | - | - | - | - | - | - | - | - | - | - | 22-03-18 | 8476.9 | 8476.9 | - | - | - | - | - | - | - | - | - | - | - | -
23-03-18 | 9344 | 9344 | - | - | - | - | - | - | - | - | - | - | - | - | 23-03-18 | 7267.9 | 7267.9 | - | - | - | - | - | - | - | - | - | - | - | -
24-03-18 | 9470 | 9470 | - | - | - | - | - | - | - | - | - | - | - | - | 24-03-18 | 8147 | 8147 | - | - | - | - | - | - | - | - | - | - | - | -
25-03-18 | 8962 | 8962 | - | - | - | - | - | - | - | - | - | - | - | - | 25-03-18 | 8408.9 | 8408.9 | - | - | - | - | - | - | - | - | - | - | - | -
26-03-18 | 8654 | 8654 | - | - | - | - | - | - | - | - | - | - | - | - | 26-03-18 | 7440.3 | 7440.3 | - | - | - | - | - | - | - | - | - | - | - | -
27-03-18 | 9318 | 9318 | - | - | - | - | - | - | - | - | - | - | - | - | 27-03-18 | 7897 | 7897 | - | - | - | - | - | - | - | - | - | - | - | -
28-03-18 | 9306 | 9306 | - | - | - | - | - | - | - | - | - | - | - | - | 28-03-18 | 8117.4 | 8117.4 | - | - | - | - | - | - | - | - | - | - | - | -
29-03-18 | 9147 | 9147 | - | - | - | - | - | - | - | - | - | - | - | - | 29-03-18 | 8330 | 8330 | - | - | - | - | - | - | - | - | - | - | - | -
30-03-18 | 5487 | 5487 | - | - | - | - | - | - | - | - | - | - | - | - | 30-03-18 | 6315.2 | 6315.2 | - | - | - | - | - | - | - | - | - | - | - | -
31-03-18 | 8314 | 8314 | - | - | - | - | - | - | - | - | - | - | - | - | 31-03-18 | 4893.4 | 4893.4 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10084 | 19/03/18 | 19:30
2 | Maximum day peak Genaration | MW | 8476.9 | 22/03/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 10084 | 19/03/18 | 19:30
4 | Minimum Generation | MW | 1774 | 31/03/18 | 7:00
5 | Average of the daily evening peak Genaration | MW | 9137.129
6 | Average of the daily day peak Genaration | MW | 7657.3516
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5738.5391
12 | Total Generation by IPP | MKWH | 1520.845 | % of total Gen. | 26.5023
13 | Total Generation by BPDB | MKWH | 2868.6919 | " | 49.9899
14 | A) Total Generation by RPCL | MKWH | 82.218 | '' | 1.4327
| B) Total Generation by REB | MKWH | 143.1202 | " | 2.494
| C) Total Generation by RENTAL | MKWH | 700.15 | " | 12.2008
| D) Total Imported from India (HVDC) | MKWH | 330.1127 | " | 5.7526
| E) Total Imported from Tripura, India (A.C) | MKWH | 93.4013 | " | 1.6276
15 | Fuel wise Generation.
| A) Gas | MKWH | 3545.0029 | % of total Gen. | 61.78%
| B) Oil | MKWH | 1479.4699 | '' | 25.78%
| C) Hydro | MKWH | 53.5263 | '' | 0.9328%
| D) Solar | MKWH | 0.38342 | '' | 0.006682%
| E) Coal | MKWH | 236.6426 | '' | 4.124%
| F) HVDC (Import from India) | MKWH | 330.1127 | '' | 5.753%
| G) A.C (Import from Tripura, India) | MKWH | 93.4013 | '' | 1.628%
16 | Maximun of the daily total Generation . | MKWH | 206.8764 | 22/03/18
17 | Monthly Load factor | % | 76.4884
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 18123.077
| A) Gas | M.Taka | 2889.0157
| B) Liquid fuel | M.Taka | 14984.9922
| C) Coal | M.Taka | 249.0692
| D) HVDC (Import from India) | M.Taka | 1683.5749
| E) Tripura(Import from India) | M.Taka | 638.8648
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 895.4661 | 20/03/18
| A) Gas | M.Taka | 286.453 | 20/03/18
| B) Liquid fuel | M.Taka | 652.6337 | 28/03/18
| C) Coal | M.Taka | 10.9657 | 01/03/18
| D) HVDC (Import from India) | M.Taka | 58.8781 | 17/03/18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.7023
| B) Excluding Hydro & Solar | Taka/KWHR | 3.7374
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.34 | 31/03/18 | 06:00
b) | Actual | FT (MSL) | 89.76 | 31/03/18 | 06:00
22 | Peak Genaration of March 2017 | MW | 8737 | 28/03/17 | 20:00
23 | Peak Demand of March 2017 | MW | 8737 | 28/03/17 | 20:00
24 | Maximum peak Generation recorded upto 31/03/18 | MW | 10084 | 19/03/18 | 19:30
25 | Maximum peak Demand recorded upto 31/03/18 | MW | 10084 | 19/03/18 | 19:30
26 | Maximum load shed recorded upto 31/03/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.