## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:February' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | February 2018 |  | January 2017 |  | February 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 8848 | 24/02/18 | 8251 | 29/01/18 | 8323 | 22/02/17 | 9507 | 18/10/17
|  |  | 19:30 |  | 19:30 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 2515 | 26/02/18 | 4098 | 06/01/18 | 4229 | 04/02/17 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 8848 | 24/02/18 | 8251 | 29/01/18 | 8323 | 22/02/17 | 9507 | 18/10/17
|  |  | 19:30 |  | 19:30 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 7547.8 | 25/02/18 | 6766.4 | 02/01/2018 | 6906 | 28/02/2017 | 8743 | 07/6/17
|  |  | 12:00 |  | 9:00 |  | 12:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 8848 | 24/02/18 | 8251 | 29/01/18 | 8323 | 22/02/17 | 9507 | 18/10/17
|  |  | 19:30 |  | 19:30 |  | 19:30 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 8183.6071 |  | 7796.06 |  | 7736.32 |  | 9057.07 | Aug -17
7 | Average Generation (MW) at Day Peak | 6720.4321 |  | 6055.18 |  | 6327 |  | 7210.5 | May -17
8 | Maximum Power Import from India (MW) | 485 | 05/02/18 | 497 | 22/01/18 | 494 | 22/02/17 | 509 | 2017-07-03
|  |  | 19:30 |  | 10:00 |  | 22:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 152 | 28/02/18 | 132 | 25/01/18 | 116 | 22/02/17 | 172 | 04/10/17
|  |  | 18:30 |  | 18:30 |  | 19:00 |  | 19:30
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2291.7234 |  | 2096.37 |  | 2010.65
21 | Station Use of BPDB (MKWH) | 77.2059 |  | 74.33 |  | 93.69
22 | Net Generation of BPDB (MKWH) | 2214.5174 |  | 2022.03 |  | 1916.96
23 | Net Generation of IPP & RPCL (MKWH) | 1131.2938 |  | 1343.21 |  | 782.86
24 | Net Generation of REB (MKWH) | 129.418 |  | 144.18 |  | 102.11
24 | Net Generation of Rental Power Plant (MKWH) | 494.9814 |  | 459.37 |  | 853.04
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 3970.2106 |  | 3968.79 |  | 3654.97 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3002.4748 |  | 3085.21 |  | 2813.03 |  | 3531.44 | Oct-17
27 | Energy Generation by Diesel (MKWH) | 15.6516 |  | 11 |  | 98.08 |  | 424.76 | May-17
28 | Energy Generation by Furnace Oil (MKWH) | 754.4697 |  | 744.01 |  | 688.45 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 52.4366 |  | 44.1 |  | 55.02 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.28493 |  | 0.17 |  | - |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 222.0989 |  | 158.65 |  | 94.09 |  | 158.65 | Jan-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 329.4473 |  | 339.25 |  | 361.08 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 73.612 |  | 71.39 |  | 73.48 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:February' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 8848 | 24/02/18 | 19:30
Generation Period
| Dhaka | MW | 3190
| Chittagong | MW | 870
| Comilla | MW | 749
| Mymensingh | MW | 600
| Sylhet | MW | 323
a) | Total supply in East zone | MW | 5732
| Khulna | MW | 943
| Barisal | MW | 186
| Rajshahi | MW | 916
| Rangpur | MW | 559
b) | Total supply in West zone | MW | 2604
c) | Total supply in both zone ( a+b) | MW | 8336
Ref: | 27.21.2604.603.16.084.18.70 | Date: 20/03/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:February' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 900 | 21/02/18 | 8:00
| b) Ishurdi end | MW | 80 | 28/02/18 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 230 | 28/02/18 | 16:00
| b) Ishurdi end | MW | 400 | 21/02/18 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.9565 | 20/02/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 5.8545 | 20/02/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 106.6372
| b) Ishurdi end | MKWH | 3.68
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.56
| b) Ishurdi end | MKWH | 103.825
23 | Transmission loss of EWI/ NO-1 | % | 2.63
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 530 | 08/02/18 | 8:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 520 | 08/02/18 | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 9.708 | 20/02/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 9.534 | 20/02/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 202.896
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 200.368
30 | Transmission loss of EWI /NO-2 | % | 1.246
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | 132/33 kV Transformer-Tr-3 | 2018-02-06 18:07 | 2018-02-06 18:11 | 0:04 | T | Tripped showing O/C relay | 100 | 6.6667 | Power interruption
Tongi | 132/33 kV Transformers-T-2 | 2018-02-12 06:40 | 2018-02-12 06:52 | 0:12 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T-3 | 2018-02-26 04:05 | 2018-02-27 20:09 | 40:04 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T-3 | 2018-02-26 04:03 | 2018-02-26 16:42 | 12:39 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
|  |  | Total : | 52:59 |  | Unserved Energy: |  | 6.6667
Dhaka (South) Grid Circle :
Haripur | 230/132 kV Transformers-T-R2 | 2018-02-15 05:06 | 2018-02-15 11:06 | 6:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
|  |  | Total : | 6:00 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Hathazari | 230/132 kV Transformer-T-3 | 2018-02-28 19:27 | 2018-02-28 20:35 | 1:08 | E/O | Due to red hot maintenance | 32 | 36.2667 | Power interruption
| 230/132 kV Transformer-T-4 | 2018-02-28 21:04 | 2018-02-28 22:18 | 1:14 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 2:22 |  | Unserved Energy: |  | 36.2667
Comilla Grid Circle :
Comilla(N) | 132/33 kV Transformer-T-04 | 2018-02-02 01:08 | 2018-02-02 10:50 | 9:42 | T | Tripped showing high voltage | 0 | 0 | No interruption
|  |  | Total : | 9:42 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformers-T-1 | 2018-02-02 16:24 | 2018-02-02 19:18 | 2:54 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformers-T-1 | 2018-02-11 16:35 | 2018-02-11 16:58 | 0:23 | E/O | Due to red hot maintenance | 50 | 19.1667 | Power interruption
Noapara | 132/33 kV Transformers-T-1 | 2018-02-17 06:15 | 2018-02-17 06:45 | 0:30 | T | Tripped showing E/F & O/C relay | 11 | 2.0167 | Power interruption 06:15 to 06:26
| 132/33 kV Transformers-T-2 | 2018-02-17 06:15 | 2018-02-17 06:26 | 0:11 | T
|  |  | Total : | 3:17 |  | Unserved Energy: |  | 21.1833
HVDC Grid Circle :
Bottail | 132/33 kV Transformer-T-1 | 2018-02-06 12:43 | 2018-02-06 13:00 | 0:17 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bottail | 132/33 kV Transformers-T-1 | 2018-02-15 08:15 | 2018-02-15 08:22 | 0:07 | T | Tripped showing O/C relay | 23 | 2.6833 | Power interruption
Shahjadpur | 132/33 kV Transformers-T-3 | 2018-02-26 01:15 | 2018-02-26 09:48 | 8:33 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 8:57 |  | Unserved Energy: |  | 2.6833
Bogra Grid Circle:
Purbasadipur | 132/33 kV Transformers-Tr-3 | 2018-02-07 14:58 | 2018-02-07 19:12 | 4:14 | E/O | Due to red hot maintenance | 20 | 84.6667 | Power interruption
Baghabari | 230/132 kV Transformer-T-2 | 2018-02-17 18:36 | 2018-02-17 19:04 | 0:28 | T | Tripped showing O/C relay | 30 | 14 | Power interruption
Niyamatpur | 132/33 kV Transformers-T-1 | 2018-02-19 20:27 | 2018-02-19 21:00 | 0:33 | E/O | Due to bursting of CT | 75 | 41.25 | Power interruption 20:27 to 21:00
| 132/33 kV Transformers-T-2 | 2018-02-19 20:27 | 2018-02-20 12:05 | 15:38 | E/O
Rajshahi | 132/33 kV Transformers-T-2 | 2018-02-25 23:50 | 2018-02-26 00:23 | 0:33 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 21:26 |  | Unserved Energy: |  | 139.9167
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 104:43 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-02-04 07:28 | 2018-02-04 17:41 | 10:13 | T | Tripped showing dist. relay | 90 | 468 | Power interruption 07:28 to 12:40
Joydevpur | Joydevpur-Korda 132 kV line-2 | 2018-02-06 06:48 | 2018-02-06 07:06 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2018-02-23 05:55 | 2018-02-23 05:59 | 0:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2018-02-26 02:45 | 2018-02-26 02:53 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2018-02-26 04:13 | 2018-02-26 04:54 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir -Kabirpur 132 kV line-1 | 2018-02-26 03:58 | 2018-02-26 04:30 | 0:32 | T | Tripped showing dist. relay | 3 | 1.6 | Power interruption 03:58 to 04:30
| Kabirpur-Kaliakoir -Kabirpur 132 kV line-2 | 2018-02-26 03:58 | 2018-02-26 11:01 | 7:03 | T
Kaliakoir | Kaliakoir -Tangail 132 kV line-1 | 2018-02-26 11:00 | 2018-02-26 15:58 | 4:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 23:57 |  | Unserved Energy: |  | 469.6
Dhaka (South) Grid Circle :
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2018-02-02 14:14 | 2018-02-02 14:20 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2018-02-06 04:25 | 2018-02-06 05:14 | 0:49 | T | Tripped showing dist. PTA5,PDC,PTAW signal | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-02-06 05:23 | 2018-02-06 06:02 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-02-06 07:42 | 2018-02-06 07:51 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2018-02-07 06:28 | 2018-02-07 07:11 | 0:43 | T | Tripped showing LZ96DR,R-phase PTAW ,PTA5,PDC,PTAWsignal | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-2 | 2018-02-09 11:06 | 2018-02-09 12:06 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-02-12 19:13 | 2018-02-13 00:12 | 4:59 | T | Tripped showing dist. relay | 88 | 438.5333 | Power interruption
Haripur | Haripur-Siddhirganj 230 kV line-1 | 2018-02-15 05:06 | 2018-02-15 05:13 | 0:07 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Haripur-Siddhirganj 230 kV line-2 | 2018-02-15 05:06 | 2018-02-15 05:22 | 0:16 | T |  | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-02-19 17:24 | 2018-02-19 17:36 | 0:12 | T | Tripped showing dist. relay | 56 | 11.2 | Power interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-1 | 2018-02-23 16:20 | 2018-02-23 16:33 | 0:13 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj P/S 132 kV line | 2018-02-23 16:20 | 2018-02-23 16:41 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-02-23 06:31 | 2018-02-23 08:52 | 2:21 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV line-1 | 2018-02-23 06:31 | 2018-02-23 06:42 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-02-23 07:41 | 2018-02-23 09:37 | 1:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2018-02-25 04:22 | 2018-02-25 05:38 | 1:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 & 2 | 2018-02-26 04:06 | 2018-02-26 05:43 | 1:37 | T | Tripped showing dist. relay | 95 | 153.5833 | Power interruption
Narsinghdi | Narsinghdi-Haripur 132 kV line | 2018-02-26 18:43 | 2018-02-26 22:04 | 3:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-02-26 20:39 | 2018-02-26 20:46 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 20:23 |  | Unserved Energy: |  | 603.3167
Chittagong Grid Circle :
Baraulia | Baraulia-AkSML 132 kV line | 2018-02-17 02:20 | 2018-02-17 13:51 | 11:31 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2018-02-22 23:37 | 2018-02-23 01:27 | 1:50 | E/O | Due to bursting of PT | 0 | 0 | No interruption
|  |  | Total : | 13:21 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Comiila(N) | Comiila(N)-Feni 132 kV line | 2018-02-01 04:53 | 2018-02-01 17:19 | 12:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2018-02-03 09:49 | 2018-02-03 12:33 | 2:44 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Comiila(N) | Comiila(N)-Ashuganj 230 kV line-2 | 2018-02-04 08:00 | 2018-02-04 08:25 | 0:25 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-2 | 2018-02-05 12:03 | 2018-02-05 12:41 | 0:38 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-2 | 2018-02-09 08:35 | 2018-02-10 15:48 | 31:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Comilla(N) 132 kV line | 2018-02-09 08:37 | 2018-02-09 08:52 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-02-11 17:01 | 2018-02-11 17:09 | 0:08 | T | Tripped showing O/C. relay | 175 | 23.3333 | Power interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-13 07:31 | 2018-02-13 16:28 | 8:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla (S) | Comilla (S)-Surjonagar 132 kV line-2 | 2018-02-17 19:24 | 2018-02-18 17:09 | 21:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-22 16:51 | 2018-02-22 17:05 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-02-23 12:27 | 2018-02-23 12:37 | 0:10 | T | Tripped showing dist. relay | 120 | 20 | Power interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2018-02-26 04:29 | 2018-02-26 05:00 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2018-02-26 17:16 | 2018-02-26 18:13 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-02-26 14:01 | 2018-02-26 14:19 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla (N) | Comilla (N)-Chandpur 132 kV line-1 | 2018-02-27 20:57 | 2018-02-27 21:00 | 0:03 | T | Tripped showing O/C relay | 220 | 33 | Power interruption 20:57 to 21:06
| Comilla (N)-Chandpur 132 kV line-1 | 2018-02-27 20:57 | 2018-02-27 21:06 | 0:09 | T
|  |  | Total : | 80:53 |  | Unserved Energy: |  | 76.3333
Khulna Grid Circle :
Madaripur | Madaripur-Faridpur 132 kV line-1 | 2018-02-01 15:55 | 2018-02-01 16:59 | 1:04 | T | Tripped showing dist.(3-phase )relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barisal 132 kV line | 2018-02-07 13:31 | 2018-02-07 14:01 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2018-02-17 00:49 | 2018-02-17 01:16 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2018-02-22 18:59 | 2018-02-22 22:35 | 3:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:04 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2018-02-04 03:43 | 2018-02-04 09:21 | 5:38 | T | Tripped showing dist.PTAW,PD3, signal | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-02-06 06:28 | 2018-02-06 06:55 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-2 | 2018-02-10 18:35 | 2018-02-11 04:34 | 9:59 | E/O | Due to bursting of lightning arrester | 80 | 20 | Power interruption 18:35 to 18:50
Bheramara | Bheramara-Bottail 132 kV line-1 | 2018-02-16 07:22 | 2018-02-16 08:24 | 1:02 | E/O | Due to red hot maintenance | 40 | 41.3333 | Power interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2018-02-21 09:14 | 2018-02-21 12:01 | 2:47 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-02-21 09:14 | 2018-02-21 12:01 | 2:47 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2018-02-22 09:43 | 2018-02-22 13:02 | 3:19 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2018-02-22 09:43 | 2018-02-22 15:35 | 5:52 | E/O |  | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2018-02-23 05:55 | 2018-02-23 06:17 | 0:22 | T | Tripped showing dist.PTAW,PD3, signal | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2018-02-23 06:12 | 2018-02-23 06:24 | 0:12 | T | Tripped showing dist.PTAW,PD3, signal | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2018-02-23 07:01 | 2018-02-23 07:41 | 0:40 | T | Tripped showing dist.PTAW,PD3, signal | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2018-02-24 07:22 | 2018-02-24 07:41 | 0:19 | T | Tripped showing dist.PTAW,PD3, signal | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-02-24 12:42 | 2018-02-24 15:24 | 2:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Jhenidah | Jhenidah-Bottail 132 kV line-1 | 2018-02-26 04:14 | 2018-02-26 06:33 | 2:19 | T | Tripped showing dist. relay | 25 | 57.9167 | Power interruption 04:14 to 06:33
| Jhenidah-Bottail 132 kV line-2 | 2018-02-26 04:14 | 2018-02-26 04:36 | 0:22 | T
Shahjadpur | Shahjadpur-Sirajganj 132 kV line | 2018-02-27 10:46 | 2018-02-27 11:06 | 0:20 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
|  |  | Total : | 39:07 |  | Unserved Energy: |  | 119.25
Bogra Grid Circle :
Palashbari | Palashbari-Bogra 132 kV line-1 | 2018-02-02 09:10 | 2018-02-02 10:58 | 1:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-02-02 11:52 | 2018-02-02 13:56 | 2:04 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra-Bogra(N) 132 kV line-2 | 2018-02-16 10:20 | 2018-02-16 14:07 | 3:47 | E/O | Due to red hot maintenance | 35 | 132.4167 | Power interruption
Natore | Natore-Rajshahi 132 kV line-2 | 2018-02-26 02:48 | 2018-02-26 02:54 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 7:45 |  | Unserved Energy: |  | 132.4167
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2018-02-17 19:39 | 2018-02-17 22:54 | 3:15 | T | Tripped showing pilot wire protection relay | 0 | 0 | No interruption
|  |  | Total : | 3:15 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 189:45 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | 230/132 kV Transformer-TR-3 | 2018-02-03 09:20 | 2018-02-03 15:49 | 6:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-TR-3 | 2018-02-04 09:17 | 2018-02-04 15:14 | 5:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-TR-3 | 2018-02-05 09:17 | 2018-02-05 17:50 | 8:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T-3 | 2018-02-05 09:17 | 2018-02-05 11:08 | 1:51 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-TR-3 | 2018-02-06 09:28 | 2018-02-06 16:10 | 6:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T-R2 | 2018-02-08 09:37 | 2018-02-08 16:52 | 7:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kabirpur | 132 kV main bus | 2018-02-12 06:40 | 2018-02-12 08:40 | 2:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T-1 | 2018-02-12 09:39 | 2018-02-12 20:09 | 10:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T-02 | 2018-02-15 09:25 | 2018-02-15 14:11 | 4:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T-2 | 2018-02-16 07:19 | 2018-02-16 17:45 | 10:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T-02 | 2018-02-17 10:06 | 2018-02-17 19:25 | 9:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T-2 | 2018-02-20 09:46 | 2018-02-20 11:08 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | 132 kV reserve Bus | 2018-02-22 09:35 | 2018-02-22 13:15 | 3:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 78:50 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj | 132/33 kV Transformer-T-1 | 2018-02-02 15:25 | 2018-02-02 17:33 | 2:08 | S/O | Due to replacement work | 0 | 0 | No interruption
Haripur | 132/33 kV Transformer-T-1 | 2018-02-12 10:37 | 2018-02-12 14:02 | 3:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T-1 | 2018-02-19 12:48 | 2018-02-19 23:53 | 11:05 | S/O | Due to replacement work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T-3 | 2018-02-26 11:25 | 2018-02-26 15:00 | 3:35 | S/O | Due to changing work | 0 | 0 | No interruption
|  |  | Total : | 20:13 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Chandraghona | 132/33 kV Transformer-T-1 | 2018-02-09 06:11 | 2018-02-09 08:08 | 1:57 | S/O | Due to D/W work | 5 | 9.75 | Power interruption
Cox'sbazar | 132/33 kV Transformer-T-1 | 2018-02-16 10:19 | 2018-02-16 17:47 | 7:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T-3 | 2018-02-16 09:05 | 2018-02-16 12:35 | 3:30 | S/O | Due to Delta test | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T-2 | 2018-02-19 06:51 | 2018-02-19 13:58 | 7:07 | S/O | Due to Delta test | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T-2 | 2018-02-27 09:45 | 2018-02-27 16:12 | 6:27 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 26:29 |  | Unserved Energy: |  | 9.75
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
B.baria | 132 kV main bus | 2018-02-02 09:12 | 2018-02-02 17:06 | 7:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-1 | 2018-02-04 08:59 | 2018-02-04 10:08 | 1:09 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | 230/132 kV Transformer-T1 | 2018-02-11 08:26 | 2018-02-11 15:39 | 7:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | 230/132 kV Transformer-T2 | 2018-02-14 10:35 | 2018-02-14 15:43 | 5:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2018-02-15 08:22 | 2018-02-15 11:22 | 3:00 | S/O | Due to testing work | 0 | 0 | No interruption
|  |  | Total | 24:24 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Faridpur | 132/33 kV Transformer-TR1 | 2018-02-09 08:40 | 2018-02-09 12:56 | 4:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 | 2018-02-10 22:16 | 2018-02-12 23:22 | 49:06 | S/O | Due to project work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2018-02-14 08:40 | 2018-02-14 18:11 | 9:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2018-02-14 10:05 | 2018-02-14 13:29 | 3:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2018-02-15 09:49 | 2018-02-15 16:32 | 6:43 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 73:00 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
Jessore | 132/33 kV Transformer-T3 | 2018-02-27 08:11 | 2018-02-27 09:12 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 1:01 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Shahjiadpur | 132/33 kV Transformers-T3 | 2018-02-08 07:22 | 2018-02-10 17:50 | 58:28 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 58:28 |  | Unserved Energy : |  | 0
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 282:25 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-02-03 10:35 | 2018-02-03 12:40 | 2:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2018-02-04 11:29 | 2018-02-04 16:44 | 5:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2018-02-06 05:05 | 2018-02-06 05:32 | 0:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2018-02-07 08:35 | 2018-02-07 18:14 | 9:39 | S/O | Due to changing work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2018-02-08 11:11 | 2018-02-08 11:39 | 0:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-02-17 09:20 | 2018-02-17 17:48 | 8:28 | S/O | Due to replacement work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-02-19 12:50 | 2018-02-19 16:14 | 3:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2018-02-25 13:28 | 2018-02-25 17:24 | 3:56 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 33:42 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur | Haripur-Narsinghdi 132 kV line | 2018-02-01 10:39 | 2018-02-01 17:02 | 6:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-02-01 09:18 | 2018-02-01 16:24 | 7:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2018-02-01 08:51 | 2018-02-01 16:56 | 8:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-02-02 08:28 | 2018-02-02 11:38 | 3:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2018-02-02 08:51 | 2018-02-02 15:38 | 6:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-1 | 2018-02-03 07:53 | 2018-02-04 17:44 | 33:51 | S/O | Due to project work | 0 | 0 | No interruption
| Meghnaghat-Aminbazar 230 kV line-2 | 2018-02-02 07:55 | 2018-02-04 17:46 | 57:51 | S/O | Due to Jumper open 79 and 98 of Aminbazar -2 | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line-1 | 2018-02-04 09:07 | 2018-02-04 16:30 | 7:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shitalakyha 132 kV line | 2018-02-05 08:57 | 2018-02-05 21:00 | 12:03 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shitalakyha 132 kV line | 2018-02-06 08:45 | 2018-02-06 14:42 | 5:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur P/S | Haripur P/S-Haripur S/S 132 kV line | 2018-02-08 10:18 | 2018-02-08 20:23 | 10:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta-Rampura 230 kV line-1 | 2018-02-09 09:20 | 2018-02-09 17:46 | 8:26 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashiganj 230 kV line-2 | 2018-02-09 08:07 | 2018-02-09 17:50 | 9:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV line-2 | 2018-02-10 08:25 | 2018-02-10 17:39 | 9:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2018-02-10 07:52 | 2018-02-10 18:04 | 10:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV line-2 | 2018-02-11 12:42 | 2018-02-11 17:03 | 4:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV line-1 | 2018-02-15 09:55 | 2018-02-15 12:21 | 2:26 | S/O | Due to maintenance work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-Haripur 132 kV line | 2018-02-16 07:14 | 2018-02-16 18:54 | 11:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat IEL 132 kV line | 2018-02-17 08:30 | 2018-02-17 11:42 | 3:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV line-1 | 2018-02-19 08:18 | 2018-02-19 17:18 | 9:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Rampura 230 kV line-1 | 2018-02-23 07:01 | 2018-02-23 17:36 | 10:35 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-02-23 07:04 | 2018-02-23 13:00 | 5:56 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Haripur (Bhulta) 230 kV line-2 | 2018-02-24 07:18 | 2018-02-24 15:21 | 8:03 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2018-02-24 11:32 | 2018-02-24 13:15 | 1:43 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-1 | 2018-02-24 14:16 | 2018-02-24 15:46 | 1:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur S/S -Haripur P/S 132 line-1 | 2018-02-28 14:45 | 2018-02-28 23:07 | 8:22 | S/O | Due to CB problem | 0 | 0 | No interruption
|  |  | Total : | 263:04 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Juldah | Juldah-Hathazari 132 kV line-2 | 2018-02-03 08:45 | 2018-02-03 16:33 | 7:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2018-02-06 08:17 | 2018-02-06 15:01 | 6:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
BSRM | BSRM-Hathazari 230 kV line | 2018-02-09 05:55 | 2018-02-09 17:53 | 11:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-02-09 10:55 | 2018-02-09 14:02 | 3:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
BSRM | BSRM-Hathazari 230 kV line | 2018-02-10 06:01 | 2018-02-10 16:43 | 10:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2018-02-15 08:58 | 2018-02-15 14:11 | 5:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2018-02-18 08:02 | 2018-02-18 16:32 | 8:30 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2018-02-19 06:01 | 2018-02-19 16:29 | 10:28 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2018-02-19 09:56 | 2018-02-19 17:03 | 7:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2018-02-20 09:08 | 2018-02-20 17:08 | 8:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2018-02-20 08:21 | 2018-02-20 16:17 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2018-02-28 09:01 | 2018-02-28 16:07 | 7:06 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 94:39 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-02 09:03 | 2018-02-02 19:05 | 10:02 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Shahjibazar 230 kV line-2 | 2018-02-03 08:49 | 2018-02-03 16:24 | 7:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Meghnaghat 230 kV line-2 | 2018-02-03 08:38 | 2018-02-03 15:00 | 6:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line-2 | 2018-02-03 08:13 | 2018-02-03 19:05 | 10:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-2 | 2018-02-03 11:46 | 2018-02-03 17:45 | 5:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Shahjibazar 230 kV line-2 | 2018-02-04 09:38 | 2018-02-04 15:25 | 5:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2018-02-04 10:15 | 2018-02-05 11:55 | 25:40 | S/O | Due to tower maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-02-04 08:00 | 2018-02-04 18:33 | 10:33 | S/O | Due to tower maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-05 10:37 | 2018-02-05 17:45 | 7:08 | S/O | Due to project work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2018-02-05 09:30 | 2018-02-05 18:41 | 9:11 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2018-02-06 08:45 | 2018-02-06 15:46 | 7:01 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Comilla(N) 132 kV line | 2018-02-06 10:35 | 2018-02-06 13:58 | 3:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-06 08:22 | 2018-02-06 18:00 | 9:38 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Sylhet 12 kV line-2 | 2018-02-06 08:50 | 2018-02-06 20:22 | 11:32 | S/O | Due to project work | 0 | 0 | No interruption
Comilla(S) | Comilla(S)-Surjonagar 132 kV line-1 | 2018-02-07 08:50 | 2018-02-07 17:01 | 8:11 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-07 08:23 | 2018-02-07 17:28 | 9:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line-2 | 2018-02-07 09:22 | 2018-02-07 18:45 | 9:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-02-09 10:55 | 2018-02-09 14:01 | 3:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Comilla(S) | Comilla(S)-Surjonagar 132 kV line-2 | 2018-02-11 09:12 | 2018-02-11 15:25 | 6:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-02-11 09:35 | 2018-02-11 18:45 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Comilla(S) | Comilla(S)-Tripura 132 kV line-1 | 2018-02-18 09:50 | 2018-02-18 17:09 | 7:19 | S/O | Due to PT change | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-2 | 2018-02-24 09:24 | 2018-02-24 15:23 | 5:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-02-24 09:13 | 2018-02-24 17:16 | 8:03 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 197:12 |  | Unserved Energy: |  | 0
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal(N) | Barisal(N)-Madaripur 132 kV line-1 | 2018-02-03 07:59 | 2018-02-03 12:45 | 4:46 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Barisal(N)-Madaripur 132 kV line-2 | 2018-02-03 09:07 | 2018-02-03 13:43 | 4:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna© | Khulna©-KPCL 132 kV line-2 | 2018-02-09 06:49 | 2018-02-09 19:25 | 12:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-1 | 2018-02-11 08:52 | 2018-02-11 15:55 | 7:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-1 | 2018-02-12 08:21 | 2018-02-12 16:55 | 8:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-1 | 2018-02-14 08:57 | 2018-02-14 17:22 | 8:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2018-02-15 12:35 | 2018-02-15 13:30 | 0:55 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 46:55 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2018-02-02 09:12 | 2018-02-02 14:53 | 5:41 | S/O | Due to project work | 0 | 0 | No interruption
| Bheramara-Ishurdi 132 kV line-2 | 2018-02-02 09:12 | 2018-02-02 12:01 | 2:49 | S/O |  | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-2 | 2018-02-09 06:02 | 2018-02-09 19:15 | 13:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2018-02-28 09:03 | 2018-02-28 10:37 | 1:34 | S/O | Due to problem with 132 kV B-phase L/A | 0 | 0 | No interruption
|  |  | Total : | 23:17 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Natore 132 kV line-2 | 2018-02-03 14:30 | 2018-02-03 17:05 | 2:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-02-09 10:35 | 2018-02-09 13:48 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 3:13 |  | Unserved Energy: |  | 0
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-2 | 2018-02-09 09:21 | 2018-02-09 12:06 | 2:45 | S/O | Due to DPDC work | 0 | 0 | No interruption
|  |  | Total : | 2:45 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 633:50 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:February' 2018
| Area | Previous Month (January 2018) |  |  |  | Current Month (February 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 4 | 3 | 74 | 81 | 11 | 1 | 21 | 33
2 | Dhaka (South) Grid Circle. | 3 | 2 | 61 | 66 | 18 | 2 | 18 | 38
3 | Chittagong Grid Circle. | 3 | 1 | 48 | 52 | 1 | 3 | 17 | 21
4 | Comilla Grid Circle. | 18 | 5 | 63 | 86 | 15 | 2 | 28 | 45
5 | Khulna Grid Circle. | 2 | - | 50 | 52 | 6 | 2 | 12 | 20
6 | Bheramara HVDC Grid Circle | 3 | - | 21 | 24 | 12 | 7 | 5 | 24
7 | Bogra Grid Circle. | 13 | 1 | 59 | 73 | 3 | 6 | 3 | 12
8 | Others | 4 | - | 3 | 7 | 1 | - | 1 | 2
9 | Total | 50 | 12 | 379 | 441 | 67 | 23 | 105 | 195
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:February' 2018
| Area | Previous Month (January 2018) |  |  |  | Current Month (February 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 186.33 | - | 132 | 318.33 | 476.27 | - | - | 476.27
2 | Dhaka ( South) grid circle | 10.83 | - | 157 | 167.83 | 603.32 | - | - | 603.32
3 | Chittagong grid circle. | 28.8 | - | - | 28.8 | - | 36.27 | 9.75 | 46.02
4 | Comilla grid circle. | 45.27 | 124.48 | 57.5 | 227.25 | 76.33 | - | - | 76.33
5 | Khulna grid circle. | 67.08 | - | 821.05 | 888.13 | 2.02 | 19.17 | - | 21.19
6 | Bheramara HVDC grid circle | - | - | 363.08 | 363.08 | 60.6 | 61.33 | - | 121.93
7 | Bogra grid circle. | 65.32 |  | 1014.57 | 1079.89 | 14 | 258.34 | - | 272.34
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 403.63 | 124.48 | 2545.2 | 3073.31 | 1232.54 | 375.11 | 9.75 | 1617.4
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:February' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 |  | 1 | 1 | - | - | 6.67
2 | Dhaka (South) | 5031.6 | - | - | - | - | - | - | -
3 | Chittagong | 2042 | 1 | 1 | 2 | - |  | 2 | 46.02
4 | Khulna | 2434 | 2 | - | 2 | - | - | - | 21.18
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | 1 | - | - | 2.68
6 | Bogra | 3145.6 | 3 | - | 3 | 1 | 1 | 1 | 139.92
7 | Comilla | 2981 | - | - | - | - | - | - | -
| Total | 23365.5 | [6 empty] | 216.47
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.89%
2 | Dhaka (South) | 99.99%
3 | Chittagong | 99.97%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.97% | [6 empty] | Executive Engineer
6 | Bogra | 99.87% | [6 empty] | Information Management Division
7 | Comilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:February' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 | - | 2 |  | 1 | 1 | 469.6
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 1 | - | 2 | 603.32
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 598.7 |  | 3 | - | 3 | 1 | - | 2 | 119.25
6 | Bogra | 1803.3 | 38 | 1 | - | 1 | - | - | 1 | 132.42
7 | Comilla | 1648.16 | 17 | 3 | - | 3 | 3 | - | - | 76.33
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1400.92
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.88%
2 | Dhaka (South) | 99.91%
3 | Chittagong | 99.99%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 99.55% | [7 empty] | Executive Engineer
6 | Bogra | 99.99% | [7 empty] | Information Management Division
7 | Comilla | 99.61% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:February' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
February | 14 | - | 4 | 6hr18 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:February' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Joydevpur | 1 | 0:04 | 100 | 6.6667 | Due to tripping of 132/33 kV Transformer T3
Mymensingh | 1 | 5:12 | 90 | 468 | Due to tripping of Mymensingh-Jamalpur 132 kV line-1
Kaliakoir |  | 5:22 | 3 | 1.6 | Due to tripping of Kaliakoir-Kabirpur 132 kV line-1 & 2
Haripur | 2 | 4:59 | 88 | 438.53 | Due to tripping of Haripur-Bhulta 132 kV line
|  | 0:12 | 56 | 11.2 | Due to tripping of Haripur-Shyampur 132 kV line
Ranmpura | 1 | 1:37 | 95 | 153.5833 | Due to tripping of Rampura-Bashundhara 132 kV line-1 & 2
Hathazari | 1 | 1:08 | 32 | 36.2667 | Due to red-hot maintenance of 230/132 kV X-formmer T3
Chandraghona | 1 | 1:57 | 5 | 9.75 | Due to S/D of 132/33 kV Transformer T 1
Ashuganj | 1 | 0:08 | 175 | 23.3333 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-1
| 1 | 0:10 | 120 | 20 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-1
Comilla(N) | 1 | 0:09 | 220 | 33 | Due to tripping of Comilla(N) -Chandpur 132 kV line-1 & 2
Faridpur | 1 | 23:00 | 50 | 19.1667 | Due to red-hot maintenance of 132/33 kV Transformer T1
Bottail |  | 0:07 | 23 | 2.6833 | Due to tripping of 132/33 kV Transformer T1
Bheramara | 2 | 0:15 | 80 | 20 | Due to tripping of Bheramara-Bottail 132 kV line-2
|  | 1:02 | 40 | 41.3333 | Due to tripping of Bheramara-Bottail 132 kV line-1
Jhenidah | 1 | 2:19 | 25 | 57.9167 | Due to tripping of Jhenidah-Bottail 132 kV line-1 & 2
Bogra | 1 | 4:14 | 20 | 84.6667 | Due to tripping of 132/33 kV Transformer Tr3
Noapara | 1 | 0:30 | 11 | 2.0167 | Due to tripping of 132/33 kV Transformer T1
Baghabari | 1 | 0:28 | 30 | 14 | Due to tripping of 230/132 kV Transformer Tr2
Niyamatpur | 1 | 0:33 | 75 | 41.25 | Due to bursting of 132/33 kV Transformer T01
Bogra | 1 | 3:47 | 35 | 132.4167 | Due to red-hot maintenance of Bogra-Bogra(N) 132 kV line-2
| Total unserved energy : |  |  | 1617.38 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:February'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 108 | 27 | 2018-02-01 | 18:00
2 | Munsiganj | 88 | 25 | 2018-02-01 | 21:00
3 | Megnaghat | 48 | 26 | 2018-02-01 | 11:00
4 | Shyampur | 148 | 22 | 2018-02-01 | 13:00
5 | Bhulta | 162 | 20 | 2018-02-01 | 19:30
6 | Madanganj | 51 | 19 | 2018-02-01 | 18:30
7 | Shitalakhya | 101 | 25 | 2018-02-01 | 12:00
8 | Rahim steel | 17 | 7 | 2018-02-01 | 13:00
9 | Matuail | 84 | 20 | 2018-02-01 | 12:00
10 | Ghorasal | 135 | 4 | 2018-02-01 | 7:00
11 | Narsingdi | 96 | 26 | 2018-02-01 | 20:00
12 | Haripur (SBU) | 92 | 26 | 2018-02-01 | 19:00
13 | Ullon | 69 | 25 | 2018-02-01 | 20:00
14 | Hasnabad | 158 | 25 | 2018-02-01 | 20:00
15 | Magbazar | 103 | 26 | 2018-02-01 | 15:00
16 | Maniknagar | 76 | 25 | 2018-02-01 | 18:30
17 | Bangabhaban | 30 | 25 | 2018-02-01 | 13:00
18 | Narinda | 64 | 19 | 2018-02-01 | 13:00
19 | Dhanmondi | 115 | 25 | 2018-02-01 | 13:00
20 | Lalbag | 86 | 25 | 2018-02-01 | 18:30
21 | Madartek | 51 | 27 | 2018-02-01 | 1:00
22 | Mirpur | 93 | 14 | 2018-02-01 | 18:30
23 | Kalyanpur | 84 | 24 | 2018-02-01 | 18:30
24 | Gulshan | 98 | 25 | 2018-02-01 | 13:00
25 | Uttara | 80 | 19 | 2018-02-01 | 19:00
26 | Kamrangirchar | 69 | 22 | 2018-02-01 | 19:00
27 | Savar | 122 | 22 | 2018-02-01 | 19:00
28 | Bhasantec | 123 | 27 | 2018-02-01 | 18:30
29 | Agargaon | 37 | 25 | 2018-02-01 | 19:30
30 | Satmosjid | 75 | 25 | 2018-02-01 | 19:00
31 | Tongi | 120 | 27 | 2018-02-01 | 19:00
32 | Kabirpur | 168 | 26 | 2018-02-01 | 19:00
33 | Basundhara | 118 | 17 | 2018-02-01 | 19:30
34 | Manikganj | 90 | 25 | 2018-02-01 | 20:00
35 | Joydevpur | 209 | 5 | 2018-02-01 | 18:30
36 | New Tongi | 100 | 14 | 2018-02-01 | 11:00
37 | Kodda | 225 | 25 | 2018-02-01 | 18:00
38 | Tangail | 151 | 22 | 2018-02-01 | 19:00
39 | Mymensing | 188 | 25 | 2018-02-01 | 18:30
40 | Kishorganj | 76 | 25 | 2018-02-01 | 19:00
41 | Netrokona | 79 | 24 | 2018-02-01 | 18:30
42 | Jamalpur | 90 | 1 | 2018-02-01 | 19:30
43 | Sherpur | 76 | 4 | 2018-02-01 | 18:30
44 | Srimongal | 35 | 25 | 2018-02-01 | 19:30
45 | Shahjibazar | 88 | 25 | 2018-02-01 | 18:30
46 | Fenchuganj | 33 | 6 | 2018-02-01 | 18:30
47 | Khulawara | 28 | 19 | 2018-02-01 | 19:30
48 | Sylhet | 126 | 25 | 2018-02-01 | 18:30
49 | Chatak | 45 | 25 | 2018-02-01 | 19:00
50 | Comilla (S) | 150 | 25 | 2018-02-01 | 18:30
51 | Comilla(N) | 85 | 21 | 2018-02-01 | 19:00
52 | Chandpur | 90 | 23 | 2018-02-01 | 21:00
53 | Feni | 85 | 15 | 2018-02-01 | 18:00
54 | Chowmuhani | 154 | 24 | 2018-02-01 | 19:00
55 | Ashuganj | 48 | 24 | 2018-02-01 | 19:00
56 | Daudkandi | 84 | 24 | 2018-02-01 | 19:00
57 | B.Baria | 104 | 25 | 2018-02-01 | 19:00
58 | Madanhat | 51 | 17 | 2018-02-01 | 19:00
59 | Hathazari | 91 | 3 | 2018-02-01 | 8:00
60 | Khulshi | 167 | 27 | 2018-02-01 | 15:00
61 | Halishahar | 112 | 25 | 2018-02-01 | 15:00
62 | Baraulia | 133 | 26 | 2018-02-01 | 06:00
63 | Sikalbaha | 30 | 14 | 2018-02-01 | 19:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:February'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
64 | Dohazari | 74 | 24 | 2018-02-01 | 18:30
65 | Cox'sbazar | 82 | 23 | 2018-02-01 | 18:30
66 | Chandraghona | 34 | 13 | 2018-02-01 | 13:00
67 | Kaptai | 4.5 | 8 | 2018-02-01 | 18:00
68 | A. Khaer Stl. | 16 | 1 | 2018-02-01 | 23:00
69 | Bakulia | 95 | 27 | 2018-02-01 | 19:00
70 | Julda | 20 | 22 | 2018-02-01 | 11:00
71 | TK chemical | 6.6 | 4 | 2018-02-01 | 19:30
72 | Modern Steel | 113 | 18 | 2018-02-01 | 16:00
73 | Shahmirpur | 24 | 7 | 2018-02-01 | 18:00
74 | Abul Khair 230 | 230 | 8 | 2018-02-01 | 2:00
75 | BSRM | 110 | 23 | 2018-02-01 | 20:00
76 | Goalpara | 35 | 18 | 2018-02-01 | 12:00
77 | Central s/s | 75 | 17 | 2018-02-01 | 15:00
78 | Noapara | 75 | 24 | 2018-02-01 | 21:00
79 | Jessore | 112 | 17 | 2018-02-01 | 19:00
80 | Jhenida | 76 | 13 | 2018-02-01 | 19:00
81 | Bottail | 78 | 13 | 2018-02-01 | 19:00
82 | G.K Project | 48 | 26 | 2018-02-01 | 19:00
83 | Faridpur | 118 | 14 | 2018-02-01 | 19:00
84 | Madaripur | 99 | 28 | 2018-02-01 | 19:00
85 | Gopalganj | 61 | 7 | 2018-02-01 | 19:30
86 | Bagerhat | 70 | 26 | 2018-02-01 | 19:00
87 | Mongla | 39 | 27 | 2018-02-01 | 11:00
88 | Satkhira | 75 | 14 | 2018-02-01 | 19:00
89 | Gallamari | 43 | 28 | 2018-02-01 | 13:00
90 | Magura | 40 | 13 | 2018-02-01 | 19:00
91 | Chuadanga | 66 | 27 | 2018-02-01 | 19:00
92 | Barisal | 96 | 24 | 2018-02-01 | 20:00
93 | Patuakhali | 63 | 22 | 2018-02-01 | 20:00
94 | Bhandaria | 36 | 7 | 2018-02-01 | 20:00
95 | Ishurdi | 42 | 4 | 2018-02-01 | 18:30
96 | Ruppur Paromanobik | 1 | 1 | 2018-02-01 | 1:00
97 | Natore | 88 | 14 | 2018-02-01 | 19:00
98 | Bogra | 189 | 24 | 2018-02-01 | 19:00
99 | Noagaon | 102 | 6 | 2018-02-01 | 18:30
100 | Rajshahi | 105 | 24 | 2018-02-01 | 19:30
101 | C.Nawabganj | 61 | 9 | 2018-02-01 | 11:00
102 | Amnura | 36 | 20 | 2018-02-01 | 19:30
103 | Pabna | 84 | 22 | 2018-02-01 | 20:00
104 | Shahjadpur | 76 | 25 | 2018-02-01 | 19:00
105 | Serajganj | 79 | 20 | 2018-02-01 | 7:00
106 | Niyamatpur | 86 | 16 | 2018-02-01 | 18:30
107 | Joypurhat | 44 | 10 | 2018-02-01 | 19:30
108 | Rangpur | 101 | 4 | 2018-02-01 | 19:00
109 | Lalmonirhat | 82 | 14 | 2018-02-01 | 18:30
110 | Saidpur | 109 | 24 | 2018-02-01 | 19:00
111 | Purbasadipur | 86 | 19 | 2018-02-01 | 19:00
112 | Thakurgaon | 67 | 19 | 2018-02-01 | 19:00
113 | Palashbari | 89 | 11 | 2018-02-01 | 18:30
114 | Barapukuria | 51 | 10 | 2018-02-01 | 8:00
115 | Panchagar | 39 | 19 | 2018-02-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:February' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 3325 | 25.02.18 | 19:00
Chittagong | 999 | 28.02.18 | 12:00
Khulna | 1006 | 27.02.18 | 20:00
Rajshahi | 925 | 19.02.18 | 19:00
Comilla | 758 | 24.02.18 | 19:00
Mymensingh | 624 | 25.02.18 | 18:30
Sylhet | 338 | 25.02.18 | 18:30
Barisal | 195 | 24.02.18 | 20:00
Rangpur | 579 | 20.02.18 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 417 | 9 | 2018-02-01 | 14:00 | 379 | 28 | 2018-02-01 | 11:00
2 | Bheramara | 400 | 422 | 1 | 2018-02-01 | 3:00 | 396 | 5 | 2018-02-01 | 11:00
3 | Kaliakoir | 400 | 410 | 9 | 2018-02-01 | 04:00 | 363 | 28 | 2018-02-01 | 11:00
| 230 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
SL. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. |  | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 242 | 8 | 2018-02-01 | 07:00 | 226 | 28 | 2018-02-01 | 8:00
2 | Ishurdi | 230 | 242 | 2 | 2018-02-01 | 10:00 | 218 | 17 | 2018-02-01 | 18:30
3 | Ashuganj | 230 | 247 | 11 | 2018-02-01 | 11:00 | 228 | 26 | 2018-02-01 | 7:00
4 | Serajganj | 230 | 232 | 1 | 2018-02-01 | 4:00 | 212 | 17 | 2018-02-01 | 18:30
5 | Baghabari | 230 | 232 | 1 | 2018-02-01 | 2:00 | 217 | 24 | 2018-02-01 | 19:00
6 | Barapukuria | 230 | 240 | 26 | 2018-02-01 | 3:00 | 212 | 9 | 2018-02-01 | 8:00
7 | Bogra | 230 | 231 | 26 | 2018-02-01 | 02':00 | 208 | 18 | 2018-02-01 | 8:00
8 | Khulna South | 230 | 244 | 2 | 2018-02-01 | 09'00 | 211 | 15 | 2018-02-01 | 7:00
9 | Rampura | 230 | 231 | 1 | 2018-02-01 | 02:00 | 217 | 28 | 2018-02-01 | 10:00
10 | Haripur | 230 | 232 | 2 | 2018-02-01 | 18:00 | 218 | 25 | 2018-02-01 | 12:00
11 | Hasnabad | 230 | 236 | 9 | 2018-02-01 | 19:00 | 220 | 25 | 2018-02-01 | 12:00
12 | Aminbazar | 230 | 237 | 9 | 2018-02-01 | 05:00 | 219 | 25 | 2018-02-01 | 12:00
13 | Tongi | 230 | 234 | 2 | 2018-02-01 | 13:00 | 212 | 25 | 2018-02-01 | 11:00
14 | Comilla (N) | 230 | 242 | 9 | 2018-02-01 | 3:00 | 225 | 27 | 2018-02-01 | 18:00
15 | Hathazari | 230 | 232 | 2 | 2018-02-01 | 14:00 | 210 | 27 | 2018-02-01 | 12:00
16 | Megnaghat | 230 | 240 | 9 | 2018-02-01 | 10:00 | 218 | 22 | 2018-02-01 | 13:00
17 | Fenchuganj | 230 | 245 | 7 | 2018-02-01 | 13:00 | 224 | 28 | 2018-02-01 | 11:00
18 | Siddhirganj | 230 | 242 | 2 | 2018-02-01 | 09:00 | 213 | 7 | 2018-02-01 | 12:00
19 | Maniknagar | 230 | 242 | 26 | 2018-02-01 | 21:00 | 211 | 5 | 2018-02-01 | 12:00
20 | Old Airport | 230 | 236 | 9 | 2018-02-01 | 04:00 | 218 | 19 | 2018-02-01 | 17:00
21 | Barisal | 230 | 240 | 26 | 2018-02-01 | 05:00 | 224 | 2 | 2018-02-01 | 18:30
22 | AKSML | 230 | 233 | 2 | 2018-02-01 | 10:00 | 205 | 27 | 2018-02-01 | 18:30
23 | BSRM | 230 | 236 | 2 | 2018-02-01 | 14:00 | 210 | 27 | 2018-02-01 | 12:00
24 | Bibiyana | 230 | 247 | 9 | 2018-02-01 | 14:00 | 227 | 23 | 2018-02-01 | 20:00
132 kV Substation
1 | Siddhirganj | 132 | 141 | 9 | 2018-02-01 | 14:00 | 124 | 26 | 2018-02-01 | 12:00
2 | Munsiganj | 132 | 141 | 9 | 2018-02-01 | 13:00 | 124 | 26 | 2018-02-01 | 12:00
3 | Megnaghat | 132 | 140 | 9 | 2018-02-01 | 13:00 | 124 | 26 | 2018-02-01 | 12:00
4 | Shyampur | 132 | 137 | 1 | 2018-02-01 | 18:30 | 120 | 27 | 2018-02-01 | 11:00
5 | Bhulta | 132 | 143 | 9 | 2018-02-01 | 14:00 | 120 | 3 | 2018-02-01 | 12:00
6 | Madanganj | 132 | 140 | 9 | 2018-02-01 | 14:00 | 123 | 26 | 2018-02-01 | 12:00
7 | Shitalakhya | 132 | 141 | 2 | 2018-02-01 | 18:00 | 124 | 7 | 2018-02-01 | 11:00
8 | Rahim Steal | 132 | 140 | 2 | 2018-02-01 | 10:00 | 126 | 26 | 2018-02-01 | 12:00
9 | Matuail | 132 | 139 | 9 | 2018-02-01 | 13:00 | 118 | 13 | 2018-02-01 | 11:00
10 | Ghorasal | 132 | 142 | 2 | 2018-02-01 | 13:00 | 133 | 28 | 2018-02-01 | 9:00
11 | Narsinghdi | 132 | 142 | 9 | 2018-02-01 | 11:00 | 120 | 15 | 2018-02-01 | 12:00
12 | Haripur (SBU) | 132 | 140 | 9 | 2018-02-01 | 14:00 | 127 | 27 | 2018-02-01 | 13:00
13 | Ullon | 132 | 138 | 26 | 2018-02-01 | 4:00 | 122 | 25 | 2018-02-01 | 12:00
14 | Hasnabad | 132 | 138 | 26 | 2018-02-01 | 4:00 | 125 | 7 | 2018-02-01 | 12:00
15 | Magbazar | 132 | 138 | 9 | 2018-02-01 | 6:00 | 122 | 24 | 2018-02-01 | 17:00
16 | Maniknagar | 132 | 142 | 26 | 2018-02-01 | 6:00 | 120 | 1 | 2018-02-01 | 12:00
17 | Bangabhaban | 132 | 142 | 26 | 2018-02-01 | 6:00 | 120 | 1 | 2018-02-01 | 12:00
18 | Narinda | 132 | 136 | 1 | 2018-02-01 | 5:00 | 120 | 5 | 2018-02-01 | 12:00
19 | Dhanmondi | 132 | 139 | 14 | 2018-02-01 | 02:00 | 122 | 8 | 2018-02-01 | 11:00
20 | Lalbag | 132 | 142 | 26 | 2018-02-01 | 6:00 | 120 | 22 | 2018-02-01 | 11:00
21 | Madartek | 132 | 136 | 1 | 2018-02-01 | 5:00 | 122 | 25 | 2018-02-01 | 11:00
22 | Mirpur | 132 | 138 | 2 | 2018-02-01 | 6:00 | 120 | 22 | 2018-02-01 | 12:00
23 | Kalyanpur | 132 | 138 | 9 | 2018-02-01 | 3:00 | 120 | 22 | 2018-02-01 | 12:00
24 | Gulshan | 132 | 136 | 2 | 2018-02-01 | 6:00 | 121 | 25 | 2018-02-01 | 11:00
25 | Uttara | 132 | 136 | 17 | 2018-02-01 | 6:00 | 122 | 24 | 2018-02-01 | 18:30
26 | Kamrangirchar | 132 | 142 | 26 | 2018-02-01 | 6:00 | 122 | 21 | 2018-02-01 | 11:00
27 | Savar | 132 | 135 | 2 | 2018-02-01 | 6:00 | 122 | 21 | 2018-02-01 | 12:00
28 | Bhasantec | 132 | 136 | 20 | 2018-02-01 | 3:00 | 121 | 25 | 2018-02-01 | 13:00
29 | Agargaon | 132 | 136 | 9 | 2018-02-01 | 4:00 | 124 | 6 | 2018-02-01 | 15:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 136 | 3 | 2018-02-01 | 6:00 | 123 | 25 | 2018-02-01 | 15:00
31 | Tongi | 132 | 140 | 2 | 2018-02-01 | 24:00 | 125 | 24 | 2018-02-01 | 18:00
32 | Kabirpur | 132 | 140 | 9 | 2018-02-01 | 22:00 | 120 | 19 | 2018-02-01 | 11:00
33 | Basundhara | 132 | 137 | 3 | 2018-02-01 | 3:00 | 122 | 24 | 2018-02-01 | 18:30
34 | Manikganj | 132 | 144 | 2 | 2018-02-01 | 4:00 | 124 | 24 | 2018-02-01 | 19:00
35 | Joydevpur | 132 | 144 | 2 | 2018-02-01 | 14:00 | 129 | 28 | 2018-02-01 | 10:00
36 | New Tongi | 132 | 140 | 2 | 2018-02-01 | 14:00 | 123 | 24 | 2018-02-01 | 19:00
37 | Kodda | 132 | 142 | 1 | 2018-02-01 | 13:00 | 130 | 6 | 2018-02-01 | 3:00
38 | Tangail | 132 | 140 | 2 | 2018-02-01 | 5:00 | 120 | 25 | 2018-02-01 | 19:00
39 | Mymensing | 132 | 138 | 6 | 2018-02-01 | 03:00 | 107 | 11 | 2018-02-01 | 21:00
40 | Kishorganj | 132 | 138 | 7 | 2018-02-01 | 04:00 | 115 | 11 | 2018-02-01 | 22:00
41 | Netrokona | 132 | 140 | 26 | 2018-02-01 | 05:00 | 113 | 22 | 2018-02-01 | 18:30
42 | Jamalpur | 132 | 138 | 8 | 2018-02-01 | 19:00 | 107 | 15 | 2018-02-01 | 5:00
43 | Sherpur | 132 | 145 | 20 | 2018-02-01 | 4:00 | 108 | 15 | 2018-02-01 | 6:00
44 | Srimongal | 132 | 145 | 26 | 2018-02-01 | 5:00 | 136 | 25 | 2018-02-01 | 18:00
45 | Shahjibazar | 132 | 143 | 26 | 2018-02-01 | 06:00 | 134 | 25 | 2018-02-01 | 18:30
46 | Fenchuganj | 132 | 142 | 26 | 2018-02-01 | 05:00 | 133 | 5 | 2018-02-01 | 16:00
47 | Khulawara | 132 | 141 | 10 | 2018-02-01 | 04:00 | 130 | 8 | 2018-02-01 | 11:00
48 | Sylhet | 132 | 141 | 26 | 2018-02-01 | 5:00 | 129 | 3 | 2018-02-01 | 19:00
49 | Chattak | 132 | 142 | 26 | 2018-02-01 | 05:00 | 127 | 6 | 2018-02-01 | 16:00
50 | Comilla(South) | 132 | 135 | 13 | 2018-02-01 | 23:00 | 122 | 27 | 2018-02-01 | 12:00
51 | Comilla (North) | 132 | 144 | 8 | 2018-02-01 | 23:00 | 133 | 25 | 2018-02-01 | 11:00
52 | Chandpur | 132 | 140 | 9 | 2018-02-01 | 2:00 | 128 | 11 | 2018-02-01 | 19:00
53 | Feni | 132 | 130 | 2 | 2018-02-01 | 2:00 | 118 | 27 | 2018-02-01 | 18:30
54 | Chowmuhani | 132 | 136 | 2 | 2018-02-01 | 10:00 | 117 | 20 | 2018-02-01 | 17:00
55 | Ashuganj | 132 | 145 | 2 | 2018-02-01 | 9:00 | 135 | 25 | 2018-02-01 | 15:00
56 | Daudkandi | 132 | 141 | 9 | 2018-02-01 | 13:00 | 129 | 28 | 2018-02-01 | 12:00
57 | Brahminbaria | 132 | 144 | 26 | 2018-02-01 | 6:00 | 125 | 20 | 2018-02-01 | 11:00
58 | Madanhat | 132 | 140 | 2 | 2018-02-01 | 14:00 | 126 | 27 | 2018-02-01 | 12:00
59 | Hathazari | 132 | 140 | 2 | 2018-02-01 | 14:00 | 124 | 27 | 2018-02-01 | 12:00
60 | Khulshi | 132 | 137 | 2 | 2018-02-01 | 13:00 | 121 | 26 | 2018-02-01 | 4:00
61 | Halishahar | 132 | 140 | 2 | 2018-02-01 | 14:00 | 118 | 18 | 2018-02-01 | 15:00
62 | Baraulia | 132 | 138 | 2 | 2018-02-01 | 14:00 | 123 | 27 | 2018-02-01 | 12:00
63 | Sikalbaha | 132 | 139 | 9 | 2018-02-01 | 09:00 | 123 | 6 | 2018-02-01 | 14:00
64 | Dohazari | 132 | 140 | 2 | 2018-02-01 | 10:00 | 122 | 27 | 2018-02-01 | 12:00
65 | Cox'sbazar | 132 | 136 | 2 | 2018-02-01 | 14:00 | 113 | 28 | 2018-02-01 | 12:00
66 | Chandraghona | 132 | 139 | 2 | 2018-02-01 | 10:00 | 125 | 27 | 2018-02-01 | 13:00
67 | Kaptai | 132 | 140 | 2 | 2018-02-01 | 22:00 | 126 | 27 | 2018-02-01 | 12:00
68 | A. Khaer Stl. | 132 | 136 | 2 | 2018-02-01 | 10:00 | 124 | 27 | 2018-02-01 | 12:00
69 | Bakulia | 132 | 138 | 2 | 2018-02-01 | 14:00 | 122 | 27 | 2018-02-01 | 12:00
70 | Julda | 132 | 139 | 2 | 2018-02-01 | 22:00 | 123 | 27 | 2018-02-01 | 12:00
71 | TK Chemical | 132 | 142 | 2 | 2018-02-01 | 14:00 | 127 | 27 | 2018-02-01 | 12:00
72 | Modern Steel | 132 | 137 | 2 | 2018-02-01 | 10:00 | 108 | 18 | 2018-02-01 | 14:00
73 | Shahmirpur | 132 | 137 | 2 | 2018-02-01 | 10:00 | 123 | 27 | 2018-02-01 | 12:00
74 | Goalpara | 132 | 142 | 26 | 2018-02-01 | 4:00 | 119 | 19 | 2018-02-01 | 7:00
75 | Khulna Central | 132 | 141 | 26 | 2018-02-01 | 5:00 | 120 | 19 | 2018-02-01 | 7:00
76 | Noapara | 132 | 140 | 26 | 2018-02-01 | 5:00 | 120 | 13 | 2018-02-01 | 18:30
77 | Jessore | 132 | 135 | 26 | 2018-02-01 | 4:00 | 110 | 22 | 2018-02-01 | 07:00
78 | Jhenida | 132 | 140 | 26 | 2018-02-01 | 4:00 | 107 | 17 | 2018-02-01 | 18:30
79 | Bottail | 132 | 144 | 26 | 2018-02-01 | 04:00 | 110 | 9 | 2018-02-01 | 19:00
80 | G.K.Project | 132 | 146 | 26 | 2018-02-01 | 04:00 | 127 | 16 | 2018-02-01 | 20:00
81 | Faridpur | 132 | 140 | 26 | 2018-02-01 | 05:00 | 123 | 28 | 2018-02-01 | 19:00
82 | Madaripur | 132 | 140 | 26 | 2018-02-01 | 5:00 | 122 | 10 | 2018-02-01 | 19:00
83 | Gopalganj | 132 | 142 | 26 | 2018-02-01 | 5:00 | 119 | 28 | 2018-02-01 | 19:00
84 | Bagerhat | 132 | 140 | 18 | 2018-02-01 | 13:00 | 120 | 13 | 2018-02-01 | 18:30
85 | Mongla | 132 | 138 | 8 | 2018-02-01 | 18:00 | 117 | 19 | 2018-02-01 | 7:00
86 | Satkhira | 132 | 141 | 26 | 2018-02-01 | 5:00 | 121 | 17 | 2018-02-01 | 19:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
87 | Gallamari | 132 | 140 | 6 | 2018-02-01 | 4:00 | 121 | 17 | 2018-02-01 | 18:30
88 | Magura | 132 | 142 | 26 | 2018-02-01 | 4:00 | 106 | 9 | 2018-02-01 | 19:00
89 | Chuadanga | 132 | 137 | 8 | 2018-02-01 | 6:00 | 104 | 24 | 2018-02-01 | 18:30
90 | Barisal | 132 | 140 | 26 | 2018-02-01 | 6:00 | 123 | 27 | 2018-02-01 | 18:30
91 | Patuakhali | 132 | 140 | 26 | 2018-02-01 | 6:00 | 123 | 27 | 2018-02-01 | 18:30
92 | Bhandaria | 132 | 137 | 7 | 2018-02-01 | 13:00 | 125 | 2 | 2018-02-01 | 18:00
93 | Ishurdi | 132 | 145 | 26 | 2018-02-01 | 4:00 | 124 | 17 | 2018-02-01 | 18:30
94 | Ruppur Paromanobik | 132 | 134 | 1 | 2018-02-01 | 1:00 | 129 | 13 | 2018-02-01 | 18:30
95 | Natore | 132 | 144 | 26 | 2018-02-01 | 4:00 | 119 | 19 | 2018-02-01 | 7:00
96 | Bogra | 132 | 142 | 26 | 2018-02-01 | 5:00 | 113 | 13 | 2018-02-01 | 18:30
97 | Noagaon | 132 | 142 | 26 | 2018-02-01 | 4:00 | 111 | 17 | 2018-02-01 | 18:30
98 | Rajshahi | 132 | 140 | 26 | 2018-02-01 | 3:00 | 121 | 19 | 2018-02-01 | 16:00
99 | C.Nawabganj | 132 | 138 | 26 | 2018-02-01 | 3:00 | 119 | 19 | 2018-02-01 | 7:00
100 | Amnura | 132 | 140 | 16 | 2018-02-01 | 10:00 | 120 | 19 | 2018-02-01 | 7:00
101 | Pabna | 132 | 135 | 2 | 2018-02-01 | 10:00 | 120 | 17 | 2018-02-01 | 18:30
102 | Shahjadpur | 132 | 145 | 26 | 2018-02-01 | 2:00 | 125 | 11 | 2018-02-01 | 12:00
103 | Serajganj | 132 | 143 | 26 | 2018-02-01 | 4:00 | 122 | 17 | 2018-02-01 | 19:00
104 | Niyamatpur | 132 | 143 | 26 | 2018-02-01 | 3:00 | 105 | 7 | 2018-02-01 | 12:00
105 | Joypurhat | 132 | 144 | 26 | 2018-02-01 | 4:00 | 111 | 7 | 2018-02-01 | 12:00
106 | Rangpur | 132 | 134 | 26 | 2018-02-01 | 9:00 | 104 | 7 | 2018-02-01 | 18:30
107 | Lalmonirhat | 132 | 135 | 26 | 2018-02-01 | 9:00 | 97 | 9 | 2018-02-01 | 8:00
108 | Saidpur | 132 | 134 | 26 | 2018-02-01 | 5:00 | 101 | 8 | 2018-02-01 | 9:00
109 | Purbasadipur | 132 | 134 | 26 | 2018-02-01 | 1:00 | 105 | 18 | 2018-02-01 | 8:00
110 | Thakurgaon | 132 | 130 | 26 | 2018-02-01 | 5:00 | 95 | 17 | 2018-02-01 | 18:30
111 | Palashbari | 132 | 136 | 26 | 2018-02-01 | 4:00 | 110 | 18 | 2018-02-01 | 8:00
112 | Barapukuria | 132 | 140 | 26 | 2018-02-01 | 3:00 | 112 | 9 | 2018-02-01 | 8:00
113 | Panchagar | 132 | 129 | 26 | 2018-02-01 | 4:00 | 92 | 17 | 2018-02-01 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:February' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 120 | 350
IP-299421 | Hasnabad | TR2 | 225 | 110 | 350 | 04.02.18 | 16:00
|  | TR3 | 225 | 112 | 340
|  | TR1 | 225 | 130 | 380
IP-299866 | Tongi | TR2 | 225 | 130 | 380 | 24.02.18 | 18:00
|  | TR3 | 225 | 130 | 380
|  | TR1 | 225 | 168 | 400
IP-299427 | Haripur | TR2 | 225 | 168 | 400 | 24.02.18 | 20:00
|  | TR3 | 225 | 168 | 400
|  | TR1 | 225 | 140 | 560
IP-299728 | Rampura | TR2 | 225 | 140 | 560 | 24.02.18 | 18:30
|  | TR3 | 225 | 140 | 560
|  | TR1 | 225 | 99 | 276
IP-299264 | Aminbazar | TR2 | 225 | 99 | 276 | 14.02.18 | 19:00
|  | TR3 | 225 | 102 | 285
| Maniknagar | TR1 | 300 | 113 | 360 | 08.02.18 | 12:00
|  | TR2 | 300 | 113 | 360
IP-399266 | Comilla (N) | TR1 | 225 | 140 | 395 | 02.02.18 | 20:00
|  | TR2 | 225 | 138 | 371
| Fenchuganj | TR1 | 300 | - | - | - | - | Transformer is unavailable since 12.12.17
|  | TR1 | 150 | 90 | 260
IP-399428 | Hathazari | TR3 | 150 | 90 | 260 | 01.02.18 | 18:00
|  | TR4 | 150 | 90 | 260
|  | TR1 | 225 | 182 | 500
| Ishurdi | TR2 | 225 | 182 | 500 | 16.02.18 | 20:00
IP-499474 |  | TR3 | 225 | 182 | 500
| Khulna(S) | TR1 | 225 | 183 | 494
IP-58001/58002 |  | TR2 | 225 | 183 | 494 | 23.02.18 | 18:30
| Bogra | TR1 | 225 | 185 | 390 | 17.02.18 | 19:00
IP-43002/499264 |  | TR2 | 225 | 185 | 390
IP-499224 | Baghabari | TR1 | 225 | 180 | 540 | 25.02.18 | 8:00
| Barapukuria | TR1 | 225 | 211 | 1055 | 12.02.18 | 18:30 | Due to unavailability of 230 kV side meters
|  | TR2 | 225 | 211 | 1055 |  |  | 132 kV current is being provided
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:February' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:February' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-02-18 | 8162 | 8162 | - | - | - | - | - | - | - | - | - | - | - | - | 01-02-18 | 6878.5 | 6878.5 | - | - | - | - | - | - | - | - | - | - | - | -
02-02-18 | 7262 | 7262 | - | - | - | - | - | - | - | - | - | - | - | - | 02-02-18 | 5730.5 | 5730.5 | - | - | - | - | - | - | - | - | - | - | - | -
03-02-18 | 8109 | 8109 | - | - | - | - | - | - | - | - | - | - | - | - | 03-02-18 | 6632.1 | 6632.1 | - | - | - | - | - | - | - | - | - | - | - | -
04-02-18 | 8139 | 8139 | - | - | - | - | - | - | - | - | - | - | - | - | 04-02-18 | 6511.6 | 6511.6 | - | - | - | - | - | - | - | - | - | - | - | -
05-02-18 | 8247 | 8247 | - | - | - | - | - | - | - | - | - | - | - | - | 05-02-18 | 6805.2 | 6805.2 | - | - | - | - | - | - | - | - | - | - | - | -
06-02-18 | 7976 | 7976 | - | - | - | - | - | - | - | - | - | - | - | - | 06-02-18 | 6549.4 | 6549.4 | - | - | - | - | - | - | - | - | - | - | - | -
07-02-18 | 8258 | 8258 | - | - | - | - | - | - | - | - | - | - | - | - | 07-02-18 | 6956.7 | 6956.7 | - | - | - | - | - | - | - | - | - | - | - | -
08-02-18 | 8115 | 8115 | - | - | - | - | - | - | - | - | - | - | - | - | 08-02-18 | 7185.2 | 7185.2 | - | - | - | - | - | - | - | - | - | - | - | -
09-02-18 | 7449 | 7449 | - | - | - | - | - | - | - | - | - | - | - | - | 09-02-18 | 5819 | 5819 | - | - | - | - | - | - | - | - | - | - | - | -
11-02-18 | 8144 | 8144 | - | - | - | - | - | - | - | - | - | - | - | - | 11-02-18 | 6782.5 | 6782.5 | - | - | - | - | - | - | - | - | - | - | - | -
12-02-18 | 8032 | 8032 | - | - | - | - | - | - | - | - | - | - | - | - | 12-02-18 | 6842.3 | 6842.3 | - | - | - | - | - | - | - | - | - | - | - | -
13-02-18 | 8165 | 8165 | - | - | - | - | - | - | - | - | - | - | - | - | 13-02-18 | 6882 | 6882 | - | - | - | - | - | - | - | - | - | - | - | -
14-02-18 | 7842 | 7842 | - | - | - | - | - | - | - | - | - | - | - | - | 14-02-18 | 6128 | 6128 | - | - | - | - | - | - | - | - | - | - | - | -
15-02-18 | 8419 | 8419 | - | - | - | - | - | - | - | - | - | - | - | - | 15-02-18 | 6831.7 | 6831.7 | - | - | - | - | - | - | - | - | - | - | - | -
16-02-18 | 8288 | 8288 | - | - | - | - | - | - | - | - | - | - | - | - | 16-02-18 | 7130.2 | 7130.2 | - | - | - | - | - | - | - | - | - | - | - | -
17-02-18 | 7455 | 7455 | - | - | - | - | - | - | - | - | - | - | - | - | 17-02-18 | 5743.2 | 5743.2 | - | - | - | - | - | - | - | - | - | - | - | -
18-02-18 | 8158 | 8158 | - | - | - | - | - | - | - | - | - | - | - | - | 18-02-18 | 6790.1 | 6790.1 | - | - | - | - | - | - | - | - | - | - | - | -
19-02-18 | 8465 | 8465 | - | - | - | - | - | - | - | - | - | - | - | - | 19-02-18 | 7069.8 | 7069.8 | - | - | - | - | - | - | - | - | - | - | - | -
20-02-18 | 8551 | 8551 | - | - | - | - | - | - | - | - | - | - | - | - | 20-02-18 | 7079.8 | 7079.8 | - | - | - | - | - | - | - | - | - | - | - | -
21-02-18 | 8553 | 8553 | - | - | - | - | - | - | - | - | - | - | - | - | 21-02-18 | 7364.8 | 7364.8 | - | - | - | - | - | - | - | - | - | - | - | -
22-02-18 | 7631 | 7631 | - | - | - | - | - | - | - | - | - | - | - | - | 22-02-18 | 6040.8 | 6040.8 | - | - | - | - | - | - | - | - | - | - | - | -
23-02-18 | 8508 | 8508 | - | - | - | - | - | - | - | - | - | - | - | - | 23-02-18 | 7176.7 | 7176.7 | - | - | - | - | - | - | - | - | - | - | - | -
24-02-18 | 7980 | 7980 | - | - | - | - | - | - | - | - | - | - | - | - | 24-02-18 | 6044.8 | 6044.8 | - | - | - | - | - | - | - | - | - | - | - | -
25-02-18 | 8848 | 8848 | - | - | - | - | - | - | - | - | - | - | - | - | 25-02-18 | 7205 | 7205 | - | - | - | - | - | - | - | - | - | - | - | -
26-02-18 | 8763 | 8763 | - | - | - | - | - | - | - | - | - | - | - | - | 26-02-18 | 7547.8 | 7547.8 | - | - | - | - | - | - | - | - | - | - | - | -
27-02-18 | 8060 | 8060 | - | - | - | - | - | - | - | - | - | - | - | - | 27-02-18 | 6020 | 6020 | - | - | - | - | - | - | - | - | - | - | - | -
28-02-18 | 8768 | 8768 | - | - | - | - | - | - | - | - | - | - | - | - | 28-02-18 | 7005.1 | 7005.1 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:February' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 8848 | 24/02/18 | 19:30
2 | Maximum day peak Genaration | MW | 7547.8 | 25/02/18 | 12:00
3 | Maximum Evening Peak Demand | MW | 8848 | 24/02/18 | 19:30
4 | Minimum Generation | MW | 2515 | 26/02/18 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8187.4333
6 | Average of the daily day peak Genaration | MW | 6720.4321
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 28 days in the month) | MW | -
11 | Total Generation | MKWH | 4376.8638
12 | Total Generation by IPP | MKWH | 1036.2724 | % of total Gen. | 23.6761
13 | Total Generation by BPDB | MKWH | 2291.7234 | " | 52.3599
14 | A) Total Generation by RPCL | MKWH | 95.0213 | '' | 2.171
| B) Total Generation by REB | MKWH | 129.418 | " | 2.9569
| C) Total Generation by RENTAL | MKWH | 494.9814 | " | 11.309
| D) Total Imported from India (HVDC) | MKWH | 263.9716 | " | 6.0311
| E) Total Imported from Tripura, India (A.C) | MKWH | 65.4756 | " | 1.4959
15 | Fuel wise Generation.
| A) Gas | MKWH | 3002.4748 | % of total Gen. | 68.6%
| B) Oil | MKWH | 770.1213 | '' | 17.6%
| C) Hydro | MKWH | 52.4366 | '' | 1.198%
| D) Solar | MKWH | 0.28493 | '' | 0.00651%
| E) Coal | MKWH | 222.0989 | '' | 5.074%
| F) HVDC (Import from India) | MKWH | 263.9716 | '' | 6.031%
| G) A.C (Import from Tripura, India) | MKWH | 65.4756 | '' | 1.496%
16 | Maximun of the daily total Generation . | MKWH | 176.02 | 25/02/18
17 | Monthly Load factor | % | 73.612
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 8913.4773
| A) Gas | M.Taka | 2272.2384
| B) Liquid fuel | M.Taka | 6384.2294
| C) Coal | M.Taka | 257.0096
| D) HVDC (Import from India) | M.Taka | 1346.2553
| E) Tripura(Import from India) | M.Taka | 447.8534
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 411.1715 | 24/02/18
| A) Gas | M.Taka | 90.955 | 25/02/18
| B) Liquid fuel | M.Taka | 332.7404 | 08/02/18
| C) Coal | M.Taka | 43.2937 | 24/02/18
| D) HVDC (Import from India) | M.Taka | 31.649 | 27/02/18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.8277
| B) Excluding Hydro & Solar | Taka/KWHR | 2.8622
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93.15 | 28/02/18 | 06:00
b) | Actual | FT (MSL) | 94.66 | 28/02/18 | 06:00
22 | Peak Genaration of February 2017 | MW | 8323 | 22/02/17 | 19:30
23 | Peak Demand of February 2017 | MW | 8323 | 22/02/17 | 19:30
24 | Maximum peak Generation recorded upto 28/02/18 | MW | 9507 | 18/10/17 | 19:30
25 | Maximum peak Demand recorded upto 28/02/18 | MW | 9507 | 18/10/17 | 19:30
26 | Maximum load shed recorded upto 28/02/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.