## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January' 2018
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | January 2018 |  | December 2017 |  | January 2017
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 8251 | 29/01/18 | 8028 | 11/12/17 | 7836 | 26/01/17 | 9507 | 18/10/17
|  |  | 19:30 |  | 19:00 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 4098 | 06/01/18 | 4019 | 09/12/17 | 3771 | 07/01/17 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 8251 | 29/01/18 | 8028 | 11/12/17 | 7836 | 26/01/17 | 9507 | 18/10/17
|  |  | 19:30 |  | 19:00 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 6766.4 | 02/01/18 | 6293.1 | 11/12/2017 | 6332 | 31/01/2017 | 8743 | 07/6/17
|  |  | 9:00 |  | 12:00 |  | 11:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 8251 | 29/01/18 | 8028 | 11/12/17 | 7836 | 26/01/17 | 9507 | 18/10/17
|  |  | 19:30 |  | 19:00 |  | 19:30 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 7796.0645 |  | 7644.48 |  | 7400.16 |  | 9057.07 | Aug -17
7 | Average Generation (MW) at Day Peak | 6055.1839 |  | 5688.31 |  | 5731.97 |  | 7210.5 | May -17
8 | Maximum Power Import from India (MW) | 497 | 22/01/18 | 491 | 28/12/17 | 502 | 08/01/17 | 509 | 2017-07-03
|  |  | 10:00 |  | 10:00 |  | 22:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 132 | 25/01/18 | 132 | 19/12/17 | 108 | 23/01/17 | 172 | 04/10/17
|  |  | 18:30 |  | 18:00 |  | 18:00 |  | 19:30
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 2096.367 |  | 2383.86 |  | 2077.51
21 | Station Use of BPDB (MKWH) | 74.3349 |  | 78.1 |  | 100.78
22 | Net Generation of BPDB (MKWH) | 2022.0321 |  | 2305.76 |  | 1976.73
23 | Net Generation of IPP & RPCL (MKWH) | 1343.212 |  | 1108.89 |  | 889.39
24 | Net Generation of REB (MKWH) | 144.1813 |  | 133.88 |  | 106.24
24 | Net Generation of Rental Power Plant (MKWH) | 459.3671 |  | 399.95 |  | 810.99
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 3968.7925 |  | 3948.49 |  | 3783.36 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3085.212 |  | 3141.52 |  | 3115.49 |  | 3531.44 | Oct-17
27 | Energy Generation by Diesel (MKWH) | 10.995 |  | 67.64 |  | 11.17 |  | 424.76 | May-17
28 | Energy Generation by Furnace Oil (MKWH) | 744.0051 |  | 595.86 |  | 634.6 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 44.0999 |  | 60.48 |  | 41.89 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.16732 |  | 0.27 |  |  |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 158.6481 |  | 160.82 |  | 80.99 |  | 158.65 | Jan-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 339.2477 |  | 294.34 |  | 316.73 |  | 449.86 | Aug-17
33 | Monthly Load Factor (%) | 71.3888 |  | 72.34 |  | 72.06 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:January' 2018
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 8251 | 29/01/18 | 19:30
Generation Period
| Dhaka | MW | 2752
| Chittagong | MW | 898
| Comilla | MW | 664
| Mymensingh | MW | 581
| Sylhet | MW | 301
a) | Total supply in East zone | MW | 5196
| Khulna | MW | 968
| Barisal | MW | 173
| Rajshahi | MW | 907
| Rangpur | MW | 559
b) | Total supply in West zone | MW | 2607
c) | Total supply in both zone ( a+b) | MW | 7803
Ref: | 27.21.0603.2604.16.084.18.68 | Date: 22/02/2018
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:January' 2018
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 900 | 19/01/18 | 19:30
| b) Ishurdi end | MW | 140 | 02/01/18 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 310 | 02/01/18 | 15:00
| b) Ishurdi end | MW | 440 | 18/01/18 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.775 | 20/01/18
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 5.6873 | 20/01/18
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 99.3876
| b) Ishurdi end | MKWH | 2.3084
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 2.2391
| b) Ishurdi end | MKWH | 96.796
23 | Transmission loss of EWI/ NO-1 | % | 2.607
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 570 | 19/01/18 | 19:30
| b)Serajganj end | MW | 10 | 29/01/18 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 15 | 29/01/18 | 15:00
| b)Sirajganj end | MW | 540 | 19/01/18 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 10.14 | 20/01/18
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 9.976 | 20/01/18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 216.766
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 214.25
30 | Transmission loss of EWI /NO-2 | % | 1.161
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Transformer-Tr-3 | 2018-01-04 08:13 | 2018-01-04 09:03 | 0:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer T1 | 2018-01-13 06:47 | 2018-01-13 07:37 | 0:50 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformers-T-01 | 2018-01-24 09:36 | 2018-01-24 17:20 | 7:44 | E/O | Due to bursing of lightning arrester | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T-2 | 2018-01-26 14:13 | 2018-01-26 15:19 | 1:06 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T-2 | 2018-01-31 09:05 | 2018-01-31 10:13 | 1:08 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
|  |  | Total : | 11:38 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Munshiganj | 132 kV Bus-1 | 2018-01-06 11:32 | 2018-01-06 11:58 | 0:26 | T | Tripped showing bus protection relay | 25 | 10.8333 | Power interruption
|  |  | Total : | 0:26 |  | Unserved Energy: |  | 10.8333
Chittagong Grid Circle :
Cox'sbazar | 132/33 kV Transformers-T-1 | 2018-01-10 13:56 | 2018-01-10 14:50 | 0:54 | T | Tripped showing E/F relay | 32 | 28.8 | Power interruption
| 132/33 kV Transformers-T-2 | 2018-01-10 13:56 | 2018-01-10 15:11 | 1:15 | T
Cox'sbazar | 132/33 kV Transformers-T-2 | 2018-01-23 11:49 | 2018-01-23 12:49 | 1:00 | E/O | Tripped showing SF6 gas filling | 0 | 0 | No interruption
|  |  | Total : | 3:09 |  | Unserved Energy: |  | 28.8
Comilla Grid Circle :
B.Baria | 132/33 kV Transformers-T-1,T2 & T3 | 2018-01-05 08:45 | 2018-01-05 09:18 | 0:33 | T | Tripped showing high voltage | 42 | 23.1 | Power interruption
Comilla(N) | 132/33 kV Transformers-T-4 | 2018-01-09 02:52 | 2018-01-09 06:35 | 3:43 | T | Tripped showing Over Voltage | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformers-T-4 | 2018-01-12 05:07 | 2018-01-13 11:47 | 30:40 | T | Tripped showing Diff. & lock out realy | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformers-T-4 | 2018-01-13 01:22 | 2018-01-13 11:47 | 10:25 | T | Tripped showing dist.87T,B7 realy | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformers-T-3 | 2018-01-16 12:54 | 2018-01-16 13:37 | 0:43 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T-4 | 2018-01-16 12:54 | 2018-01-16 13:33 | 0:39 | T |  | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformers-T-1, T2 & T3 | 2018-01-20 06:45 | 2018-01-20 07:08 | 0:23 | E/O | Tripped showing Oil leakage | 40 | 15.3333 | Power interruption
Comilla(N) | 132/33 kV Transformers-T-4 | 2018-01-27 03:13 | 2018-01-27 03:34 | 0:21 | T | Tripped showing O/C relay | 10 | 3.5 | Power interruption
Comilla(N) | 132/33 kV Transformers-T-4 | 2018-01-29 06:41 | 2018-01-29 07:45 | 1:04 | T | Tripped showing Over Voltage | 0 | 0 | No interruption
|  |  | Total : | 48:31 |  | Unserved Energy: |  | 41.9333
Khulna Grid Circle :
Khulna(S) | 230/132 kV Transformer-T-R1 | 2018-01-01 11:19 | 2018-01-01 22:22 | 11:03 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 11:03 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenidah | 132/33 kV Transformers-T-2 | 2018-01-31 09:34 | 2018-01-31 09:41 | 0:07 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 4:36 |  | Unserved Energy: |  | 0
Bogra Grid Circle:
Naogaon | 132/33 kV Transformers-Tr-2 | 2018-01-04 13:30 | 2018-01-05 13:01 | 23:31 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformers-T-1 | 2018-01-12 02:30 | 2018-01-12 02:45 | 0:15 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Natore | 132/33 kV Transformers-T-3 | 2018-01-31 15:58 | 2018-01-31 18:55 | 2:57 | T
|  |  | Total : | 26:43 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 106:06 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2018
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Kaliakor 132 kV line-2 | 2018-01-04 04:02 | 2018-01-04 07:04 | 3:02 | E/O | Due to Breaker problem | 0 | 0 | No interruption
Mymensingh | Mymensingh-RPCL 132 kV line-1 | 2018-01-20 18:39 | 2018-01-20 19:31 | 0:52 | T | Tripped showing O/C relay | 215 | 186.3333 | Power interruption
|  |  | Total : | 3:54 |  | Unserved Energy: |  | 186.3333
Dhaka (South) Grid Circle :
Haripur | Haripur-Meghnaghat 230 kV line-1 | 2018-01-02 10:20 | 2018-01-02 12:58 | 2:38 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Comilla(N) 230 kV line-2 | 2018-01-03 11:16 | 2018-01-03 14:38 | 3:22 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2018-01-10 19:21 | 2018-01-10 20:17 | 0:56 | T | Tripped showing PTAW,PTAS, & PD3 signal | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line | 2018-01-18 11:50 | 2018-01-18 12:06 | 0:16 | T | Tripped showing dist.relay | 0 | 0 | No interruption
|  |  | Total : | 7:12 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Khulshi | Khulshi-Madunagaht 132 kV line | 2018-01-15 12:54 | 2018-01-15 13:14 | 0:20 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
|  |  | Total : | 0:20 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-01-02 18:03 | 2018-01-02 19:30 | 1:27 | T | Tripped showing dist.(Z1) relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 | 2018-01-02 22:04 | 2018-01-02 22:43 | 0:39 | E/O |  | 177 | 109.15 | Power interruption 22:04 to 22:41
| Shahjibazar-Sreemongal 132 kV line-2 | 2018-01-02 22:04 | 2018-01-02 22:41 | 0:37 | E/O
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2018-01-05 10:12 | 2018-01-05 10:27 | 0:15 | T | Tripped showing A/R block realy | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2018-01-07 15:49 | 2018-01-07 16:46 | 0:57 | T | Tripped showing O/C relay | 140 | 18.6667 | Power interruption 15:49 to 15:57
Sylhet | Sylhet-Chatak 132 kV line-2 | 2018-01-10 09:28 | 2018-01-10 11:18 | 1:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2018-01-19 07:40 | 2018-01-19 07:44 | 0:04 | T | Tripped showing lockout realy | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2018-01-20 06:21 | 2018-01-20 07:10 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV line-2 | 2018-01-20 06:24 | 2018-01-20 07:23 | 0:59 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV line-2 | 2018-01-22 21:25 | 2018-01-23 12:47 | 15:22 | E/O | Due to breaker problem | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV line-1 | 2018-01-24 14:31 | 2018-01-24 15:09 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2018-01-26 11:57 | 2018-01-26 12:03 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2018-01-26 12:31 | 2018-01-27 12:03 | 23:32 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132 kV line-1 | 2018-01-26 15:36 | 2018-01-31 17:05 | 121:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 167:17 |  | Unserved Energy: |  | 127.8167
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: December 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line | 2017-01-27 09:46 | 2017-01-27 11:41 | 1:55 | T | Tripped showing dist. relay | 35 | 67.0833 | Power interruption
|  |  | Total : | 1:55 |  | Unserved Energy: |  | 67.0833
HVDC Grid Circle :
Jessore | Jessore-Jhenidah 230 kV line-2 | 2018-01-07 05:50 | 2018-01-07 09:39 | 3:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Jessore | Jessore-Jhenidah 230 kV line-2 | 2018-01-10 05:50 | 2018-01-10 10:15 | 4:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 8:14 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
C.nawabganj | C.nawabganj-Rajshahi 132 kV line-1 | 2018-01-03 23:22 | 2018-01-03 23:40 | 0:18 | T | Tripped showing dist. relay | 54 | 16.2 | Power interruption
Rajshahi | Rajshahi-Amnura 132 kV line | 2018-01-03 23:22 | 2018-01-03 23:58 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-01-03 23:22 | 2018-01-04 16:01 | 16:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Amnura | Amnura-C.nawabganj 132 kV line | 2018-01-06 06:01 | 2018-01-06 06:13 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Amnura-Rajshahi 132 kV line | 2018-01-06 06:13 | 2018-01-06 07:06 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line-1 | 2018-01-06 06:13 | 2018-01-06 07:22 | 1:09 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Bogra | Bogra -Palashbari 132 kV line-2 | 2018-01-10 06:50 | 2018-01-10 16:18 | 9:28 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Bogra | Bogra -Naogaon 132 kV line-2 | 2018-01-16 21:23 | 2018-01-16 21:34 | 0:11 | T | Tripped showing dist. relay | 175 | 32.0833 | Power interruption
Bogra | Bogra -Naogaon 132 kV line-1 | 2018-01-16 21:23 | 2018-01-16 21:38 | 0:15 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2018-01-20 18:16 | 2018-01-20 18:25 | 0:09 | T | Tripped showing O/C relay | 78 | 11.7 | Power interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2018-01-22 18:18 | 2018-01-22 18:22 | 0:04 | T | Tripped showing O/C relay | 80 | 5.3333 | Power interruption
|  |  | Total : | 29:54 |  | Unserved Energy: |  | 65.3167
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2018-01-09 23:49 | 2018-01-10 00:09 | 0:20 | T | Tripped showing pilot wire protection relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2018-01-20 12:52 | 2018-01-20 13:10 | 0:18 | T | Tripped showing Pilot protection relay | 0 | 0 | No interruption
| Maniknagar-Bangabhaban 132 kV line-2 | 2018-01-20 13:14 | 2018-01-20 13:34 | 0:20 | T | Tripped showing min protection relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2018-01-20 14:43 | 2018-01-20 15:32 | 0:49 | T | Tripped showing min protection relay | 0 | 0 | No interruption
|  |  | Total : | 1:47 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 220:33 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi(new) | 132/33 kV Transformer-T-1 | 2018-01-03 08:29 | 2018-01-03 15:24 | 6:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T-02 | 2018-01-03 09:49 | 2018-01-03 16:20 | 6:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer T01 | 2018-01-03 09:19 | 2018-01-03 15:44 | 6:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T-1 | 2018-01-05 09:29 | 2018-01-05 16:32 | 7:03 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T-1 | 2018-01-06 11:02 | 2018-01-06 15:29 | 4:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T-1 | 2018-01-06 09:39 | 2018-01-06 17:15 | 7:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T-1 | 2018-01-07 08:12 | 2018-01-07 12:30 | 4:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-GT-3 | 2018-01-08 09:09 | 2018-01-08 17:09 | 8:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2018-01-08 09:43 | 2018-01-08 16:13 | 6:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T-1 | 2018-01-08 08:52 | 2018-01-08 11:24 | 2:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T-3 | 2018-01-09 09:19 | 2018-01-09 15:46 | 6:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-2 | 2018-01-09 10:02 | 2018-01-09 16:10 | 6:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-1 | 2018-01-10 08:16 | 2018-01-10 16:16 | 8:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T-3 | 2018-01-10 10:53 | 2018-01-10 11:53 | 1:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T-2 | 2018-01-13 09:19 | 2018-01-13 14:59 | 5:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132 kV Bus-1 | 2018-01-15 10:18 | 2018-01-15 13:24 | 3:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T-3 | 2018-01-15 10:18 | 2018-01-15 13:23 | 3:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | 132/33 kV Transformers-T-1 & T2 | 2018-01-19 08:56 | 2018-01-19 15:30 | 6:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T-4 | 2018-01-21 10:04 | 2018-01-21 14:28 | 4:24 | S/O | Due to annual maintenance | 30 | 132 | Power interruption
Aminbazar | 230 kV Bus-2 | 2018-01-21 09:56 | 2018-01-21 15:40 | 5:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-01 | 2018-01-23 09:09 | 2018-01-23 16:17 | 7:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-01 | 2018-01-24 09:36 | 2018-01-24 17:20 | 7:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Jamlapur | 132/33 kV Transformer-T-1 | 2018-01-27 10:04 | 2018-01-27 15:05 | 5:01 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | 132 kV bus-1 | 2018-01-27 11:17 | 2018-01-27 17:50 | 6:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T-3 | 2018-01-28 09:26 | 2018-01-28 17:34 | 8:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132 kV bus-B | 2018-01-28 10:05 | 2018-01-28 15:48 | 5:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | 132 kV bus-2 | 2018-01-28 10:05 | 2018-01-28 15:50 | 5:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T-1 | 2018-01-28 11:01 | 2018-01-28 15:50 | 4:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-02 | 2018-01-29 09:22 | 2018-01-29 17:26 | 8:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T-3 | 2018-01-29 08:58 | 2018-01-29 17:30 | 8:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-1 | 2018-01-29 11:41 | 2018-01-29 14:02 | 2:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-02 | 2018-01-30 09:40 | 2018-01-30 16:35 | 6:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T-02 | 2018-01-31 09:43 | 2018-01-31 17:43 | 8:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-1 | 2018-01-31 10:07 | 2018-01-31 11:47 | 1:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 196:48 |  | Unserved Energy: |  | 132
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-TR3 | 2018-01-02 07:39 | 2018-01-02 17:47 | 10:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-1 | 2018-01-02 10:15 | 2018-01-02 17:17 | 7:02 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR3 | 2018-01-03 08:45 | 2018-01-03 18:08 | 9:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T-r2 | 2018-01-03 09:47 | 2018-01-03 16:51 | 7:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | 230 kV bus-1 | 2018-01-04 07:32 | 2018-01-04 16:06 | 8:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR3 | 2018-01-04 08:31 | 2018-01-04 17:17 | 8:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T-r2 | 2018-01-04 10:38 | 2018-01-04 15:59 | 5:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Lalbagh | 132/33 kV Transformer-GT-1 | 2018-01-04 09:14 | 2018-01-04 12:21 | 3:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T-1 | 2018-01-05 09:14 | 2018-01-05 17:54 | 8:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T-3 | 2018-01-05 09:46 | 2018-01-05 17:53 | 8:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T-1 | 2018-01-06 08:35 | 2018-01-06 14:46 | 6:11 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | 230 kV bus-1 | 2018-01-07 08:13 | 2018-01-07 17:25 | 9:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | 230 kV bus-1 | 2018-01-08 08:42 | 2018-01-08 15:18 | 6:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | 230 kV bus-2 | 2018-01-11 09:16 | 2018-01-11 14:04 | 4:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T-r-1 | 2018-01-14 08:51 | 2018-01-14 15:25 | 6:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T-r2 | 2018-01-15 08:32 | 2018-01-15 13:52 | 5:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer-T-r1 | 2018-01-15 14:15 | 2018-01-15 17:27 | 3:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | 132 kV bus-2 | 2018-01-16 10:30 | 2018-01-16 17:08 | 6:38 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T-2 | 2018-01-16 10:27 | 2018-01-16 16:42 | 6:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-2 | 2018-01-18 08:52 | 2018-01-18 15:26 | 6:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T-1 | 2018-01-19 08:59 | 2018-01-19 14:13 | 5:14 | S/O | Due to annual maintenance | 26 | 157 | Power interruption
Siddhirganj | 230/132 kV Transformer-TR-2 | 2018-01-20 08:59 | 2018-01-20 14:13 | 5:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-3 | 2018-01-22 12:10 | 2018-01-22 16:16 | 4:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T-2 | 2018-01-25 09:04 | 2018-01-25 16:28 | 7:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madartek | 132/33 kV Transformer-T-1 | 2018-01-25 09:14 | 2018-01-25 15:13 | 5:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-TR-2 | 2018-01-26 08:41 | 2018-01-26 15:28 | 6:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Siddhirganj | 230/132 kV Transformer-TR-2 | 2018-01-27 09:10 | 2018-01-27 14:12 | 5:02 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-TR-2 | 2018-01-28 08:38 | 2018-01-28 13:17 | 4:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 181:57 |  | Unserved Energy: |  | 157
Chittagong Grid Circle :
Bakulia | 132/33 kV Transformer-T-3 | 2018-01-06 07:29 | 2018-01-06 14:41 | 7:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T-1 | 2018-01-08 09:40 | 2018-01-08 13:39 | 3:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-1 | 2018-01-08 09:59 | 2018-01-08 16:33 | 6:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T-2 | 2018-01-09 09:54 | 2018-01-09 15:26 | 5:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T-1 | 2018-01-10 09:19 | 2018-01-10 21:27 | 12:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T-2 | 2018-01-11 09:51 | 2018-01-11 15:47 | 5:56 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-TR-4 | 2018-01-13 09:22 | 2018-01-13 19:40 | 10:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-TR-3 | 2018-01-18 12:26 | 2018-01-20 17:12 | 52:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Cox'sbazar | 230/132 kV Transformer-TR-3 | 2018-01-18 08:08 | 2018-01-18 14:16 | 6:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T-1 | 2018-01-20 09:43 | 2018-01-20 17:32 | 7:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T-1 | 2018-01-22 11:50 | 2018-01-22 13:21 | 1:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T-1 | 2018-01-23 09:50 | 2018-01-23 17:09 | 7:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T-2 | 2018-01-24 08:40 | 2018-01-24 15:15 | 6:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T-2 | 2018-01-25 10:50 | 2018-01-25 16:26 | 5:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T-1 | 2018-01-26 09:37 | 2018-01-26 13:09 | 3:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T-2 | 2018-01-27 08:54 | 2018-01-27 11:58 | 3:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T-2 | 2018-01-29 12:06 | 2018-01-29 13:53 | 1:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 147:46 |  | Unserved Energy: |  | 0
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Bibiyna | 230 kV bus-2 | 2018-01-02 09:52 | 2018-01-02 13:45 | 3:53 | S/O | Due to annual maintenance | 30 | 57.5 | Power interruption
Bibiyana | 400 kV bus-2 | 2018-01-04 09:08 | 2018-01-04 13:58 | 4:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2018-01-10 09:08 | 2018-01-10 18:08 | 9:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2018-01-11 08:30 | 2018-01-11 17:20 | 8:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | 230/132 kV Transformer-T-R2 | 2018-01-13 08:53 | 2018-01-13 16:44 | 7:51 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | 132 kV bus-1 | 2018-01-13 10:18 | 2018-01-13 16:13 | 5:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | 132 kV bus-2 | 2018-01-14 09:54 | 2018-01-14 16:36 | 6:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | 132 kV Bus | 2018-01-18 07:15 | 2018-01-18 10:15 | 3:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | 230/132 kV Transformer-T-R2 | 2018-01-20 08:46 | 2018-01-20 15:02 | 6:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T2 | 2018-01-20 10:44 | 2018-01-20 14:33 | 3:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T3 | 2018-01-21 09:20 | 2018-01-21 17:50 | 8:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T1 | 2018-01-23 11:07 | 2018-01-23 15:10 | 4:03 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | 132 kV bus-2 | 2018-01-27 09:40 | 2018-01-27 16:17 | 6:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | 132 kV bus-2 | 2018-01-28 10:05 | 2018-01-28 15:50 | 5:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | 132 kV bus-1 | 2018-01-31 12:33 | 2018-01-31 17:16 | 4:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total | 89:44 |  | Unserved Energy : |  | 57.5
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformer-T1 | 2018-01-05 08:19 | 2018-01-05 14:50 | 6:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T4 | 2018-01-11 08:32 | 2018-01-11 14:59 | 6:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2018-01-14 09:31 | 2018-01-14 17:59 | 8:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer-TR1 | 2018-01-18 10:08 | 2018-01-18 11:18 | 1:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformer-Tr1 | 2018-01-23 09:45 | 2018-01-23 17:30 | 7:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformer-T01 & T02 | 2018-01-24 09:38 | 2018-01-24 14:06 | 4:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2018-01-31 10:07 | 2018-01-31 12:28 | 2:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 37:10 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T1 | 2018-01-02 09:28 | 2018-01-02 17:58 | 8:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T3 | 2018-01-08 10:19 | 2018-01-08 15:40 | 5:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ishurdi | 230 kV Bus-2 | 2018-01-15 10:22 | 2018-01-15 14:10 | 3:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformers-T2 | 2018-01-17 09:19 | 2018-01-17 17:19 | 8:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Shahjadpur | 132 kV Bus | 2018-01-19 08:48 | 2018-01-19 15:10 | 6:22 | S/O | Due to annual maintenance | 30 | 191 | Power interruption
Ishurdi | 132/33 kV Transformers-T2 | 2018-01-20 13:12 | 2018-01-20 15:08 | 1:56 | S/O | Due to checking the HT Bushing Oil | 0 | 0 | No interruption
Bheramara | 132 kV Bus-A | 2018-01-29 14:40 | 2018-01-29 14:40 | 0:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | 132 kV Bus-2 | 2018-01-30 15:12 | 2018-01-30 16:05 | 0:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 34:50 |  | Unserved Energy : |  | 191
Bogra Grid Circle:
C.nawabganj | 230/132 kV Transformers-T03 | 2017-01-03 08:40 | 2017-01-03 12:26 | 3:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T2 | 2018-01-05 09:35 | 2018-01-05 14:11 | 4:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformers-T2 | 2018-01-05 15:42 | 2018-01-05 16:05 | 0:23 | S/O | Due to relay checking | 0 | 0 | No interruption
Natore | 132/33 kV Transformers-T4 | 2018-01-07 08:47 | 2018-01-07 15:35 | 6:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T02 | 2018-01-08 08:50 | 2018-01-08 16:20 | 7:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | 132/33 kV Transformers-T3 | 2018-01-09 10:35 | 2018-01-09 11:35 | 1:00 | S/O | Due to replacement work | 40 | 40 | Power interruption
Sirajganj | 132/33 kV Transformers-T1 | 2018-01-09 09:30 | 2018-01-09 13:25 | 3:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2018-01-09 13:48 | 2018-01-09 15:06 | 1:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformers-T2 | 2018-01-10 10:15 | 2018-01-10 13:15 | 3:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T02 | 2018-01-10 09:25 | 2018-01-10 17:07 | 7:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformers-T1 | 2018-01-13 10:40 | 2018-01-13 14:08 | 3:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformers-TR1 | 2018-01-15 08:13 | 2018-01-15 16:20 | 8:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformers-TR1 | 2018-01-16 09:20 | 2018-01-16 14:40 | 5:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformers-T2 | 2018-01-17 08:48 | 2018-01-17 10:06 | 1:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformers-T3 | 2018-01-18 22:28 | 2018-01-20 21:55 | 47:27 | S/O | Due to project work | 0 | 0 | No interruption
Purbasadipur | 132 kV Bus | 2018-01-19 07:58 | 2018-01-19 15:30 | 7:32 | S/O | Due to project work | 58 | 436.9333 | Power interruption
| 132 kV Bus | 2018-01-20 08:04 | 2018-01-20 15:05 | 7:01 | S/O |  | 58 | 406.9667 | Power interruption
Saidpur | 132/33 kV Transformers-T4 | 2018-01-19 12:20 | 2018-01-19 12:40 | 0:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rangpur | 132 kV Bus | 2018-01-20 08:34 | 2018-01-20 15:43 | 7:09 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Amnura | 132/33 kV Transformers-T1 | 2018-01-22 12:21 | 2018-01-22 16:50 | 4:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | 132 kV main Bus | 2018-01-26 09:05 | 2018-01-26 17:27 | 8:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | 132 kV Bus-B | 2018-01-26 08:35 | 2018-01-26 12:55 | 4:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 144:51 |  | Unserved Energy : |  | 883.9
Others :
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 833:06 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kadda | Kadda-Joydevpur 132 kV line-1 & 2 | 2018-01-01 09:06 | 2018-01-01 16:16 | 7:10 | S/O | Due to project work | 0 | 0 | No interruption
Tongi | Tongi-Ghorshal 230 kV line-2 | 2018-01-01 08:48 | 2018-01-01 16:35 | 7:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal -Ishurdi 230 kV line-2 | 2018-01-01 08:52 | 2018-01-01 17:27 | 8:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-01-01 12:08 | 2018-01-01 14:43 | 2:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | Tongi-Ghorshal 230 kV line-2 | 2018-01-01 08:28 | 2018-01-01 17:20 | 8:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | Savar-Aminbazar 230 kV line-2 | 2018-01-02 09:26 | 2018-01-02 17:10 | 7:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2018-01-03 09:36 | 2018-01-03 14:30 | 4:54 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2018-01-03 12:53 | 2018-01-03 16:43 | 3:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2018-01-04 09:40 | 2018-01-04 15:48 | 6:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2018-01-05 09:31 | 2018-01-05 18:06 | 8:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2018-01-06 09:55 | 2018-01-06 17:24 | 7:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2018-01-07 09:13 | 2018-01-07 14:05 | 4:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2018-01-09 09:50 | 2018-01-09 16:30 | 6:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-01-09 08:16 | 2018-01-09 16:30 | 8:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2018-01-10 09:08 | 2018-01-10 14:41 | 5:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2018-01-10 08:57 | 2018-01-10 15:25 | 6:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-01-10 08:16 | 2018-01-10 15:14 | 6:58 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 230 kV line-1 | 2018-01-11 09:33 | 2018-01-11 17:16 | 7:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Netrakona | Netrakona-Mymensigh 132 kV line-2 | 2018-01-11 08:12 | 2018-01-11 15:44 | 7:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal -Joydevpur 132 kV line-2 | 2018-01-11 08:33 | 2018-01-11 16:55 | 8:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | Savar-Aminbazar 230 kV line-1 | 2018-01-13 10:08 | 2018-01-13 16:16 | 6:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2018-01-13 08:24 | 2018-01-13 15:18 | 6:54 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | Savar-Aminbazar 230 kV line-2 | 2018-01-14 10:16 | 2018-01-14 16:10 | 5:54 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Tongi 132 kV line | 2018-01-15 09:28 | 2018-01-15 15:37 | 6:09 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Savar | Savar-Aminbazar 230 kV line-2 | 2018-01-15 09:10 | 2018-01-15 15:50 | 6:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2018-01-15 08:35 | 2018-01-15 16:12 | 7:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 & 2 | 2018-01-15 10:18 | 2018-01-15 13:30 | 3:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Tongi 132 kV line | 2018-01-16 09:00 | 2018-01-16 20:32 | 11:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-2 | 2018-01-17 09:38 | 2018-01-17 17:15 | 7:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2018-01-20 11:30 | 2018-01-20 14:45 | 3:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Netrakona | Netrakona-Mymensigh 132 kV line-1 | 2018-01-21 08:48 | 2018-01-21 15:44 | 6:56 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Uttara | Uttara-Tongi 132 kV line | 2018-01-22 09:37 | 2018-01-22 16:36 | 6:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2018-01-22 09:16 | 2018-01-22 15:35 | 6:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-01-23 08:17 | 2018-01-23 15:12 | 6:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-01-25 08:30 | 2018-01-25 12:47 | 4:17 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV line | 2018-01-28 09:10 | 2018-01-28 15:16 | 6:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2018-01-28 12:10 | 2018-01-28 16:10 | 4:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2018-01-29 09:54 | 2018-01-29 11:38 | 1:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-2 | 2018-01-29 11:47 | 2018-01-29 13:32 | 1:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2018-01-30 08:57 | 2018-01-30 15:56 | 6:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Page: 2/7 | [8 empty] | QF-LDC-26
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 132 kV line-3 | 2018-01-01 12:09 | 2018-01-01 17:37 | 5:28 | S/O | Due to project work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-1 | 2018-01-02 08:01 | 2018-01-02 16:06 | 8:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV line | 2018-01-03 08:32 | 2018-01-03 20:24 | 11:52 | S/O | Due to project work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narshingdi 132 kV line | 2018-01-03 09:32 | 2018-01-03 15:48 | 6:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Comilla(N) 230 kV line-2 | 2018-01-04 05:59 | 2018-01-04 15:15 | 9:16 | S/O | Due to isolator problem | 0 | 0 | No interruption
Haripur | Haripur-Rampura 230 kV line-1 & 2 | 2018-01-05 06:44 | 2018-01-05 17:47 | 11:03 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Narsinghdi 132 kV line | 2018-01-05 07:04 | 2018-01-06 20:15 | 37:11 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2018-01-05 07:04 | 2018-01-06 20:14 | 37:10 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2018-01-07 09:08 | 2018-01-07 20:20 | 11:12 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2018-01-08 08:45 | 2018-01-08 16:20 | 7:35 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV line-2 | 2018-01-10 09:18 | 2018-01-10 15:32 | 6:14 | S/O | Due to maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line-2 | 2018-01-10 15:40 | 2018-01-10 18:00 | 2:20 | S/O | Due to isolator fault | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-2 | 2018-01-14 09:47 | 2018-01-14 14:56 | 5:09 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 132 kV line-1 | 2018-01-14 09:40 | 2018-01-14 16:00 | 6:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj P/S - Haripur 230 kV line | 2018-01-15 09:34 | 2018-01-15 15:44 | 6:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | Rampura-Madartek 132 kV line-2 | 2018-01-16 09:48 | 2018-01-16 21:40 | 11:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line-2 | 2018-01-16 08:10 | 2018-01-16 14:35 | 6:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line-1 | 2018-01-17 11:12 | 2018-01-17 15:05 | 3:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | Rampura-Madartek 132 kV line-1 | 2018-01-17 09:59 | 2018-01-17 16:38 | 6:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 132 kV line-2 | 2018-01-21 08:42 | 2018-01-21 16:10 | 7:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2018-01-21 14:53 | 2018-01-21 15:24 | 0:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-2 | 2018-01-21 14:53 | 2018-01-21 15:25 | 0:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat 132 kV line | 2018-01-23 08:41 | 2018-01-23 16:48 | 8:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat 132 kV line-1 | 2018-01-24 08:40 | 2018-01-24 16:52 | 8:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-IEL 132 kV line | 2018-01-24 08:50 | 2018-01-24 15:44 | 6:54 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | Rampura-Ghorashal 230 kV line-2 | 2018-01-26 06:24 | 2018-01-27 16:11 | 33:47 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-2 | 2018-01-26 08:22 | 2018-01-26 15:28 | 7:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | Haripur-Haripur P/S 230 kV line-1 | 2018-01-28 09:40 | 2018-01-28 16:24 | 6:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | Rampura-Ghorashal 230 kV line-1 | 2018-01-29 09:23 | 2018-01-29 13:58 | 4:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-01-30 08:10 | 2018-01-30 16:50 | 8:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2018-01-30 09:24 | 2018-01-30 14:57 | 5:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV line | 2018-01-30 08:48 | 2018-01-30 16:45 | 7:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2018-01-31 10:32 | 2018-01-31 15:54 | 5:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 311:38 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-01 10:12 | 2018-01-01 16:52 | 6:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2018-01-01 09:15 | 2018-01-01 17:03 | 7:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2018-01-01 11:35 | 2018-01-01 14:43 | 3:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-02 08:07 | 2018-01-02 16:36 | 8:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2018-01-02 08:33 | 2018-01-02 14:37 | 6:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2018-01-02 08:59 | 2018-01-02 16:48 | 7:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2018-01-02 08:40 | 2018-01-02 16:04 | 7:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-03 08:22 | 2018-01-03 17:40 | 9:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-2 | 2018-01-03 08:50 | 2018-01-03 16:39 | 7:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K Chemical 132 kV line | 2018-01-03 09:50 | 2018-01-03 10:35 | 0:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-04 08:05 | 2018-01-04 16:23 | 8:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2018-01-05 07:14 | 2018-01-05 09:59 | 2:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2018-01-05 10:01 | 2018-01-05 12:05 | 2:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2018-01-06 09:09 | 2018-01-06 15:30 | 6:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-06 09:32 | 2018-01-06 16:52 | 7:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-07 08:22 | 2018-01-07 16:37 | 8:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line-2 | 2018-01-07 09:50 | 2018-01-07 11:55 | 2:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2018-01-08 09:16 | 2018-01-08 11:56 | 2:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Hathazari P/S 132 kV line | 2018-01-14 10:20 | 2018-01-14 14:39 | 4:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2018-01-17 08:55 | 2018-01-17 13:50 | 4:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 & 2 | 2018-01-19 07:02 | 2018-01-19 07:08 | 0:06 | S/O | Due to project work | 0 | 0 | No interruption
Baraulia | Baraulia-BSRM 132 kV line | 2018-01-20 09:19 | 2018-01-20 17:13 | 7:54 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-21 10:35 | 2018-01-21 16:04 | 5:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV line-2 | 2018-01-21 09:45 | 2018-01-21 13:22 | 3:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2018-01-22 08:50 | 2018-01-22 16:24 | 7:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-kaptai 132 kV line-1 | 2018-01-23 07:07 | 2018-01-23 16:44 | 9:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Hathazari-kaptai 132 kV line-2 | 2018-01-23 16:44 | 2018-01-23 16:45 | 0:01 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2018-01-29 11:37 | 2018-01-29 12:43 | 1:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-1 | 2018-01-30 09:10 | 2018-01-30 12:15 | 3:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baraulia | Baraulia-AKSML 132 kV line | 2018-01-30 11:16 | 2018-01-30 15:34 | 4:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.k chemical 132 kV line | 2018-01-31 14:40 | 2018-01-31 17:32 | 2:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 159:55 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
B.Baria | B.Baria -Shahjibazar 230 kV line-2 | 2018-01-01 09:19 | 2018-01-01 16:59 | 7:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-01-01 09:08 | 2018-01-01 17:24 | 8:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-1 | 2018-01-02 09:04 | 2018-01-02 16:08 | 7:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-01-02 09:25 | 2018-01-02 15:44 | 6:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-1 | 2018-01-02 09:50 | 2018-01-02 14:10 | 4:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-1 | 2018-01-02 13:50 | 2018-01-02 17:07 | 3:17 | S/O | Due to PT maintenance | 0 | 0 | No interruption
B.Baria | B.Baria -Shahjibazar 132 kV line-2 | 2018-01-02 09:18 | 2018-01-02 13:50 | 4:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Ashuganj 132 kV line-1 | 2018-01-03 08:37 | 2018-01-03 17:18 | 8:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2018-01-03 09:36 | 2018-01-03 15:51 | 6:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Feni 132 kV line-2 | 2018-01-03 14:54 | 2018-01-03 17:35 | 2:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV line-2 | 2018-01-06 09:14 | 2018-01-06 16:42 | 7:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Ashuganj 230 kV line-2 | 2018-01-07 09:41 | 2018-01-07 16:41 | 7:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj P/S-Fenchuganj S/S 132 kV line-2 | 2018-01-07 09:20 | 2018-01-07 17:06 | 7:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Ashuganj 230 kV line-2 | 2018-01-08 09:47 | 2018-01-08 21:04 | 11:17 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2018-01-08 09:06 | 2018-01-08 18:08 | 9:02 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2018-01-09 09:01 | 2018-01-09 16:47 | 7:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2018-01-10 09:02 | 2018-01-10 16:33 | 7:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2018-01-14 09:19 | 2018-01-14 16:42 | 7:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2018-01-14 09:11 | 2018-01-14 15:10 | 5:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2018-01-15 09:11 | 2018-01-15 17:10 | 7:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-01-15 09:42 | 2018-01-15 18:28 | 8:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Meghnaghat 230 kV line-2 | 2018-01-16 10:10 | 2018-01-16 15:20 | 5:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2018-01-16 09:09 | 2018-01-16 16:33 | 7:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Sylhet 132 kV line | 2018-01-16 09:38 | 2018-01-16 18:03 | 8:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2018-01-17 09:20 | 2018-01-17 16:30 | 7:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-01-17 08:39 | 2018-01-17 18:20 | 9:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2018-01-19 00:27 | 2018-01-19 15:17 | 14:50 | S/O | Due to high voltage at Fenchuganj S/S | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-2 | 2018-01-18 06:34 | 2018-01-18 14:12 | 7:38 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-01-18 09:27 | 2018-01-18 16:16 | 6:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line | 2018-01-20 08:15 | 2018-01-20 17:08 | 8:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line-1 | 2018-01-21 08:18 | 2018-01-21 16:09 | 7:51 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2018-01-21 10:11 | 2018-01-21 16:44 | 6:33 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comilla(N) 230 kV line-1 | 2018-01-22 04:34 | 2018-01-22 05:14 | 0:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-1 | 2018-01-22 09:04 | 2018-01-22 17:28 | 8:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2018-01-23 09:48 | 2018-01-23 11:26 | 1:38 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV line-2 | 2018-01-23 11:28 | 2018-01-23 12:58 | 1:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2018-01-24 11:14 | 2018-01-24 14:50 | 3:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-2 | 2018-01-24 09:02 | 2018-01-24 16:25 | 7:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line-2 | 2018-01-25 09:45 | 2018-01-25 17:12 | 7:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-2 | 2018-01-25 10:03 | 2018-01-25 13:08 | 3:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV line-1 | 2018-01-25 13:10 | 2018-01-25 16:29 | 3:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-1 | 2018-01-25 11:50 | 2018-01-25 12:11 | 0:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line-2 | 2018-01-27 09:30 | 2018-01-27 15:50 | 6:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Chandpur 132 kV line-2 | 2018-01-28 09:30 | 2018-01-28 17:28 | 7:58 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comillla(N) | Comillla(N)-Shahjibazar 230 kV line-1 | 2018-01-29 09:54 | 2018-01-29 11:58 | 2:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-1 | 2018-01-29 08:21 | 2018-01-29 12:58 | 4:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Feni-Hathazari 132 kV line-1 | 2018-01-30 08:30 | 2018-01-30 11:56 | 3:26 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Comiila(N) 230 kV line-1 | 2018-01-31 09:11 | 2018-01-31 16:39 | 7:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 306:42 |  | Unserved Energy: |  | 0
Page: 6/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Noapara | Noapara-Jessore 132 kV line-2 | 2018-01-01 09:09 | 2018-01-01 14:04 | 4:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bhola | Bhola-Barisal 230 kV line-2 | 2018-01-01 08:12 | 2018-01-01 17:00 | 8:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2018-01-02 09:18 | 2018-01-02 14:56 | 5:38 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-2 | 2018-01-02 09:24 | 2018-01-02 16:53 | 7:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bhearamara 132 kV line-1 | 2018-01-02 08:30 | 2018-01-02 15:57 | 7:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-2 | 2018-01-03 08:24 | 2018-01-03 14:49 | 6:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line-2 | 2018-01-03 08:33 | 2018-01-03 16:24 | 7:51 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bhearamara 132 kV line-1 | 2018-01-03 09:30 | 2018-01-03 16:20 | 6:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-2 | 2018-01-04 09:10 | 2018-01-04 14:50 | 5:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2018-01-04 08:21 | 2018-01-04 16:26 | 8:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bhearamara 132 kV line-1 | 2018-01-04 08:55 | 2018-01-04 16:09 | 7:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-07 08:01 | 2018-01-07 17:17 | 9:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bhearamara 132 kV line-2 | 2018-01-07 08:14 | 2018-01-07 15:56 | 7:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-08 08:10 | 2018-01-08 18:23 | 10:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2018-01-09 08:07 | 2018-01-09 16:21 | 8:14 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-09 08:20 | 2018-01-09 17:08 | 8:48 | S/O | Due to annual maintenance | 18 | 158.4 | Power interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-01-14 07:53 | 2018-01-14 16:55 | 9:02 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-14 08:44 | 2018-01-14 17:09 | 8:25 | S/O | Due to annual maintenance | 18 | 67.5 | Power interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2018-01-15 08:13 | 2018-01-15 17:05 | 8:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-15 08:28 | 2018-01-15 15:32 | 7:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2018-01-16 08:06 | 2018-01-16 15:50 | 7:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-16 08:15 | 2018-01-16 17:26 | 9:11 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-17 08:20 | 2018-01-17 17:25 | 9:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-2 | 2018-01-18 08:22 | 2018-01-18 16:37 | 8:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-18 08:18 | 2018-01-18 16:53 | 8:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulna(C) | Khulna©-Noapara 132 kV line-2 | 2018-01-18 10:22 | 2018-01-18 12:50 | 2:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-19 08:09 | 2018-01-19 17:59 | 9:50 | S/O | Due to annual maintenance | 30 | 295 | Power interruption
Gopalganj | Gopalganj-Madaripur 132 kV line | 2018-01-19 08:07 | 2018-01-19 17:58 | 9:51 | S/O | Due to annual maintenance | 24 | 236.4 | Power interruption
Goalpara | Goalpara-Khulna© 132 kV line-1 | 2018-01-19 10:25 | 2018-01-19 12:07 | 1:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Goalpara-Khulna© 132 kV line-2 | 2018-01-19 11:35 | 2018-01-19 13:03 | 1:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-20 08:15 | 2018-01-20 17:16 | 9:01 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2018-01-21 09:13 | 2018-01-21 13:28 | 4:15 | S/O | Due to annual maintenance | 15 | 63.75 | Power interruption
Faridpur P/S | Faridpur P/S-Faridpur S/S 132 kV line | 2018-01-22 09:06 | 2018-01-22 15:36 | 6:30 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur P/S | Faridpur P/S-Faridpur S/S 132 kV line | 2018-01-23 09:26 | 2018-01-23 16:10 | 6:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-1 & 2 | 2018-01-24 09:03 | 2018-01-24 16:48 | 7:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-1 | 2018-01-25 08:40 | 2018-01-25 17:20 | 8:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-2 | 2018-01-26 08:07 | 2018-01-26 14:32 | 6:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2018-01-26 14:37 | 2018-01-26 16:25 | 1:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV line-1 | 2018-01-27 11:05 | 2018-01-27 17:09 | 6:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Bheramara 230 kV line-1 | 2018-01-27 14:01 | 2018-01-27 15:09 | 1:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2018-01-28 09:24 | 2018-01-28 16:07 | 6:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barisal(Old) 132 kV line-2 | 2018-01-29 08:23 | 2018-01-29 09:45 | 1:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2018-01-29 09:02 | 2018-01-29 15:51 | 6:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 295:21 |  | Unserved Energy: |  | 821.05
Page: 7/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2018
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2018-01-01 09:12 | 2018-01-01 16:18 | 7:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2018-01-09 08:28 | 2018-01-09 15:51 | 7:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2018-01-10 09:15 | 2018-01-10 12:57 | 3:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2018-01-10 13:02 | 2018-01-10 14:59 | 1:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-2 | 2018-01-11 09:27 | 2018-01-11 17:13 | 7:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Jhenidah 132 kV line-1 | 2018-01-13 08:36 | 2018-01-13 14:54 | 6:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bottail | Bottail-Jhenidah 132 kV line-1 | 2018-01-14 09:02 | 2018-01-14 17:39 | 8:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2018-01-15 08:55 | 2018-01-15 17:31 | 8:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bottail | Bottail-Jhenidah 132 kV line-2 | 2018-01-16 08:47 | 2018-01-16 17:04 | 8:17 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-2 | 2018-01-17 08:37 | 2018-01-17 15:34 | 6:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-2 | 2018-01-18 09:01 | 2018-01-18 15:24 | 6:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Ishrdi 132 kV line-2 | 2018-01-25 09:03 | 2018-01-25 16:03 | 7:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-GK 132 kV line | 2018-01-26 09:10 | 2018-01-26 16:03 | 6:53 | S/O | Due to annual maintenance | 25 | 172.0833 | Power interruption
|  |  | Total : | 86:55 |  | Unserved Energy: |  | 172.0833
Bogra Grid Circle :
Bogra | Bogra-Natore 132 kV line-2 | 2018-01-02 08:45 | 2018-01-02 15:21 | 6:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Natore | Natore-Bogra 132 kV line-2 | 2018-01-03 08:52 | 2018-01-03 15:45 | 6:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Natore 132 kV line-2 | 2018-01-04 09:26 | 2018-01-04 15:22 | 5:56 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-01-06 09:20 | 2018-01-06 15:52 | 6:32 | S/O | Due to annual maintenance | 20 | 130.6667 | Power interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-01-07 08:55 | 2018-01-07 11:39 | 2:44 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 | 2018-01-08 10:34 | 2018-01-08 11:14 | 0:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-10 06:50 | 2018-01-10 16:18 | 9:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-12 06:46 | 2018-01-12 16:50 | 10:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-13 07:04 | 2018-01-13 16:28 | 9:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2018-01-13 10:14 | 2018-01-13 15:55 | 5:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-14 07:03 | 2018-01-14 16:40 | 9:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2018-01-14 10:37 | 2018-01-14 16:29 | 5:52 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-15 07:06 | 2018-01-15 15:51 | 8:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2018-01-15 10:26 | 2018-01-15 15:52 | 5:26 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-15 07:06 | 2018-01-15 15:41 | 8:35 | S/O | Due to project work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-2 | 2018-01-15 14:13 | 2018-01-15 14:55 | 0:42 | S/O | Due to high temperature at R-phase CT | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-16 07:07 | 2018-01-16 15:50 | 8:43 | S/O | Due to project work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2018-01-16 10:05 | 2018-01-16 16:14 | 6:09 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-2 | 2018-01-17 10:25 | 2018-01-17 16:07 | 5:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2018-01-18 09:26 | 2018-01-18 17:48 | 8:22 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-01-19 07:32 | 2018-01-19 16:50 | 9:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-01-19 09:14 | 2018-01-19 15:20 | 6:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Saidpur-Purbasadipur 132 kV line-2 | 2018-01-19 09:14 | 2018-01-19 15:10 | 5:56 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-01-20 07:26 | 2018-01-20 15:41 | 8:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-01-21 07:23 | 2018-01-21 17:49 | 10:26 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-01-22 07:47 | 2018-01-22 16:55 | 9:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-01-23 09:09 | 2018-01-24 00:30 | 15:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2018-01-23 08:12 | 2018-01-23 16:39 | 8:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2018-01-24 09:05 | 2018-01-24 16:26 | 7:21 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 & 2 | 2018-01-24 08:17 | 2018-01-24 16:49 | 8:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-2 | 2018-01-25 06:42 | 2018-01-25 16:54 | 10:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-01-25 09:05 | 2018-01-25 16:50 | 7:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2018-01-26 10:16 | 2018-01-26 12:57 | 2:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Bogra | Bogra 132 S/S-Bogra 230 kV line-1 | 2018-01-26 14:37 | 2018-01-26 17:27 | 2:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2018-01-27 09:29 | 2018-01-27 15:47 | 6:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2018-01-28 09:30 | 2018-01-28 15:10 | 5:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV line-2 | 2018-01-29 09:30 | 2018-01-29 14:43 | 5:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 261:20 |  | Unserved Energy: |  | 130.6667
Others :
Ullon | Ullon-Dhanmondi 132 kV line-2 | 2018-01-03 08:12 | 2018-01-03 16:48 | 8:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Maniknagar | Maniknagar-Narinda 132 kV line-2 | 2018-01-12 09:20 | 2018-01-12 16:37 | 7:17 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Ullon | Ullon-Dhanmondi 132 kV line-1 | 2018-01-30 09:34 | 2018-01-30 13:45 | 4:11 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 20:04 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 1461:59 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January' 2018
| Area | Previous Month (December 2017) |  |  |  | Current Month (January 2018)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 5 | 1 | 84 | 90 | 4 | 3 | 74 | 81
2 | Dhaka (South) Grid Circle. | 6 | 3 | 79 | 88 | 3 | 2 | 61 | 66
3 | Chittagong Grid Circle. | 3 | 2 | 46 | 51 | 3 | 1 | 48 | 52
4 | Comilla Grid Circle. | 8 | 2 | 57 | 67 | 18 | 5 | 63 | 86
5 | Khulna Grid Circle. | 10 | 1 | 57 | 68 | 2 | - | 50 | 52
6 | Bheramara HVDC Grid Circle | 3 | - | 15 | 18 | 3 | - | 21 | 24
7 | Bogra Grid Circle. | 4 | 4 | 48 | 56 | 13 | 1 | 59 | 73
8 | Others | 1 | - | 7 | 8 | 4 | - | 3 | 7
9 | Total | 40 | 13 | 393 | 446 | 50 | 12 | 379 | 441
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January' 2018
| Area | Previous Month (December 2017) |  |  |  | Current Month (January 2018)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 19.17 | - | 414.5 | 433.67 | 186.33 | - | 132 | 318.33
2 | Dhaka ( South) grid circle | 31.43 | - | 61.33 | 92.76 | 10.83 | - | 157 | 167.83
3 | Chittagong grid circle. | - | - | 216.7 | 216.7 | 28.8 | - | - | 28.8
4 | Comilla grid circle. | 398.93 |  | 57.5 | 456.43 | 45.27 | 124.48 | 57.5 | 227.25
5 | Khulna grid circle. | 12.53 | - | - | 12.53 | 67.08 | - | 821.05 | 888.13
6 | Bheramara HVDC grid circle | - | - | 49.17 | 49.17 | - | - | 363.08 | 363.08
7 | Bogra grid circle. | - | 10.53 | 381.25 | 391.78 | 65.32 |  | 1014.57 | 1079.89
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 462.06 | 10.53 | 1180.45 | 1653.04 | 403.63 | 124.48 | 2545.2 | 3073.31
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January' 2018
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | - | 1 | 1 | - | - | 1 | 132
2 | Dhaka (South) | 5031.6 | 1 | 1 | 2 | 1 |  | 1 | 167.83
3 | Chittagong | 2042 | 1 |  | 1 | - | 1 |  | 28.8
4 | Khulna | 2434 | - | - | - | - | - | - | -
5 | Bheramara (HVDC) | 2423.3 | - | 1 | 1 |  | - | 1 | 191
6 | Bogra | 3145.6 |  | 3 | 3 | 2 | 1 | - | 883.9
7 | Comilla | 2981 | 3 | 1 | 4 | 2 | 1 | 1 | 99.43
| Total | 23365.5 | [6 empty] | 1502.96
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chittagong | 99.99%
4 | Khulna | 99.87%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.93% | [6 empty] | Information Management Division
7 | Comilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January' 2018
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 |  | 1 | - | 186.33
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 1 | 5 | 6 | - | - | 6 | 888.13
5 | Bheramara (HVDC) | 598.7 |  | - | 1 | 1 | - | - | 1 | 172.08
6 | Bogra | 1803.3 | 38 | 4 | 1 | 5 | 4 | - | 1 | 195.99
7 | Comilla | 1648.16 | 17 | 2 | - | 2 |  | 2 | - | 127.82
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1570.35
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.94%
3 | Chittagong | 99.99%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.97% | [7 empty] | Executive Engineer
6 | Bogra | 100% | [7 empty] | Information Management Division
7 | Comilla | 99.92% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January' 2018
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
January | 16 | - | 1 | 23 min | - | - | - | - | 1 | 37min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:January' 2018
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 1 | 0:52 | 215 | 186.3333 | Due to tripping of Mymensingh -RPCL 132 kV line-1
Joydevpur | 1 | 4:24 | 30 | 132 | Due to S/D of 132/33 kV Transformer T-4
Munshiganj | 1 | 0:26 | 25 | 10.8333 | Due to tripping of 132 kV Bus
Siddhirganj | 1 | 5:14 | 26 | 157 | Due to S/D of 132/33 kV Transformer T-1
Cox'sbazar | 1 | 0:54 | 32 | 28.8 | Due to tripping of 132/33 kV Transformer T1
B.baria | 2 | 0:33 | 42 | 23.1 | Due to tripping of 132/33 kV Transformers T1 , T2& T3
|  | 0:23 | 40 | 15.3333 | Due to tripping of 132/33 kV Transformers T1 , T2& T3
Comilla(N) | 1 | 0:21 | 10 | 3.5 | Due to tripping of 132/33 kV Transformer T4
Shahjibazar | 1 | 0:37 | 177 | 109.15 | Due to tripping of Shahjibazar-Sreemongal 132 kV line-1 & 2
Ashuganj | 1 | 0:57 | 140 | 18.6667 | Due to tripping of Ashuganj-Kishoreganj 132 kV line-1
Bibiyana | 1 | 3:53 | 30 | 57.5 | Due to S/D of 230 kV bus-2
Madaripur | 1 | 1:55 | 35 | 67.0833 | Due to tripping of Madaripur-Gopalganj 132 kV line
Barisal | 3 | 8:48 | 18 | 158.4 | Due to S/D of Barisal-Patuakhali 132 kV line
|  | 8:25 | 18 | 67.5 | Due to S/D of Barisal-Patuakhali 132 kV line
|  | 9:50 | 30 | 295 | Due to S/D of Barisal-Patuakhali 132 kV line
Gopalganj | 1 | 9:51 | 24 | 236.4 | Due to S/D of Gopalganj-Madaripur 132 kV line
Barisal | 1 | 4:15 | 15 | 63.75 | Due to S/D of Barisal-Patuakhali 132 kV line
Bheramara HVDC | 2 | 6:22 | 30 | 191 | Due to S/D of 132 kV bus
|  | 6:53 | 25 | 172.0833 | Due to S/D of Bharamara-GK project 132 kV line
Rajshahi | 1 | 0:18 | 54 | 16.2 | Due to tripping of Rajshahi-C.Nawabganj 132 kV line
Bogra | 1 | 0:11 | 175 | 32.0833 | Due to tripping of Bogra-Naogaon 132 kV line-2
Rangpur | 1 | 0:09 | 78 | 11.7 | Due to tripping of Rangpur-Lalmonirhat 132 kV line
Rangpur | 1 | 0:04 | 80 | 5.3333 | Due to tripping of Rangpur-Lalmonirhat 132 kV line
Bogra | 1 | 1:00 | 40 | 40 | Due to S/D of 132/33 kV Transformer-T3
Purbasadipur | 2 | 7:32 | 58 | 436.9333 | Due to S/D of 132 kV Bus
|  | 7:01 | 58 | 406.9667 | Due to S/D of 132 kV Bus
Saidpur | 1 | 6:32 | 20 | 130.6667 | Due to tripping of Saidpur-Purbasadipur 132 kV line
| Total unserved energy : |  |  | 3073.3167 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 96 | 13 | 2018-01-01 | 10:00
2 | Munsiganj | 86 | 23 | 2018-01-01 | 19:00
3 | Megnaghat | 56 | 4 | 2018-01-01 | 11:00
4 | Shyampur | 146 | 25 | 2018-01-01 | 09:00
5 | Bhulta | 158 | 22 | 2018-01-01 | 19:30
6 | Madanganj | 44 | 18 | 2018-01-01 | 12:00
7 | Shitalakhya | 97 | 9 | 2018-01-01 | 10:00
8 | Rahim steel | 22 | 30 | 2018-01-01 | 9:00
9 | Matuail | 78 | 11 | 2018-01-01 | 12:00
10 | Ghorasal | 68 | 1 | 2018-01-01 | 18:30
11 | Narsingdi | 95 | 20 | 2018-01-01 | 20:00
12 | Haripur (SBU) | 78 | 25 | 2018-01-01 | 19:00
13 | Ullon | 63 | 1 | 2018-01-01 | 18:00
14 | Hasnabad | 156 | 1 | 2018-01-01 | 19:30
15 | Magbazar | 79 | 17 | 2018-01-01 | 18:00
16 | Maniknagar | 66 | 30 | 2018-01-01 | 18:30
17 | Bangabhaban | 26 | 23 | 2018-01-01 | 17:00
18 | Narinda | 62 | 1 | 2018-01-01 | 19:00
19 | Dhanmondi | 88 | 9 | 2018-01-01 | 18:30
20 | Lalbag | 68 | 18 | 2018-01-01 | 13:00
21 | Madartek | 33 | 15 | 2018-01-01 | 19:00
22 | Mirpur | 88 | 11 | 2018-01-01 | 19:00
23 | Kalyanpur | 84 | 2 | 2018-01-01 | 18:00
24 | Gulshan | 72 | 1 | 2018-01-01 | 18:00
25 | Uttara | 58 | 2 | 2018-01-01 | 17:00
26 | Kamrangirchar | 60 | 25 | 2018-01-01 | 18:30
27 | Savar | 119 | 10 | 2018-01-01 | 18:30
28 | Bhasantec | 98 | 29 | 2018-01-01 | 19:00
29 | Agargaon | 38 | 28 | 2018-01-01 | 18:00
30 | Satmosjid | 64 | 18 | 2018-01-01 | 13:00
31 | Tongi | 108 | 7 | 2018-01-01 | 18:00
32 | Kabirpur | 149 | 30 | 2018-01-01 | 19:30
33 | Basundhara | 100 | 2 | 2018-01-01 | 19:30
34 | Manikganj | 76 | 18 | 2018-01-01 | 18:30
35 | Joydevpur | 202 | 17 | 2018-01-01 | 15:00
36 | New Tongi | 98 | 31 | 2018-01-01 | 12:00
37 | Kodda | 191 | 11 | 2018-01-01 | 15:00
38 | Tangail | 145 | 25 | 2018-01-01 | 20:00
39 | Mymensing | 170 | 28 | 2018-01-01 | 18:30
40 | Kishorganj | 65 | 9 | 2018-01-01 | 19:30
41 | Netrokona | 78 | 25 | 2018-01-01 | 18:30
42 | Jamalpur | 86 | 31 | 2018-01-01 | 18:30
43 | Sherpur | 78 | 28 | 2018-01-01 | 18:30
44 | Srimongal | 30 | 19 | 2018-01-01 | 18:30
45 | Shahjibazar | 77 | 18 | 2018-01-01 | 18:30
46 | Fenchuganj | 30 | 4 | 2018-01-01 | 18:30
47 | Khulawara | 28 | 1 | 2018-01-01 | 18:00
48 | Sylhet | 122 | 20 | 2018-01-01 | 19:00
49 | Chatak | 45 | 30 | 2018-01-01 | 19:30
50 | Comilla (S) | 132 | 25 | 2018-01-01 | 18:30
51 | Comilla(N) | 73 | 1 | 2018-01-01 | 19:00
52 | Chandpur | 83 | 6 | 2018-01-01 | 18:30
53 | Feni | 80 | 29 | 2018-01-01 | 19:00
54 | Chowmuhani | 136 | 6 | 2018-01-01 | 19:00
55 | Ashuganj | 44 | 31 | 2018-01-01 | 20:00
56 | Daudkandi | 76 | 15 | 2018-01-01 | 19:30
57 | B.Baria | 84 | 29 | 2018-01-01 | 18:30
58 | Madanhat | 50 | 10 | 2018-01-01 | 19:00
59 | Hathazari | 86 | 25 | 2018-01-01 | 19:00
60 | Khulshi | 154 | 29 | 2018-01-01 | 13:00
61 | Halishahar | 93 | 30 | 2018-01-01 | 15:00
62 | Baraulia | 131 | 13 | 2018-01-01 | 13:00
63 | Sikalbaha | 130 | 2 | 2018-01-01 | 19:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2018
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
64 | Dohazari | 72 | 28 | 2018-01-01 | 19:00
65 | Cox'sbazar | 71 | 2 | 2018-01-01 | 18:00
66 | Chandraghona | 30 | 6 | 2018-01-01 | 19:00
67 | Kaptai | 4 | 5 | 2018-01-01 | 18:30
68 | A. Khaer Stl. | 24 | 1 | 2018-01-01 | 18:00
69 | Bakulia | 84 | 2 | 2018-01-01 | 19:00
70 | Julda | 20 | 21 | 2018-01-01 | 12:00
71 | TK chemical | 7 | 18 | 2018-01-01 | 17:00
72 | Modern Steel | 17 | 2 | 2018-01-01 | 07:00
73 | Shahmirpur | 23 | 6 | 2018-01-01 | 18:30
74 | Abul Khair 230 | 223 | 16 | 2018-01-01 | 9:00
75 | BSRM | 110 | 22 | 2018-01-01 | 9:00
76 | Goalpara | 29 | 29 | 2018-01-01 | 19:00
77 | Central s/s | 66 | 15 | 2018-01-01 | 19:30
78 | Noapara | 79 | 10 | 2018-01-01 | 18:30
79 | Jessore | 112 | 8 | 2018-01-01 | 18:00
80 | Jhenida | 78 | 13 | 2018-01-01 | 18:30
81 | Bottail | 88 | 9 | 2018-01-01 | 18:30
82 | G.K Project | 44 | 29 | 2018-01-01 | 18:30
83 | Faridpur | 118 | 9 | 2018-01-01 | 19:00
84 | Madaripur | 99 | 9 | 2018-01-01 | 20:00
85 | Gopalganj | 62 | 19 | 2018-01-01 | 20:00
86 | Bagerhat | 70 | 6 | 2018-01-01 | 18:30
87 | Mongla | 37 | 30 | 2018-01-01 | 12:00
88 | Satkhira | 68 | 29 | 2018-01-01 | 18:30
89 | Gallamari | 39 | 18 | 2018-01-01 | 13:00
90 | Magura | 38 | 16 | 2018-01-01 | 19:30
91 | Chuadanga | 62 | 13 | 2018-01-01 | 18:30
92 | Barisal | 88 | 17 | 2018-01-01 | 19:30
93 | Patuakhali | 68 | 8 | 2018-01-01 | 20:00
94 | Bhandaria | 64 | 23 | 2018-01-01 | 19:30
95 | Ishurdi | 138 | 3 | 2018-01-01 | 18:30
96 | Ruppur Paromanobik | 1 | 1 | 2018-01-01 | 1:00
97 | Natore | 88 | 25 | 2018-01-01 | 18:30
98 | Bogra | 181 | 23 | 2018-01-01 | 18:30
99 | Noagaon | 104 | 28 | 2018-01-01 | 19:00
100 | Rajshahi | 102 | 9 | 2018-01-01 | 20:00
101 | C.Nawabganj | 65 | 21 | 2018-01-01 | 19:30
102 | Amnura | 40 | 29 | 2018-01-01 | 18:30
103 | Pabna | 83 | 2 | 2018-01-01 | 19:00
104 | Shahjadpur | 74 | 31 | 2018-01-01 | 19:00
105 | Serajganj | 71 | 16 | 2018-01-01 | 19:30
106 | Niyamatpur | 86 | 21 | 2018-01-01 | 19:30
107 | Joypurhat | 43 | 10 | 2018-01-01 | 19:00
108 | Rangpur | 100 | 29 | 2018-01-01 | 19:00
109 | Lalmonirhat | 78 | 23 | 2018-01-01 | 19:00
110 | Saidpur | 106 | 30 | 2018-01-01 | 18:30
111 | Purbasadipur | 83 | 19 | 2018-01-01 | 19:30
112 | Thakurgaon | 55 | 17 | 2018-01-01 | 18:30
113 | Palashbari | 90 | 31 | 2018-01-01 | 18:30
114 | Barapukuria | 55 | 29 | 2018-01-01 | 18:30
115 | Panchagar | 34 | 30 | 2018-01-01 | 19:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January' 2018
Area | MW | Date | Hour | Remarks
Dhaka | 2805 | 25.01.18 | 18:30
Chittagong | 939 | 31.01.18 | 12:00
Khulna | 977 | 10.01.18 | 18:30
Rajshahi | 916 | 29.01.18 | 19:00
Comilla | 679 | 27.01.18 | 18:30
Mymensingh | 605 | 28.01.18 | 18:30
Sylhet | 313 | 31.01.18 | 19:30
Barisal | 186 | 17.01.18 | 19:30
Rangpur | 581 | 31.01.18 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2018
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 413 | 31 | 2018-01-01 | 20:00 | 393 | 9 | 2018-01-01 | 18:00
2 | Bheramara | 400 | 425 | 12 | 2018-01-01 | 3:00 | 401 | 25 | 2018-01-01 | 19:00
3 | Kaliakoir | 400 | 409 | 3 | 2018-01-01 | 14:00 | 383 | 22 | 2018-01-01 | 16:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 17 | 2018-01-01 | 01:00 | 225 | 2 | 2018-01-01 | 13:00
2 | Ishurdi | 230 | 243 | 19 | 2018-01-01 | 14:00 | 227 | 19 | 2018-01-01 | 20:00
3 | Ashuganj | 230 | 245 | 19 | 2018-01-01 | 9:00 | 234 | 1 | 2018-01-01 | 13:00
4 | Serajganj | 230 | 231 | 30 | 2018-01-01 | 3:00 | 214 | 19 | 2018-01-01 | 18:00
5 | Baghabari | 230 | 237 | 6 | 2018-01-01 | 4:00 | 219 | 20 | 2018-01-01 | 18:30
6 | Barapukuria | 230 | 232 | 6 | 2018-01-01 | 5:00 | 216 | 20 | 2018-01-01 | 18:30
7 | Bogra | 230 | 234 | 19 | 2018-01-01 | 14':00 | 212 | 19 | 2018-01-01 | 18:30
8 | Khulna South | 230 | 244 | 9 | 2018-01-01 | 17'00 | 218 | 4 | 2018-01-01 | 8:00
9 | Rampura | 230 | 233 | 5 | 2018-01-01 | 24:00 | 214 | 1 | 2018-01-01 | 12:00
10 | Haripur | 230 | 232 | 21 | 2018-01-01 | 2:00 | 213 | 1 | 2018-01-01 | 12:00
11 | Hasnabad | 230 | 236 | 22 | 2018-01-01 | 3:00 | 215 | 1 | 2018-01-01 | 13:00
12 | Aminbazar | 230 | 235 | 20 | 2018-01-01 | 06:00 | 215 | 1 | 2018-01-01 | 12:00
13 | Tongi | 230 | 235 | 19 | 2018-01-01 | 13:00 | 220 | 1 | 2018-01-01 | 11:00
14 | Comilla (N) | 230 | 241 | 29 | 2018-01-01 | 7:00 | 228 | 3 | 2018-01-01 | 15:00
15 | Hathazari | 230 | 233 | 3 | 2018-01-01 | 22:00 | 205 | 2 | 2018-01-01 | 12:00
16 | Megnaghat | 230 | 238 | 21 | 2018-01-01 | 2:00 | 221 | 3 | 2018-01-01 | 12:00
17 | Fenchuganj | 230 | 245 | 3 | 2018-01-01 | 22:00 | 235 | 9 | 2018-01-01 | 18:00
18 | Siddhirganj | 230 | 242 | 16 | 2018-01-01 | 03:00 | 209 | 27 | 2018-01-01 | 12:00
19 | Maniknagar | 230 | 240 | 15 | 2018-01-01 | 4:00 | 210 | 27 | 2018-01-01 | 12:00
20 | Old Airport | 230 | 233 | 19 | 2018-01-01 | 03:00 | 216 | 3 | 2018-01-01 | 12:00
21 | Barisal | 230 | 241 | 20 | 2018-01-01 | 10:00 | 226 | 3 | 2018-01-01 | 12:00
22 | AKSML | 230 | 233 | 20 | 2018-01-01 | 14:00 | 206 | 18 | 2018-01-01 | 12:00
23 | BSRM | 230 | 236 | 20 | 2018-01-01 | 14:00 | 211 | 2 | 2018-01-01 | 11:00
24 | Bibiyana | 230 | 245 | 22 | 2018-01-01 | 03:00 | 233 | 22 | 2018-01-01 | 16:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 12 | 2018-01-01 | 05:00 | 131 | 3 | 2018-01-01 | 12:00
2 | Munsiganj | 132 | 140 | 12 | 2018-01-01 | 13:00 | 130 | 1 | 2018-01-01 | 12:00
3 | Megnaghat | 132 | 139 | 20 | 2018-01-01 | 7:00 | 130 | 21 | 2018-01-01 | 15:00
4 | Shyampur | 132 | 138 | 28 | 2018-01-01 | 19:00 | 125 | 2 | 2018-01-01 | 16:00
5 | Bhulta | 132 | 139 | 5 | 2018-01-01 | 11:00 | 120 | 3 | 2018-01-01 | 12:00
6 | Madanganj | 132 | 140 | 21 | 2018-01-01 | 18:00 | 130 | 1 | 2018-01-01 | 12:00
7 | Shitalakhya | 132 | 140 | 16 | 2018-01-01 | 5:00 | 126 | 3 | 2018-01-01 | 11:00
8 | Rahim Steal | 132 | 140 | 6 | 2018-01-01 | 03:00 | 132 | 9 | 2018-01-01 | 13:00
9 | Matuail | 132 | 139 | 15 | 2018-01-01 | 5:00 | 118 | 14 | 2018-01-01 | 12:00
10 | Ghorasal | 132 | 144 | 16 | 2018-01-01 | 9:00 | 135 | 22 | 2018-01-01 | 18:00
11 | Narsinghdi | 132 | 136 | 1 | 2018-01-01 | 1:00 | 134 | 1 | 2018-01-01 | 12:00
12 | Haripur (SBU) | 132 | 141 | 13 | 2018-01-01 | 8:00 | 130 | 20 | 2018-01-01 | 12:00
13 | Ullon | 132 | 137 | 5 | 2018-01-01 | 7:00 | 125 | 1 | 2018-01-01 | 12:00
14 | Hasnabad | 132 | 138 | 12 | 2018-01-01 | 18:30 | 126 | 3 | 2018-01-01 | 11:00
15 | Magbazar | 132 | 138 | 5 | 2018-01-01 | 8:00 | 125 | 8 | 2018-01-01 | 12:00
16 | Maniknagar | 132 | 135 | 12 | 2018-01-01 | 18:30 | 119 | 14 | 2018-01-01 | 12:00
17 | Bangabhaban | 132 | 138 | 6 | 2018-01-01 | 5:00 | 119 | 14 | 2018-01-01 | 12:00
18 | Narinda | 132 | 136 | 16 | 2018-01-01 | 6:00 | 116 | 4 | 2018-01-01 | 12:00
19 | Dhanmondi | 132 | 137 | 5 | 2018-01-01 | 07:00 | 120 | 3 | 2018-01-01 | 12:00
20 | Lalbag | 132 | 138 | 6 | 2018-01-01 | 5:00 | 121 | 3 | 2018-01-01 | 12:00
21 | Madartek | 132 | 137 | 5 | 2018-01-01 | 7:00 | 126 | 2 | 2018-01-01 | 12:00
22 | Mirpur | 132 | 139 | 5 | 2018-01-01 | 1:00 | 126 | 29 | 2018-01-01 | 15:00
23 | Kalyanpur | 132 | 140 | 3 | 2018-01-01 | 4:00 | 128 | 24 | 2018-01-01 | 11:00
24 | Gulshan | 132 | 137 | 5 | 2018-01-01 | 9:00 | 126 | 1 | 2018-01-01 | 11:00
25 | Uttara | 132 | 138 | 4 | 2018-01-01 | 3:00 | 126 | 22 | 2018-01-01 | 16:00
26 | Kamrangirchar | 132 | 139 | 19 | 2018-01-01 | 18:00 | 123 | 3 | 2018-01-01 | 12:00
27 | Savar | 132 | 137 | 3 | 2018-01-01 | 3:00 | 126 | 22 | 2018-01-01 | 16:00
28 | Bhasantec | 132 | 136 | 4 | 2018-01-01 | 5:00 | 126 | 3 | 2018-01-01 | 12:00
29 | Agargaon | 132 | 136 | 4 | 2018-01-01 | 5:00 | 127 | 7 | 2018-01-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Satmosjid | 132 | 136 | 5 | 2018-01-01 | 16:00 | 125 | 28 | 2018-01-01 | 18:00
31 | Tongi | 132 | 140 | 12 | 2018-01-01 | 4:00 | 128 | 4 | 2018-01-01 | 1:00
32 | Kabirpur | 132 | 141 | 3 | 2018-01-01 | 13:00 | 127 | 8 | 2018-01-01 | 18:00
33 | Basundhara | 132 | 137 | 17 | 2018-01-01 | 2:00 | 127 | 1 | 2018-01-01 | 13:00
34 | Manikganj | 132 | 145 | 21 | 2018-01-01 | 2:00 | 134 | 2 | 2018-01-01 | 15:00
35 | Joydevpur | 132 | 143 | 5 | 2018-01-01 | 13:00 | 129 | 3 | 2018-01-01 | 12:00
36 | New Tongi | 132 | 141 | 26 | 2018-01-01 | 03:00 | 130 | 1 | 2018-01-01 | 12:00
37 | Kodda | 132 | 140 | 5 | 2018-01-01 | 13:00 | 130 | 6 | 2018-01-01 | 9:00
38 | Tangail | 132 | 140 | 3 | 2018-01-01 | 10:00 | 125 | 8 | 2018-01-01 | 18:00
39 | Mymensing | 132 | 140 | 20 | 2018-01-01 | 10:00 | 119 | 25 | 2018-01-01 | 18:30
40 | Kishorganj | 132 | 138 | 6 | 2018-01-01 | 06:00 | 126 | 25 | 2018-01-01 | 18:30
41 | Netrokona | 132 | 140 | 20 | 2018-01-01 | 20:00 | 115 | 23 | 2018-01-01 | 15:00
42 | Jamalpur | 132 | 140 | 7 | 2018-01-01 | 17:00 | 115 | 26 | 2018-01-01 | 12:00
43 | Sherpur | 132 | 141 | 20 | 2018-01-01 | 20:00 | 115 | 13 | 2018-01-01 | 6:00
44 | Srimongal | 132 | 144 | 5 | 2018-01-01 | 9:00 | 137 | 3 | 2018-01-01 | 13:00
45 | Shahjibazar | 132 | 143 | 20 | 2018-01-01 | 09:00 | 137 | 3 | 2018-01-01 | 11:00
46 | Fenchuganj | 132 | 143 | 5 | 2018-01-01 | 10:00 | 133 | 3 | 2018-01-01 | 12:00
47 | Khulawara | 132 | 144 | 2 | 2018-01-01 | 23:00 | 132 | 3 | 2018-01-01 | 12:00
48 | Sylhet | 132 | 142 | 20 | 2018-01-01 | 5:00 | 131 | 3 | 2018-01-01 | 12:00
49 | Chattak | 132 | 142 | 19 | 2018-01-01 | 05:00 | 125 | 9 | 2018-01-01 | 18:00
50 | Comilla(South) | 132 | 134 | 27 | 2018-01-01 | 01:00 | 123 | 1 | 2018-01-01 | 18:00
51 | Comilla (North) | 132 | 145 | 20 | 2018-01-01 | 23:00 | 126 | 31 | 2018-01-01 | 12:00
52 | Chandpur | 132 | 140 | 12 | 2018-01-01 | 1:00 | 122 | 22 | 2018-01-01 | 18:00
53 | Feni | 132 | 131 | 29 | 2018-01-01 | 7:00 | 120 | 23 | 2018-01-01 | 20:00
54 | Chowmuhani | 132 | 137 | 16 | 2018-01-01 | 2:00 | 111 | 31 | 2018-01-01 | 18:00
55 | Ashuganj | 132 | 145 | 5 | 2018-01-01 | 9:00 | 138 | 27 | 2018-01-01 | 15:00
56 | Daudkandi | 132 | 141 | 12 | 2018-01-01 | 14:00 | 121 | 24 | 2018-01-01 | 11:00
57 | Brahminbaria | 132 | 143 | 16 | 2018-01-01 | 8:00 | 136 | 4 | 2018-01-01 | 11:00
58 | Madanhat | 132 | 140 | 3 | 2018-01-01 | 22:00 | 126 | 2 | 2018-01-01 | 12:00
59 | Hathazari | 132 | 138 | 10 | 2018-01-01 | 24:00 | 125 | 2 | 2018-01-01 | 12:00
60 | Khulshi | 132 | 136 | 20 | 2018-01-01 | 14:00 | 119 | 2 | 2018-01-01 | 12:00
61 | Halishahar | 132 | 140 | 20 | 2018-01-01 | 07:00 | 122 | 2 | 2018-01-01 | 12:00
62 | Baraulia | 132 | 137 | 3 | 2018-01-01 | 22:00 | 120 | 2 | 2018-01-01 | 12:00
63 | Sikalbaha | 132 | 139 | 20 | 2018-01-01 | 07:00 | 121 | 2 | 2018-01-01 | 12:00
64 | Dohazari | 132 | 139 | 20 | 2018-01-01 | 14:00 | 122 | 1 | 2018-01-01 | 6:00
65 | Cox'sbazar | 132 | 136 | 20 | 2018-01-01 | 14:00 | 116 | 10 | 2018-01-01 | 18:00
66 | Chandraghona | 132 | 138 | 21 | 2018-01-01 | 14:00 | 122 | 31 | 2018-01-01 | 10:00
67 | Kaptai | 132 | 140 | 27 | 2018-01-01 | 24:00 | 124 | 31 | 2018-01-01 | 13:00
68 | A. Khaer Stl. | 132 | 136 | 4 | 2018-01-01 | 16:00 | 124 | 1 | 2018-01-01 | 6:00
69 | Bakulia | 132 | 137 | 29 | 2018-01-01 | 07:00 | 120 | 2 | 2018-01-01 | 12:00
70 | Julda | 132 | 138 | 9 | 2018-01-01 | 23:00 | 121 | 2 | 2018-01-01 | 12:00
71 | TK Chemical | 132 | 141 | 3 | 2018-01-01 | 22:00 | 125 | 2 | 2018-01-01 | 12:00
72 | Modern Steel | 132 | 137 | 9 | 2018-01-01 | 24:00 | 122 | 13 | 2018-01-01 | 17:00
73 | Shahmirpur | 132 | 138 | 27 | 2018-01-01 | 23:00 | 120 | 2 | 2018-01-01 | 12:00
74 | Goalpara | 132 | 140 | 17 | 2018-01-01 | 22:00 | 122 | 4 | 2018-01-01 | 8:00
75 | Khulna Central | 132 | 139 | 14 | 2018-01-01 | 22:00 | 121 | 4 | 2018-01-01 | 8:00
76 | Noapara | 132 | 137 | 8 | 2018-01-01 | 22:00 | 118 | 24 | 2018-01-01 | 7:00
77 | Jessore | 132 | 133 | 8 | 2018-01-01 | 22:00 | 111 | 24 | 2018-01-01 | 08:00
78 | Jhenida | 132 | 135 | 1 | 2018-01-01 | 2:00 | 106 | 24 | 2018-01-01 | 18:00
79 | Bottail | 132 | 140 | 6 | 2018-01-01 | 03:00 | 125 | 19 | 2018-01-01 | 08:00
80 | G.K.Project | 132 | 142 | 6 | 2018-01-01 | 03:00 | 130 | 19 | 2018-01-01 | 18:30
81 | Faridpur | 132 | 135 | 2 | 2018-01-01 | 17:00 | 125 | 22 | 2018-01-01 | 21:00
82 | Madaripur | 132 | 136 | 10 | 2018-01-01 | 17:00 | 123 | 19 | 2018-01-01 | 19:00
83 | Gopalganj | 132 | 139 | 6 | 2018-01-01 | 17:00 | 120 | 19 | 2018-01-01 | 18:30
84 | Bagerhat | 132 | 140 | 17 | 2018-01-01 | 22:00 | 121 | 4 | 2018-01-01 | 8:00
85 | Mongla | 132 | 136 | 19 | 2018-01-01 | 13:00 | 118 | 16 | 2018-01-01 | 13:00
86 | Satkhira | 132 | 139 | 29 | 2018-01-01 | 10:00 | 123 | 4 | 2018-01-01 | 8:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2018
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
87 | Gallamari | 132 | 140 | 21 | 2018-01-01 | 10:00 | 122 | 10 | 2018-01-01 | 7:00
88 | Magura | 132 | 138 | 18 | 2018-01-01 | 3:00 | 110 | 14 | 2018-01-01 | 18:00
89 | Chuadanga | 132 | 136 | 6 | 2018-01-01 | 1:00 | 101 | 24 | 2018-01-01 | 8:00
90 | Barisal | 132 | 141 | 10 | 2018-01-01 | 17:00 | 130 | 9 | 2018-01-01 | 7:00
91 | Patuakhali | 132 | 141 | 10 | 2018-01-01 | 17:00 | 130 | 9 | 2018-01-01 | 7:00
92 | Bhandaria | 132 | 140 | 17 | 2018-01-01 | 14:00 | 120 | 7 | 2018-01-01 | 11:00
93 | Ishurdi | 132 | 140 | 6 | 2018-01-01 | 5:00 | 129 | 19 | 2018-01-01 | 20:00
94 | Ruppur Paromanobik | 132 | 138 | 22 | 2018-01-01 | 3:00 | 130 | 18 | 2018-01-01 | 8:00
95 | Natore | 132 | 140 | 13 | 2018-01-01 | 3:00 | 127 | 6 | 2018-01-01 | 18:00
96 | Bogra | 132 | 140 | 19 | 2018-01-01 | 14:00 | 124 | 24 | 2018-01-01 | 20:00
97 | Noagaon | 132 | 136 | 6 | 2018-01-01 | 5:00 | 120 | 19 | 2018-01-01 | 18:30
98 | Rajshahi | 132 | 136 | 3 | 2018-01-01 | 3:00 | 123 | 24 | 2018-01-01 | 8:00
99 | C.Nawabganj | 132 | 134 | 2 | 2018-01-01 | 17:00 | 120 | 4 | 2018-01-01 | 8:00
100 | Amnura | 132 | 142 | 23 | 2018-01-01 | 18:30 | 120 | 4 | 2018-01-01 | 8:00
101 | Pabna | 132 | 135 | 13 | 2018-01-01 | 4:00 | 120 | 11 | 2018-01-01 | 20:00
102 | Shahjadpur | 132 | 142 | 12 | 2018-01-01 | 14:00 | 131 | 9 | 2018-01-01 | 12:00
103 | Serajganj | 132 | 138 | 8 | 2018-01-01 | 4:00 | 123 | 13 | 2018-01-01 | 19:00
104 | Niyamatpur | 132 | 137 | 13 | 2018-01-01 | 13:00 | 113 | 27 | 2018-01-01 | 19:00
105 | Joypurhat | 132 | 137 | 5 | 2018-01-01 | 2:00 | 117 | 31 | 2018-01-01 | 8:00
106 | Rangpur | 132 | 130 | 5 | 2018-01-01 | 7:00 | 109 | 27 | 2018-01-01 | 18:30
107 | Lalmonirhat | 132 | 130 | 14 | 2018-01-01 | 1:00 | 102 | 21 | 2018-01-01 | 19:30
108 | Saidpur | 132 | 130 | 1 | 2018-01-01 | 5:00 | 106 | 31 | 2018-01-01 | 8:00
109 | Purbasadipur | 132 | 132 | 5 | 2018-01-01 | 3:00 | 112 | 23 | 2018-01-01 | 19:00
110 | Thakurgaon | 132 | 126 | 1 | 2018-01-01 | 6:00 | 104 | 20 | 2018-01-01 | 19:00
111 | Palashbari | 132 | 131 | 6 | 2018-01-01 | 6:00 | 112 | 25 | 2018-01-01 | 8:00
112 | Barapukuria | 132 | 132 | 6 | 2018-01-01 | 12:00 | 116 | 20 | 2018-01-01 | 18:30
113 | Panchagar | 132 | 125 | 3 | 2018-01-01 | 4:00 | 99 | 20 | 2018-01-01 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:January' 2018
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 114 | 330
IP-299421 | Hasnabad | TR2 | 225 | 100 | 330 | 25.01.18 | 23:00
|  | TR3 | 225 | 106 | 320
|  | TR1 | 225 | 105 | 295
IP-299866 | Tongi | TR2 | 225 | 105 | 295 | 27.01.18 | 18:30
|  | TR3 | 225 | 105 | 295
|  | TR1 | 225 | 150 | 410
IP-299427 | Haripur | TR2 | 225 | 150 | 410 | 03.01.18 | 23:00
|  | TR3 | 225 | 150 | 410
|  | TR1 | 225 | 120 | 330
IP-299728 | Rampura | TR2 | 225 | 120 | 330 | 17.01.18 | 18:30
|  | TR3 | 225 | 120 | 330
|  | TR1 | 225 | 109 | 302
IP-299264 | Aminbazar | TR2 | 225 | 109 | 302 | 08.12.17 | 15:00
|  | TR3 | 225 | 116 | 331
| Maniknagar | TR1 | 300 | 107 | 340 | 03.01.18 | 12:00
|  | TR2 | 300 | 107 | 340
IP-399266 | Comilla (N) | TR1 | 225 | 130 | 360 | 28.12.17 | 20:00
|  | TR2 | 225 | 133 | 368
| Fenchuganj | TR1 | 300 | - | - | - | - | Transformer is unavailable since 12.12.17
|  | TR1 | 150 | 100 | 280
IP-399428 | Hathazari | TR3 | 150 | 100 | 280 | 22.01.18 | 18:00
|  | TR4 | 150 | 100 | 280
|  | TR1 | 225 | 170 | 460
| Ishurdi | TR2 | 225 | 170 | 460 | 19.01.18 | 18:30
IP-499474 |  | TR3 | 225 | 170 | 460
| Khulna(S) | TR1 | 225 | 169 | 433
IP-58001/58002 |  | TR2 | 225 | 169 | 433 | 31.01.18 | 21:00
| Bogra | TR1 | 225 | 191 | 554 | 29.01.18 | 7:00
IP-43002/499264 |  | TR2 | 225 | 191 | 554
IP-499224 | Baghabari | TR1 | 225 | 135 | 410 | 20.01.18 | 19:00
| Barapukuria | TR1 | 225 | 208 | 1040 | 28.01.18 | 18:00 | Due to unavailability of 230 kV side meters
|  | TR2 | 225 | 208 | 1040 |  |  | 132 kV current is being provided
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:January' 2018 | [6 empty] | (For Evening Peak) | [7 empty] | Month:January' 2018 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-01-18 | 7651 | 7651 | - | - | - | - | - | - | - | - | - | - | - | - | 01-01-18 | 5926.5 | 5926.5 | - | - | - | - | - | - | - | - | - | - | - | -
02-01-18 | 7782 | 7782 | - | - | - | - | - | - | - | - | - | - | - | - | 02-01-18 | 5563 | 5563 | - | - | - | - | - | - | - | - | - | - | - | -
03-01-18 | 7717 | 7717 | - | - | - | - | - | - | - | - | - | - | - | - | 03-01-18 | 5927.9 | 5927.9 | - | - | - | - | - | - | - | - | - | - | - | -
04-01-18 | 7739 | 7739 | - | - | - | - | - | - | - | - | - | - | - | - | 04-01-18 | 5954.2 | 5954.2 | - | - | - | - | - | - | - | - | - | - | - | -
05-01-18 | 6967 | 6967 | - | - | - | - | - | - | - | - | - | - | - | - | 05-01-18 | 5130.2 | 5130.2 | - | - | - | - | - | - | - | - | - | - | - | -
06-01-18 | 7657 | 7657 | - | - | - | - | - | - | - | - | - | - | - | - | 06-01-18 | 5455 | 5455 | - | - | - | - | - | - | - | - | - | - | - | -
07-01-18 | 7700 | 7700 | - | - | - | - | - | - | - | - | - | - | - | - | 07-01-18 | 5770.5 | 5770.5 | - | - | - | - | - | - | - | - | - | - | - | -
08-01-18 | 7868 | 7868 | - | - | - | - | - | - | - | - | - | - | - | - | 08-01-18 | 5888 | 5888 | - | - | - | - | - | - | - | - | - | - | - | -
09-01-18 | 7895 | 7895 | - | - | - | - | - | - | - | - | - | - | - | - | 09-01-18 | 5997.3 | 5997.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-01-18 | 7755 | 7755 | - | - | - | - | - | - | - | - | - | - | - | - | 11-01-18 | 5894.2 | 5894.2 | - | - | - | - | - | - | - | - | - | - | - | -
12-01-18 | 7972 | 7972 | - | - | - | - | - | - | - | - | - | - | - | - | 12-01-18 | 6191.4 | 6191.4 | - | - | - | - | - | - | - | - | - | - | - | -
13-01-18 | 7020 | 7020 | - | - | - | - | - | - | - | - | - | - | - | - | 13-01-18 | 5357 | 5357 | - | - | - | - | - | - | - | - | - | - | - | -
14-01-18 | 7842 | 7842 | - | - | - | - | - | - | - | - | - | - | - | - | 14-01-18 | 6128 | 6128 | - | - | - | - | - | - | - | - | - | - | - | -
15-01-18 | 7627 | 7627 | - | - | - | - | - | - | - | - | - | - | - | - | 15-01-18 | 6176 | 6176 | - | - | - | - | - | - | - | - | - | - | - | -
16-01-18 | 7970 | 7970 | - | - | - | - | - | - | - | - | - | - | - | - | 16-01-18 | 6250 | 6250 | - | - | - | - | - | - | - | - | - | - | - | -
17-01-18 | 7784 | 7784 | - | - | - | - | - | - | - | - | - | - | - | - | 17-01-18 | 6120.4 | 6120.4 | - | - | - | - | - | - | - | - | - | - | - | -
18-01-18 | 8061 | 8061 | - | - | - | - | - | - | - | - | - | - | - | - | 18-01-18 | 6170.3 | 6170.3 | - | - | - | - | - | - | - | - | - | - | - | -
19-01-18 | 7878 | 7878 | - | - | - | - | - | - | - | - | - | - | - | - | 19-01-18 | 6324.5 | 6324.5 | - | - | - | - | - | - | - | - | - | - | - | -
20-01-18 | 7273 | 7273 | - | - | - | - | - | - | - | - | - | - | - | - | 20-01-18 | 5368.3 | 5368.3 | - | - | - | - | - | - | - | - | - | - | - | -
21-01-18 | 7684 | 7684 | - | - | - | - | - | - | - | - | - | - | - | - | 21-01-18 | 5776 | 5776 | - | - | - | - | - | - | - | - | - | - | - | -
22-01-18 | 7841 | 7841 | - | - | - | - | - | - | - | - | - | - | - | - | 22-01-18 | 6216.5 | 6216.5 | - | - | - | - | - | - | - | - | - | - | - | -
23-01-18 | 7810 | 7810 | - | - | - | - | - | - | - | - | - | - | - | - | 23-01-18 | 6368.6 | 6368.6 | - | - | - | - | - | - | - | - | - | - | - | -
24-01-18 | 7881 | 7881 | - | - | - | - | - | - | - | - | - | - | - | - | 24-01-18 | 6303.8 | 6303.8 | - | - | - | - | - | - | - | - | - | - | - | -
25-01-18 | 7973 | 7973 | - | - | - | - | - | - | - | - | - | - | - | - | 25-01-18 | 6492.9 | 6492.9 | - | - | - | - | - | - | - | - | - | - | - | -
26-01-18 | 8183 | 8183 | - | - | - | - | - | - | - | - | - | - | - | - | 26-01-18 | 6541.9 | 6541.9 | - | - | - | - | - | - | - | - | - | - | - | -
27-01-18 | 7285 | 7285 | - | - | - | - | - | - | - | - | - | - | - | - | 27-01-18 | 5644.2 | 5644.2 | - | - | - | - | - | - | - | - | - | - | - | -
28-01-18 | 8051 | 8051 | - | - | - | - | - | - | - | - | - | - | - | - | 28-01-18 | 6180.3 | 6180.3 | - | - | - | - | - | - | - | - | - | - | - | -
29-01-18 | 8144 | 8144 | - | - | - | - | - | - | - | - | - | - | - | - | 29-01-18 | 6497.9 | 6497.9 | - | - | - | - | - | - | - | - | - | - | - | -
30-01-18 | 8251 | 8251 | - | - | - | - | - | - | - | - | - | - | - | - | 30-01-18 | 6576.8 | 6576.8 | - | - | - | - | - | - | - | - | - | - | - | -
30-01-18 | 8231 | 8231 | - | - | - | - | - | - | - | - | - | - | - | - | 30-01-18 | 6752.7 | 6752.7 | - | - | - | - | - | - | - | - | - | - | - | -
31-01-18 | 8186 | 8186 | - | - | - | - | - | - | - | - | - | - | - | - | 31-01-18 | 6766.4 | 6766.4 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January' 2018
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 8251 | 29/01/18 | 19:30
2 | Maximum day peak Genaration | MW | 6766.4 | 02/01/18 | 9:00
3 | Maximum Evening Peak Demand | MW | 8251 | 29/01/18 | 19:30
4 | Minimum Generation | MW | 4098 | 06/01/18 | 5:00
5 | Average of the daily evening peak Genaration | MW | 7796.0645
6 | Average of the daily day peak Genaration | MW | 6055.1839
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 4382.3751
12 | Total Generation by IPP | MKWH | 1249.5282 | % of total Gen. | 28.5126
13 | Total Generation by BPDB | MKWH | 2096.367 | " | 47.8363
14 | A) Total Generation by RPCL | MKWH | 93.6838 | '' | 2.1377
| B) Total Generation by REB | MKWH | 144.1813 | " | 3.29
| C) Total Generation by RENTAL | MKWH | 459.3671 | " | 10.4821
| D) Total Imported from India (HVDC) | MKWH | 274.1533 | " | 6.2558
| E) Total Imported from Tripura, India (A.C) | MKWH | 65.0944 | " | 1.4854
15 | Fuel wise Generation.
| A) Gas | MKWH | 3085.212 | % of total Gen. | 70.4%
| B) Oil | MKWH | 755.0002 | '' | 17.23%
| C) Hydro | MKWH | 44.0999 | '' | 1.006%
| D) Solar | MKWH | 0.16732 | '' | 0.003818%
| E) Coal | MKWH | 158.6481 | '' | 3.62%
| F) HVDC (Import from India) | MKWH | 274.1533 | '' | 6.256%
| G) A.C (Import from Tripura, India) | MKWH | 65.0944 | '' | 1.485%
16 | Maximun of the daily total Generation . | MKWH | 158.2832 | 25/01/18
17 | Monthly Load factor | % | 71.3888
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 7766.7946
| A) Gas | M.Taka | 2370.8689
| B) Liquid fuel | M.Taka | 5169.6499
| C) Coal | M.Taka | 226.2758
| D) HVDC (Import from India) | M.Taka | 1398.1817
| E) Tripura(Import from India) | M.Taka | 445.2458
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 424.8096 | 14/01/18
| A) Gas | M.Taka | 148.6433 | 14/01/18
| B) Liquid fuel | M.Taka | 264.9569 | 14/01/18
| C) Coal | M.Taka | 12.3669 | 15/01/18
| D) HVDC (Import from India) | M.Taka | 29.0253 | 02/01/18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.4299
| B) Excluding Hydro & Solar | Taka/KWHR | 2.4547
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97 | 31/01/18 | 06:00
b) | Actual | FT (MSL) | 98.56 | 31/01/18 | 06:00
22 | Peak Genaration of January 2017 | MW | 7836 | 26/01/17 | 19:30
23 | Peak Demand of January 2017 | MW | 7836 | 26/01/17 | 19:30
24 | Maximum peak Generation recorded upto 31/01/18 | MW | 9507 | 18/10/17 | 19:30
25 | Maximum peak Demand recorded upto 31/01/18 | MW | 9507 | 18/10/17 | 19:30
26 | Maximum load shed recorded upto 31/01/18 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.