## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October' 2017
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | October 2017 |  | September 2017 |  | October 2016
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9507 | 18/10/17 | 9431 | 26/09/17 | 8864 | 09/10/16 | 9507 | 18/10/17
|  |  | 19:30 |  | 21:00 |  | 19:30 |  | 19:30
2 | Minimum Generation (MW) | 3198 | 21/10/17 | 4928 | 02/09/17 | 5095 | 12/10/16 | - | -
|  |  | 7:00 |  | 10:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9507 | 18/10/17 | 9431 | 26/09/17 | 8864 | 09/10/16 | 9507 | 18/10/17
|  |  | 19:30 |  | 21:00 |  | 19:30 |  | 19:30
4 | Maximum Day Peak Generation (MW) | 8271.2 | 04/10/17 | 8614.2 | 28/9/2017 | 8598 | 12/10/2016 | 8743 | 07/6/17
|  |  | 10:00 |  | 11:00 |  | 12:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9507 | 18/10/17 | 9431 | 26/09/17 | 8900 | 02/10/16 | 9507 | 18/10/17
|  |  | 19:30 |  | 21:00 |  | 20:00 |  | 19:30
6 | Average Generation (MW) at Evening Peak | 8769.2258 |  | 8743.39 |  | 8515.65 |  | 9057.07 | Aug -17
7 | Average Generation (MW) at Day Peak | 7259.4897 |  | 7323.81 |  | 7089.06 |  | 7210.5 | May -17
8 | Maximum Power Import from India (MW) | 501 | 15/10/17 | 492 | 03/09/17 | 506 | 25/10/16 | 509 | 2017-07-03
|  |  | 7:00 |  | 2:00 |  | 19:30 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 04/10/17 | 168 | 14/09/17 | 110 | 17/10/2016 | 172 | 04/10/17
|  |  | 19:30 |  | 20:00 |  | 19:30 |  | 19:30
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | 234 | 2016-03-10 | 1459 | 2010-05-04
|  |  | - |  | - |  | 20:00 |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | 8640 | 2016-03-10 | 3707.5 | 05/04/10
|  |  | - |  | - |  | 20:00 |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | 100 | 02/10/16
|  |  | - |  | - |  | 20:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | 8789 | 02/10/16
|  |  | - |  | - |  | 20:00
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - |  | 02/10/16
[5 empty] | - | 234 | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - |  | 02/10/16
|  |  | - |  | - | 7490 | 12:00
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - |  | 02/10/16
|  |  | - |  | - | 234 | 12:00
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - |  | 02/10/16
|  |  | - |  | - | 7490 | 12:00
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | 8
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | 1
20 | Gross Generation of BPDB (MKWH) | 2597.5559 |  | 2695.82 |  | 2302
21 | Station Use of BPDB (MKWH) | 110.4848 |  | 102.17 |  | 106.74
22 | Net Generation of BPDB (MKWH) | 2487.0711 |  | 2593.65 |  | 2195.26
23 | Net Generation of IPP & RPCL (MKWH) | 1293.6906 |  | 1169.93 |  | 1503.11
24 | Net Generation of REB (MKWH) | 117.5319 |  | 117.9 |  | 111.68
24 | Net Generation of Rental Power Plant (MKWH) | 1138.9265 |  | 1144.63 |  | 1061.32
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5037.2201 |  | 5026.12 |  | 4871.37 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3531.4383 |  | 3432.58 |  | 3455.8 |  | 3531.44 | Oct-17
27 | Energy Generation by Diesel (MKWH) | 382.1462 |  | 389.61 |  | 319.4 |  | 424.76 | May-17
28 | Energy Generation by Furnace Oil (MKWH) | 1058.613 |  | 1107.93 |  | 965.03 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 119.1411 |  | 114.41 |  | 127.9 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.34114 |  | 0.17 |  |  |  |  | 26/09/17
31 | Energy Generation by Coal (MKWH) | 56.0252 |  | 83.59 |  | 109.98 |  | 123.5872 | April-14
32 | Enegry Import from India (HVDC & AC) (MKWH) | 424.4145 |  | 436.15 |  | 394.97 |  | 449.86 | August-17
33 | Monthly Load Factor (%) | 78.7778 |  | 81.95 |  | 81.47 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:October' 2017
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9507 | 18/10/17 | 19:30
Generation Period
| Dhaka | MW | 3782
| Chittagong | MW | 1047
| Comilla | MW | 882
| Mymensingh | MW | 581
| Sylhet | MW | 479
a) | Total supply in East zone | MW | 6771
| Khulna | MW | 903
| Barisal | MW | 180
| Rajshahi | MW | 874
| Rangpur | MW | 396
b) | Total supply in West zone | MW | 2353
c) | Total supply in both zone ( a+b) | MW | 9124
Ref: | 27.21.2604.16.084.17.57 | Date: 20/09/2017
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October' 2017
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 960 | 05/10/17 | 19:30
| b) Ishurdi end | MW | 120 | 02/10/17 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 340 | 02/10/17 | 15:00
| b) Ishurdi end | MW | 440 | 22/10/17 | 7:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 4.059 | 13/10/17
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 4.0145 | 13/10/17
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 74.4631
| b) Ishurdi end | MKWH | 4.5833
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 4.4458
| b) Ishurdi end | MKWH | 72.4375
23 | Transmission loss of EWI/ NO-1 | % | 2.7202
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 430 | 31/10/17 | 19:30
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 430 | 31/10/17 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.48 | 31/10/17
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 6.384 | 31/10/17
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 158.09
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 155.61
30 | Transmission loss of EWI /NO-2 | % | 1.569
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | 230/132 kV Transformer-T-3 | 2017-10-01 07:10 | 2017-10-01 10:49 | 3:39 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T-1 | 2017-10-02 09:19 | 2017-10-02 11:03 | 1:44 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T-3 | 2017-10-07 09:48 | 2017-10-07 13:20 | 3:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer TR2 | 2017-10-08 05:46 | 2017-10-08 07:59 | 2:13 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer TR-1 | 2017-10-09 05:39 | 2017-10-09 06:48 | 1:09 | E/O | Due to red hot maintenance | 20 | 23 | Power interruption
Joydevpur | 132/33 kV Transformer-T-4 | 2017-10-10 08:33 | 2017-10-10 08:45 | 0:12 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-4 | 2017-10-13 08:34 | 2017-10-13 08:38 | 0:04 | T | Tripped showing REF relay | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T-1 | 2017-10-23 06:48 | 2017-10-23 08:39 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T-1 | 2017-10-27 23:10 | 2017-10-27 23:59 | 0:49 | T | Tripped showing differential relay | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T-1 | 2017-10-30 05:06 | 2017-10-30 06:15 | 1:09 | T | Tripped showing REF relay | 0 | 0 | No interruption
|  |  | Total : | 16:22 |  | Unserved Energy: |  | 23
Dhaka (South) Grid Circle :
Siddhirganj | 132/33 kV Transformer-T-1 | 2017-10-08 12:58 | 2017-10-08 14:32 | 1:34 | E/O | Due to red hot maintenance | 60 | 94 | Power interruption
Hasnabad | 132/33 kV Transformer-T-2 | 2017-10-15 07:20 | 2017-10-15 10:55 | 3:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-4 | 2017-10-15 14:05 | 2017-10-15 14:22 | 0:17 | T | Tripped showing REF relay | 70 | 19.8333 | Power interruption
Maniknagar | 230/132 kV Transformers-TR1 | 2017-10-21 07:47 | 2017-10-21 08:30 | 0:43 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-3 | 2017-10-23 13:27 | 2017-10-23 13:45 | 0:18 | T | Tripped showing O/C & E/F relay | 45 | 13.5 | Power interruption
Bashundhara | 132/33 kV Transformers-T-1 ,T2 & T3 | 2017-10-24 20:25 | 2017-10-24 21:05 | 0:40 | T | Tripped showing E/F relay | 109 | 72.6667 | Power interruption
Rampura | 230/132 kV Transformers-TR1 | 2017-10-25 06:55 | 2017-10-25 07:53 | 0:58 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformers-TR1 | 2017-10-29 07:04 | 2017-10-29 09:12 | 2:08 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T-1 | 2017-10-30 09:50 | 2017-10-30 10:31 | 0:41 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 10:54 |  | Unserved Energy: |  | 200
Chittagong Grid Circle :
Fenchuganj | 132/33 kV Transformers-T-1 | 2017-10-07 05:46 | 2017-10-07 05:56 | 0:10 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformers-T-2 | 2017-10-07 05:56 | 2017-10-07 06:01 | 0:05 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformers-MT-1 | 2017-10-10 12:05 | 2017-10-10 12:58 | 0:53 | E/O | Due to Oil leavel checking | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformers-T-1 | 2017-10-11 10:50 | 2017-10-11 12:12 | 1:22 | E/O | Due to Oil filling | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformers-MT-4 | 2017-10-11 17:26 | 2017-10-11 18:35 | 1:09 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
|  |  | Total : | 0:10 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Chatak | 132/33 kV Transformer-T-3 | 2017-10-10 12:31 | 2017-10-10 13:58 | 1:27 | E/O | Due to CB checking | 18 | 15.9 | Power interruption 12:05 to 12:58
BSRM | 230/132 kV Transformers-T-1 | 2017-10-11 16:48 | 2017-10-11 17:15 | 0:27 | T | Tripped showing dist & E/F. relay | 0 | 0 | No interruption
| 230/132 kV Transformers-T-2 | 2017-10-11 16:48 | 2017-10-11 17:17 | 0:29 | T |  | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformers-T-4 | 2017-10-11 18:35 | 2017-10-11 19:51 | 1:16 | E/O | Due to red hot maintenance | 25 | 31.6667 | Power interruption
Sylhet | 132/33 kV Transformers-T-4 | 2017-10-17 08:29 | 2017-10-17 10:15 | 1:46 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Comilla(N) | 230/132 kV Transformers-T-R2 | 2017-10-21 09:25 | 2017-10-21 15:25 | 6:00 | E/O | Due to OLTC problem | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T-3 | 2017-10-24 09:25 | 2017-10-24 10:11 | 0:46 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 12:11 |  | Unserved Energy: |  | 47.5667
Khulna Grid Circle :
Faridpur | 132/33 kV Transformers-T-1 & T2 | 2017-10-04 12:56 | 2017-10-04 13:14 | 0:18 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T-2 | 2017-10-09 03:13 | 2017-10-09 03:15 | 0:02 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T-2 | 2017-10-12 04:12 | 2017-10-12 04:32 | 0:20 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Mongla | 132/33 kV Transformers-T-1 & T2 | 2017-10-12 09:56 | 2017-10-12 10:05 | 0:09 | T | Tripped showing E/F relay | 33 | 4.95 | Power interruption
Madaripur | 132/33 kV Transformers-T2 | 2017-10-13 10:05 | 2017-10-13 10:30 | 0:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | 230/132 kV Transformer-T-1 | 2017-10-14 10:31 | 2017-10-14 10:45 | 0:14 | T | Tripped showing dist relay | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T-4 | 2017-10-15 09:15 | 2017-10-15 11:03 | 1:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T-1 | 2017-10-17 10:26 | 2017-10-17 11:13 | 0:47 | E/O | Due to red hot maintenance | 20 | 15.6667 | Power interruption
Gopalganj | 132/33 kV Transformers-T-1 & T2 | 2017-10-17 21:10 | 2017-10-17 21:20 | 0:10 | T | Tripped showing winding temperature high | 74 | 12.3333 | Power interruption
Faridpur | 132/33 kV Transformers-T2 | 2017-10-18 00:06 | 2017-10-18 00:55 | 0:49 | E/O | Due to red hot maintenance | 50 | 40.8333 | Power interruption
Satkhira | 132/33 kV Transformers-T2 | 2017-10-19 08:50 | 2017-10-19 08:53 | 0:03 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T-2 | 2017-10-19 12:03 | 2017-10-19 12:44 | 0:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T-1 & T2 | 2017-10-21 06:52 | 2017-10-21 07:06 | 0:14 | T | Tripped showing O/C relay | 5 | 1.1667 | Power interruption
Barisal | 132/33 kV Transformer-T-2 | 2017-10-23 11:35 | 2017-10-23 11:38 | 0:03 | T | Tripped showing O/C relay | 50 | 2.5 | Power interruption
Barisal | 132/33 kV Transformer-T-2 | 2017-10-23 15:05 | 2017-10-23 15:06 | 0:01 | T | Tripped showing O/C relay | 57 | 0.95 | Power interruption
Goalpara | 132/33 kV Transformers-T-5 & T6 | 2017-10-24 19:37 | 2017-10-24 19:47 | 0:10 | T | Tripped showing O/C relay | 30 | 5 | Power interruption
Khulna© | 132/33 kV Transformers-T-1 , T2 & T3 | 2017-10-24 20:17 | 2017-10-24 20:44 | 0:27 | T | Tripped showing inst.E/F relay | 72 | 32.4 | Power interruption
Khulna© | 132/33 kV Transformer-T-2 | 2017-10-29 01:53 | 2017-10-29 02:01 | 0:08 | T | Tripped showing E/F relay | 10 | 1.3333 | Power interruption
|  |  | Total : | 6:49 |  | Unserved Energy: |  | 117.1333
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Jessore | 132/33 kV Transformer-T-3 | 2017-10-09 03:56 | 2017-10-09 04:05 | 0:09 | T | Tripped showing over load at 132 kV side | 20 | 3 | Power interruption
Shahjadpur | 132/33 kV Transformer-T-1 | 2017-10-09 09:55 | 2017-10-09 10:23 | 0:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T-1 | 2017-10-17 09:44 | 2017-10-17 10:18 | 0:34 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T-1 | 2017-10-20 09:42 | 2017-10-20 12:11 | 2:29 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T-2 | 2017-10-21 11:33 | 2017-10-21 12:12 | 0:39 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T-2 | 2017-10-25 08:01 | 2017-10-25 10:44 | 2:43 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 7:02 |  | Unserved Energy: |  | 3
Bogra Grid Circle:
Rangpur | 132/33 kV Transformer T2 | 2017-10-02 10:30 | 2017-10-02 11:05 | 0:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T-1 | 2017-10-18 09:58 | 2017-10-18 12:20 | 2:22 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 2:57 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 56:25 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2017-10-02 23:30 | 2017-10-03 04:13 | 4:43 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Basila RPP 132 kV line | 2017-10-06 12:48 | 2017-10-06 14:27 | 1:39 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 & 2 | 2017-10-07 05:45 | 2017-10-07 06:15 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2017-10-12 10:48 | 2017-10-12 11:30 | 0:42 | T | Tripped showing dist.(B-phase) relay | 423 | 296.1 | Power interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2017-10-12 10:48 | 2017-10-12 12:27 | 1:39 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2017-10-12 10:48 | 2017-10-12 12:45 | 1:57 | T |  | 0 | 0 | No interruption
|  |  | Total : | 11:10 |  | Unserved Energy: |  | 296.1
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2017-10-09 15:28 | 2017-10-09 15:36 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2017-10-21 03:34 | 2017-10-21 03:49 | 0:15 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2017-10-23 11:46 | 2017-10-23 11:51 | 0:05 | T | Tripped showing dist. relay | 90 | 7.5 | Power interruption
Hasnabad | Hasnabad-Sitalakyha 132 kV line | 2017-10-24 11:27 | 2017-10-24 14:38 | 3:11 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2017-10-24 20:25 | 2017-10-24 20:58 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 4:12 |  | Unserved Energy: |  | 7.5
Page: 2/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Kaptai | Kaptai-Chandraghona 132 kV line | 2017-10-04 22:09 | 2017-10-04 23:53 | 1:44 | T | Tripped showing dist.(B-phase) relay | 12 | 20.8 | Power interruption
Kaptai | Kaptai-Chnadraghona-Madunaghat 132 kV line | 2017-10-05 06:55 | 2017-10-05 09:12 | 2:17 | E/O | Due to red hot maintenance | 14 | 31.9667 | Power interruption
Baraulia | Baraulia-BSRM 132 kV line | 2017-10-06 10:07 | 2017-10-06 13:07 | 3:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-Feni 132 kV line-1 | 2017-10-11 17:26 | 2017-10-11 18:23 | 0:57 | E/O | Due to bursting of 132 kV CB & MT1 X-former
| Hathazari-Feni 132 kV line-2 | 2017-10-11 17:26 | 2017-10-11 18:24 | 0:58 | E/O
Kaptai | Kaptai-Madunaghat 132 kV line-1 | 2017-10-11 17:26 | 2017-10-11 18:26 | 1:00 | E/O |  | 650 | 617.5 | Power interruption
| Kaptai-Madunaghat 132 kV line-2 | 2017-10-11 17:26 | 2017-10-11 19:04 | 1:38 | E/O
Baraulia | Baraulia-Hathazari 132 kV line-1 | 2017-10-11 17:26 | 2017-10-11 18:28 | 1:02 | E/O
| Baraulia-Hathazari 132 kV line-2 | 2017-10-11 17:26 | 2017-10-11 18:26 | 1:00 | E/O
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2017-10-12 00:46 | 2017-10-12 01:01 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2017-10-14 13:55 | 2017-10-14 14:14 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Baraulia | Baraulia-Khulshi 132 kV line | 2017-10-19 19:37 | 2017-10-19 20:22 | 0:45 | T | Tripped showing E/F relay | 15 | 11.25 | Power interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2017-10-30 18:18 | 2017-10-30 23:11 | 4:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2017-10-31 08:44 | 2017-10-31 12:18 | 3:34 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2017-10-31 10:15 | 2017-10-31 10:40 | 0:25 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 23:47 |  | Unserved Energy: |  | 681.5167
Comilla Grid Circle :
Comilla(N) | Comilla(N)-Feni 132 kV line-2 | 2017-10-01 12:11 | 2017-10-01 16:55 | 4:44 | T | Tripped showing dist.(C-phae) & O/C relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2017-10-05 10:29 | 2017-10-05 20:42 | 10:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2017-10-07 07:52 | 2017-10-07 08:03 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-1 | 2017-10-09 11:58 | 2017-10-09 12:34 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Feni 132 kV line-1 | 2017-10-10 14:12 | 2017-10-11 11:01 | 20:49 | T | Tripped showing dist. relay | 130 | 26 | Power interruption
| Comilla(N)-Feni 132 kV line-2 | 2017-10-10 14:12 | 2017-10-10 14:24 | 0:12 | T | Tripped showing O/C. relay
Feni | Feni-Comilla(N) 132 kVline-1 | 2017-10-11 12:26 | 2017-10-11 12:40 | 0:14 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Feni-Comilla(N) 132 kVline-2 | 2017-10-11 12:26 | 2017-10-11 12:41 | 0:15 | T |  | 0 | 0 | No interruption
BSRM | BSRM -Hathazari 230 kV line-1 | 2017-10-11 12:27 | 2017-10-11 13:05 | 0:38 | T | Tripped showing dist.& E/F relay | 830 | 207.5 | Power interruption 12:26 to 12:41
| BSRM -AKSTML 230 kV line | 2017-10-11 11:07 | 2017-10-11 11:13 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| BSRM -AKSTML 230 kV line | 2017-10-11 11:21 | 2017-10-11 18:44 | 7:23 | T |  | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Meghnaghat 230 kV line-1 | 2017-10-11 13:26 | 2017-10-11 15:06 | 1:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Feni 132 kV line-1 | 2017-10-11 14:18 | 2017-10-11 14:27 | 0:09 | T | Tripped showing inst.E/F relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-BSRM 230 kV line-1 | 2017-10-11 16:47 | 2017-10-11 16:54 | 0:07 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-2 | 2017-10-14 03:27 | 2017-10-14 04:02 | 0:35 | T | Tripped showing dist.(Z2) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line-1 | 2017-10-16 06:26 | 2017-10-16 07:53 | 1:27 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 & 2 | 2017-10-19 02:00 | 2017-10-19 03:43 | 1:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV line-3 | 2017-10-19 02:36 | 2017-10-19 04:27 | 1:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.baria 132 kV line-2 | 2017-10-19 03:36 | 2017-10-19 04:10 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tripura | Tripura-Comilla(S) 132 kV line-1 & 2 | 2017-10-21 09:57 | 2017-10-21 10:48 | 0:51 | T | Due to problem at palatona power station | 30 | 25.5 | Power interruption
Comilla(N) | Comilla(N)-BSRM 230 kV line-1 | 2017-10-27 13:20 | 2017-10-27 13:52 | 0:32 | T | Tripped showing dist.(C-phae) relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyna 230 kV line-1 | 2017-10-30 07:00 | 2017-10-30 13:12 | 6:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-1 | 2017-10-30 06:43 | 2017-10-30 06:59 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Feni-Hathazari 132 kV line-1 | 2017-10-30 08:29 | 2017-10-30 12:41 | 4:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 65:30 |  | Unserved Energy: |  | 259
Page: 3/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line | 2017-10-01 14:19 | 2017-10-01 14:45 | 0:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur-Barisal (N) 132 kV line-1 & 2 | 2017-10-04 12:56 | 2017-10-04 13:20 | 0:24 | T | Tripped showing dist. relay | 309 | 51.5 | Power interruption 12:56 to 13:06
Barisal(S) | Barisal(S)-Bhandaria-Bagerhat 132 kV line-1 | 2017-10-04 12:56 | 2017-10-04 13:06 | 0:10 | T
Bhandaria | Bhandaria-Barisal 132 kV line | 2017-10-04 12:58 | 2017-10-04 13:08 | 0:10 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2017-10-05 04:06 | 2017-10-05 04:13 | 0:07 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-2 | 2017-10-05 09:32 | 2017-10-05 11:50 | 2:18 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Khulna(S) | Khulna(S) -Satkhira 132 kV line-2 | 2017-10-09 06:22 | 2017-10-09 14:17 | 7:55 | T | Tripped showing dist.(Z2) realy | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madaripur 132 kV line | 2017-10-12 12:25 | 2017-10-12 12:36 | 0:11 | T | Tripped showing dist. (B-phase) relay | 40 | 7.3333 | Power interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2017-10-13 15:16 | 2017-10-13 16:15 | 0:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line 132 kV line-1 & 2 | 2017-10-14 10:31 | 2017-10-14 11:04 | 0:33 | T | Tripped showing dist. realy | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2017-10-17 07:42 | 2017-10-17 10:10 | 2:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 230 kV line 132 kV line | 2017-10-21 01:25 | 2017-10-21 01:35 | 0:10 | T | Tripped showing dist. realy | 0 | 0 | No interruption
Khulna(C) | Khulna(C) -Goalpara 132 kV line-2 | 2017-10-25 02:26 | 2017-10-25 02:35 | 0:09 | T | Tripped showing auto reclose relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2017-10-27 11:44 | 2017-10-27 11:50 | 0:06 | T | Tripped showing dist. realy | 0 | 0 | No interruption
Bhandaria | Bhandaria-Barisal 132 kV line | 2017-10-28 10:10 | 2017-10-28 12:26 | 2:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Faridpur S/S | Faridpur S/S-Faridpur P/S 132 kV line | 2017-10-28 10:21 | 2017-10-28 12:46 | 2:25 | E/O | Due to snaping of Y-phase PT | 0 | 0 | No interruption
|  |  | Total : | 20:47 |  | Unserved Energy: |  | 58.8333
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2017-10-03 11:44 | 2017-10-03 11:53 | 0:09 | E/O | Tripped showing dist. realy | 0 | 0 | No interruption
Bheramara | Bheramara HVDC-Faridpur 132 kV line-1 | 2017-10-04 12:58 | 2017-10-04 13:18 | 0:20 | T | Tripped showing dist. realy | 0 | 0 | No interruption
Bheramara | Bheramara -Faridpur 132 kV line-1 | 2017-10-05 04:06 | 2017-10-05 04:15 | 0:09 | T | Tripped showing dist. & O/C relay | 33 | 41.4167 | Power interruption 04:06 to 04:13
| Bheramara -Faridpur 132 kV line-2 | 2017-10-05 04:06 | 2017-10-05 04:24 | 0:18 | T
|  |  | Total : | 0:56 |  | Unserved Energy: |  | 41.4167
Bogra Grid Circle :
Naogaon | Naogaon-Joypurhat 132 kV line | 2017-10-02 13:49 | 2017-10-02 14:02 | 0:13 | T | Tripped showing dist. realy | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-2 | 2017-10-12 11:36 | 2017-10-12 11:46 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line | 2017-10-14 13:40 | 2017-10-14 13:45 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV line | 2017-10-15 21:01 | 2017-10-15 21:20 | 0:19 | T | Tripped showing dist. relay | 33 | 10.45 | Power interruption
Sirajganj | Sirajganj-Bogra 230 kV line-1 | 2017-10-16 10:30 | 2017-10-16 12:19 | 1:49 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV line | 2017-10-17 09:43 | 2017-10-17 14:59 | 5:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV line | 2017-10-21 08:37 | 2017-10-21 08:55 | 0:18 | T | Tripped showing dist. relay | 5 | 1.5 | Power interruption
Naogaon | Naogaon-Joypurhat 132 kV line | 2017-10-28 08:18 | 2017-10-28 08:35 | 0:17 | T | Tripped showing dist. relay | 15 | 4.25 | Power interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2017-10-31 13:18 | 2017-10-31 15:20 | 2:02 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 10:29 |  | Unserved Energy: |  | 16.2
Others :
Maniknagar | Maniknagar-Bangabhaban 132 kV line-1 | 2017-10-04 15:21 | 2017-10-04 16:02 | 0:41 | T | Tripped showing main protection relay | 0 | 0 | No interruption
| Maniknagar-Bangabhaban 132 kV line-2 | 2017-10-04 15:21 | 2017-10-04 16:38 | 1:17 | T |  | 0 | 0 | No interruption
|  |  | Total : | 1:58 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 138:49 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: October 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400/132 kV Transformer-T-R1 | 2017-10-02 14:52 | 2017-10-02 17:01 | 2:09 | S/O | Due to protction test | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer TR2 | 2017-10-03 08:07 | 2017-10-03 11:20 | 3:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformers T-2 | 2017-10-03 10:02 | 2017-10-03 10:55 | 0:53 | S/O | Due to maintenance work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformers T-4 | 2017-10-05 21:26 | 2017-10-07 12:24 | 38:58 | S/O | Due to replacement work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T-1 | 2017-10-07 12:52 | 2017-10-07 13:22 | 0:30 | S/O | Due to maintenance work | 20 | 10 | Power interruption
Aminbazar | Capacitor bank-2 | 2017-10-18 08:52 | 2017-10-18 15:33 | 6:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | 132 kV bus coupler | 2017-10-18 09:20 | 2017-10-18 13:30 | 4:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T-3 | 2017-10-20 07:17 | 2017-10-23 22:05 | 86:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-TR1 | 2017-10-24 08:48 | 2017-10-24 17:30 | 8:42 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kallyanpur | 132 kV main bus | 2017-10-25 07:30 | 2017-10-25 15:54 | 8:24 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-3 | 2017-10-27 07:10 | 2017-10-27 08:17 | 1:07 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-2 | 2017-10-28 10:10 | 2017-10-28 10:44 | 0:34 | S/O | Due to isolator maintenance | 0 | 0 | No interruption
Kallyanpur | 132 kV reserve bus | 2017-10-28 08:50 | 2017-10-29 12:08 | 27:18 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T-2 | 2017-10-28 08:55 | 2017-10-28 15:51 | 6:56 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-TR2 | 2017-10-31 09:40 | 2017-10-31 16:43 | 7:03 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 203:26 |  | Unserved Energy: |  | 10
Dhaka (South) Grid Circle :
Uttara | 132/33 kV Transformer-T-2 | 2017-10-10 06:51 | 2017-10-10 07:40 | 0:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T-1 | 2017-10-11 07:10 | 2017-10-11 22:45 | 15:35 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | 132 kV bus-2 | 2017-10-17 08:09 | 2017-10-17 12:10 | 4:01 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | 132 kV bus-2 | 2017-10-24 08:48 | 2017-10-24 12:58 | 4:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T-1 | 2017-10-27 11:57 | 2017-10-27 12:15 | 0:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Narsinghdi | 132/33 kV Transformer-T-1 | 2017-10-30 07:05 | 2017-10-30 09:40 | 2:35 | S/O | Due to project work | 30 | 77.5 | Power interruption
|  |  | Total : | 27:28 |  | Unserved Energy: |  | 77.5
Chittagong Grid Circle :
Hathazari | 230/132 kV Transformer-MT1 | 2017-10-17 09:30 | 2017-10-17 13:15 | 3:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | 230 kV bus-2 | 2017-10-18 06:22 | 2017-10-18 07:56 | 1:34 | S/O | Due to maintenance work | 20 | 31.3333 | Power interruption
Halishahar | 132/33 kV Transformer-T-2 | 2017-10-27 07:30 | 2017-10-27 12:20 | 4:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 6:24 |  | Unserved Energy: |  | 31.3333
Comilla Grid Circle :
Comiila(S) | 132/33 kV Transformer-T-1 | 2017-10-15 08:45 | 2017-10-15 15:44 | 6:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformer-T-4 | 2017-10-17 09:10 | 2017-10-17 16:07 | 6:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T-2 | 2017-10-17 08:11 | 2017-10-17 18:42 | 10:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Comilla(N) | 132/33 kV Transformer-T-4 | 2017-10-18 12:30 | 2017-10-18 17:16 | 4:46 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T-1 | 2017-10-19 08:19 | 2017-10-19 15:50 | 7:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T-2 | 2017-10-22 08:28 | 2017-10-22 15:47 | 7:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | 132 kV bus-2 | 2017-10-23 06:40 | 2017-10-23 08:58 | 2:18 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T-3 | 2017-10-24 08:14 | 2017-10-24 15:18 | 7:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T-1 | 2017-10-25 08:07 | 2017-10-26 00:57 | 16:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total | 70:15 |  | Unserved Energy : |  | 0
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal | 230/132 kV Transformer-T-1 | 2017-10-08 07:26 | 2017-10-08 16:36 | 9:10 | S/O | Due to project work | 0 | 0 | No interruption
Barisal(N) | 132 kV bus | 2017-10-10 07:34 | 2017-10-10 17:10 | 9:36 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | 230 kV bus-1 | 2017-10-11 09:40 | 2017-10-11 14:20 | 4:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformers-T-02 | 2017-10-12 07:31 | 2017-10-12 17:36 | 10:05 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformers-T-01 | 2017-10-13 09:01 | 2017-10-13 12:29 | 3:28 | S/O | Due to abnormal sound at 132 kV CT | 0 | 0 | No interruption
Barisal(N) | 230/132 kV Transformers-T-02 | 2017-10-14 07:39 | 2017-10-14 12:07 | 4:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformers-T1 | 2017-10-15 08:15 | 2017-10-15 16:17 | 8:02 | S/O | Due to annual maintenance | 10 | 80.3333 | Power interruption
Faridpur | 132/33 kV Transformers-T2 | 2017-10-17 10:20 | 2017-10-17 15:23 | 5:03 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Barisal (Old) | 132/33 kV Transformers-T1 | 2017-10-23 08:03 | 2017-10-23 17:02 | 8:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rampura | 132 kV capacitor bank-1 | 2017-10-23 08:40 | 2017-10-23 14:39 | 5:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T2 | 2017-10-24 10:32 | 2017-10-24 16:25 | 5:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T2 | 2017-10-25 08:42 | 2017-10-25 16:52 | 8:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T3 | 2017-10-29 08:31 | 2017-10-29 16:30 | 7:59 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Faridpur | 132 kV Bus-B | 2017-10-29 08:30 | 2017-10-29 16:42 | 8:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 | 2017-10-30 09:13 | 2017-10-30 12:25 | 3:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 102:56 |  | Unserved Energy : |  | 80.3333
HVDC Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
C.nawabganj | 132/33 kV Transformer-T2 | 2017-10-04 08:22 | 2017-10-04 16:03 | 7:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T2 | 2017-10-05 08:13 | 2017-10-05 13:10 | 4:57 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2017-10-05 08:30 | 2017-10-05 10:40 | 2:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T3 | 2017-10-07 08:10 | 2017-10-07 16:42 | 8:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T3 | 2017-10-08 08:12 | 2017-10-08 15:40 | 7:28 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-4 | 2017-10-10 08:36 | 2017-10-10 15:55 | 7:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T2 | 2017-10-11 08:06 | 2017-10-11 13:45 | 5:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T-4 | 2017-10-11 09:05 | 2017-10-11 09:47 | 0:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2017-10-12 08:50 | 2017-10-12 11:25 | 2:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T1 | 2017-10-12 08:18 | 2017-10-12 14:30 | 6:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T1 | 2017-10-14 08:15 | 2017-10-14 20:10 | 11:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-TR3 | 2017-10-15 08:50 | 2017-10-15 13:50 | 5:00 | S/O | Due to annual maintenance | 7 | 35 | Power interruption
Niyamatpur | 132/33 kV Transformer-T1 | 2017-10-22 10:20 | 2017-10-22 16:45 | 6:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T2 | 2017-10-23 08:10 | 2017-10-23 16:50 | 8:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T2 | 2017-10-24 08:07 | 2017-10-24 16:47 | 8:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T3 | 2017-10-25 08:09 | 2017-10-25 16:52 | 8:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T1 | 2017-10-28 10:55 | 2017-10-28 16:53 | 5:58 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T3 | 2017-10-28 08:05 | 2017-10-28 13:55 | 5:50 | S/O | Due to annual maintenance | 5 | 29.1667 | Power interruption
Naogaon | 132/33 kV Transformer-T1 | 2017-10-28 08:55 | 2017-10-28 15:51 | 6:56 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2017-10-29 08:35 | 2017-10-29 15:45 | 7:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T3 | 2017-10-29 09:25 | 2017-10-29 16:05 | 6:40 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T2 | 2017-10-30 08:30 | 2017-10-30 16:40 | 8:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T3 | 2017-10-30 08:20 | 2017-10-30 16:40 | 8:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T4 | 2017-10-30 09:05 | 2017-10-30 14:20 | 5:15 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T2 | 2017-10-31 08:30 | 2017-10-31 14:59 | 6:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total | 163:26 |  | Unserved Energy : |  | 64.1667
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 573:55 | Hours
S/O=Schedule Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :(N)
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2017-10-01 09:51 | 2017-10-01 17:42 | 7:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2017-10-02 09:05 | 2017-10-02 13:56 | 4:51 | S/O | Due to protection test | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2017-10-06 00:13 | 2017-10-06 04:13 | 4:00 | S/O | Due to project work | 0 | 0 | No interruption
| Kabirpur-Kaliakoir 132 kV line-2 | 2017-10-06 00:14 | 2017-10-06 07:02 | 6:48 | S/O |  | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV line | 2017-10-06 08:26 | 2017-10-06 17:58 | 9:32 | S/O | Due to project work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 & 2 | 2017-10-12 08:35 | 2017-10-12 15:05 | 6:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-1 | 2017-10-14 09:02 | 2017-10-14 16:32 | 7:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 | 2017-10-15 07:35 | 2017-10-15 13:04 | 5:29 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 | 2017-10-16 08:40 | 2017-10-16 14:36 | 5:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2017-10-16 09:22 | 2017-10-16 18:06 | 8:44 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2017-10-17 09:45 | 2017-10-17 19:55 | 10:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-2 | 2017-10-17 09:21 | 2017-10-17 17:10 | 7:49 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2017-10-18 10:12 | 2017-10-18 17:09 | 6:57 | S/O | Due to project work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2017-10-18 09:00 | 2017-10-18 15:39 | 6:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2017-10-19 11:30 | 2017-10-19 15:23 | 3:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV line-1 | 2017-10-22 09:24 | 2017-10-22 16:21 | 6:57 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2017-10-23 09:21 | 2017-10-23 17:00 | 7:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2017-10-24 09:30 | 2017-10-24 17:07 | 7:37 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2017-10-25 07:06 | 2017-10-25 08:06 | 1:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2017-10-25 08:15 | 2017-10-25 11:50 | 3:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2017-10-25 11:22 | 2017-10-25 12:30 | 1:08 | S/O | Due to tighting work | 0 | 0 | No interruption
Mymensingh S/S | Mymensingh S/S-Mymensingh RPCL 132 kV line-2 | 2017-10-28 09:28 | 2017-10-28 12:44 | 3:16 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV line-2 | 2017-10-29 09:43 | 2017-10-29 17:08 | 7:25 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2017-10-30 08:41 | 2017-10-30 20:13 | 11:32 | S/O | Due to annual maintenance | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-2 | 2017-10-30 09:24 | 2017-10-30 16:59 | 7:35 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-1 | 2017-10-31 08:27 | 2017-10-31 17:34 | 9:07 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 169:30 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Kamrangirchar | Kamrangirchar-Lalbagh 132 kV line | 2017-10-02 12:52 | 2017-10-02 15:12 | 2:20 | S/O | Due to protection test | 0 | 0 | No interruption
Haripur | Haripur-Rampura 230 kV line-2 | 2017-10-06 05:15 | 2017-10-07 15:20 | 34:05 | S/O | Due to project work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi -Haripur 132 kV line | 2017-10-06 08:27 | 2017-10-07 15:20 | 30:53 | S/O | Due to project work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsinghdi -Bhulta 132 kV line | 2017-10-12 10:01 | 2017-10-12 16:21 | 6:20 | S/O | Due to project work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Meghnaghat 230 kV line-2 | 2017-10-15 07:01 | 2017-10-15 10:18 | 3:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shitalakyha 132 kV line | 2017-10-27 07:30 | 2017-10-27 13:09 | 5:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
Haripur | Haripur-Rampura 230 kV line-1 | 2017-10-29 07:54 | 2017-10-29 17:22 | 9:28 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 92:02 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2017-10-06 06:15 | 2017-10-06 07:58 | 1:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-2 | 2017-10-06 08:39 | 2017-10-06 10:09 | 1:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2017-10-09 14:32 | 2017-10-09 15:37 | 1:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2017-10-10 07:11 | 2017-10-10 15:35 | 8:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Tk.chemical 132 kV line | 2017-10-14 07:38 | 2017-10-14 15:46 | 8:08 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kaptai 132 kV line | 2017-10-15 06:51 | 2017-10-15 06:51 | 0:00 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 | 2017-10-15 09:08 | 2017-10-15 16:12 | 7:04 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kaptai 132 kV line | 2017-10-16 07:11 | 2017-10-16 15:05 | 7:54 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 | 2017-10-16 08:54 | 2017-10-16 15:18 | 6:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-2 | 2017-10-17 08:10 | 2017-10-17 18:51 | 10:41 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-1 | 2017-10-17 08:58 | 2017-10-17 16:11 | 7:13 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kaptai 132 kV line | 2017-10-18 08:20 | 2017-10-18 15:51 | 7:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2017-10-18 09:30 | 2017-10-18 14:42 | 5:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Kaptai | Kaptai-Madunaghat 132 kV line-1 | 2017-10-19 07:26 | 2017-10-19 15:09 | 7:43 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2017-10-23 07:08 | 2017-10-23 16:27 | 9:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2017-10-23 08:15 | 2017-10-23 16:00 | 7:45 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2017-10-24 08:30 | 2017-10-24 16:28 | 7:58 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2017-10-24 09:15 | 2017-10-24 16:25 | 7:10 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2017-10-25 07:30 | 2017-10-25 14:18 | 6:48 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-AKSML 132 kV line | 2017-10-25 08:17 | 2017-10-25 14:40 | 6:23 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2017-10-28 08:44 | 2017-10-28 15:39 | 6:55 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baraulia | Baraulia-AKSML 132 kV line | 2017-10-30 09:02 | 2017-10-30 16:11 | 7:09 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV line-1 | 2017-10-31 07:20 | 2017-10-31 14:51 | 7:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-AKSML 132 kV line-1 | 2017-10-31 08:52 | 2017-10-31 15:26 | 6:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line-1 | 2017-10-31 08:48 | 2017-10-31 15:51 | 7:03 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 161:07 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-01 08:50 | 2017-10-01 17:32 | 8:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Ashuganj 230 kV line-1 | 2017-10-01 11:37 | 2017-10-01 12:04 | 0:27 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 132 kV line-1 | 2017-10-02 09:14 | 2017-10-02 17:41 | 8:27 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-06 10:09 | 2017-10-06 17:17 | 7:08 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-07 07:42 | 2017-10-07 17:47 | 10:05 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-08 07:44 | 2017-10-08 17:33 | 9:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-10 07:52 | 2017-10-10 17:48 | 9:56 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-11 08:30 | 2017-10-11 17:50 | 9:20 | S/O | Due to project work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2017-10-12 07:52 | 2017-10-12 17:47 | 9:55 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-15 08:26 | 2017-10-15 17:15 | 8:49 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-16 08:36 | 2017-10-16 17:29 | 8:53 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-17 08:39 | 2017-10-17 17:42 | 9:03 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-19 06:29 | 2017-10-19 17:11 | 10:42 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2017-10-19 06:33 | 2017-10-19 17:08 | 10:35 | S/O | Due to project work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2017-10-19 15:08 | 2017-10-19 16:39 | 1:31 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 & 2 | 2017-10-20 06:23 | 2017-10-20 06:32 | 0:09 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-22 06:34 | 2017-10-22 17:38 | 11:04 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2017-10-22 06:22 | 2017-10-22 17:28 | 11:06 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-23 06:11 | 2017-10-23 17:12 | 11:01 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2017-10-23 06:12 | 2017-10-23 17:11 | 10:59 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-24 06:17 | 2017-10-24 16:53 | 10:36 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2017-10-24 06:18 | 2017-10-24 17:13 | 10:55 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2017-10-25 06:12 | 2017-10-25 17:39 | 11:27 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2017-10-25 06:33 | 2017-10-25 14:37 | 8:04 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2017-10-26 07:03 | 2017-10-26 17:19 | 10:16 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2017-10-26 07:04 | 2017-10-26 17:17 | 10:13 | S/O | Due to project work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-10-27 06:06 | 2017-10-27 17:07 | 11:01 | S/O | Due to project work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2017-10-27 06:22 | 2017-10-27 17:09 | 10:47 | S/O | Due to project work | 0 | 0 | No interruption
Sylhet | Sylhet -Fenchuganj P/S 132 kV line | 2017-10-30 17:46 | 2017-10-30 18:28 | 0:42 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 251:42 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2017-10-12 06:34 | 2017-10-15 00:49 | 66:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 66:15 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | Ishurdi-Pabna 132 kV line | 2017-10-18 08:36 | 2017-10-18 16:56 | 8:20 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Jhenidah | Jhenidah-Bottail 132 kV line-1 | 2017-10-27 15:48 | 2017-10-27 17:28 | 1:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV line | 2017-10-31 08:38 | 2017-10-31 16:44 | 8:06 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 18:06 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Shahjadpur | Shahjadpur-Pabna 132 kV line | 2017-10-14 08:07 | 2017-10-14 17:34 | 9:27 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Rajshahi | Rajshahi-C.nawabganj 132 kV line-2 | 2017-10-14 08:17 | 2017-10-14 18:00 | 9:43 | S/O | Due to project work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2017-10-15 08:18 | 2017-10-15 17:08 | 8:50 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2017-10-17 08:57 | 2017-10-17 17:28 | 8:31 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 | 2017-10-25 08:18 | 2017-10-25 16:52 | 8:34 | S/O | Due to annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 45:05 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 803:47 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October' 2017
| Area | Previous Month (September 2017) |  |  |  | Current Month (October 2017)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 13 | 6 | 15 | 34 | 9 | 7 | 41 | 57
2 | Dhaka (South) Grid Circle. | 13 | 8 | 13 | 34 | 9 | 5 | 13 | 27
3 | Chittagong Grid Circle. | 11 | 7 | 8 | 26 | 6 | 14 | 28 | 48
4 | Comilla Grid Circle. | 16 | - | 6 | 22 | 24 | 7 | 38 | 69
5 | Khulna Grid Circle. | 30 | 2 | 4 | 36 | 23 | 11 | 16 | 50
6 | Bheramara HVDC Grid Circle | 9 | 1 | 5 | 15 | 5 | 5 | 3 | 13
7 | Bogra Grid Circle. | 8 | 5 | 12 | 25 | 6 | 5 | 30 | 41
8 | Others | 4 | 1 | - | 5 | 2 | - | - | 2
9 | Total | 104 | 30 | 63 | 197 | 84 | 54 | 169 | 307
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October' 2017
| Area | Previous Month (September 2017) |  |  |  | Current Month (October 2017)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 375.77 | 37.5 | - | 413.27 | 296.1 | 23 | 10 | 329.1
2 | Dhaka ( South) grid circle | 109.57 | 74.97 | - | 184.54 | 113.5 | 94 | 77.5 | 285
3 | Chittagong grid circle. | - | 21.33 | 0.67 | 22 | 32.05 | 649.47 | 31.33 | 712.85
4 | Comilla grid circle. | 47.13 | - |  | 47.13 | 259 | 47.57 | - | 306.57
5 | Khulna grid circle. | 297.09 | 10.03 | - | 307.12 | 119.46 | 56.5 | 80.33 | 256.29
6 | Bheramara HVDC grid circle | 7.5 | - | - | 7.5 | 44.42 | - | - | 44.42
7 | Bogra grid circle. | 169.83 | 17.33 | - | 187.16 | 16.2 | - | 64.17 | 80.37
8 | Others | 130.67 | - | - | 130.67 | - | - | - | 0
9 | Total | 1137.56 | 161.16 | 0.67 | 1299.39 | 880.73 | 870.54 | 263.33 | 2014.6
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October' 2017
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 1 | 1 | 2 | 1 | - | 1 | 33
2 | Dhaka (South) | 5031.6 | 4 | 1 | 5 | 2 | 1 | 2 | 277.5
3 | Chittagong | 2042 | - | 1 | 1 | - | 1 | 1 | 31.33
4 | Khulna | 2434 | 10 | 1 | 11 | 8 | 2 | 1 | 197.46
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | 1 | - | - | 3
6 | Bogra | 3145.6 | - | - | - | - | - | 1 | 64.17
7 | Comilla | 2981 | 2 |  | 2 | - | - | 2 | 47.57
| Total | 23365.5 | [6 empty] | 654.03
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.94%
2 | Dhaka (South) | 99.96%
3 | Chittagong | 99.97%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 99.96% | [6 empty] | Executive Engineer
6 | Bogra | 99.98% | [6 empty] | Information Management Division
7 | Comilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October' 2017
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 | - | 1 | - | 296.1
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | 1 | - | - | 7.5
3 | Chittagong | 917 | 20+9(Partial) | 4 | - | 4 | - | 2 | 2 | 681.52
4 | Khulna | 1238.4 | 21 | 2 | - | 2 | 2 | - | - | 58.33
5 | Bheramara (HVDC) | 598.7 |  | 1 | - | 1 | 1 | - | - | 41.42
6 | Bogra | 1803.3 | 38 | 2 | - | 2 | 2 | - | - | 16.2
7 | Comilla | 1648.16 | 17 | 3 | - | 3 | 1 | 2 | - | 259
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 1360.07
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.99%
3 | Chittagong | 99.92%
4 | Khulna | 99.84%
5 | Bheramara (HVDC) | 99.81% | [7 empty] | Executive Engineer
6 | Bogra | 99.97% | [7 empty] | Information Management Division
7 | Comilla | 99.59% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October' 2017
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
October | 15 | - | 6 | 05hr42min | 2 | 03hr14min | - | - | 3 | 1hr46min | - | - | -
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:October' 2017
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kaliakoir | 1 | 1:19 | 20 | 23 | Due to tripping of 132/33 kV Transformers T1 , T2 & T3
Mymensingh | 1 | 0:42 | 423 | 296.1 | Due to tripping of Mymensingh-Kishoreganj 132 kV line- 1 & 2
Kishoreganj | 1 | 0:30 | 20 | 10 | Due to S/D of 132/33 kV Transformer T1
Siddhirganj | 1 | 1:34 | 60 | 94 | Due to red-hot maintenance of 132/33 kV Transformer T1
Shyampur | 1 | 0:17 | 70 | 19.8333 | Due to tripping of 132/33 kV Transformer T4
|  | 0:18 | 45 | 13.5 | Due to tripping of 132/33 kV Transformer T3
Bashundhara | 1 | 0:40 | 109 | 72.6667 | Due to tripping of 132/33 kV Transformers T 1, T2 & T3
Haripur | 1 | 0:05 | 90 | 7.5 | Due to tripping of Haripur-Shyampur 132 kV line
Narsinghdi | 1 | 2:35 | 30 | 77.5 | Due to S/D of 132/33 kV Transformer T 1
Kaptai | 2 | 1:44 | 12 | 20.8 | Due to tripping of Kaptai--Chandraghona 132 kV line
|  | 2:17 | 14 | 31.9667 | Due to red-hot maintenance of Kaptai--Chandraghona132 kV line
Hathazari | 1 | 0:57 | 650 | 617.5 | Due to bursting of 132 kV CB
Baraulia | 1 | 0:45 | 15 | 11.25 | Due to tripping of Baraulia-Khulshi 132 kV line
Hathazari | 1 | 1:34 | 20 | 31.3333 | Due to S/D of 230 kV bus-2
Chatak | 1 | 1:27 | 18 | 15.9 | Due to CB checking
Shahjibazar | 1 | 1:16 | 25 | 31.6667 | Due to red-hot maintenance of 132/33 kV Transformer T4
Comilla(N) | 1 | 1:12 | 130 | 26 | Due to tripping of Comilla(N)-Feni 132 kV line-1 & 2
Feni | 1 | 0:15 | 830 | 207.5 | Due to tripping of Feni -Comilla(N)132 kV line-1 & 2
Tripura | 1 | 0:51 | 30 | 25.5 | Due to tripping of Tripura -Comilla(S)132 kV line-1 & 2
Mongla | 1 | 0:09 | 33 | 4.95 | Due to tripping of 132/33 kV Transformers T1 & T2
Barisal | 3 | 0:47 | 20 | 15.6667 | Due to red-hot maintenance of 132/33 kV Transformer T1
|  | 0:03 | 50 | 2.5 | Due to tripping of 132/33 kV Transformer T2
|  | 0:01 | 57 | 0.95 | Due to tripping of 132/33 kV Transformer T2
Gopalganj | 2 | 0:10 | 74 | 12.3333 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:14 | 5 | 1.1667 | Due to tripping of 132/33 kV Transformers T1 & T2
Faridpur | 1 | 0:49 | 50 | 40.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Goalpara | 1 | 0:10 | 30 | 5 | Due to tripping of 132/33 kV Transformers T5 & T6
Khulna© | 2 | 0:27 | 72 | 32.4 | Due to tripping of 132/33 kV Transformers T1, T2 & T3
|  | 0:08 | 10 | 1.3333 | Due to tripping of 132/33 kV Transformer T2
Faridpur | 2 | 0:24 | 309 | 51.5 | Due to tripping of Faridpur -Madaripur 132 kV line-1 & 2
|  | 8:02 | 10 | 80.3333 | Due to tripping of 132/33 kV Transformer T1
Gopalganj | 1 | 0:11 | 40 | 7.3333 | Due to tripping of Gopalganj -Madaripur 132 kV line
Jessore | 1 | 0:09 | 20 | 3 | Due to tripping of 132/33 kV Transformer T3
Bheramara | 1 | 0:07 | 33 | 41.4167 | Due to tripping of Bheramara -Faridpur 132 kV line-1 & 2
Naogaon | 3 | 0:19 | 33 | 10.45 | Due to tripping of Naogaon -Joypurhat 132 kV line
|  | 0:18 | 5 | 1.5 | Due to tripping of Naogaon -Joypurhat 132 kV line
|  | 0:17 | 15 | 4.25 | Due to tripping of Naogaon -Joypurhat 132 kV line
Rangpur | 1 | 5:00 | 7 | 35 | Due to S/D of 132/33 kV TransformerT3
Saidpur | 1 | 5:50 | 5 | 29.1667 | Due to S/D of 132/33 kV TransformerT3
| Total unserved energy : |  |  | 2014.6 | MWH

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2017
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 128 | 16 | 2017-10-01 | 11:00
2 | Munsiganj | 112 | 5 | 2017-10-01 | 22:00
3 | Megnaghat | 69 | 4 | 2017-10-01 | 24:00
4 | Shyampur | 166 | 11 | 2017-10-01 | 23:00
5 | Bhulta | 165 | 15 | 2017-10-01 | 24:00
6 | Madanganj | 52 | 12 | 2017-10-01 | 18:30
7 | Shitalakhya | 112 | 18 | 2017-10-01 | 12:00
8 | Rahim steel | 20 | 24 | 2017-10-01 | 9:00
9 | Matuail | 94 | 18 | 2017-10-01 | 12:00
10 | Ghorasal | 97 | 11 | 2017-10-01 | 22:00
11 | Narsingdi | 109 | 11 | 2017-10-01 | 20:00
12 | Haripur (SBU) | 90 | 18 | 2017-10-01 | 19:00
13 | Ullon | 96 | 4 | 2017-10-01 | 18:00
14 | Hasnabad | 201 | 12 | 2017-10-01 | 21:00
15 | Magbazar | 122 | 4 | 2017-10-01 | 13:00
16 | Maniknagar | 96 | 5 | 2017-10-01 | 15:00
17 | Bangabhaban | 43 | 5 | 2017-10-01 | 13:00
18 | Narinda | 96 | 5 | 2017-10-01 | 15:00
19 | Dhanmondi | 159 | 5 | 2017-10-01 | 12:00
20 | Lalbag | 91 | 11 | 2017-10-01 | 13:00
21 | Madartek | 59 | 19 | 2017-10-01 | 18:30
22 | Mirpur | 107 | 11 | 2017-10-01 | 18:00
23 | Kalyanpur | 127 | 4 | 2017-10-01 | 15:00
24 | Gulshan | 138 | 5 | 2017-10-01 | 13:00
25 | Uttara | 77 | 12 | 2017-10-01 | 18:00
26 | Kamrangirchar | 75 | 1 | 2017-10-01 | 13:00
27 | Savar | 150 | 14 | 2017-10-01 | 19:00
28 | Bhasantec | 177 | 5 | 2017-10-01 | 22:00
29 | Agargaon | 150 | 5 | 2017-10-01 | 12:00
30 | Satmosjid | 97 | 12 | 2017-10-01 | 18:00
31 | Tongi | 163 | 4 | 2017-10-01 | 15:00
32 | Kabirpur | 208 | 17 | 2017-10-01 | 9:00
33 | Basundhara | 128 | 5 | 2017-10-01 | 12:00
34 | Manikganj | 107 | 18 | 2017-10-01 | 19:30
35 | Joydevpur | 202 | 11 | 2017-10-01 | 18:30
36 | New Tongi | 116 | 12 | 2017-10-01 | 15:00
37 | Tangail | 169 | 3 | 2017-10-01 | 19:00
38 | Mymensing | 196 | 17 | 2017-10-01 | 19:00
39 | Kishorganj | 80 | 13 | 2017-10-01 | 18:00
40 | Netrokona | 68 | 9 | 2017-10-01 | 23:00
41 | Jamalpur | 95 | 16 | 2017-10-01 | 19:00
42 | Sherpur | 89 | 9 | 2017-10-01 | 1:00
43 | Srimongal | 40 | 7 | 2017-10-01 | 2:00
44 | Shahjibazar | 96 | 5 | 2017-10-01 | 18:30
45 | Fenchuganj | 59 | 5 | 2017-10-01 | 19:30
46 | Khulawara | 42 | 11 | 2017-10-01 | 21:00
47 | Sylhet | 167 | 11 | 2017-10-01 | 18:30
48 | Chatak | 55 | 5 | 2017-10-01 | 18:30
49 | Comilla (S) | 172 | 4 | 2017-10-01 | 19:30
50 | Comilla(N) | 137 | 15 | 2017-10-01 | 18:00
51 | Chandpur | 120 | 17 | 2017-10-01 | 21:00
52 | Feni | 109 | 17 | 2017-10-01 | 21:00
53 | Chowmuhani | 180 | 6 | 2017-10-01 | 20:00
54 | Ashuganj | 62 | 17 | 2017-10-01 | 22:00
55 | Daudkandi | 96 | 12 | 2017-10-01 | 23:00
56 | B.Baria | 114 | 5 | 2017-10-01 | 19:30
57 | Madanhat | 85 | 5 | 2017-10-01 | 18:00
58 | Hathazari | 93 | 12 | 2017-10-01 | 20:00
59 | Khulshi | 192 | 2 | 2017-10-01 | 18:00
60 | Halishahar | 144 | 3 | 2017-10-01 | 18:00
61 | Baraulia | 133 | 11 | 2017-10-01 | 07:00
62 | Sikalbaha | 35 | 25 | 2017-10-01 | 19:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2017
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
63 | Dohazari | 88 | 14 | 2017-10-01 | 18:00
64 | Cox'sbazar | 86 | 11 | 2017-10-01 | 20:00
65 | Chandraghona | 33 | 11 | 2017-10-01 | 22:00
66 | Kaptai | 4.2 | 4 | 2017-10-01 | 19:00
67 | A. Khaer Stl. | 27 | 8 | 2017-10-01 | 20:00
68 | Bakulia | 111 | 3 | 2017-10-01 | 18:30
69 | Julda | 21 | 15 | 2017-10-01 | 10:00
70 | TK chemical | 6 | 2 | 2017-10-01 | 13:00
71 | Modern Steel | 19 | 7 | 2017-10-01 | 10:00
72 | Shahmirpur | 32 | 3 | 2017-10-01 | 18:00
73 | Abul Khair 230 | 204.1 | 4 | 2017-10-01 | 14:00
74 | BSRM | 118 | 16 | 2017-10-01 | 23:00
75 | Goalpara | 33 | 4 | 2017-10-01 | 19:00
76 | Central s/s | 90 | 24 | 2017-10-01 | 19:00
77 | Noapara | 81 | 25 | 2017-10-01 | 19:30
78 | Jessore | 128 | 2 | 2017-10-01 | 19:30
79 | Jhenida | 80 | 1 | 2017-10-01 | 19:00
80 | Bottail | 102 | 24 | 2017-10-01 | 18:30
81 | G.K Project | 49 | 7 | 2017-10-01 | 20:00
82 | Faridpur | 126 | 25 | 2017-10-01 | 18:00
83 | Madaripur | 114 | 25 | 2017-10-01 | 19:00
84 | Gopalganj | 74 | 17 | 2017-10-01 | 21:00
85 | Bagerhat | 72 | 6 | 2017-10-01 | 19:30
86 | Mongla | 34 | 29 | 2017-10-01 | 11:00
87 | Satkhira | 84 | 6 | 2017-10-01 | 19:30
88 | Gallamari | 59 | 15 | 2017-10-01 | 13:00
89 | Magura | 42 | 23 | 2017-10-01 | 18:30
90 | Chuadanga | 73 | 6 | 2017-10-01 | 19:30
91 | Barisal | 106 | 25 | 2017-10-01 | 18:30
92 | Patuakhali | 73 | 25 | 2017-10-01 | 20:00
93 | Bhandaria | 40 | 13 | 2017-10-01 | 21:00
94 | Ishurdi | 48 | 18 | 2017-10-01 | 18:00
95 | Natore | 99 | 4 | 2017-10-01 | 20:00
96 | Bogra | 201 | 23 | 2017-10-01 | 19:30
97 | Noagaon | 92 | 18 | 2017-10-01 | 19:30
98 | Rajshahi | 170 | 19 | 2017-10-01 | 19:00
99 | C.Nawabganj | 57 | 6 | 2017-10-01 | 20:00
100 | Amnura | 43 | 25 | 2017-10-01 | 18:30
101 | Pabna | 96 | 24 | 2017-10-01 | 18:30
102 | Shahjadpur | 86 | 24 | 2017-10-01 | 19:00
103 | Serajganj | 87 | 11 | 2017-10-01 | 12:00
104 | Niyamatpur | 51 | 8 | 2017-10-01 | 18:30
105 | Joypurhat | 39 | 8 | 2017-10-01 | 20:00
106 | Rangpur | 116 | 8 | 2017-10-01 | 21:00
107 | Lalmonirhat | 78 | 10 | 2017-10-01 | 18:00
108 | Saidpur | 94 | 1 | 2017-10-01 | 18:30
109 | Purbasadipur | 70 | 7 | 2017-10-01 | 18:00
110 | Thakurgaon | 55 | 8 | 2017-10-01 | 20:00
111 | Palashbari | 76 | 1 | 2017-10-01 | 18:30
112 | Barapukuria | 39 | 8 | 2017-10-01 | 18:30
113 | Panchagar | 30 | 13 | 2017-10-01 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October' 2017
Area | MW | Date | Hour | Remarks
Dhaka | 3842 | 18.10.17 | 18:30
Chittagong | 1155 | 06.10.17 | 1:00
Khulna | 1114 | 02.10.17 | 20:00
Rajshahi | 935 | 23.10.17 | 19:30
Comilla | 880 | 17.10.17 | 21:00
Mymensingh | 618 | 18.10.17 | 20:00
Sylhet | 479 | 18.10.17 | 19:30
Barisal | 211 | 25.10.17 | 20:00
Rangpur | 520 | 01.10.17 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2017
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 424 | 31 | 2017-10-01 | 18:30 | 371 | 18 | 2017-10-01 | 11:00
2 | Bheramara | 400 | 424 | 21 | 2017-10-01 | 07:00 | 362 | 29 | 2017-10-01 | 18:00
3 | Kaliakoir | 400 | 396 | 25 | 2017-10-01 | 18:30 | 347 | 18 | 2017-10-01 | 12:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 27 | 2017-10-01 | 24:00 | 220 | 17 | 2017-10-01 | 13:00
2 | Ishurdi | 230 | 240 | 21 | 2017-10-01 | 07:00 | 225 | 15 | 2017-10-01 | 15:00
3 | Ashuganj | 230 | 240 | 19 | 2017-10-01 | 6:00 | 227 | 28 | 2017-10-01 | 14:00
4 | Serajganj | 230 | 235 | 21 | 2017-10-01 | 6:00 | 206 | 19 | 2017-10-01 | 1:00
5 | Baghabari | 230 | 235 | 21 | 2017-10-01 | 5:00 | 214 | 19 | 2017-10-01 | 13:00
6 | Barapukuria | 230 | 238 | 21 | 2017-10-01 | 6:00 | 208 | 19 | 2017-10-01 | 21:00
7 | Bogra | 230 | 236 | 21 | 2017-10-01 | 06':00 | 200 | 19 | 2017-10-01 | 23:00
8 | Khulna South | 230 | 244 | 21 | 2017-10-01 | 06'00 | 228 | 21 | 2017-10-01 | 18:30
9 | Rampura | 230 | 221 | 21 | 2017-10-01 | 4:00 | 209 | 17 | 2017-10-01 | 12:00
10 | Haripur | 230 | 219 | 21 | 2017-10-01 | 5:00 | 206 | 18 | 2017-10-01 | 16:00
11 | Hasnabad | 230 | 223 | 21 | 2017-10-01 | 6:00 | 201 | 15 | 2017-10-01 | 12:00
12 | Aminbazar | 230 | 223 | 21 | 2017-10-01 | 4:00 | 205 | 17 | 2017-10-01 | 15:00
13 | Tongi | 230 | 227 | 21 | 2017-10-01 | 4:00 | 200 | 18 | 2017-10-01 | 12:00
14 | Comilla (N) | 230 | 230 | 30 | 2017-10-01 | 21:00 | 216 | 17 | 2017-10-01 | 10:00
15 | Hathazari | 230 | 227 | 21 | 2017-10-01 | 16:00 | 200 | 2 | 2017-10-01 | 12:00
16 | Megnaghat | 230 | 224 | 21 | 2017-10-01 | 4:00 | 210 | 17 | 2017-10-01 | 16:00
17 | Fenchuganj | 230 | 243 | 21 | 2017-10-01 | 14:00 | 227 | 4 | 2017-10-01 | 16:00
18 | Siddhirganj | 230 | 244 | 21 | 2017-10-01 | 14:00 | 208 | 5 | 2017-10-01 | 10:00
19 | Maniknagar | 230 | 243 | 21 | 2017-10-01 | 6:00 | 206 | 5 | 2017-10-01 | 10:00
20 | Old Airport | 230 | 220 | 14 | 2017-10-01 | 06:00 | 202 | 18 | 2017-10-01 | 12:00
21 | Barisal | 230 | 246 | 21 | 2017-10-01 | 07:00 | 219 | 5 | 2017-10-01 | 4:00
22 | AKSML | 230 | 224 | 21 | 2017-10-01 | 16:00 | 197 | 11 | 2017-10-01 | 7:00
23 | BSRM | 230 | 226 | 21 | 2017-10-01 | 16:00 | 203 | 11 | 2017-10-01 | 11:00
24 | Bibiyana | 230 | 240 | 22 | 2017-10-01 | 18:00 | 227 | 21 | 2017-10-01 | 11:00
132 kV Substation
1 | Siddhirganj | 132 | 141 | 27 | 2017-10-01 | 18:00 | 125 | 5 | 2017-10-01 | 10:00
2 | Munsiganj | 132 | 141 | 27 | 2017-10-01 | 18:00 | 125 | 15 | 2017-10-01 | 10:00
3 | Megnaghat | 132 | 136 | 19 | 2017-10-01 | 6:00 | 126 | 2 | 2017-10-01 | 10:00
4 | Shyampur | 132 | 134 | 16 | 2017-10-01 | 5:00 | 114 | 5 | 2017-10-01 | 9:00
5 | Bhulta | 132 | 130 | 6 | 2017-10-01 | 13:00 | 115 | 5 | 2017-10-01 | 10:00
6 | Madanganj | 132 | 137 | 21 | 2017-10-01 | 6:00 | 125 | 3 | 2017-10-01 | 11:00
7 | Shitalakhya | 132 | 136 | 5 | 2017-10-01 | 3:00 | 123 | 31 | 2017-10-01 | 12:00
8 | Rahim Steal | 132 | 138 | 20 | 2017-10-01 | 24:00 | 124 | 5 | 2017-10-01 | 10:00
9 | Matuail | 132 | 138 | 21 | 2017-10-01 | 4:00 | 124 | 15 | 2017-10-01 | 10:00
10 | Ghorasal | 132 | 140 | 21 | 2017-10-01 | 3:00 | 130 | 3 | 2017-10-01 | 10:00
11 | Narsinghdi | 132 | 138 | 21 | 2017-10-01 | 6:00 | 119 | 15 | 2017-10-01 | 10:00
12 | Haripur (SBU) | 132 | 139 | 21 | 2017-10-01 | 6:00 | 124 | 5 | 2017-10-01 | 10:00
13 | Ullon | 132 | 136 | 21 | 2017-10-01 | 6:00 | 121 | 17 | 2017-10-01 | 12:00
14 | Hasnabad | 132 | 136 | 13 | 2017-10-01 | 6:00 | 125 | 15 | 2017-10-01 | 10:00
15 | Magbazar | 132 | 137 | 21 | 2017-10-01 | 6:00 | 121 | 17 | 2017-10-01 | 16:00
16 | Maniknagar | 132 | 143 | 21 | 2017-10-01 | 6:00 | 122 | 5 | 2017-10-01 | 10:00
17 | Bangabhaban | 132 | 135 | 27 | 2017-10-01 | 1400:00 | 122 | 5 | 2017-10-01 | 12:00
18 | Narinda | 132 | 136 | 21 | 2017-10-01 | 6:00 | 122 | 5 | 2017-10-01 | 1:00
19 | Dhanmondi | 132 | 138 | 20 | 2017-10-01 | 08:00 | 122 | 5 | 2017-10-01 | 10:00
20 | Lalbag | 132 | 134 | 17 | 2017-10-01 | 4:00 | 118 | 17 | 2017-10-01 | 16:00
21 | Madartek | 132 | 136 | 21 | 2017-10-01 | 6:00 | 121 | 18 | 2017-10-01 | 12:00
22 | Mirpur | 132 | 132 | 9 | 2017-10-01 | 6:00 | 119 | 24 | 2017-10-01 | 11:00
23 | Kalyanpur | 132 | 136 | 21 | 2017-10-01 | 5:00 | 123 | 18 | 2017-10-01 | 12:00
24 | Gulshan | 132 | 136 | 21 | 2017-10-01 | 6:00 | 121 | 17 | 2017-10-01 | 11:00
25 | Uttara | 132 | 134 | 21 | 2017-10-01 | 6:00 | 120 | 17 | 2017-10-01 | 16:00
26 | Kamrangirchar | 132 | 135 | 14 | 2017-10-01 | 5:00 | 120 | 3 | 2017-10-01 | 11:00
27 | Savar | 132 | 134 | 19 | 2017-10-01 | 6:00 | 120 | 18 | 2017-10-01 | 12:00
28 | Bhasantec | 132 | 136 | 21 | 2017-10-01 | 6:00 | 120 | 17 | 2017-10-01 | 16:00
29 | Agargaon | 132 | 137 | 21 | 2017-10-01 | 6:00 | 123 | 17 | 2017-10-01 | 11:00
30 | Satmosjid | 132 | 136 | 21 | 2017-10-01 | 6:00 | 121 | 18 | 2017-10-01 | 12:00
31 | Tongi | 132 | 141 | 21 | 2017-10-01 | 5:00 | 122 | 16 | 2017-10-01 | 16:00
32 | Kabirpur | 132 | 140 | 19 | 2017-10-01 | 7:00 | 120 | 4 | 2017-10-01 | 11:00
33 | Basundhara | 132 | 137 | 21 | 2017-10-01 | 5:00 | 120 | 12 | 2017-10-01 | 19:00
34 | Manikganj | 132 | 146 | 21 | 2017-10-01 | 6:00 | 123 | 18 | 2017-10-01 | 18:30
35 | Joydevpur | 132 | 147 | 19 | 2017-10-01 | 6:00 | 124 | 3 | 2017-10-01 | 15:00
36 | New Tongi | 132 | 141 | 21 | 2017-10-01 | 08:00 | 122 | 15 | 2017-10-01 | 15:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2017
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
37 | Tangail | 132 | 143 | 21 | 2017-10-01 | 13:00 | 115 | 17 | 2017-10-01 | 19:00
38 | Mymensing | 132 | 144 | 21 | 2017-10-01 | 16:00 | 117 | 3 | 2017-10-01 | 18:00
39 | Kishorganj | 132 | 140 | 21 | 2017-10-01 | 07:00 | 123 | 3 | 2017-10-01 | 23:00
40 | Netrokona | 132 | 142 | 21 | 2017-10-01 | 14:00 | 117 | 4 | 2017-10-01 | 3:00
41 | Jamalpur | 132 | 141 | 21 | 2017-10-01 | 16:00 | 113 | 5 | 2017-10-01 | 2:00
42 | Sherpur | 132 | 143 | 21 | 2017-10-01 | 16:00 | 111 | 5 | 2017-10-01 | 2:00
43 | Srimongal | 132 | 141 | 30 | 2017-10-01 | 18:30 | 134 | 3 | 2017-10-01 | 18:30
44 | Shahjibazar | 132 | 141 | 22 | 2017-10-01 | 08:00 | 124 | 7 | 2017-10-01 | 12:00
45 | Fenchuganj | 132 | 139 | 21 | 2017-10-01 | 20:00 | 131 | 11 | 2017-10-01 | 19:30
46 | Khulawara | 132 | 138 | 21 | 2017-10-01 | 18:00 | 130 | 11 | 2017-10-01 | 20:00
47 | Sylhet | 132 | 137 | 21 | 2017-10-01 | 17:00 | 126 | 9 | 2017-10-01 | 19:30
48 | Chattak | 132 | 138 | 21 | 2017-10-01 | 20:00 | 120 | 20 | 2017-10-01 | 19:00
49 | Comilla(South) | 132 | 135 | 21 | 2017-10-01 | 14:00 | 118 | 4 | 2017-10-01 | 21:00
50 | Comilla (North) | 132 | 138 | 22 | 2017-10-01 | 8:00 | 128 | 16 | 2017-10-01 | 16:00
51 | Chandpur | 132 | 140 | 21 | 2017-10-01 | 7:00 | 120 | 18 | 2017-10-01 | 22:00
52 | Feni | 132 | 127 | 21 | 2017-10-01 | 20:00 | 115 | 11 | 2017-10-01 | 23:00
53 | Chowmuhani | 132 | 136 | 23 | 2017-10-01 | 9:00 | 109 | 11 | 2017-10-01 | 18:00
54 | Ashuganj | 132 | 144 | 21 | 2017-10-01 | 7:00 | 135 | 2 | 2017-10-01 | 22:00
55 | Daudkandi | 132 | 138 | 20 | 2017-10-01 | 8:00 | 124 | 5 | 2017-10-01 | 10:00
56 | Brahminbaria | 132 | 141 | 21 | 2017-10-01 | 7:00 | 132 | 2 | 2017-10-01 | 22:00
57 | Madanhat | 132 | 138 | 21 | 2017-10-01 | 17:00 | 121 | 15 | 2017-10-01 | 15:00
58 | Hathazari | 132 | 137 | 11 | 2017-10-01 | 13:00 | 120 | 2 | 2017-10-01 | 13:00
59 | Khulshi | 132 | 137 | 7 | 2017-10-01 | 7:00 | 116 | 2 | 2017-10-01 | 12:00
60 | Halishahar | 132 | 134 | 21 | 2017-10-01 | 16:00 | 118 | 2 | 2017-10-01 | 13:00
61 | Baraulia | 132 | 134 | 11 | 2017-10-01 | 18:30 | 118 | 21 | 2017-10-01 | 12:00
62 | Sikalbaha | 132 | 134 | 21 | 2017-10-01 | 16:00 | 118 | 21 | 2017-10-01 | 4:00
63 | Dohazari | 132 | 135 | 21 | 2017-10-01 | 16:00 | 119 | 2 | 2017-10-01 | 13:00
64 | Cox'sbazar | 132 | 132 | 21 | 2017-10-01 | 19:30 | 111 | 11 | 2017-10-01 | 20:00
65 | Chandraghona | 132 | 135 | 21 | 2017-10-01 | 16:00 | 120 | 11 | 2017-10-01 | 14:00
66 | Kaptai | 132 | 135 | 11 | 2017-10-01 | 18:30 | 125 | 2 | 2017-10-01 | 18:00
67 | A. Khaer Stl. | 132 | 134 | 11 | 2017-10-01 | 18:30 | 120 | 2 | 2017-10-01 | 13:00
68 | Bakulia | 132 | 132 | 21 | 2017-10-01 | 16:00 | 116 | 21 | 2017-10-01 | 12:00
69 | Julda | 132 | 134 | 21 | 2017-10-01 | 17:00 | 118 | 2 | 2017-10-01 | 12:00
70 | TK Chemical | 132 | 136 | 21 | 2017-10-01 | 16:00 | 121 | 11 | 2017-10-01 | 14:00
71 | Modern Steel | 132 | 134 | 21 | 2017-10-01 | 16:00 | 117 | 11 | 2017-10-01 | 14:00
72 | Shahmirpur | 132 | 134 | 11 | 2017-10-01 | 18:30 | 118 | 2 | 2017-10-01 | 12:00
73 | Goalpara | 132 | 138 | 2 | 2017-10-01 | 1:00 | 130 | 15 | 2017-10-01 | 7:00
74 | Khulna Central | 132 | 139 | 1 | 2017-10-01 | 16:00 | 132 | 11 | 2017-10-01 | 7:00
75 | Noapara | 132 | 138 | 14 | 2017-10-01 | 6:00 | 127 | 13 | 2017-10-01 | 19:00
76 | Jessore | 132 | 136 | 11 | 2017-10-01 | 10:00 | 120 | 1 | 2017-10-01 | 18:30
77 | Jhenida | 132 | 135 | 20 | 2017-10-01 | 11:00 | 115 | 5 | 2017-10-01 | 07:00
78 | Bottail | 132 | 138 | 21 | 2017-10-01 | 06:00 | 124 | 3 | 2017-10-01 | 22:00
79 | G.K.Project | 132 | 140 | 21 | 2017-10-01 | 05:00 | 123 | 9 | 2017-10-01 | 13:00
80 | Faridpur | 132 | 138 | 21 | 2017-10-01 | 19:00 | 122 | 5 | 2017-10-01 | 4:00
81 | Madaripur | 132 | 140 | 21 | 2017-10-01 | 7:00 | 123 | 23 | 2017-10-01 | 18:00
82 | Gopalganj | 132 | 143 | 9 | 2017-10-01 | 9:00 | 118 | 12 | 2017-10-01 | 15:00
83 | Bagerhat | 132 | 140 | 21 | 2017-10-01 | 2:00 | 130 | 4 | 2017-10-01 | 19:30
84 | Mongla | 132 | 136 | 21 | 2017-10-01 | 5:00 | 127 | 5 | 2017-10-01 | 2:00
85 | Satkhira | 132 | 138 | 9 | 2017-10-01 | 3:00 | 130 | 6 | 2017-10-01 | 19:30
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2017
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
86 | Gallamari | 132 | 139 | 5 | 2017-10-01 | 6:00 | 132 | 21 | 2017-10-01 | 18:30
87 | Magura | 132 | 138 | 21 | 2017-10-01 | 5:00 | 115 | 3 | 2017-10-01 | 22:00
88 | Chuadanga | 132 | 136 | 21 | 2017-10-01 | 6:00 | 109 | 3 | 2017-10-01 | 22:00
89 | Barisal | 132 | 140 | 20 | 2017-10-01 | 11:00 | 130 | 4 | 2017-10-01 | 16:00
90 | Patuakhali | 132 | 140 | 20 | 2017-10-01 | 11:00 | 130 | 4 | 2017-10-01 | 16:00
91 | Bhandaria | 132 | 140 | 21 | 2017-10-01 | 5:00 | 125 | 5 | 2017-10-01 | 1:00
92 | Ishurdi | 132 | 139 | 21 | 2017-10-01 | 6:00 | 128 | 1 | 2017-10-01 | 19:00
93 | Natore | 132 | 140 | 21 | 2017-10-01 | 6:00 | 122 | 16 | 2017-10-01 | 18:00
94 | Bogra | 132 | 143 | 21 | 2017-10-01 | 6:00 | 118 | 19 | 2017-10-01 | 21:00
95 | Noagaon | 132 | 141 | 21 | 2017-10-01 | 9:00 | 114 | 28 | 2017-10-01 | 19:00
96 | Rajshahi | 132 | 138 | 21 | 2017-10-01 | 8:00 | 123 | 9 | 2017-10-01 | 12:00
97 | C.Nawabganj | 132 | 138 | 28 | 2017-10-01 | 7:00 | 122 | 9 | 2017-10-01 | 12:00
98 | Amnura | 132 | 140 | 10 | 2017-10-01 | 17:00 | 120 | 9 | 2017-10-01 | 12:00
99 | Pabna | 132 | 135 | 21 | 2017-10-01 | 5:00 | 106 | 17 | 2017-10-01 | 10:00
100 | Shahjadpur | 132 | 142 | 21 | 2017-10-01 | 9:00 | 117 | 17 | 2017-10-01 | 10:00
101 | Serajganj | 132 | 140 | 21 | 2017-10-01 | 6:00 | 119 | 17 | 2017-10-01 | 10:00
102 | Niyamatpur | 132 | 143 | 21 | 2017-10-01 | 6:00 | 113 | 19 | 2017-10-01 | 21:00
103 | Joypurhat | 132 | 142 | 21 | 2017-10-01 | 6:00 | 114 | 19 | 2017-10-01 | 21:00
104 | Rangpur | 132 | 133 | 21 | 2017-10-01 | 7:00 | 107 | 20 | 2017-10-01 | 1:00
105 | Lalmonirhat | 132 | 137 | 21 | 2017-10-01 | 6:00 | 100 | 19 | 2017-10-01 | 21:00
106 | Saidpur | 132 | 135 | 21 | 2017-10-01 | 7:00 | 104 | 19 | 2017-10-01 | 13:00
107 | Purbasadipur | 132 | 135 | 21 | 2017-10-01 | 7:00 | 103 | 19 | 2017-10-01 | 21:00
108 | Thakurgaon | 132 | 132 | 21 | 2017-10-01 | 6:00 | 95 | 19 | 2017-10-01 | 21:00
109 | Palashbari | 132 | 135 | 21 | 2017-10-01 | 6:00 | 110 | 19 | 2017-10-01 | 13:00
110 | Barapukuria | 132 | 135 | 21 | 2017-10-01 | 5:00 | 108 | 19 | 2017-10-01 | 21:00
111 | Panchagar | 132 | 130 | 21 | 2017-10-01 | 5:00 | 94 | 1 | 2017-10-01 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:October' 2017
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 126 | 400
IP-299421 | Hasnabad | TR2 | 225 | 112 | 395 | 28.10.17 | 23:00
|  | TR3 | 225 | 110 | 360
|  | TR1 | 225 | 125 | 465
IP-299866 | Tongi | TR2 | 225 | 125 | 465 | 18.10.17 | 18:00
|  | TR3 | 225 | 125 | 465
|  | TR1 | 225 | 125 | 400
IP-299427 | Haripur | TR2 | 225 | 125 | 400 | 01.10.17 | 07:00
|  | TR3 | 225 | 125 | 400
|  | TR1 | 225 | 155 | 455
IP-299728 | Rampura | TR2 | 225 | 155 | 455 | 06.10.17 | 12:00
|  | TR3 | 225 | 155 | 455
|  | TR1 | 225 | 108 | 311
IP-299264 | Aminbazar | TR2 | 225 | 108 | 311 | 11.10.17 | 08:00
|  | TR3 | 225 | 113 | 325
| Maniknagar | TR1 | 300 | 121 | 390 | 05.10.17 | 15:00
|  | TR2 | 300 | 121 | 390
IP-399266 | Comilla (N) | TR1 | 225 | 160 | 450 | 02.10.17 | 24:00
|  | TR2 | 225 | 155 | 448
| Fenchuganj | TR1 | 300 | 244 | 618 | 30.10.17 | 10:00
|  | TR1 | 150 | 85 | 220
IP-399428 | Hathazari | TR3 | 150 | 85 | 220 | 21.10.17 | 11:00
|  | TR4 | 150 | 85 | 220
|  | TR1 | 225 | 158 | 420
| Ishurdi | TR2 | 225 | 158 | 420 | 06.10.17 | 19:00
IP-499474 |  | TR3 | 225 | 158 | 420
| Khulna(S) | TR1 | 225 | 142 | 361
IP-58001/58002 |  | TR2 | 225 | 142 | 361 | 21.10.17 | 20:00
| Bogra | TR1 | 225 | 150 | 497 | 28.09.17 | 20:00
IP-43002/499264 |  | TR2 | 225 | 150 | 497
IP-499224 | Baghabari | TR1 | 225 | 150 | 400 | 16.10.17 | 12:00
| Barapukuria | TR1 | 225 | 178 | 990 | 01.10.17 | 18:30
|  | TR2 | 225 | 178 | 990
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:October' 2017 | [6 empty] | (For Evening Peak) | [7 empty] | Month:October' 2017 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-10-17 | 8874 | 8874 | - | - | - | - | - | - | - | - | - | - | - | - | 01-10-17 | 7195 | 5706 | - | - | - | - | - | - | - | - | - | - | - | -
02-10-17 | 9377 | 9377 | - | - | - | - | - | - | - | - | - | - | - | - | 02-10-17 | 8178 | 8178 | - | - | - | - | - | - | - | - | - | - | - | -
03-10-17 | 9382 | 9382 | - | - | - | - | - | - | - | - | - | - | - | - | 03-10-17 | 8121.9 | 8121.9 | - | - | - | - | - | - | - | - | - | - | - | -
04-10-17 | 9078 | 9078 | - | - | - | - | - | - | - | - | - | - | - | - | 04-10-17 | 8271.2 | 8271.2 | - | - | - | - | - | - | - | - | - | - | - | -
05-10-17 | 9077 | 9077 | - | - | - | - | - | - | - | - | - | - | - | - | 05-10-17 | 8232.1 | 8232 | - | - | - | - | - | - | - | - | - | - | - | -
06-10-17 | 9128 | 9128 | - | - | - | - | - | - | - | - | - | - | - | - | 06-10-17 | 7332 | 7332 | - | - | - | - | - | - | - | - | - | - | - | -
07-10-17 | 9428 | 9428 | - | - | - | - | - | - | - | - | - | - | - | - | 07-10-17 | 7602.7 | 7602 | - | - | - | - | - | - | - | - | - | - | - | -
08-10-17 | 9326 | 9326 | - | - | - | - | - | - | - | - | - | - | - | - | 08-10-17 | 7825.4 | 7825 | - | - | - | - | - | - | - | - | - | - | - | -
09-10-17 | 9251 | 9251 | - | - | - | - | - | - | - | - | - | - | - | - | 09-10-17 | 7490 | 7490 | - | - | - | - | - | - | - | - | - | - | - | -
10-10-17 | 9289 | 9289 | - | - | - | - | - | - | - | - | - | - | - | - | 10-10-17 | 7756.5 | 7756 | - | - | - | - | - | - | - | - | - | - | - | -
11-10-17 | 9181 | 9181 | - | - | - | - | - | - | - | - | - | - | - | - | 11-10-17 | 8069.5 | 8069 | - | - | - | - | - | - | - | - | - | - | - | -
12-10-17 | 9261 | 9261 | - | - | - | - | - | - | - | - | - | - | - | - | 12-10-17 | 8064 | 8064 | - | - | - | - | - | - | - | - | - | - | - | -
13-10-17 | 8981 | 8981 | - | - | - | - | - | - | - | - | - | - | - | - | 13-10-17 | 7106.4 | 7106 | - | - | - | - | - | - | - | - | - | - | - | -
14-10-17 | 9168 | 9168 | - | - | - | - | - | - | - | - | - | - | - | - | 14-10-17 | 7542.1 | 7542 | - | - | - | - | - | - | - | - | - | - | - | -
15-10-17 | 9236 | 9236 | - | - | - | - | - | - | - | - | - | - | - | - | 15-10-17 | 8025 | 8025 | - | - | - | - | - | - | - | - | - | - | - | -
16-10-17 | 9154 | 9154 | - | - | - | - | - | - | - | - | - | - | - | - | 16-10-17 | 8130.7 | 8130.7 | - | - | - | - | - | - | - | - | - | - | - | -
17-10-17 | 9200 | 9200 | - | - | - | - | - | - | - | - | - | - | - | - | 17-10-17 | 8100 | 8100 | - | - | - | - | - | - | - | - | - | - | - | -
18-10-17 | 9507 | 9507 | - | - | - | - | - | - | - | - | - | - | - | - | 18-10-17 | 7964.6 | 7964.6 | - | - | - | - | - | - | - | - | - | - | - | -
19-10-17 | 8902 | 8902 | - | - | - | - | - | - | - | - | - | - | - | - | 19-10-17 | 7453.1 | 7453.1 | - | - | - | - | - | - | - | - | - | - | - | -
20-10-17 | 6638 | 6638 | - | - | - | - | - | - | - | - | - | - | - | - | 20-10-17 | 5458.3 | 5458.3 | - | - | - | - | - | - | - | - | - | - | - | -
21-10-17 | 5413 | 5413 | - | - | - | - | - | - | - | - | - | - | - | - | 21-10-17 | 3982 | 3982 | - | - | - | - | - | - | - | - | - | - | - | -
22-10-17 | 8061 | 8061 | - | - | - | - | - | - | - | - | - | - | - | - | 22-10-17 | 5878 | 5878 | - | - | - | - | - | - | - | - | - | - | - | -
23-10-17 | 9139 | 9139 | - | - | - | - | - | - | - | - | - | - | - | - | 23-10-17 | 6650.3 | 6650.3 | - | - | - | - | - | - | - | - | - | - | - | -
24-10-17 | 8859 | 8859 | - | - | - | - | - | - | - | - | - | - | - | - | 24-10-17 | 6914.9 | 6914.9 | - | - | - | - | - | - | - | - | - | - | - | -
25-10-17 | 9222 | 9222 | - | - | - | - | - | - | - | - | - | - | - | - | 25-10-17 | 6916.9 | 6916.9 | - | - | - | - | - | - | - | - | - | - | - | -
26-10-17 | 9179 | 9179 | - | - | - | - | - | - | - | - | - | - | - | - | 26-10-17 | 6927.5 | 6927.5 | - | - | - | - | - | - | - | - | - | - | - | -
27-10-17 | 7899 | 7899 | - | - | - | - | - | - | - | - | - | - | - | - | 27-10-17 | 5670 | 5670 | - | - | - | - | - | - | - | - | - | - | - | -
28-10-17 | 8444 | 8444 | - | - | - | - | - | - | - | - | - | - | - | - | 28-10-17 | 6199 | 6199 | - | - | - | - | - | - | - | - | - | - | - | -
29-10-17 | 8365 | 8365 | - | - | - | - | - | - | - | - | - | - | - | - | 29-10-17 | 6732.5 | 6732.5 | - | - | - | - | - | - | - | - | - | - | - | -
30-10-17 | 7644 | 7644 | - | - | - | - | - | - | - | - | - | - | - | - | 30-10-17 | 6400.5 | 6400.5 | - | - | - | - | - | - | - | - | - | - | - | -
31-10-17 | 8183 | 8183 | - | - | - | - | - | - | - | - | - | - | - | - | 31-10-17 | 6203.7 | 6203.7 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October' 2017
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9507 | 18/10/17 | 19:30
2 | Maximum day peak Genaration | MW | 8271.2 | 04/10/17 | 10:00
3 | Maximum Evening Peak Demand | MW | 9507 | 18/10/17 | 19:30
4 | Minimum Generation | MW | 3198 | 21/10/17 | 7:00
5 | Average of the daily evening peak Genaration | MW | 8769.2258
6 | Average of the daily day peak Genaration | MW | 7174.0065
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5572.1195
12 | Total Generation by IPP | MKWH | 1102.9499 | % of total Gen. | 19.7941
13 | Total Generation by BPDB | MKWH | 2597.5559 | " | 46.617
14 | A) Total Generation by RPCL | MKWH | 190.7408 | '' | 3.4231
| B) Total Generation by REB | MKWH | 117.5319 | " | 2.1093
| C) Total Generation by RENTAL | MKWH | 1138.9265 | " | 20.4397
| D) Total Imported from India (HVDC) | MKWH | 339.4247 | " | 6.0915
| E) Total Imported from Tripura, India (A.C) | MKWH | 84.9898 | " | 1.5253
15 | Fuel wise Generation.
| A) Gas | MKWH | 3531.4383 | % of total Gen. | 63.38%
| B) Oil | MKWH | 1440.7592 | '' | 25.86%
| C) Hydro | MKWH | 119.1411 | '' | 2.138%
| D) Solar | MKWH | 0.34114 | '' | 0.006122%
| E) Coal | MKWH | 56.0252 | '' | 1.005%
| F) HVDC (Import from India) | MKWH | 339.4247 | '' | 6.091%
| G) A.C (Import from Tripura, India) | MKWH | 84.9898 | '' | 1.525%
16 | Maximun of the daily total Generation . | MKWH | 203.6042 | 12/10/17
17 | Monthly Load factor | % | 78.7778
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 14679.3215
| A) Gas | M.Taka | 2251.4466
| B) Liquid fuel | M.Taka | 12105.6428
| C) Coal | M.Taka | 322.2321
| D) HVDC (Import from India) | M.Taka | 984.3317
| E) Tripura(Import from India) | M.Taka | 552.4334
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 802.7365 | 13/10/17
| A) Gas | M.Taka | 398.4707 | 13/10/17
| B) Liquid fuel | M.Taka | 641.114 | 05/10/17
| C) Coal | M.Taka | 59.275 | 26/10/17
| D) HVDC (Import from India) | M.Taka | 34.7241 | 27/10/17
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.3745
| B) Excluding Hydro & Solar | Taka/KWHR | 3.4484
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 109 | 31/10/17 | 06:00
b) | Actual | FT (MSL) | 108.89 | 31/10/18 | 06:00
22 | Peak Genaration of October 2016 | MW | 8864 | 09/10/16 | 21:00
23 | Peak Demand of September 2016 | MW | 8900 | 02/10/16 | 21:00
24 | Maximum peak Generation recorded upto 31/10/17 | MW | 9507 | 18/10/17 | 19:30
25 | Maximum peak Demand recorded upto 30/09/17 | MW | 9507 | 18/10/17 | 19:30
26 | Maximum load shed recorded upto 31/10/17 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.