## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September' 2017
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | September 2017 |  | August 2017 |  | September 2016
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9431 | 26/09/17 | 9470 | 05/08/17 | 8890 | 08/09/16 | 9479 | 07/06/17
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 4928 | 02/09/17 | 6149 | 13/08/17 | 4317 | 13/09/16 | - | -
|  |  | 10:00 |  | 7:00 |  | 11:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9431 | 26/09/17 | 9470 | 05/08/17 | 8890 | 08/09/16 | 9479 | 07/06/17
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 8614.2 | 28/09/17 | 8385 | 21/8/2017 | 7577 | 08/9/2016 | 8743 | 07/6/17
|  |  | 11:00 |  | 11:00 |  | 12:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9431 | 26/09/17 | 9470 | 05/08/17 | 8900 | 07/09/16 | 9479 | 07/06/17
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 8743.3871 |  | 9035.13 |  | 8263.63 |  | 9057.07 | Aug -17
7 | Average Generation (MW) at Day Peak | 7323.8065 |  | 7706.23 |  | 6677.03 |  | 7210.5 | May -17
8 | Maximum Power Import from India (MW) | 492 | 03/09/17 | 502 | 13/08/17 | 467 | 13/09/16 | 509 | 2017-07-03
|  |  | 2:00 |  | 8:00 |  | 21:00 |  | 11:00
9 | Maximum Power Import from Tripura, India (MW) | 168 | 14/09/17 | 166 | 23/08/17 | 104 | 23/9/2016 | 168 | 14/09/17
|  |  | 20:00 |  | 19:00 |  | 21:00 |  | 20:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | 439 | 2016-04-09 | 1459 | 2010-05-04
|  |  | - |  | - |  | 21:00 |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | 8212 | 2016-04-09 | 3707.5 | 05/04/10
|  |  | - |  | - |  | 21:00 |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | 104 | 20/09/16
|  |  | - |  | - |  | 21:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | 8285 | 20/09/16
|  |  | - |  | - |  | 21:00
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - |  | 06/09/16
[5 empty] | - | 212 | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - |  | 06/09/16
|  |  | - |  | - | 7164 | 12:00
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
|  |  | - |  | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
|  |  | - |  | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | 15
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | 1
20 | Gross Generation of BPDB (MKWH) | 2695.8225 |  | 2692.85 |  | 2214.1
21 | Station Use of BPDB (MKWH) | 102.1715 |  | 107.31 |  | 111.42
22 | Net Generation of BPDB (MKWH) | 2593.651 |  | 2585.54 |  | 2102.69
23 | Net Generation of IPP & RPCL (MKWH) | 1169.9318 |  | 1490.79 |  | 1357.94
24 | Net Generation of REB (MKWH) | 117.903 |  | 124.58 |  | 109.19
24 | Net Generation of Rental Power Plant (MKWH) | 1144.6308 |  | 1243.26 |  | 1092.02
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5026.1165 |  | 5444.17 |  | 4661.84 |  | 5444.15 | August-17
26 | Energy Generation by Gas (MKWH) | 3432.5779 |  | 3647.29 |  | 3284.48 |  | 3489.81 | June-17
27 | Energy Generation by Diesel (MKWH) | 389.6083 |  | 407.18 |  | 317.06 |  | 424.76 | May-17
28 | Energy Generation by Furnace Oil (MKWH) | 1107.9271 |  | 1273.84 |  | 935.73 |  | 1273.84 | August-17
29 | Energy Generation by Hydro (MKWH) | 114.4116 |  | 119.54 |  | 118.15 |  | 127.9 | Oct-16
30 | Energy Generation by Solar (MKWH) | 0.17014 | [6 empty] | 26/09/17
31 | Energy Generation by Coal (MKWH) | 83.5929 |  | 103.63 |  | 117.82 |  | 123.5872 | April-14
32 | Enegry Import from India (HVDC & AC) (MKWH) | 436.1469 |  | 449.86 |  | 380.83 |  | 449.86 | August-17
33 | Monthly Load Factor (%) | 81.9466 |  | 85.18 |  | 80.52 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September' 2017
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9431 | 26/09/17 | 21:00
Generation Period
| Dhaka | MW | 3593
| Chittagong | MW | 934
| Comilla | MW | 756
| Mymensingh | MW | 575
| Sylhet | MW | 405
a) | Total supply in East zone | MW | 6263
| Khulna | MW | 1072
| Barisal | MW | 215
| Rajshahi | MW | 810
| Rangpur | MW | 457
b) | Total supply in West zone | MW | 2554
c) | Total supply in both zone ( a+b) | MW | 8817
Ref: | 27.21.2604.16.084.17.41 | Date: 20/09/2017
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September' 2017
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1080 | 07/09/17 | 0:00
| b) Ishurdi end | MW | 130 | 27/09/17 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 360 | 27/09/17 | 17:00
| b) Ishurdi end | MW | 440 | 16/09/17 | 1:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 5.7255 | 09/09/17
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 5.7709 | 09/09/17
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 137.6376
| b) Ishurdi end | MKWH | 1.2044
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 1.1682
| b) Ishurdi end | MKWH | 133.8534
23 | Transmission loss of EWI/ NO-1 | % | 2.7494
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 351 | 26/09/17 | 5:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 335 | 26/09/17 | 5:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 6.038 | 26/09/17
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 5.866 | 26/09/17
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 24.676
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 24.4
30 | Transmission loss of EWI /NO-2 | % | 1.13
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV Transformers-T-1 | 2017-09-01 19:52 | 2017-09-01 20:10 | 0:18 | T | Tripped showing O/C relay | 82 | 17.7667 | Power interruption
| 132/33 kV Transformers-T-2 & T3 | 2017-09-01 19:52 | 2017-09-01 20:05 | 0:13 | T
Aminbazar | 230/132 kV Transformer-AT-1 | 2017-09-02 12:40 | 2017-09-02 18:00 | 5:20 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers-T-3 | 2017-09-03 18:12 | 2017-09-03 20:08 | 1:56 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T-1 | 2017-09-09 09:47 | 2017-09-09 15:20 | 5:33 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformers-T-3 | 2017-09-09 15:06 | 2017-09-09 15:17 | 0:11 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T-2 | 2017-09-14 07:47 | 2017-09-14 09:07 | 1:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer T2 | 2017-09-23 16:26 | 2017-09-23 17:46 | 1:20 | T | Tripped showing O/C relay | 236 | 314.6667 | Power interruption
Mymensingh | 132/33 kV Transformers-T-2 & T3 | 2017-09-27 23:17 | 2017-09-27 23:27 | 0:10 | T | Tripped showing O/C & E/F relay | 128 | 21.3333 | Power interruption
Aminbazar | 230/132 kV Transformer-T-3 | 2017-09-30 22:18 | 2017-09-30 22:55 | 0:37 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 16:58 |  | Unserved Energy: |  | 353.7667
Dhaka (South) Grid Circle :
Rampura | 230/132 kV Transformer-T-2 | 2017-09-07 05:54 | 2017-09-07 09:53 | 3:59 | E/O | Due to red hot maintenance | 5 | 0.41667 | Power interruption 03:05 to 3:10
Manikganj | 132/33 kV Transformer-T-2 | 2017-09-15 07:49 | 2017-09-15 08:30 | 0:41 | E/O | Due to red hot maintenance | 18 | 12.3 | Power interruption
Bashundhara | 132/33 kV Transformer-T-3 | 2017-09-17 21:10 | 2017-09-17 22:10 | 1:00 | E/O | Due to red hot maintenance | 47 | 47 | Power interruption
Rampura | 132 kV bus-2 | 2017-09-24 05:40 | 2017-09-24 07:52 | 2:12 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformers-T-1 & T2 | 2017-09-25 11:48 | 2017-09-25 11:52 | 0:04 | T | Tripped showing O/C relay | 116 | 7.7333 | Power interruption
Munshiganj | 132/33 kV Transformer-T-2 | 2017-09-28 15:34 | 2017-09-28 16:21 | 0:47 | E/O | Due to red hot maintenance | 20 | 15.6667 | Power interruption
Shyampur | 132/33 kV Transformer-GT-2 | 2017-09-29 03:38 | 2017-09-29 14:59 | 11:21 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-3 & T4 | 2017-09-29 18:28 | 2017-09-29 19:26 | 0:58 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformers-GT-3 | 2017-09-30 00:02 | 2017-09-30 00:55 | 0:53 | T | Tripped showing O/C & E/F relay | 70 | 61.8333 | Power interruption
| 132/33 kV Transformers-GT-4 | 2017-09-30 00:02 | 2017-09-30 01:24 | 1:22 | T
Ghorashal | 230/132 kV Transformer-T-1 | 2017-09-30 02:05 | 2017-09-30 02:30 | 0:25 | T | Tripped showing O/C relay | 40 | 16.6667 | Power interruption
|  |  | Total : | 23:42 |  | Unserved Energy: |  | 161.6167
Chittagong Grid Circle :
Cos'xbazar | 132/33 kV Transformers-T-3 | 2017-09-03 15:50 | 2017-09-03 16:30 | 0:40 | E/O | Due to red hot maintenance | 15 | 10 | Power interruption
Hathazari | 132/33 kV Transformer-T-1 | 2017-09-04 21:43 | 2017-09-04 22:03 | 0:20 | E/O | Due to red hot maintenance | 40 | 11.3333 | Power interruption 21:43 to 22:00
Hathazari | 132/33 kV Transformer-T-1 | 2017-09-08 05:07 | 2017-09-08 09:30 | 4:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T-1 | 2017-09-16 20:27 | 2017-09-16 21:21 | 0:54 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 0:40 |  | Unserved Energy: |  | 21.3333
Comilla Grid Circle :
Shahjibazar | 132/33 kV Transformer-T-2 | 2017-09-18 15:46 | 2017-09-18 15:55 | 0:09 | T | Tripped showing O/C relay | 22 | 3.3 | Power interruption
Fenchuganj | 132/33 kV Transformer-T-1 | 2017-09-19 14:36 | 2017-09-19 14:40 | 0:04 | T | Tripped showing back-up protection relay | 20 | 1.3333 | Power interruption
Comilla(N) | 230/132 kV Transformer-T-2 | 2017-09-29 11:49 | 2017-09-29 17:33 | 5:44 | T | Tripped showing PRD relay | 0 | 0 | No interruption
|  |  | Total : | 5:57 |  | Unserved Energy: |  | 4.6333
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj | 132/33 kV Transformers-T-1 & T2 | 2017-09-02 21:41 | 2017-09-02 21:45 | 0:04 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T-6 | 2017-09-09 19:55 | 2017-09-09 20:02 | 0:07 | T | Tripped showing O/C relay | 30 | 3.5 | Power interruption
Satkhira | 132/33 kV Transformer-T-2 | 2017-09-14 07:14 | 2017-09-14 08:40 | 1:26 | E/O | Due to red hot maintenance | 7 | 10.0333 | Power interruption
Bagerhat | 132/33 kV Transformer-T-2 | 2017-09-16 02:50 | 2017-09-16 03:06 | 0:16 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T-1 | 2017-09-17 23:35 | 2017-09-17 23:40 | 0:05 | T | Tripped showing O/C relay | 60 | 5 | Power interruption
| 132/33 kV Transformers-T-2 | 2017-09-17 23:35 | 2017-09-17 23:44 | 0:09 | T
Faridpur | 132/33 kV Transformers-T-1 & T2 | 2017-09-18 19:38 | 2017-09-18 19:53 | 0:15 | T | Tripped showing E/F relay | 96 | 24 | Power interruption
| 132/33 kV Transformers-T-1 & T2 | 2017-09-18 20:06 | 2017-09-18 20:20 | 0:14 | T |  | 85 | 19.8333 | Power interruption
Goalpara | 132/33 kV Transformer-T-6 | 2017-09-20 01:42 | 2017-09-20 01:50 | 0:08 | T | Tripped showing O/C relay | 19 | 2.5333 | Power interruption
Noapara | 132/33 kV Transformer-T-1 | 2017-09-21 09:40 | 2017-09-21 11:30 | 1:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T-1 & T2 | 2017-09-23 19:59 | 2017-09-23 20:04 | 0:05 | T | Tripped showing O/C relay | 70 | 5.8333 | Power interruption
Golapara | 132/33 kV Transformer-T-6 | 2017-09-28 11:30 | 2017-09-28 11:35 | 0:05 | T |  | 20 | 1.6667 | Power interruption
Bagerhat | 132/33 kV Transformers-T-1 & T2 | 2017-09-30 02:55 | 2017-09-30 03:05 | 0:10 | T | Tripped showing O/C relay | 58 | 9.6667 | Power interruption
|  |  | Total : | 4:54 |  | Unserved Energy: |  | 82.0667
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T-1 | 2017-09-04 18:13 | 2017-09-04 19:02 | 0:49 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Bottail | 132/33 kV Transformers T-1 & T-2 | 2017-09-23 09:40 | 2017-09-23 09:46 | 0:06 | T | Tripped showing E/F relay | 75 | 7.5 | Power interruption
|  |  | Total : | 0:55 |  | Unserved Energy: |  | 7.5
Bogra Grid Circle:
Lalmonirhat | 132/33 kV Transformer T4 | 2017-09-04 10:55 | 2017-09-04 11:46 | 0:51 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-4 | 2017-09-05 01:44 | 2017-09-05 16:52 | 15:08 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T-4 | 2017-09-17 21:35 | 2017-09-17 22:40 | 1:05 | E/O | Due to red hot maintenance | 16 | 17.3333 | Power interruption
Barapukuria | 132/33 kV Transformer-T-4 | 2017-09-26 07:08 | 2017-09-26 11:30 | 4:22 | E/O | Due to SF6 gas filling | 0 | 0 | No interruption
Bogra | 132/33 kV Transformer-T-3 | 2017-09-26 11:20 | 2017-09-26 19:33 | 8:13 | E/O | Due to SF6 gas filling | 0 | 0 | No interruption
|  |  | Total : | 29:39 |  | Unserved Energy: |  | 17.3333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 82:45 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/3 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-2 | 2017-09-04 09:51 | 2017-09-04 10:06 | 0:15 | T | Tripped showing CAT,CSW,PD & CE signal | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2017-09-08 11:57 | 2017-09-08 12:09 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mirpur | Mirpur-Tongi 132 kV line | 2017-09-08 10:16 | 2017-09-08 12:27 | 2:11 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2017-09-09 10:22 | 2017-09-09 11:15 | 0:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2017-09-11 08:15 | 2017-09-11 08:23 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2017-09-14 22:39 | 2017-09-14 23:07 | 0:28 | T | Tripped showing E/F & O/C relay | 88 | 22 | Power interruption
| Kabirpur-Manikganj 132 kV line-2 | 2017-09-14 22:39 | 2017-09-14 22:54 | 0:15 | T
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2017-09-25 06:05 | 2017-09-25 07:20 | 1:15 | E/O | Due to red hot maintenance | 30 | 37.5 | Power interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2017-09-25 06:42 | 2017-09-25 08:10 | 1:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 7:05 |  | Unserved Energy: |  | 59.5
Dhaka (South) Grid Circle :
Rampura | Rampura-Basundhara 132 kV line-2 | 2017-09-05 16:46 | 2017-09-05 17:02 | 0:16 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2017-09-09 13:59 | 2017-09-09 14:37 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 | 2017-09-11 05:55 | 2017-09-11 08:56 | 3:01 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shyampur | Shyampur-Haripur 132 kV line | 2017-09-22 15:37 | 2017-09-22 15:38 | 0:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2017-09-23 10:27 | 2017-09-23 10:49 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 & 2 | 2017-09-23 10:29 | 2017-09-23 10:34 | 0:05 | T | Tripped showing dist.& E/F relay | 275 | 22.9167 | Power interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2017-09-25 00:54 | 2017-09-25 01:38 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2017-09-25 16:27 | 2017-09-25 16:47 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 | 2017-09-27 05:52 | 2017-09-27 08:08 | 2:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Ghorashal 230 kV line-1 | 2017-09-30 10:31 | 2017-09-30 14:47 | 4:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 11:59 |  | Unserved Energy: |  | 22.9167
Chittagong Grid Circle :
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2017-09-02 07:52 | 2017-09-02 16:43 | 8:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sikalbaha-Bakulia 132 kV line-2 | 2017-09-02 08:45 | 2017-09-03 08:45 | 24:00 | T |  | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV line-2 | 2017-09-04 11:39 | 2017-09-04 12:27 | 0:48 | T | Tripped showing dist. & O/C relay | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2017-09-12 00:15 | 2017-09-12 01:30 | 1:15 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2017-09-15 06:56 | 2017-09-15 08:12 | 1:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
BSRM | BSRM-AKSTML 230 kV line | 2017-09-16 12:59 | 2017-09-16 13:06 | 0:07 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
Hathazari | Hathazari-Feni 132 kV line-1 | 2017-09-16 15:57 | 2017-09-16 16:13 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Juldah S/S | Juldah S/S -Juldah P/S 132 kV line | 2017-09-18 05:20 | 2017-09-18 06:58 | 1:38 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line-2 | 2017-09-18 13:12 | 2017-09-18 13:35 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2017-09-19 12:05 | 2017-09-19 12:22 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaptai | Kaptai-Madunaghat-Chanraghona 132 kV line | 2017-09-25 01:33 | 2017-09-25 02:28 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 & 2 | 2017-09-25 01:07 | 2017-09-25 07:31 | 6:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaptai | Kaptai-Madunaghat 132 kV line-1 | 2017-09-26 10:41 | 2017-09-26 11:43 | 1:02 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
BSRM | BSRM -Abul Khair 132 kV line | 2017-09-29 11:12 | 2017-09-29 11:30 | 0:18 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 47:30 |  | Unserved Energy: |  | 0
Page: 2/3 | [8 empty] | QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Comilla Grid Circle :
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2017-09-08 06:56 | 2017-09-08 07:07 | 0:11 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2017-09-08 14:02 | 2017-09-08 14:19 | 0:17 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2017-09-08 22:29 | 2017-09-08 23:12 | 0:43 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-09-14 13:34 | 2017-09-14 17:08 | 3:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2017-09-14 01:50 | 2017-09-14 02:29 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sreemongal-Fenchuganj 132 kV line-2 | 2017-09-14 01:50 | 2017-09-14 02:32 | 0:42 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comilla(N) 230 kV line-1 | 2017-09-15 12:40 | 2017-09-15 14:07 | 1:27 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Tripura 132 kV line-1 | 2017-09-23 17:16 | 2017-09-23 17:33 | 0:17 | T | Tripped showing dist. relay | 30 | 42.5 | Power interruption
| Comilla(N)-Tripura 132 kV line-2 | 2017-09-23 17:16 | 2017-09-23 17:40 | 0:24 | T
Fenchuganj | Fenchuganj-Bibiyana 230 kV line-2 | 2017-09-25 08:32 | 2017-09-25 08:50 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Hathazari 132 kV line-2 | 2017-09-26 07:18 | 2017-09-26 07:31 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-BSRM 230 kV line-1 | 2017-09-27 05:20 | 2017-09-27 05:33 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2017-09-29 00:53 | 2017-09-29 01:54 | 1:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:59 |  | Unserved Energy: |  | 42.5
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line | 2017-09-02 16:27 | 2017-09-02 16:35 | 0:08 | T | Tripped showing dist. relay | 40 | 5.3333 | Power interruption
Barisal | Barisal-Patuakhali 132 kV line | 2017-09-04 06:47 | 2017-09-04 07:35 | 0:48 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2017-09-06 09:02 | 2017-09-06 13:53 | 4:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2017-09-06 12:28 | 2017-09-06 12:40 | 0:12 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
| Faridpur-Madaripur 132 kV line-2 | 2017-09-06 12:28 | 2017-09-06 13:02 | 0:34 | T |  | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal(N) 132 kV line-1 | 2017-09-06 12:28 | 2017-09-06 12:48 | 0:20 | T | Tripped showing O/C. relay | 265 | 88.3333 | Power interruption
| Madaripur-Barisal(N) 132 kV line-2 | 2017-09-06 12:28 | 2017-09-06 12:49 | 0:21 | T
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2017-09-08 23:07 | 2017-09-08 23:26 | 0:19 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2017-09-15 12:13 | 2017-09-15 12:41 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2017-09-16 18:54 | 2017-09-17 00:26 | 5:32 | T | Tripped showing E/F relay | 70 | 43.1667 | Power interruption 18:54 to 19:31
| Faridpur-Bheramara 132 kV line-1 | 2017-09-16 18:54 | 2017-09-16 19:12 | 0:18 | T | Tripped showing E/F relay
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2017-09-16 18:54 | 2017-09-16 19:19 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2017-09-17 10:14 | 2017-09-17 16:48 | 6:34 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Goalpara | Goalpara-NWPGCL 132 kV line | 2017-09-17 10:14 | 2017-09-17 11:13 | 0:59 | T | Tripped showing back-up protection relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2017-09-18 07:27 | 2017-09-18 12:02 | 4:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S) -Satkhira 132 kV line-1 | 2017-09-27 13:02 | 2017-09-27 16:04 | 3:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2017-09-28 13:13 | 2017-09-28 15:19 | 2:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Goalpara | Goalpara-Bagerhat 132 kV line-1 | 2017-09-28 13:50 | 2017-09-28 14:10 | 0:20 | T | Tripped showing dist. relay | 33 | 9.35 | Power interruption 13:50 to 14:07
Barisal | Barisal-Patuakhali 132 kV line | 2017-09-28 14:24 | 2017-09-28 17:13 | 2:49 | T | Tripped showing dist. relay | 28 | 78.8667 | Power interruption
|  |  | Total : | 34:41 |  | Unserved Energy: |  | 225.05
Page: 3/3 | [8 empty] | QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2017
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara | Bheramara-Bahrampur 400 kV line-2 | 2017-09-08 13:03 | 2017-09-08 17:25 | 4:22 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 & 2 | 2017-09-08 23:04 | 2017-09-09 12:03 | 12:59 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 & 2 | 2017-09-08 23:13 | 2017-09-08 23:45 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 230 kV line | 2017-09-10 13:05 | 2017-09-10 13:19 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Khulna(s) 230 kV line-1 | 2017-09-16 11:43 | 2017-09-16 12:43 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Khulna(s) 230 kV line-2 | 2017-09-23 13:16 | 2017-09-23 14:34 | 1:18 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Pabna 132 kV line | 2017-09-24 15:38 | 2017-09-24 16:01 | 0:23 | T | Tripped showing dist.(Z1 relay) | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-1 | 2017-09-24 14:16 | 2017-09-24 14:52 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 21:24 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Sirajganj 230 kV line-1 & 2 | 2017-09-10 13:05 | 2017-09-10 13:29 | 0:24 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-1 | 2017-09-10 13:05 | 2017-09-10 13:17 | 0:12 | T | Tripped showing dist. relay | 140 | 28 | Power interruption
| Baghabari-Sirajganj 230 kV line-2 | 2017-09-10 13:05 | 2017-09-10 13:22 | 0:17 | T
Bogra | Bogra-Palashbari 132 kV line-1 | 2017-09-16 14:19 | 2017-09-16 18:25 | 4:06 | T | Tripped showing dist. relay | 45 | 120.75 | Power interruption 18:25 to 17:00
Rangpur | Rangpur-Pasahbari 132 kV line-1 | 2017-09-16 14:19 | 2017-09-16 14:40 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogra | Bogra-Naogaon 132 kV line-1 | 2017-09-17 12:52 | 2017-09-17 13:11 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 230 kV line-1 | 2017-09-22 21:49 | 2017-09-23 09:30 | 11:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Pabna 132 kV line | 2017-09-24 15:38 | 2017-09-24 16:01 | 0:23 | T | Tripped showing dist. relay | 55 | 21.0833 | No interruption
|  |  | Total : | 17:43 |  | Unserved Energy: |  | 169.8333
Others :
Maniknagar | Maniknagar-Narinda 132 kV line-1 | 2017-09-10 21:58 | 2017-09-10 23:50 | 1:52 | T | Tripped showing main protection relay | 70 | 130.6667 | Power interruption
| Maniknagar-Narinda 132 kV line-2 | 2017-09-10 22:05 | 2017-09-10 22:26 | 0:21 | T |  | 0 | 0 | No interruption
Maniknagar | Maniknagar-Narinda 132 kV line-1 | 2017-09-19 06:56 | 2017-09-19 10:05 | 3:09 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Matuail | Matuail-Haripur 132 kV line | 2017-09-29 01:35 | 2017-09-29 01:44 | 0:09 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line | 2017-09-29 01:43 | 2017-09-29 03:06 | 1:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:54 |  | Unserved Energy: |  | 130.6667
Total outage period of Sub-station Equipment : |  |  |  | 157:15 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/1 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhulta | 132/33 kV Transformer-T-2 | 2017-09-07 11:10 | 2017-09-07 13:32 | 2:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T-3 | 2017-09-08 10:01 | 2017-09-08 12:21 | 2:20 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T-2 | 2017-09-11 06:05 | 2017-09-11 14:26 | 8:21 | S/O | Due to project work | 0 | 0 | No interruption
Jamalpur | 132/33 kV TransformersT-1 ,T2 , T3 & T4 | 2017-09-17 05:26 | 2017-09-17 15:52 | 10:26 | S/O | Due to project work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T-2 | 2017-09-28 10:25 | 2017-09-28 11:35 | 1:10 | S/O | Due to high temperature of 132 kV Y-phase isolator | 0 | 0 | No interruption
|  |  | Total : | 24:39 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | 230 kV Bus-2 | 2017-09-14 10:10 | 2017-09-14 18:27 | 8:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T-3 | 2017-09-22 14:25 | 2017-09-22 15:37 | 1:12 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shitalakhya | 132/33 kV Transformers T-2 | 2017-09-24 14:45 | 2017-09-24 15:42 | 0:57 | S/O | Due to relay test | 0 | 0 | No interruption
| 132/33 kV Transformers T-3 | 2017-09-24 14:45 | 2017-09-24 17:58 | 3:13 | S/O |  | 0 | 0 | No interruption
Shitalakhya | 132/33 kV Transformers T-2 | 2017-09-26 14:16 | 2017-09-26 14:30 | 0:14 | S/O | Due to relay test | 0 | 0 | No interruption
| 132/33 kV Transformers T-3 | 2017-09-26 15:40 | 2017-09-26 16:01 | 0:21 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 14:14 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Halishahar | 132/33 kV Transformers-T-2 | 2017-09-06 10:21 | 2017-09-06 10:38 | 0:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T-1 | 2017-09-07 14:58 | 2017-09-08 11:25 | 20:27 | S/O | Due to maintenance work | 20 | 0.66667 | Power interruption 14:58 to 15:00
Hathazari | 132/33 kV Transformer-T-1 | 2017-09-15 07:48 | 2017-09-17 11:05 | 51:17 | S/O | Due to maintenance work | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformer-T-1 | 2017-09-22 07:08 | 2017-09-22 15:18 | 8:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 80:11 |  | Unserved Energy: |  | 0.66667
Comilla Grid Circle : Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Khulna Grid Circle : Nil
|  |  | Total : | 0:00 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
Bheramara | 132 kV bus-B | 2017-09-14 07:04 | 2017-09-14 17:33 | 10:29 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 10:29 |  | Unserved Energy : |  | 0
Bogra Grid Circle:
Shahjadpur | 132/33 kV Transformers-T4 | 2017-09-19 12:01 | 2017-09-19 13:28 | 1:27 | S/O | Due to DC supply problem | 0 | 0 | No interruption
|  |  | Total | 1:27 |  | Unserved Energy : |  | 0
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0 |  | `
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 131:00 | Hours
S/O=Schedule Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :(N)
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2017-09-04 09:33 | 2017-09-04 10:36 | 1:03 | S/O | Due to maintenance work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2017-09-04 11:15 | 2017-09-04 13:50 | 2:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2017-09-19 06:55 | 2017-09-19 08:59 | 2:04 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2017-09-23 09:13 | 2017-09-23 21:26 | 12:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2017-09-23 09:49 | 2017-09-23 10:31 | 0:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2017-08-24 10:44 | 2017-09-24 17:25 | 750:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2017-09-25 09:53 | 2017-09-25 12:28 | 2:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-2 | 2017-09-26 09:26 | 2017-09-26 17:24 | 7:58 | S/O | Due to maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2017-09-28 09:46 | 2017-09-28 17:15 | 7:29 | S/O | Due to project work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2017-09-30 09:22 | 2017-09-30 12:54 | 3:32 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 790:52 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Munshiganj | Munshiganj-Madanganj 132 kV line-1 | 2017-09-16 10:08 | 2017-09-16 15:45 | 5:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Hasnabad 132 kV line | 2017-09-23 08:55 | 2017-09-23 09:13 | 0:18 | S/O | Due to project work | 0 | 0 | No interruption
Shitalakhya | Shitalakhya-Madanganj 132 kV line | 2017-09-24 11:18 | 2017-09-24 18:20 | 7:02 | S/O | Due to relay test | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-2 | 2017-09-25 07:32 | 2017-09-25 10:06 | 2:34 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakyha 132 kV line | 2017-09-26 10:00 | 2017-09-26 13:33 | 3:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
Shitalakhya | Shitalakhya-Gagnagar 132 kV line | 2017-09-26 15:50 | 2017-09-26 17:25 | 1:35 | S/O | Due to relay test | 0 | 0 | No interruption
| Shitalakhya-Madanganj 132 kV line | 2017-09-26 16:55 | 2017-09-26 17:58 | 1:03 | S/O | Due to relay test | 0 | 0 | No interruption
|  |  | Total : | 21:42 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2017-09-21 06:33 | 2017-09-21 17:13 | 10:40 | S/O | Due to project work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2017-09-22 05:20 | 2017-09-22 17:25 | 12:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2017-09-23 08:55 | 2017-09-23 09:55 | 1:00 | S/O | Due to project work | 0 | 0 | No interruption
Khulshi | Khulshi-AK steel 132 kV line | 2017-09-28 16:16 | 2017-09-28 16:37 | 0:21 | S/O | Due to replacement work | 0 | 0 | No interruption
|  |  | Total : | 24:06 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Comilla (S) | Comilla (S)-S.M.Nagar 132 kV line-1 | 2017-09-03 17:16 | 2017-09-03 20:15 | 2:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2017-09-09 15:13 | 2017-09-09 17:42 | 2:29 | S/O | Due to replacement work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Comilla(N) 230 kV line-2 | 2017-09-21 07:19 | 2017-09-21 13:37 | 6:18 | S/O | Due to breaker problem | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-09-24 08:16 | 2017-09-24 16:09 | 7:53 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2017-09-25 11:10 | 2017-09-25 12:12 | 1:02 | S/O | Due to tree trimming | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2017-09-27 11:19 | 2017-09-27 21:08 | 9:49 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 30:30 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2017-09-07 09:54 | 2017-09-07 12:04 | 2:10 | S/O | Due to project work | 0 | 0 | No interruption
Khulna© | Khulna©-Khulna 225 MW 132 kV line-1 | 2017-09-19 07:30 | 2017-09-19 09:09 | 1:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna© | Khulna©-KPCL 132 kV line | 2017-09-23 11:22 | 2017-09-23 13:04 | 1:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhola | Bhola-Barisal 230 kV line-1 | 2017-09-27 09:36 | 2017-09-27 14:09 | 4:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 10:04 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2017
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | Ishurdi-Bheramara 132 kVline-2 | 2017-09-09 17:33 | 2017-09-09 17:46 | 0:13 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV line-2 | 2017-09-15 09:43 | 2017-09-15 17:02 | 7:19 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2017-09-20 07:02 | 2017-09-20 09:28 | 2:26 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV line-1 | 2017-09-21 09:56 | 2017-09-21 16:22 | 6:26 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 16:24 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
Bogra | Bogra-Naogaon 132 kV line-1 | 2017-09-18 07:33 | 2017-09-18 10:10 | 2:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2017-09-21 05:10 | 2017-09-21 17:32 | 12:22 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2017-09-22 05:20 | 2017-09-22 18:42 | 13:22 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2017-09-23 05:02 | 2017-09-23 21:13 | 16:11 | S/O | Due to project work | 0 | 0 | No interruption
Rangpur | Rangpur-Palashbari 132 kV line-2 | 2017-09-24 05:48 | 2017-09-24 12:52 | 7:04 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra-Palashbari 132 kV line-1 | 2017-09-24 06:01 | 2017-09-24 12:52 | 6:51 | S/O | Due to project work | 0 | 0 | No interruption
Bogra | Bogra -Sirajganj 132 kV line-2 | 2017-09-25 05:35 | 2017-09-25 05:49 | 0:14 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra -Sirajganj 132 kV line-2 | 2017-09-26 05:28 | 2017-09-26 17:11 | 11:43 | S/O | Due to project work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogra 132 kV line | 2017-09-27 05:20 | 2017-09-27 18:05 | 12:45 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra-Natore 132 kV line-1 | 2017-09-27 07:21 | 2017-09-27 09:36 | 2:15 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogra | Bogra -Sirajganj 132 kV line-2 | 2017-09-28 05:14 | 2017-09-28 18:04 | 12:50 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 98:14 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 991:52 | Hours |  |  | Executive Engineer
S/O=Schedule Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September' 2017
| Area | Previous Month (August 2017) |  |  |  | Current Month (September 2017)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 19 | 2 | 22 | 43 | 13 | 6 | 15 | 34
2 | Dhaka (South) Grid Circle. | 11 | 5 | 7 | 23 | 13 | 8 | 13 | 34
3 | Chittagong Grid Circle. | 6 | 5 | 6 | 17 | 11 | 7 | 8 | 26
4 | Comilla Grid Circle. | 17 | 8 | 12 | 37 | 16 | - | 6 | 22
5 | Khulna Grid Circle. | 12 | 4 | 8 | 24 | 30 | 2 | 4 | 36
6 | Bheramara HVDC Grid Circle | 1 | 3 | 14 | 18 | 9 | 1 | 5 | 15
7 | Bogra Grid Circle. | 2 | 4 | 21 | 27 | 8 | 5 | 12 | 25
8 | Others | 1 | - | - | 1 | 4 | 1 | - | 5
9 | Total | 69 | 31 | 90 | 190 | 104 | 30 | 63 | 197
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September' 2017
| Area | Previous Month (August 2017) |  |  |  | Current Month (September 2017)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 1101.7 | - | 367.33 | 1469.03 | 375.77 | 37.5 | - | 413.27
2 | Dhaka ( South) grid circle | 50.35 | 43.33 | - | 93.68 | 109.57 | 74.97 | - | 184.54
3 | Chittagong grid circle. | 35.77 | 40.67 | 25.67 | 102.11 | - | 21.33 | 0.67 | 22
4 | Comilla grid circle. | 98.1 | 156.67 | 80.17 | 334.94 | 47.13 | - |  | 47.13
5 | Khulna grid circle. | 52 | - | - | 52 | 297.09 | 10.03 | - | 307.12
6 | Bheramara HVDC grid circle | - | - | - | 0 | 7.5 | - | - | 7.5
7 | Bogra grid circle. | - | - | - | 0 | 169.83 | 17.33 | - | 187.16
8 | Others | - | - | - | 0 | 130.67 | - | - | 130.67
9 | Total | 1337.92 | 240.67 | 473.17 | 2051.76 | 1137.56 | 161.16 | 0.67 | 1299.39
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September' 2017
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 3 | - | 3 | 2 | - | 1 | 353.77
2 | Dhaka (South) | 5031.6 | 7 | - | 7 | 1 | 5 | 1 | 161.62
3 | Chittagong | 2042 | 2 | 1 | 3 | 2 | 1 |  | 22
4 | Khulna | 2434 | 8 | - | 8 | 8 | - | - | 82.07
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | 1 | - | - | 7.5
6 | Bogra | 3145.6 | 1 | - | 1 | - | - | 1 | 17.33
7 | Comilla | 2981 | 2 |  | 2 | 2 | - |  | 4.63
| Total | 23365.5 | [6 empty] | 648.92
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.93%
2 | Dhaka (South) | 99.94%
3 | Chittagong | 99.97%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.95% | [6 empty] | Information Management Division
7 | Comilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September' 2017
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 2 | - | 2 | 1 |  | 1 | 78.5667
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | 1 | - | - | 22.92
3 | Chittagong | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 5 | - | 5 | 3 | 1 | 1 | 225.05
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogra | 1803.3 | 38 | 3 | - | 3 | 2 | - | 1 | 169.83
7 | Comilla | 1648.16 | 17 | 1 | - | 1 | 1 | - | - | 42.5
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 538.8667
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.96%
3 | Chittagong | 99.96%
4 | Khulna | 99.81%
5 | Bheramara (HVDC) | 99.71% | [7 empty] | Executive Engineer
6 | Bogra | 99.91% | [7 empty] | Information Management Division
7 | Comilla | 99.92% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September' 2017
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
September | 31 | - | 8 | 06hr04min | 1 | 01hr15min | - | - | - | - | - | - | -
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:September' 2017
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishireganj | 1 | 0:13 | 82 | 17.7667 | Due to tripping of 132/33 kV Transformers T1 , T2 & T3
Kaliakoir | 1 | 1:20 | 236 | 314.6667 | Due to tripping of Mymensingh-Jamalpur 132 kV line-1 & 2
Mymensingh | 1 | 0:10 | 128 | 21.3333 | Due to tripping of 132/33 kV Transformers T 2 & T3
Kabirpur | 2 | 0:15 | 88 | 22 | Due to tripping of Kabirpur-Manikganj 132 kV line-1 & 2
|  | 1:15 | 30 | 37.5 | Due to red-hot maintenance of Kabirpur-Kaliakoir 132 kV line-1
Rampura | 1 | 3:59 | 5 | 0.41667 | Due to red-hot maintenance of 230/132 kV Transformer T2
Manikganj | 1 | 0:41 | 18 | 12.3 | Due to red-hot maintenance of 132/33 kV Transformer T2
Bashundhara |  | 0:01 | 47 | 47 | Due to red-hot maintenance of 132/33 kV Transformer T3
Siddhirganj | 1 | 0:04 | 116 | 7.7333 | Due to tripping of 132/33 kV Transformers T 1 & T2
Munshiganj | 1 | 0:47 | 20 | 15.6667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Shyampur | 1 | 0:53 | 70 | 61.8333 | Due to tripping of 132/33 kV Transformers GT 3 & GT4
Ghorashal | 2 | 0:25 | 40 | 16.6667 | Due to tripping of 132/33 kV Transformer T 1
|  | 0:05 | 275 | 22.9167 | Due to tripping of Ghorashal -Joydevpur 132 kV line-1 & 2
Maniknagar | 1 | 1:52 | 70 | 130.6667 | Due to tripping of Maniknagar-Narinda 132 kV line-1 & 2
Cox'sbazar | 1 | 0:40 | 15 | 10 | Due to tripping of 132/33 kV Transformer T3
Hathazari | 1 | 0:20 | 40 | 11.3333 | Due to tripping of 132/33 kV Transformer T1
Bottail | 1 | 0:02 | 20 | 0.66667 | Due to S/D of 132/33 kV Transformer T1
Shahjibazar | 1 | 0:09 | 22 | 3.3 | Due to tripping of 132/33 kV Transformer T2
Fenchuganj | 1 | 0:04 | 20 | 1.3333 | Due to tripping of 132/33 kV Transformer T1
Comilla(N) | 1 | 0:17 | 30 | 42.5 | Due to tripping of Comilla(N) -Tripura 132 kV line-1 & 2
Goalpara | 4 | 0:07 | 30 | 3.5 | Due to tripping of 132/33 kV Transformer T6
|  | 0:08 | 19 | 2.5333 | Due to tripping of 132/33 kV Transformer T6
|  | 0:05 | 20 | 1.6667 | Due to tripping of 132/33 kV Transformer T6
|  | 0:20 | 33 | 9.35 | Due to tripping of Goalpara-Bagerhat 132 kV line-1
Satkhira | 1 | 1:26 | 7 | 10.0333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Gopalganj | 2 | 0:05 | 60 | 5 | Due to tripping of 132/33 kV Transformer T1
|  | 0:05 | 70 | 5.8333 | Due to tripping of 132/33 kV Transformers T1 & T2
Bagerhat | 1 | 0:10 | 58 | 9.67 | Due to tripping of 132/33 kV Transformers T1 & T2
Faridpur | 2 | 0:15 | 96 | 24 | Due to tripping of 132/33 kV Transformers T1 & T2
|  | 0:14 | 85 | 19.8333 | Due to tripping of 132/33 kV Transformers T1 & T2
Madaripur | 2 | 0:20 | 265 | 88.3333 | Due to tripping of Madaripur-Barisal (N)132 kV line-1 & 2
|  | 0:08 | 40 | 5.3333 | Due to tripping of Madaripur-Gopalganj 132 kV line
Barisal | 1 | 2:49 | 28 | 78.8667 | Due to tripping of Barisal -Patuakhali 132 kV line
Bottail | 1 | 0:06 | 75 | 7.5 | Due to tripping of 132/33 kV Transformers T1 & T2
Lalmonirhat | 1 | 1:05 | 16 | 17.3333 | Due to red-hot maintenance of 132/33 kV Transformer T4
Baghabari | 1 | 0:12 | 140 | 28 | Due to tripping Baghabari-Sirajganj 230 kV line-1 & 2
Faridpur | 1 | 0:37 | 70 | 43.1667 | Due to tripping Faridpur-Bheramara 132 kV line-1 & 2
Bogra | 1 | 2:41 | 45 | 120.75 | Due to tripping Bogra-Palashbari 132 kV line-1
Shahjadpur | 1 | 0:23 | 55 | 21.0833 | Due to tripping of Shahjadpur -Pabna 132 kV line
| Total unserved energy : |  |  | 1299.3867 | MWH

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2017
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 126 | 25 | 2017-09-01 | 9:00
2 | Munsiganj | 114 | 16 | 2017-09-01 | 19:30
3 | Megnaghat | 69 | 26 | 2017-09-01 | 20:00
4 | Shyampur | 166 | 23 | 2017-09-01 | 10:00
5 | Bhulta | 152 | 18 | 2017-09-01 | 19:30
6 | Madanganj | 57 | 27 | 2017-09-01 | 18:30
7 | Shitalakhya | 108 | 26 | 2017-09-01 | 10:00
8 | Rahim steel | 21 | 27 | 2017-09-01 | 9:00
9 | Matuail | 92 | 25 | 2017-09-01 | 10:00
10 | Ghorasal | 90 | 22 | 2017-09-01 | 01:00
11 | Narsingdi | 107 | 27 | 2017-09-01 | 20:00
12 | Haripur (SBU) | 93 | 23 | 2017-09-01 | 18:30
13 | Ullon | 99 | 22 | 2017-09-01 | 20:00
14 | Hasnabad | 200 | 23 | 2017-09-01 | 21:00
15 | Magbazar | 127 | 26 | 2017-09-01 | 1:00
16 | Maniknagar | 96 | 26 | 2017-09-01 | 15:00
17 | Bangabhaban | 44 | 25 | 2017-09-01 | 11:00
18 | Narinda | 94 | 28 | 2017-09-01 | 13:00
19 | Dhanmondi | 165 | 24 | 2017-09-01 | 15:00
20 | Lalbag | 88 | 25 | 2017-09-01 | 13:00
21 | Madartek | 55 | 16 | 2017-09-01 | 22:00
22 | Mirpur | 94 | 25 | 2017-09-01 | 19:30
23 | Kalyanpur | 126 | 23 | 2017-09-01 | 20:00
24 | Gulshan | 138 | 25 | 2017-09-01 | 14:00
25 | Uttara | 80 | 10 | 2017-09-01 | 12:00
26 | Kamrangirchar | 80 | 21 | 2017-09-01 | 18:00
27 | Savar | 139 | 27 | 2017-09-01 | 18:30
28 | Bhasantec | 183 | 26 | 2017-09-01 | 13:00
29 | Agargaon | 141 | 30 | 2017-09-01 | 18:00
30 | Satmosjid | 105 | 24 | 2017-09-01 | 19:00
31 | Tongi | 188 | 24 | 2017-09-01 | 18:00
32 | Kabirpur | 211 | 24 | 2017-09-01 | 9:00
33 | Basundhara | 211 | 27 | 2017-09-01 | 19:00
34 | Manikganj | 165 | 27 | 2017-09-01 | 3:00
35 | Joydevpur | 225 | 17 | 2017-09-01 | 19:00
36 | New Tongi | 115 | 17 | 2017-09-01 | 9:00
37 | Tangail | 165 | 16 | 2017-09-01 | 20:00
38 | Mymensing | 202 | 25 | 2017-09-01 | 22:00
39 | Kishorganj | 85 | 2 | 2017-09-01 | 19:00
40 | Netrokona | 80 | 1 | 2017-09-01 | 20:00
41 | Jamalpur | 96 | 20 | 2017-09-01 | 19:30
42 | Sherpur | 75 | 22 | 2017-09-01 | 18:30
43 | Srimongal | 40 | 19 | 2017-09-01 | 18:30
44 | Shahjibazar | 96 | 15 | 2017-09-01 | 21:00
45 | Fenchuganj | 54 | 24 | 2017-09-01 | 18:30
46 | Khulawara | 41 | 9 | 2017-09-01 | 19:00
47 | Sylhet | 172 | 16 | 2017-09-01 | 20:00
48 | Chatak | 55 | 28 | 2017-09-01 | 19:30
49 | Comilla (S) | 168 | 14 | 2017-09-01 | 20:00
50 | Comilla(N) | 129 | 26 | 2017-09-01 | 22:00
51 | Chandpur | 121 | 2 | 2017-09-01 | 21:00
52 | Feni | 111 | 25 | 2017-09-01 | 22:00
53 | Chowmuhani | 178 | 14 | 2017-09-01 | 22:00
54 | Ashuganj | 63 | 18 | 2017-09-01 | 09:30
55 | Daudkandi | 94 | 14 | 2017-09-01 | 18:30
56 | B.Baria | 114 | 4 | 2017-09-01 | 21:00
57 | Madanhat | 72 | 24 | 2017-09-01 | 18:30
58 | Hathazari | 99 | 20 | 2017-09-01 | 18:00
59 | Khulshi | 190 | 26 | 2017-09-01 | 16:00
60 | Halishahar | 151 | 24 | 2017-09-01 | 18:00
61 | Baraulia | 124 | 22 | 2017-09-01 | 01:00
62 | Sikalbaha | 36 | 21 | 2017-09-01 | 20:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September'2017
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
63 | Dohazari | 88 | 6 | 2017-09-01 | 20:00
64 | Cox'sbazar | 83 | 11 | 2017-09-01 | 21:00
65 | Chandraghona | 36 | 13 | 2017-09-01 | 21:00
66 | Kaptai | 5 | 24 | 2017-09-01 | 18:30
67 | A. Khaer Stl. | 17 | 17 | 2017-09-01 | 13:00
68 | Bakulia | 111 | 16 | 2017-09-01 | 19:00
69 | Julda | 20 | 27 | 2017-09-01 | 9:00
70 | TK chemical | 6 | 30 | 2017-09-01 | 16:00
71 | Modern Steel | 18 | 21 | 2017-09-01 | 04:00
72 | Shahmirpur | 31 | 17 | 2017-09-01 | 18:30
73 | Abul Khair 230 | 196 | 28 | 2017-09-01 | 10:00
74 | BSRM | 112 | 19 | 2017-09-01 | 19:00
75 | Goalpara | 38 | 6 | 2017-09-01 | 21:00
76 | Central s/s | 84 | 13 | 2017-09-01 | 19:00
77 | Noapara | 72 | 2 | 2017-09-01 | 20:00
78 | Jessore | 136 | 10 | 2017-09-01 | 21:00
79 | Jhenida | 86 | 5 | 2017-09-01 | 19:00
80 | Bottail | 110 | 9 | 2017-09-01 | 20:00
81 | G.K Project | 72 | 10 | 2017-09-01 | 1:00
82 | Faridpur | 130 | 1 | 2017-09-01 | 20:00
83 | Madaripur | 129 | 9 | 2017-09-01 | 20:00
84 | Gopalganj | 171 | 2 | 2017-09-01 | 19:30
85 | Bagerhat | 74 | 21 | 2017-09-01 | 23:00
86 | Mongla | 34 | 26 | 2017-09-01 | 12:00
87 | Satkhira | 89 | 8 | 2017-09-01 | 21:00
88 | Gallamari | 55 | 24 | 2017-09-01 | 13:00
89 | Magura | 38 | 1 | 2017-09-01 | 20:00
90 | Chuadanga | 73 | 2 | 2017-09-01 | 20:00
91 | Barisal | 106 | 10 | 2017-09-01 | 19:30
92 | Patuakhali | 77 | 4 | 2017-09-01 | 20:00
93 | Bhandaria | 42 | 2 | 2017-09-01 | 20:00
94 | Ishurdi | 47 | 9 | 2017-09-01 | 19:30
95 | Natore | 109 | 5 | 2017-09-01 | 20:00
96 | Bogra | 207 | 28 | 2017-09-01 | 20:00
97 | Noagaon | 91 | 4 | 2017-09-01 | 20:00
98 | Rajshahi | 132 | 9 | 2017-09-01 | 19:00
99 | C.Nawabganj | 64 | 9 | 2017-09-01 | 21:00
100 | Amnura | 35 | 5 | 2017-09-01 | 19:00
101 | Pabna | 97 | 5 | 2017-09-01 | 21:00
102 | Shahjadpur | 84 | 4 | 2017-09-01 | 20:00
103 | Serajganj | 71 | 27 | 2017-09-01 | 18:00
104 | Niyamatpur | 51 | 4 | 2017-09-01 | 20:00
105 | Joypurhat | 42 | 18 | 2017-09-01 | 18:30
106 | Rangpur | 112 | 4 | 2017-09-01 | 20:00
107 | Lalmonirhat | 78 | 2 | 2017-09-01 | 20:00
108 | Saidpur | 90 | 2 | 2017-09-01 | 20:00
109 | Purbasadipur | 82 | 25 | 2017-09-01 | 18:30
110 | Thakurgaon | 60 | 1 | 2017-09-01 | 19:00
111 | Palashbari | 93 | 2 | 2017-09-01 | 20:00
112 | Barapukuria | 38 | 2 | 2017-09-01 | 20:00
113 | Panchagar | 33 | 29 | 2017-09-01 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September' 2017
Area | MW | Date | Hour | Remarks
Dhaka | 3749 | 26.09.17 | 15:00
Chittagong | 1127 | 25.09.17 | 23:00
Khulna | 1130 | 08.09.17 | 21:00
Rajshahi | 887 | 21.09.17 | 20:00
Comilla | 888 | 25.09.17 | 22:00
Mymensingh | 639 | 04.09.17 | 19:30
Sylhet | 422 | 16.09.17 | 22:00
Barisal | 231 | 14.09.17 | 9:00
Rangpur | 531 | 02.09.17 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2017
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 1 | 2017-09-01 | 1:00 | 220 | 17 | 2017-09-01 | 15:00
2 | Ishurdi | 230 | 236 | 5 | 2017-09-01 | 18:30 | 223 | 9 | 2017-09-01 | 06:00
3 | Ashuganj | 230 | 240 | 9 | 2017-09-01 | 23:00 | 225 | 23 | 2017-09-01 | 20:00
4 | Serajganj | 230 | 224 | 16 | 2017-09-01 | 17:00 | 210 | 10 | 2017-09-01 | 14:00
5 | Baghabari | 230 | 227 | 1 | 2017-09-01 | 17:00 | 212 | 27 | 2017-09-01 | 12:00
6 | Barapukuria | 230 | 227 | 29 | 2017-09-01 | 17:00 | 210 | 6 | 2017-09-01 | 20:00
7 | Bogra | 230 | 226 | 17 | 2017-09-01 | 16':00 | 204 | 10 | 2017-09-01 | 20:00
8 | Khulna South | 230 | 242 | 8 | 2017-09-01 | 06'00 | 229 | 2 | 2017-09-01 | 15:00
9 | Rampura | 230 | 220 | 1 | 2017-09-01 | 3:00 | 206 | 24 | 2017-09-01 | 15:00
10 | Haripur | 230 | 227 | 7 | 2017-09-01 | 13:00 | 205 | 24 | 2017-09-01 | 11:00
11 | Hasnabad | 230 | 224 | 1 | 2017-09-01 | 8:00 | 206 | 23 | 2017-09-01 | 16:00
12 | Aminbazar | 230 | 222 | 1 | 2017-09-01 | 6:00 | 203 | 24 | 2017-09-01 | 12:00
13 | Tongi | 230 | 222 | 1 | 2017-09-01 | 5:00 | 200 | 23 | 2017-09-01 | 12:00
14 | Comilla (N) | 230 | 227 | 6 | 2017-09-01 | 5:00 | 216 | 23 | 2017-09-01 | 10:00
15 | Hathazari | 230 | 222 | 1 | 2017-09-01 | 8:00 | 205 | 23 | 2017-09-01 | 10:00
16 | Megnaghat | 230 | 225 | 1 | 2017-09-01 | 9:00 | 208 | 24 | 2017-09-01 | 15:00
17 | Fenchuganj | 230 | 240 | 12 | 2017-09-01 | 10:00 | 227 | 8 | 2017-09-01 | 17:00
18 | Siddhirganj | 230 | 237 | 1 | 2017-09-01 | 06:00 | 211 | 17 | 2017-09-01 | 11:00
19 | Maniknagar | 230 | 236 | 1 | 2017-09-01 | 7:00 | 208 | 24 | 2017-09-01 | 11:00
20 | Old Airport | 230 | 221 | 1 | 2017-09-01 | 06:00 | 202 | 24 | 2017-09-01 | 11:00
21 | Barisal | 230 | 241 | 17 | 2017-09-01 | 08:00 | 200 | 6 | 2017-09-01 | 13:00
22 | AKSML | 230 | 220 | 17 | 2017-09-01 | 02:00 | 202 | 23 | 2017-09-01 | 2:00
23 | BSRM | 230 | 223 | 2 | 2017-09-01 | 08:00 | 204 | 23 | 2017-09-01 | 11:00
24 | Bibiyana | 230 | 236 | 29 | 2017-09-01 | 18:00 | 215 | 21 | 2017-09-01 | 21:00
132 kV Substation
1 | Siddhirganj | 132 | 139 | 1 | 2017-09-01 | 08:00 | 127 | 17 | 2017-09-01 | 11:00
2 | Munsiganj | 132 | 139 | 1 | 2017-09-01 | 7:00 | 126 | 17 | 2017-09-01 | 11:00
3 | Megnaghat | 132 | 134 | 1 | 2017-09-01 | 17:00 | 126 | 17 | 2017-09-01 | 12:00
4 | Shyampur | 132 | 135 | 22 | 2017-09-01 | 18:30 | 122 | 14 | 2017-09-01 | 9:00
5 | Bhulta | 132 | 130 | 29 | 2017-09-01 | 2:00 | 117 | 23 | 2017-09-01 | 12:00
6 | Madanganj | 132 | 134 | 1 | 2017-09-01 | 9:00 | 124 | 14 | 2017-09-01 | 8:00
7 | Shitalakhya | 132 | 139 | 8 | 2017-09-01 | 19:00 | 124 | 23 | 2017-09-01 | 11:00
8 | Rahim Steal | 132 | 137 | 1 | 2017-09-01 | 9:00 | 126 | 17 | 2017-09-01 | 12:00
9 | Matuail | 132 | 136 | 1 | 2017-09-01 | 7:00 | 124 | 24 | 2017-09-01 | 11:00
10 | Ghorasal | 132 | 140 | 1 | 2017-09-01 | 6:00 | 128 | 24 | 2017-09-01 | 16:00
11 | Narsinghdi | 132 | 137 | 1 | 2017-09-01 | 7:00 | 122 | 17 | 2017-09-01 | 12:00
12 | Haripur (SBU) | 132 | 137 | 1 | 2017-09-01 | 6:00 | 126 | 24 | 2017-09-01 | 16:00
13 | Ullon | 132 | 135 | 1 | 2017-09-01 | 7:00 | 120 | 24 | 2017-09-01 | 12:00
14 | Hasnabad | 132 | 136 | 8 | 2017-09-01 | 19:00 | 124 | 24 | 2017-09-01 | 12:00
15 | Magbazar | 132 | 135 | 1 | 2017-09-01 | 7:00 | 120 | 23 | 2017-09-01 | 12:00
16 | Maniknagar | 132 | 138 | 1 | 2017-09-01 | 10:00 | 120 | 14 | 2017-09-01 | 12:00
17 | Bangabhaban | 132 | 136 | 5 | 2017-09-01 | 13:00 | 120 | 30 | 2017-09-01 | 16:00
18 | Narinda | 132 | 135 | 1 | 2017-09-01 | 10:00 | 121 | 13 | 2017-09-01 | 10:00
19 | Dhanmondi | 132 | 135 | 1 | 2017-09-01 | 07:00 | 120 | 24 | 2017-09-01 | 13:00
20 | Lalbag | 132 | 136 | 5 | 2017-09-01 | 13:00 | 118 | 24 | 2017-09-01 | 12:00
21 | Madartek | 132 | 135 | 1 | 2017-09-01 | 10:00 | 120 | 24 | 2017-09-01 | 11:00
22 | Mirpur | 132 | 132 | 29 | 2017-09-01 | 2:00 | 116 | 17 | 2017-09-01 | 12:00
23 | Kalyanpur | 132 | 135 | 1 | 2017-09-01 | 6:00 | 124 | 23 | 2017-09-01 | 13:00
24 | Gulshan | 132 | 135 | 1 | 2017-09-01 | 6:00 | 120 | 24 | 2017-09-01 | 11:00
25 | Uttara | 132 | 132 | 29 | 2017-09-01 | 4:00 | 114 | 27 | 2017-09-01 | 10:00
26 | Kamrangirchar | 132 | 136 | 7 | 2017-09-01 | 19:00 | 119 | 21 | 2017-09-01 | 12:00
27 | Savar | 132 | 134 | 5 | 2017-09-01 | 4:00 | 118 | 1 | 2017-09-01 | 13:00
28 | Bhasantec | 132 | 134 | 29 | 2017-09-01 | 3:00 | 120 | 24 | 2017-09-01 | 11:00
29 | Agargaon | 132 | 135 | 29 | 2017-09-01 | 3:00 | 121 | 21 | 2017-09-01 | 12:00
30 | Satmosjid | 132 | 134 | 29 | 2017-09-01 | 3:00 | 120 | 21 | 2017-09-01 | 13:00
31 | Tongi | 132 | 138 | 1 | 2017-09-01 | 8:00 | 121 | 25 | 2017-09-01 | 11:00
32 | Kabirpur | 132 | 138 | 1 | 2017-09-01 | 7:00 | 118 | 24 | 2017-09-01 | 18:00
33 | Basundhara | 132 | 135 | 1 | 2017-09-01 | 8:00 | 119 | 25 | 2017-09-01 | 10:00
34 | Manikganj | 132 | 141 | 3 | 2017-09-01 | 17:00 | 120 | 12 | 2017-09-01 | 19:30
35 | Joydevpur | 132 | 143 | 10 | 2017-09-01 | 14:00 | 124 | 25 | 2017-09-01 | 12:00
36 | New Tongi | 132 | 139 | 1 | 2017-09-01 | 10:00 | 120 | 24 | 2017-09-01 | 12:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2017
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
37 | Tangail | 132 | 140 | 12 | 2017-09-01 | 5:00 | 115 | 23 | 2017-09-01 | 18:00
38 | Mymensing | 132 | 138 | 29 | 2017-09-01 | 09:00 | 112 | 4 | 2017-09-01 | 18:30
39 | Kishorganj | 132 | 136 | 29 | 2017-09-01 | 08:00 | 120 | 5 | 2017-09-01 | 1:00
40 | Netrokona | 132 | 140 | 29 | 2017-09-01 | 09:00 | 110 | 5 | 2017-09-01 | 1:00
41 | Jamalpur | 132 | 137 | 17 | 2017-09-01 | 13:00 | 108 | 4 | 2017-09-01 | 18:30
42 | Sherpur | 132 | 138 | 17 | 2017-09-01 | 13:00 | 109 | 1 | 2017-09-01 | 15:00
43 | Srimongal | 132 | 140 | 16 | 2017-09-01 | 4:00 | 133 | 4 | 2017-09-01 | 18:30
44 | Shahjibazar | 132 | 139 | 16 | 2017-09-01 | 6:00 | 130 | 25 | 2017-09-01 | 22:00
45 | Fenchuganj | 132 | 137 | 11 | 2017-09-01 | 08:00 | 131 | 5 | 2017-09-01 | 1:00
46 | Khulawara | 132 | 137 | 16 | 2017-09-01 | 05:00 | 131 | 1 | 2017-09-01 | 22:00
47 | Sylhet | 132 | 135 | 14 | 2017-09-01 | 05:00 | 127 | 4 | 2017-09-01 | 18:30
48 | Chattak | 132 | 135 | 10 | 2017-09-01 | 07:00 | 123 | 6 | 2017-09-01 | 13:00
49 | Comilla(South) | 132 | 133 | 27 | 2017-09-01 | 07:00 | 110 | 23 | 2017-09-01 | 17:00
50 | Comilla (North) | 132 | 137 | 2 | 2017-09-01 | 8:00 | 121 | 16 | 2017-09-01 | 14:00
51 | Chandpur | 132 | 138 | 29 | 2017-09-01 | 6:00 | 112 | 16 | 2017-09-01 | 20:00
52 | Feni | 132 | 124 | 17 | 2017-09-01 | 9:00 | 110 | 16 | 2017-09-01 | 21:00
53 | Chowmuhani | 132 | 129 | 17 | 2017-09-01 | 10:00 | 110 | 16 | 2017-09-01 | 22:00
54 | Ashuganj | 132 | 140 | 7 | 2017-09-01 | 9:00 | 131 | 26 | 2017-09-01 | 15:00
55 | Daudkandi | 132 | 135 | 11 | 2017-09-01 | 19:30 | 123 | 16 | 2017-09-01 | 12:00
56 | Brahminbaria | 132 | 139 | 16 | 2017-09-01 | 7:00 | 129 | 25 | 2017-09-01 | 23:00
57 | Madanhat | 132 | 135 | 26 | 2017-09-01 | 08:00 | 125 | 16 | 2017-09-01 | 16:00
58 | Hathazari | 132 | 132 | 26 | 2017-09-01 | 08:00 | 121 | 16 | 2017-09-01 | 16:00
59 | Khulshi | 132 | 129 | 1 | 2017-09-01 | 11:00 | 119 | 4 | 2017-09-01 | 24:00
60 | Halishahar | 132 | 131 | 2 | 2017-09-01 | 19:00 | 119 | 16 | 2017-09-01 | 16:00
61 | Baraulia | 132 | 130 | 26 | 2017-09-01 | 8:00 | 119 | 16 | 2017-09-01 | 16:00
62 | Sikalbaha | 132 | 132 | 9 | 2017-09-01 | 24:00 | 119 | 16 | 2017-09-01 | 16:00
63 | Dohazari | 132 | 133 | 25 | 2017-09-01 | 6:00 | 120 | 4 | 2017-09-01 | 24:00
64 | Cox'sbazar | 132 | 131 | 10 | 2017-09-01 | 17:00 | 109 | 16 | 2017-09-01 | 16:00
65 | Chandraghona | 132 | 131 | 1 | 2017-09-01 | 8:00 | 122 | 16 | 2017-09-01 | 16:00
66 | Kaptai | 132 | 132 | 1 | 2017-09-01 | 09:00 | 125 | 4 | 2017-09-01 | 23:00
67 | A. Khaer Stl. | 132 | 130 | 10 | 2017-09-01 | 15:00 | 121 | 27 | 2017-09-01 | 16:00
68 | Bakulia | 132 | 131 | 26 | 2017-09-01 | 08:00 | 119 | 1 | 2017-09-01 | 13:00
69 | Julda | 132 | 132 | 26 | 2017-09-01 | 07:00 | 117 | 16 | 2017-09-01 | 16:00
70 | TK Chemical | 132 | 134 | 25 | 2017-09-01 | 05:00 | 123 | 16 | 2017-09-01 | 16:00
71 | Modern Steel | 132 | 131 | 26 | 2017-09-01 | 05:00 | 119 | 16 | 2017-09-01 | 16:00
72 | Shahmirpur | 132 | 131 | 25 | 2017-09-01 | 07:00 | 117 | 16 | 2017-09-01 | 16:00
73 | Goalpara | 132 | 138 | 1 | 2017-09-01 | 5:00 | 131 | 12 | 2017-09-01 | 13:00
74 | Khulna Central | 132 | 139 | 1 | 2017-09-01 | 6:00 | 124 | 12 | 2017-09-01 | 11:00
75 | Noapara | 132 | 137 | 1 | 2017-09-01 | 6:00 | 127 | 9 | 2017-09-01 | 20:00
76 | Jessore | 132 | 136 | 3 | 2017-09-01 | 18:00 | 119 | 7 | 2017-09-01 | 01:00
77 | Jhenida | 132 | 134 | 3 | 2017-09-01 | 8:00 | 117 | 9 | 2017-09-01 | 13:00
78 | Bottail | 132 | 135 | 3 | 2017-09-01 | 18:00 | 117 | 13 | 2017-09-01 | 1:00
79 | G.K.Project | 132 | 137 | 1 | 2017-09-01 | 17:00 | 125 | 22 | 2017-09-01 | 8:00
80 | Faridpur | 132 | 134 | 29 | 2017-09-01 | 06:00 | 118 | 26 | 2017-09-01 | 22:00
81 | Madaripur | 132 | 135 | 11 | 2017-09-01 | 12:00 | 121 | 4 | 2017-09-01 | 1:00
82 | Gopalganj | 132 | 138 | 29 | 2017-09-01 | 3:00 | 116 | 2 | 2017-09-01 | 23:00
83 | Bagerhat | 132 | 141 | 28 | 2017-09-01 | 15:00 | 130 | 6 | 2017-09-01 | 22:00
84 | Mongla | 132 | 136 | 1 | 2017-09-01 | 5:00 | 127 | 7 | 2017-09-01 | 13:00
85 | Satkhira | 132 | 137 | 2 | 2017-09-01 | 5:00 | 129 | 9 | 2017-09-01 | 20:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: September '2017
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
86 | Gallamari | 132 | 139 | 1 | 2017-09-01 | 12:00 | 119 | 6 | 2017-09-01 | 10:00
87 | Magura | 132 | 130 | 3 | 2017-09-01 | 18:00 | 115 | 3 | 2017-09-01 | 21:00
88 | Chuadanga | 132 | 129 | 3 | 2017-09-01 | 17:00 | 109 | 5 | 2017-09-01 | 19:30
89 | Barisal | 132 | 142 | 6 | 2017-09-01 | 13:00 | 128 | 6 | 2017-09-01 | 20:00
90 | Patuakhali | 132 | 142 | 6 | 2017-09-01 | 13:00 | 128 | 6 | 2017-09-01 | 20:00
91 | Bhandaria | 132 | 135 | 1 | 2017-09-01 | 18:30 | 122 | 7 | 2017-09-01 | 13:00
92 | Ishurdi | 132 | 135 | 1 | 2017-09-01 | 1:00 | 127 | 9 | 2017-09-01 | 5:00
93 | Natore | 132 | 137 | 8 | 2017-09-01 | 17:00 | 125 | 7 | 2017-09-01 | 18:30
94 | Bogra | 132 | 136 | 17 | 2017-09-01 | 15:00 | 118 | 10 | 2017-09-01 | 20:00
95 | Noagaon | 132 | 132 | 17 | 2017-09-01 | 15:00 | 115 | 4 | 2017-09-01 | 1:00
96 | Rajshahi | 132 | 137 | 8 | 2017-09-01 | 17:00 | 124 | 9 | 2017-09-01 | 12:00
97 | C.Nawabganj | 132 | 138 | 20 | 2017-09-01 | 8:00 | 116 | 10 | 2017-09-01 | 14:00
98 | Amnura | 132 | 140 | 20 | 2017-09-01 | 13:00 | 120 | 10 | 2017-09-01 | 14:00
99 | Pabna | 132 | 131 | 2 | 2017-09-01 | 13:00 | 122 | 28 | 2017-09-01 | 20:00
100 | Shahjadpur | 132 | 139 | 3 | 2017-09-01 | 7:00 | 124 | 5 | 2017-09-01 | 20:00
101 | Serajganj | 132 | 134 | 3 | 2017-09-01 | 18:00 | 123 | 4 | 2017-09-01 | 20:00
102 | Niyamatpur | 132 | 135 | 17 | 2017-09-01 | 16:00 | 111 | 4 | 2017-09-01 | 20:00
103 | Joypurhat | 132 | 136 | 17 | 2017-09-01 | 15:00 | 113 | 4 | 2017-09-01 | 20:00
104 | Rangpur | 132 | 127 | 29 | 2017-09-01 | 17:00 | 109 | 1 | 2017-09-01 | 19:00
105 | Lalmonirhat | 132 | 128 | 29 | 2017-09-01 | 17:00 | 100 | 3 | 2017-09-01 | 19:00
106 | Saidpur | 132 | 125 | 23 | 2017-09-01 | 9:00 | 105 | 10 | 2017-09-01 | 20:00
107 | Purbasadipur | 132 | 132 | 30 | 2017-09-01 | 6:00 | 108 | 1 | 2017-09-01 | 19:00
108 | Thakurgaon | 132 | 121 | 30 | 2017-09-01 | 7:00 | 95 | 1 | 2017-09-01 | 19:00
109 | Palashbari | 132 | 127 | 17 | 2017-09-01 | 15:00 | 103 | 16 | 2017-09-01 | 18:00
110 | Barapukuria | 132 | 127 | 29 | 2017-09-01 | 17:00 | 110 | 6 | 2017-09-01 | 20:00
111 | Panchagar | 132 | 119 | 1 | 2017-09-01 | 19:00 | 90 | 1 | 2017-09-01 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:September' 2017
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 120 | 375
IP-299421 | Hasnabad | TR2 | 225 | 105 | 360 | 30.09.17 | 09:00
|  | TR3 | 225 | 100 | 330
|  | TR1 | 225 | 135 | 465
IP-299866 | Tongi | TR2 | 225 | 135 | 465 | 25.09.17 | 09:00
|  | TR3 | 225 | 135 | 465
|  | TR1 | 225 | 162 | 500
IP-299427 | Haripur | TR2 | 225 | 162 | 500 | 30.09.17 | 01:00
|  | TR3 | 225 | 162 | 500
|  | TR1 | 225 | 157 | 465
IP-299728 | Rampura | TR2 | 225 | 157 | 465 | 24.09.17 | 14:00
|  | TR3 | 225 | 157 | 465
|  | TR1 | 225 | 112 | 328
IP-299264 | Aminbazar | TR2 | 225 | 112 | 328 | 09.09.17 | 22:00
|  | TR3 | 225 | 117 | 333
| Maniknagar | TR1 | 300 | 118 | 402 | 26.09.17 | 16:00
|  | TR2 | 300 | 118 | 402
IP-399266 | Comilla (N) | TR1 | 225 | 156 | 500 | 16.09.17 | 23:00
|  | TR2 | 225 | 156 | 504
| Fenchuganj | TR1 | 300 | 200 | 516 | 23.09.17 | 11:00
|  | TR1 | 150 | 60 | 180
| Hathazari | TR2 | 150 | 60 | 180 | 01.09.17 | 13:00
IP-399428 |  | TR3 | 150 | 60 | 180
|  | TR4 | 150 | 60 | 180
|  | TR1 | 225 | 176 | 465
| Ishurdi | TR2 | 225 | 176 | 465 | 26.09.17 | 18:30
IP-499474 |  | TR3 | 225 | 176 | 465
| Khulna(S) | TR1 | 225 | 127 | 315
IP-58001/58002 |  | TR2 | 225 | 127 | 315 | 03.09.17 | 15:00
| Bogra | TR1 | 225 | 150 | 497 | 28.09.17 | 20:00
IP-43002/499264 |  | TR2 | 225 | 150 | 497
IP-499224 | Baghabari | TR1 | 225 | 125 | 370 | 26.09.17 | 02:00
| Barapukuria | TR1 | 225 | 180 | 900 | 16.09.17 | 18:00
|  | TR2 | 225 | 180 | 900
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:September' 2017 | [6 empty] | (For Evening Peak) | [7 empty] | Month:September' 2017 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-09-17 | 7889 | 7889 | - | - | - | - | - | - | - | - | - | - | - | - | 01-09-17 | 5706 | 5706 | - | - | - | - | - | - | - | - | - | - | - | -
02-09-17 | 7951 | 7951 | - | - | - | - | - | - | - | - | - | - | - | - | 02-09-17 | 5104 | 5104 | - | - | - | - | - | - | - | - | - | - | - | -
03-09-17 | 7719 | 7719 | - | - | - | - | - | - | - | - | - | - | - | - | 03-09-17 | 5979 | 5979 | - | - | - | - | - | - | - | - | - | - | - | -
04-09-17 | 8079 | 8079 | - | - | - | - | - | - | - | - | - | - | - | - | 04-09-17 | 6213 | 6213 | - | - | - | - | - | - | - | - | - | - | - | -
05-09-17 | 8245 | 8245 | - | - | - | - | - | - | - | - | - | - | - | - | 05-09-17 | 6581 | 6581 | - | - | - | - | - | - | - | - | - | - | - | -
06-09-17 | 8422 | 8422 | - | - | - | - | - | - | - | - | - | - | - | - | 06-09-17 | 6890 | 6890 | - | - | - | - | - | - | - | - | - | - | - | -
07-09-17 | 8449 | 8449 | - | - | - | - | - | - | - | - | - | - | - | - | 07-09-17 | 7067 | 7067 | - | - | - | - | - | - | - | - | - | - | - | -
08-09-17 | 8672 | 8672 | - | - | - | - | - | - | - | - | - | - | - | - | 08-09-17 | 6690 | 6690 | - | - | - | - | - | - | - | - | - | - | - | -
09-09-17 | 8804 | 8804 | - | - | - | - | - | - | - | - | - | - | - | - | 09-09-17 | 7363 | 7363 | - | - | - | - | - | - | - | - | - | - | - | -
10-09-17 | 8358 | 8358 | - | - | - | - | - | - | - | - | - | - | - | - | 10-09-17 | 7289 | 7289 | - | - | - | - | - | - | - | - | - | - | - | -
11-09-17 | 8583 | 8583 | - | - | - | - | - | - | - | - | - | - | - | - | 11-09-17 | 6745 | 6745 | - | - | - | - | - | - | - | - | - | - | - | -
12-09-17 | 9016 | 9016 | - | - | - | - | - | - | - | - | - | - | - | - | 12-09-17 | 7419 | 7419 | - | - | - | - | - | - | - | - | - | - | - | -
13-09-17 | 9049 | 9049 | - | - | - | - | - | - | - | - | - | - | - | - | 13-09-17 | 7934 | 7934 | - | - | - | - | - | - | - | - | - | - | - | -
14-09-17 | 9194 | 9194 | - | - | - | - | - | - | - | - | - | - | - | - | 14-09-17 | 7799 | 7799 | - | - | - | - | - | - | - | - | - | - | - | -
15-09-17 | 8839 | 8839 | - | - | - | - | - | - | - | - | - | - | - | - | 15-09-17 | 7124 | 7124 | - | - | - | - | - | - | - | - | - | - | - | -
16-09-17 | 8984 | 8984 | - | - | - | - | - | - | - | - | - | - | - | - | 16-09-17 | 7958 | 7958 | - | - | - | - | - | - | - | - | - | - | - | -
17-09-17 | 9094 | 9094 | - | - | - | - | - | - | - | - | - | - | - | - | 17-09-17 | 7445 | 7445 | - | - | - | - | - | - | - | - | - | - | - | -
18-09-17 | 8959 | 8959 | - | - | - | - | - | - | - | - | - | - | - | - | 18-09-17 | 8127 | 8127 | - | - | - | - | - | - | - | - | - | - | - | -
19-09-17 | 9047 | 9047 | - | - | - | - | - | - | - | - | - | - | - | - | 19-09-17 | 7824 | 7824 | - | - | - | - | - | - | - | - | - | - | - | -
20-09-17 | 9122 | 9122 | - | - | - | - | - | - | - | - | - | - | - | - | 20-09-17 | 7711.6 | 7711.6 | - | - | - | - | - | - | - | - | - | - | - | -
21-09-17 | 9215 | 9215 | - | - | - | - | - | - | - | - | - | - | - | - | 21-09-17 | 7966.9 | 7966.9 | - | - | - | - | - | - | - | - | - | - | - | -
22-09-17 | 8930 | 8930 | - | - | - | - | - | - | - | - | - | - | - | - | 22-09-17 | 7127 | 7127 | - | - | - | - | - | - | - | - | - | - | - | -
23-09-17 | 9056 | 9056 | - | - | - | - | - | - | - | - | - | - | - | - | 23-09-17 | 7988.1 | 7988.1 | - | - | - | - | - | - | - | - | - | - | - | -
24-09-17 | 9276 | 9276 | - | - | - | - | - | - | - | - | - | - | - | - | 24-09-17 | 8542.9 | 8542.9 | - | - | - | - | - | - | - | - | - | - | - | -
25-09-17 | 9272 | 9272 | - | - | - | - | - | - | - | - | - | - | - | - | 25-09-17 | 8555.3 | 8555.3 | - | - | - | - | - | - | - | - | - | - | - | -
26-09-17 | 9431 | 9431 | - | - | - | - | - | - | - | - | - | - | - | - | 26-09-17 | 8475 | 8475 | - | - | - | - | - | - | - | - | - | - | - | -
27-09-17 | 9231 | 9231 | - | - | - | - | - | - | - | - | - | - | - | - | 27-09-17 | 8444.3 | 8444.3 | - | - | - | - | - | - | - | - | - | - | - | -
28-09-17 | 8910 | 8910 | - | - | - | - | - | - | - | - | - | - | - | - | 28-09-17 | 8614.2 | 8614.2 | - | - | - | - | - | - | - | - | - | - | - | -
29-09-17 | 8187 | 8187 | - | - | - | - | - | - | - | - | - | - | - | - | 29-09-17 | 5987.5 | 5987.5 | - | - | - | - | - | - | - | - | - | - | - | -
30-09-17 | 9009 | 9009 | - | - | - | - | - | - | - | - | - | - | - | - | 30-09-17 | 7201.2 | 7201.2 | - | - | - | - | - | - | - | - | - | - | - | -
31-08-17 | 8053 | 8053 | - | - | - | - | - | - | - | - | - | - | - | - | 31-08-17 | 7167 | 7167 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:September' 2017
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9431 | 26/09/17 | 21:00
2 | Maximum day peak Genaration | MW | 8614.2 | 28/09/17 | 11:00
3 | Maximum Evening Peak Demand | MW | 9431 | 26/09/17 | 21:00
4 | Minimum Generation | MW | 4928 | 02/09/17 | 10:00
5 | Average of the daily evening peak Genaration | MW | 8743.3871
6 | Average of the daily day peak Genaration | MW | 7323.8065
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW | -
11 | Total Generation | MKWH | 5564.4349
12 | Total Generation by IPP | MKWH | 975.7582 | % of total Gen. | 17.5356
13 | Total Generation by BPDB | MKWH | 2695.8225 | " | 48.4474
14 | A) Total Generation by RPCL | MKWH | 194.1735 | '' | 3.4895
| B) Total Generation by REB | MKWH | 117.903 | " | 2.1189
| C) Total Generation by RENTAL | MKWH | 1144.6308 | " | 20.5705
| D) Total Imported from India (HVDC) | MKWH | 347.3917 | " | 6.2431
| E) Total Imported from Tripura, India (A.C) | MKWH | 88.7552 | " | 1.595
15 | Fuel wise Generation.
| A) Gas | MKWH | 3432.5779 | % of total Gen. | 61.69%
| B) Oil | MKWH | 1497.5355 | '' | 26.91%
| C) Hydro | MKWH | 114.4116 | '' | 2.056%
| D) Solar | MKWH | 0.17014 | '' | 0.003058%
| E) Coal | MKWH | 83.5929 | '' | 1.502%
| F) HVDC (Import from India) | MKWH | 347.3917 | '' | 6.243%
| G) A.C (Import from Tripura, India) | MKWH | 88.7552 | '' | 1.595%
16 | Maximun of the daily total Generation . | MKWH | 211.9719 | 26/09/17
17 | Monthly Load factor | % | 81.9466
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 13906.1513
| A) Gas | M.Taka | 2109.3771
| B) Liquid fuel | M.Taka | 11370.7065
| C) Coal | M.Taka | 426.0676
| D) HVDC (Import from India) | M.Taka | 1007.436
| E) Tripura(Import from India) | M.Taka | 576.9088
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 628.4023 | 25/09/17
| A) Gas | M.Taka | 82.1448 | 26/09/17
| B) Liquid fuel | M.Taka | 532.3291 | 25/09/17
| C) Coal | M.Taka | 17.8125 | 20/09/17
| D) HVDC (Import from India) | M.Taka | 34.5279 | 12/09/17
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.458
| B) Excluding Hydro & Solar | Taka/KWHR | 3.5307
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 99 | 30/09/17 | 06:00
b) | Actual | FT (MSL) | 107.8 | 30/09/18 | 06:00
22 | Peak Genaration of September 2016 | MW | 8890 | 08/09/16 | 21:00
23 | Peak Demand of September 2016 | MW | 8900 | 07/09/16 | 21:00
24 | Maximum peak Generation recorded upto 30/09/17 | MW | 9479 | 07/06/17 | 21:00
25 | Maximum peak Demand recorded upto 30/09/17 | MW | 9479 | 07/06/17 | 21:00
26 | Maximum load shed recorded upto 30/09/17 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.