## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-27 | Sunday
|  | Date (day): | 2019-10-27 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13398 | MW |  |  | (b) At Evening Peak Hour : |  | 14624 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-26 | 2019-10-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 199 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 350 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 52 | 342 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 357 | 357 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 430 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 12 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 230 | 230 | 230 | 75 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 9 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 10 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 17 | 47 | 45 | 46
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 68 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 143 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 34 | 88 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1922 | 2495 | 3867 | 4268 | 576 | 973
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 82 | 92 | 90 | 90 | 140 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 206 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 143 | 134 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 68 | 105 | 0 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 10 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 10 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 97 | 95 | 96 |  | 12 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.1 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 645.1 | 974 | 1465.4 | 1592 | 400 | 110
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 191 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 370 | 320 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 360 | 360
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 30 | 33 | 33 |  | 12 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 45 | 50 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 112 | 112 | 112 | 112 | 83 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 35 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 10 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 127 | 126 | 140 | 141
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 130 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 150 | 129 | 169
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 15 | 20 | 20 |  | 5 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1272 | 1409 | 2037 | 2328 | 381 | 33
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 145 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 2 | 150 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 181 | 317 | 593.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 22 | 22 | 72 | 72
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 98 | 99 | 100 | 100 |  | 230 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 32 | 28 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 18 | 47 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 66 | 68 | 68 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 78 | 76 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 28 | 36 | 41 | 41 |  | 9 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 280 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 824 | 982 | 1127 | 1130 | 0 | 798
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 390 | 929 | 944 | 944
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 45 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 290 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 109 | 70 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 824 | 1400 | 1994 | 2154 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 23 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 174 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 57 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 244 | 326 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 50 | 0 | 0 | 0 | 50 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 182 | 225 | 225 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 205 | 190 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 432 | 394 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 12 | 12
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 9 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 72 | 113 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 26 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 963 | 932 | 1467 | 1617 | 270 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 70 | 68 | 68
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 290 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 352.3 | 447 | 469 | 495 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 7227.4 | 9282 | 13398 | 14624 | 1669 | 2078
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6881.6808 | 8838 | 12757.1131 | 13924.468
A. |  | 2019-10-26 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 9282 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5208 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9282 | MW
3 | Day peak Generation : |  |  | 7227.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8838 | MW
4 | Evening peak Generation : |  |  | 9282 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 171.3509 | MKWHr | By Solar | 0.1888 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 127.0935 | MKWHr |  | By Oil: | 18.0116 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.0191 | MKWHr |  | By Hydro: | 1.8669 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1669 | MW | Dhaka | 3340 | 3340 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2078 | MW | Chittagong | 1092 | 1092 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3747 | MW | Khulna | 1046 | 1046 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1109.88 | MMCFD |  |  | Rajshahi | 810 | 810 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 116466146.68 | ii) Oil : | Taka | 120104213.62 | Comilla | 822 | 822 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 36573799 | Total | Taka | 273144159.3 | Mymensingh | 579 | 579 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 341 | 341 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 306 | MW (E to W) at | 19:00 | hrs | Barisal | 264 | 264 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 242 | MW at | 18:30 | hrs | Rangpur | 544 | 544 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.8° C |  |  | Total | 8838 | 8838 |  | 0
B. |  | 2019-10-27 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 29.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14624 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 4124 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 193.8359 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6192.91 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.3658 | MKWHr. | ii) HVDC Flow at Peak Time |  | 929 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8051 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 102.37 | 102.46 |  | (b) Today: | 102.37 |  | (c) Rule Curve: |  | 108.5
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-10-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 207 | 242 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 25 | 30 | 0 | 29 | 0 | 0 | 73 | 0 | 100 | 0 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 34 | 10 | 24 | 6 | 19 | 41 | 80 | 100 | 0 | 260 | 0 | 161 | 8 | 121 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 17 | 104 | 161 | 0 | 0 | 0 | 40 | 65 | 5 | 5 | 100 | 100 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 620 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 154 | 0 | 0 | 0 | 13 | 0 | 155 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3874 | 2071 | 5945 | 3148 | 620 | 1353 | 316 | 297 | 73 | 34 | 104 | 0 | 0 | 102.48
2:00 | 35 | 0 | 101 | 0 | 230 | 0 | 0 | 290 | 242 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 25 | 30 | 0 | 29 | 0 | 0 | 73 | 0 | 100 | 0 | 0 | 204 | 0 | 146 | 0 |  | 0 | 0 | 34 | 10 | 24 | 6 | 19 | 41 | 80 | 100 | 0 | 260 | 0 | 161 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 17 | 100 | 161 | 0 | 0 | 0 | 40 | 65 | 5 | 5 | 100 | 100 | 45 | 5 | 5 | 0 | 0 | 7 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 391 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 11 | 0 | 155 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3968 | 1843 | 5811 | 3247 | 391 | 1353 | 316 | 297 | 73 | 34 | 100 | 0 | 0 | 102.48
3:00 | 35 | 0 | 101 | 0 | 230 | 0 | 0 | 294 | 242 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 0 | 29 | 0 | 0 | 74 | 0 | 100 | 0 | 0 | 204 | 0 | 147 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 41 | 80 | 100 | 0 | 260 | 0 | 160 | 8 | 121 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 17 | 96 | 124 | 0 | 0 | 0 | 40 | 65 | 5 | 5 | 100 | 100 | 45 | 5 | 5 | 0 | 0 | 7 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 391 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 153 | 0 | 0 | 0 | 11 | 0 | 140 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3818 | 1790 | 5608 | 3156 | 391 | 1347 | 230 | 297 | 74 | 17 | 96 | 0 | 0 | 102.47
4:00 | 35 | 0 | 101 | 0 | 210 | 0 | 0 | 295 | 242 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 0 | 29 | 0 | 0 | 74 | 0 | 100 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 60 | 100 | 0 | 230 | 0 | 160 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 90 | 105 | 0 | 0 | 0 | 40 | 65 | 5 | 5 | 100 | 100 | 45 | 5 | 5 | 0 | 0 | 7 | 0 | 260 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 391 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 135 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3609 | 1766 | 5375 | 2956 | 391 | 1337 | 230 | 297 | 74 | 0 | 90 | 0 | 0 | 102.47
5:00 | 35 | 0 | 101 | 0 | 210 | 0 | 0 | 225 | 262 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 29 | 0 | 0 | 76 | 0 | 100 | 0 | 0 | 218 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 60 | 100 | 0 | 230 | 0 | 180 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 88 | 104 | 0 | 0 | 0 | 10 | 65 | 5 | 5 | 100 | 20 | 32 | 5 | 5 | 0 | 0 | 7 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 390 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 135 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3443 | 1765 | 5208 | 2794 | 390 | 1333 | 230 | 297 | 76 | 0 | 88 | 0 | 0 | 102.46
6:00 | 35 | 0 | 98 | 0 | 220 | 0 | 0 | 205 | 262 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 29 | 0 | 0 | 76 | 0 | 100 | 0 | 0 | 204 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 60 | 100 | 0 | 230 | 0 | 162 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 88 | 104 | 0 | 0 | 0 | 10 | 65 | 5 | 5 | 100 | 20 | 32 | 5 | 5 | 0 | 0 | 7 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 391 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 135 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3439 | 1814 | 5253 | 2761 | 391 | 1410 | 230 | 297 | 76 | 0 | 88 | 0 | 0 | 102.46
7:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 205 | 282 |  | 0 | 310 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 29 | 0 | 0 | 76 | 0 | 100 | 0 | 0 | 217 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 60 | 100 | 0 | 280 | 0 | 182 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 86 | 104 | 0 | 0 | 0.1 | 10 | 65 | 5 | 5 | 100 | 20 | 32 | 5 | 5 | 0 | 0 | 5 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 390 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 230 | 0 | 0 | 142 | 0 | 0 | 0 | 11 | 0 | 134 | 0 | 392 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3560.1 | 1979 | 5539.1 | 2900 | 390 | 1455 | 330 | 299 | 76 | 0 | 86 | 3.1 | 0 | 102.45
8:00 | 35 | 0 | 100 | 0 | 280 | 0 | 0 | 230 | 282 |  | 0 | 360 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 29 | 0 | 0 | 77 | 0 | 100 | 0 | 0 | 219 | 0 | 127 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 19 | 2 | 60 | 100 | 0 | 325 | 0 | 183 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 105 | 0 | 0 | 0.2 | 10 | 65 | 5 | 5 | 100 | 20 | 32 | 5 | 5 | 0 | 0 | 5 | 0 | 325 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 0 | 0 | 0 |  | 390 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 67 | 230 | 0 | 0 | 200 | 0 | 0 | 0 | 11 | 0 | 135 | 0 | 433 | 110 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 3760.78 | 2211.8 | 5972.58 | 3188 | 390 | 1579 | 345 | 297 | 77 | 0 | 82 | 14.58 | 0 | 102.45
9:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 279 | 356 |  | 0 | 400 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 29 | 0 | 0 | 47 | 0 | 100 | 0 | 0 | 229 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 2 | 60 | 100 | 0 | 365 | 0 | 199 | 8 | 127 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 13 | 0 | 0 | 10 | 98 | 159 | 0 | 22 | 0.8 | 10 | 65 | 5 | 5 | 130 | 100 | 40 | 5 | 5 | 0 | 0 | 5 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 2.2 | 0 | 0 | 0 |  | 391 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 12 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 3 | 0 | 67 | 230 | 0 | 0 | 205 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 432 | 110 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 |  | 4261.1 | 2245.3 | 6506.4 | 3542 | 391 | 1720 | 392 | 297 | 47 | 0 | 98 | 19.4 | 0 | 102.45
10:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 287 | 358 |  | 0 | 400 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 29 | 0 | 0 | 47 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 2 | 60 | 100 | 0 | 350 | 0 | 193 | 35 | 127 | 30 | 5 | 0 | 5 | 0 | 0 | 0 | 16 | 0 | 33 | 12 | 104 | 159 | 0 | 22 | 1 | 10 | 65 | 5 | 5 | 130 | 96 | 40 | 5 | 5 | 0 | 0 | 6 | 0 | 315 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 4.4 | 0 | 0 | 0 |  | 391 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 13 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 0 | 67 | 280 | 0 | 0 | 204 | 0 | 0 | 0 | 11 | 0 | 210 | 0 | 430 | 108 | 0 | 0 | 0 | 0 | 0 | 4.8 | 15 |  | 4392.8 | 2347.8 | 6740.6 | 3641 | 391 | 1752 | 436 | 347 | 47 | 0 | 104 | 22.6 | 0 | 102.44
11:00 | 35 | 0 | 100 | 0 | 380 | 0 | 0 | 280 | 359 |  | 0 | 400 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 23 | 29 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 2 | 60 | 100 | 0 | 340 | 0 | 184 | 63 | 127 | 33 | 25 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 110 | 155 | 0 | 20 | 0.8 | 20 | 22 | 7 | 5 | 130 | 97 | 40 | 5 | 5 | 0 | 0 | 6 | 0 | 310 | 0 | 8 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 4.8 | 0 | 0 | 0 |  | 391 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 14 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 66 | 280 | 0 | 0 | 193 | 0 | 0 | 0 | 10 | 0 | 208 | 0 | 433 | 109 | 0 | 0 | 0 | 0 | 0 | 6.4 | 19 |  | 4543.9 | 2339.4 | 6883.3 | 3650 | 391 | 1800 | 465 | 346 | 92 | 0 | 110 | 29.3 | 0 | 102.44
12:00 | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 52 | 357 |  | 0 | 430 | 260 | 12 | 0 | 9 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 29 | 0 | 0 | 32 | 50 | 100 | 0 | 0 | 204 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 4 | 80 | 100 | 0 | 370 | 0 | 202 | 112 | 127 | 33 | 45 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 120 | 156 | 0 | 22 | 1 | 60 | 22 | 32 | 18 | 130 | 98 | 65 | 5 | 40 | 0 | 0 | 28 | 9 | 315 | 0 | 2 | 0 | 30 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 34 | 68 | 4.1 | 0 | 0 | 0 |  | 390 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 13 | 0 | 0 | 50 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 67 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 57 | 0 | 205 | 0 | 432 | 109 | 0 | 0 | 0 | 0 | 0 | 5.3 | 26 |  | 4844.1 | 2383.3 | 7227.4 | 3586 | 390 | 2068 | 612 | 347 | 82 | 9 | 120 | 13.4 | 0 | 102.44
13:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 28 | 358 |  | 0 | 430 | 260 | 10 | 0 | 15 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 24 | 0 | 41 | 17 | 0 | 0 | 22 | 25 | 25 | 30 | 29 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 205 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 9 | 80 | 100 | 0 | 340 | 0 | 179 | 112 | 126 | 33 | 44 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 118 | 136 | 0 | 22 | 0.6 | 60 | 22 | 47 | 46 | 163 | 95 | 53 | 79 | 40 | 0 | 18 | 29 | 10 | 280 | 24 | 8 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 35 | 80 | 4.5 | 0 | 0 | 0 |  | 391 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 70 | 280 | 0 | 0 | 205 | 0 | 0 | 0 | 89 | 0 | 195 | 0 | 376 | 109 | 0 | 18 | 0 | 0 | 0 | 8.5 | 45 |  | 5113.6 | 2278.5 | 7392.1 | 3450 | 391 | 2199 | 766 | 350 | 90 | 0 | 118 | 28.1 | 0 | 102.43
14:00 | 35 | 0 | 201 | 0 | 370 | 0 | 0 | 63 | 305 |  | 0 | 360 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 25 | 33 | 29 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 19 | 4 | 80 | 100 | 0 | 340 | 0 | 180 | 112 | 126 | 33 | 44 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 126 | 127 | 0 | 22 | 0.5 | 60 | 22 | 50 | 46 | 100 | 98 | 54 | 79 | 40 | 0 | 18 | 30 | 10 | 270 | 24 | 8 | 0 | 30 | 0 | 0 | 50 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 35 | 85 | 1.3 | 0 | 0 | 0 |  | 391 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 70 | 280 | 0 | 0 | 174 | 0 | 0 | 0 | 97 | 0 | 167 | 0 | 401 | 109 | 0 | 35 | 0 | 0 | 0 | 2.9 | 47 |  | 4867.6 | 2241.9 | 7109.5 | 3391 | 391 | 2034 | 706 | 350 | 90 | 0 | 126 | 21.5 | 0 | 102.43
15:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 120 | 356 |  | 0 | 360 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 0 | 33 | 29 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 1 | 18 | 19 | 4 | 80 | 100 | 0 | 340 | 0 | 181 | 105 | 126 | 33 | 45 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 128 | 126 | 0 | 22 | 0.5 | 59 | 22 | 47 | 47 | 130 | 100 | 60 | 78 | 40 | 0 | 18 | 32 | 10 | 300 | 23 | 8 | 0 | 35 | 0 | 0 | 50 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 52 | 103 | 2.5 | 0 | 0 | 0 |  | 391 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 3 | 0 | 69 | 290 | 0 | 0 | 175 | 0 | 0 | 0 | 95 | 0 | 170 | 0 | 407 | 35 | 0 | 35 | 0 | 0 | 0 | 1.2 | 37 |  | 5052.5 | 2167.2 | 7219.7 | 3430 | 391 | 2142 | 663 | 359 | 90 | 0 | 128 | 16.7 | 0 | 102.43
16:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 300 | 355 |  | 0 | 360 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 15 | 0 | 0 | 17 | 22 | 25 | 0 | 33 | 29 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 211 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 10 | 18 | 19 | 4 | 80 | 100 | 0 | 360 | 0 | 198 | 112 | 126 | 33 | 10 | 0 | 35 | 0 | 0 | 0 | 19 | 5 | 33 | 0 | 120 | 144 | 0 | 22 | 0.1 | 60 | 22 | 11 | 10 | 130 | 105 | 65 | 40 | 10 | 0 | 18 | 13 | 10 | 290 | 23 | 8 | 0 | 45 | 0 | 0 | 50 | 0 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 52 | 105 | 1.4 | 0 | 0 | 0 |  | 391 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 3 | 0 | 69 | 290 | 0 | 0 | 167 | 0 | 0 | 0 | 60 | 0 | 162 | 0 | 394 | 17 | 0 | 35 | 0 | 0 | 0 | 0.2 | 46 |  | 5127.6 | 2097.2 | 7224.8 | 3650 | 391 | 1894 | 713 | 359 | 90 | 0 | 120 | 7.8 | 0 | 102.42
17:00 | 35 | 0 | 200 | 0 | 320 | 0 | 0 | 300 | 302 |  | 0 | 360 | 230 | 7 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 70 | 0 | 23 | 17 | 35 | 55 | 22 | 25 | 30 | 33 | 29 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 27 | 22 | 19 | 4 | 80 | 100 | 0 | 280 | 0 | 180 | 112 | 121 | 33 | 10 | 0 | 35 | 0 | 0 | 0 | 19 | 5 | 33 | 0 | 122 | 145 | 18 | 22 | 0 | 60 | 22 | 11 | 10 | 100 | 101 | 65 | 40 | 10 | 0 | 18 | 13 | 10 | 290 | 24 | 11 | 0 | 62 | 0 | 0 | 65 | 0 | 8 | 0.9 | 40 | 47 | 11 | 0 | 0 | 88 | 105 | 0.1 | 0 | 9 | 0 |  | 391 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 173 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 14 | 3 | 0 | 68 | 290 | 0 | 0 | 173 | 0 | 0 | 0 | 41 | 0 | 161 | 0 | 332 | 17 | 0 | 35 | 17 | 50 | 0 | 0.1 | 22 |  | 5322 | 2143.1 | 7465.1 | 3505 | 391 | 1730 | 1223 | 358 | 90 | 45 | 122 | 1.1 | 0 | 102.42
18:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 324 | 345 |  | 0 | 430 | 230 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 69 | 0 | 47 | 17 | 55 | 55 | 22 | 25 | 19 | 33 | 29 | 0 | 0 | 41 | 50 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 51 | 100 | 85 | 50 | 19 | 8 | 80 | 100 | 0 | 315 | 0 | 181 | 112 | 126 | 33 | 10 | 0 | 35 | 0 | 0 | 8 | 19 | 8 | 33 | 0 | 150 | 145 | 40 | 22 | 0 | 60 | 22 | 53 | 33 | 163 | 100 | 66 | 78 | 40 | 0 | 18 | 31 | 10 | 270 | 24 | 11 | 0 | 95 | 0 | 0 | 102 | 0 | 15 | 0 | 40 | 105 | 50 | 0 | 0 | 88 | 105 | 0 | 0 | 17 | 0 |  | 928 | 0 | 275 | 0 | 16 | 0 | 0 | 0 | 41 | 0 | 40 | 174 | 20 | 16 | 0 | 50 | 0 | 0 | 0 | 50 | 12 | 8 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 69 | 290 | 0 | 0 | 165 | 0 | 0 | 0 | 91 | 0 | 165 | 0 | 367 | 45 | 0 | 45 | 23 | 70 | 0 | 0 | 0 |  | 6208 | 3001 | 9209 | 3691 | 928 | 2132 | 1700 | 359 | 91 | 158 | 150 | 0 | 0 | 102.42
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 199 | 0 | 350 | 0 | 0 | 342 | 357 |  | 0 | 430 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 47 | 0 | 35 | 17 | 22 | 25 | 30 | 33 | 29 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 206 | 0 | 134 | 0 |  | 0 | 0 | 51 | 100 | 97 | 50 | 19 | 10 | 80 | 100 | 0 | 320 | 0 | 191 | 112 | 126 | 30 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 150 | 145 | 0 | 22 | 0 | 60 | 22 | 28 | 47 | 163 | 99 | 66 | 78 | 40 | 0 | 18 | 36 | 10 | 280 | 24 | 11 | 0 | 143 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 130 | 10 | 0 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 929 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 45 | 0 | 0 | 174 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 70 | 290 | 0 | 17 | 182 | 0 | 0 | 0 | 97 | 0 | 190 | 0 | 394 | 70 | 0 | 72 | 50 | 70 | 0 | 0 | 0 |  | 6177 | 3105 | 9282 | 3757 | 929 | 2226 | 1655 | 360 | 92 | 113 | 150 | 0 | 0 | 102.42
19:30 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 361 | 358 |  | 0 | 430 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 47 | 0 | 17 | 17 | 22 | 25 | 21 | 33 | 29 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 217 | 0 | 135 | 0 |  | 0 | 0 | 51 | 100 | 97 | 18 | 19 | 17 | 80 | 100 | 0 | 335 | 0 | 197 | 112 | 126 | 30 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 146 | 145 | 0 | 22 | 0 | 60 | 22 | 28 | 47 | 163 | 101 | 66 | 78 | 40 | 0 | 18 | 35 | 10 | 315 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 50 | 10 | 0 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 928 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 69 | 290 | 0 | 17 | 192 | 0 | 0 | 0 | 96 | 0 | 198 | 0 | 394 | 70 | 0 | 74 | 50 | 70 | 0 | 0 | 0 |  | 6097 | 3066 | 9163 | 3826 | 928 | 2267 | 1477 | 359 | 92 | 68 | 146 | 0 | 0 | 0
20:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 358 | 358 |  | 0 | 430 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 46 | 0 | 17 | 17 | 22 | 25 | 21 | 33 | 29 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 207 | 0 | 135 | 0 |  | 0 | 0 | 51 | 100 | 97 | 18 | 19 | 20 | 60 | 100 | 0 | 335 | 0 | 188 | 112 | 126 | 30 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 148 | 143 | 0 | 22 | 0 | 59 | 22 | 28 | 47 | 163 | 101 | 66 | 78 | 40 | 0 | 18 | 35 | 10 | 305 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 75 | 10 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 929 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 69 | 290 | 0 | 17 | 196 | 0 | 0 | 0 | 96 | 0 | 198 | 0 | 394 | 70 | 0 | 74 | 33 | 70 | 0 | 0 | 0 |  | 6054 | 3070 | 9124 | 3785 | 929 | 2260 | 1483 | 359 | 92 | 68 | 148 | 0 | 0 | 102.41
21:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 359 |  | 0 | 430 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 31 | 0 | 0 | 43 | 50 | 100 | 0 | 0 | 204 | 0 | 133 | 0 |  | 0 | 0 | 51 | 90 | 97 | 18 | 19 | 28 | 60 | 100 | 0 | 320 | 0 | 181 | 112 | 126 | 30 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 146 | 145 | 0 | 22 | 0 | 59 | 22 | 53 | 47 | 163 | 102 | 66 | 78 | 40 | 0 | 18 | 35 | 10 | 290 | 24 | 11 | 0 | 132 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 50 | 10 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 927 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 68 | 291 | 0 | 17 | 190 | 0 | 0 | 0 | 94 | 0 | 198 | 0 | 430 | 70 | 0 | 74 | 33 | 35 | 0 | 0 | 0 |  | 5935 | 3010 | 8945 | 3728 | 927 | 2313 | 1311 | 359 | 93 | 68 | 146 | 0 | 0 | 102.41
22:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 342 | 359 |  | 0 | 430 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 31 | 0 | 0 | 43 | 50 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 51 | 90 | 97 | 18 | 19 | 38 | 60 | 100 | 0 | 320 | 0 | 179 | 112 | 122 | 33 | 48 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 140 | 147 | 0 | 22 | 0 | 60 | 22 | 53 | 47 | 130 | 99 | 67 | 78 | 40 | 0 | 18 | 35 | 10 | 275 | 24 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 926 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 67 | 290 | 0 | 0 | 184 | 0 | 0 | 0 | 95 | 0 | 192 | 0 | 383 | 35 | 0 | 35 | 33 | 0 | 0 | 0 | 0 |  | 5744 | 2759 | 8503 | 3722 | 926 | 2227 | 987 | 357 | 93 | 51 | 140 | 0 | 0 | 102.41
23:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 341 | 362 |  | 0 | 430 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 31 | 0 | 0 | 44 | 50 | 100 | 0 | 0 | 204 | 0 | 109 | 0 |  | 0 | 0 | 51 | 90 | 51 | 18 | 19 | 40 | 60 | 100 | 0 | 320 | 0 | 179 | 112 | 126 | 33 | 47 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 17 | 134 | 159 | 0 | 22 | 0 | 60 | 22 | 5 | 5 | 100 | 101 | 67 | 40 | 40 | 0 | 18 | 8 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 925 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 5 | 0 | 66 | 281 | 0 | 0 | 181 | 0 | 0 | 0 | 96 | 0 | 191 | 0 | 398 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 |  | 5210 | 2674 | 7884 | 3687 | 925 | 2008 | 638 | 347 | 94 | 51 | 134 | 0 | 0 | 102.41
24:00 | 35 | 0 | 148 | 0 | 350 | 0 | 0 | 343 | 362 |  | 0 | 430 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 44 | 50 | 100 | 0 | 0 | 204 | 0 | 109 | 0 |  | 0 | 0 | 51 | 70 | 30 | 18 | 19 | 41 | 60 | 100 | 0 | 320 | 0 | 180 | 112 | 122 | 33 | 50 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 17 | 128 | 159 | 0 | 0 | 0 | 60 | 22 | 5 | 5 | 100 | 101 | 40 | 5 | 5 | 0 | 0 | 8 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 926 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 66 | 280 | 0 | 0 | 183 | 0 | 0 | 0 | 83 | 0 | 190 | 0 | 378 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 4915 | 2608 | 7523 | 3540 | 926 | 1902 | 536 | 346 | 94 | 51 | 128 | 0 | 0 | 102.41
KWH | 805000 | 0 | 3612000 | 0 | 7438009 | 0 | 0 | 6196230 | 7542000 |  | 0 | 8979625 | 5899375 | 47040 | 0 | 191172 | 0 | 0 | 0 | 0 | 26880 | 0 | 31200 | 0 | 477120 | 0 | 504528 | 79200 | 149659 | 138836 | 357732 | 600000 | 653760 | 440700 | 758100 | 0 | 0 | 1210936 | 656000 | 2300000 | 0 | 0 | 4969430 | 0 | 3030676 | 0 |  | 0 | 0 | 447150 | 738360 | 691200 | 387360 | 428160 | 456000 | 1660848 | 2384695 | 0 | 7686000 | 0 | 4422000 | 1572363 | 2976960 | 528264 | 653280 | 0 | 469704 | 0 | 0 | 10469 | 339516 | 132300 | 450600 | 324680 | 2805100 | 3263080 | 64320 | 312696 | 5150 | 1005000 | 977679 | 462000 | 533376 | 3151857 | 1931000 | 1227264 | 843840 | 600480 | 0 | 207000 | 413820 | 113220 | 7298700 | 247656 | 207696 | 0 | 853091 | 0 | 0 | 1137600 | 0 | 34560 | 118935 | 133440 | 451200 | 185434 | 0 | 0 | 712980 | 1416799 | 28440 | 0 | 31928 | 0 |  | 13365818 | 0 | 7261344 | 0 | 47040 | 0 | 0 | 0 | 94080 | 0 | 89250 | 4045225 | 393400 | 68160 | 0 | 639300 | 0 | 52559 | 0 | 50428 | 151840 | 19902 | 0 | 12480 | 0 | 308880 | 158400 | 67320 | 0 | 1656000 | 6363100 | 0 | 49000 | 4483173 | 0 | 0 | 0 | 1194319 | 0 | 4366309 | 0 | 9210870 | 1211040 | 0 | 513080 | 230112 | 316800 | 0 | 36275 | 264960 |  | 114630458 | 56720464 | 171350922 | 82737402 | 13365818 | 44356134 | 17287215 | 8019100 | 1866936 | 724417 | 2805100 | 188800 | 0
Fuel Cost | 901600 | 0 | 3864840 | 0 | 5504126.66 | 0 | 0 | 4461285.6 | 5731920 |  | 0 | 7183700 | 5309437.5 | 479808 | 0 | 1961424.72 | 0 | 0 | 0 | 0 | 298368 | 0 | 309192 | 0 | 4341792 | 0 | 4722382.08 | 759528 | 1427746.86 | 1382806.56 | 268299 | 450000 | 0 | 0 | 0 | 0 | 0 | 314843.36 | 170560 | 3519000 | 0 | 0 | 5217901.5 | 0 | 3848958.52 | 0 |  | 0 | 0 | 4690603.5 | 7597724.4 | 6573312 | 3625689.6 | 393907.2 | 1267680 | 1743890.4 | 2503929.75 | 0 | 5687640 | 0 | 4068240 | 1540915.74 | 3959356.8 | 433176.48 | 672878.4 | 0 | 671676.72 | 0 | 0 | 98408.6 | 346306.32 | 99225 | 851634 | 243510 | 19355190 | 2675725.6 | 611683.2 | 318949.92 | 84460 | 1366800 | 1329643.44 | 628320 | 666720 | 3908302.68 | 1776520 | 1828623.36 | 1485158.4 | 666532.8 | 0 | 329130 | 484169.4 | 266067 | 5182077 | 185742 | 157848.96 | 0 | 8931862.77 | 0 | 0 | 10943712 | 0 | 348710.4 | 1372509.9 | 1243660.8 | 4232256 | 1737516.58 | 0 | 0 | 6352651.8 | 13388750.55 | 0 | 0 | 0 | 0 |  | 36087708.6 | 0 | 5663848.32 | 0 | 453465.6 | 0 | 0 | 0 | 1091328 | 0 | 882682.5 | 3236180 | 609770 | 732038.4 | 0 | 1201884 | 0 | 585507.26 | 0 | 499237.2 | 1574580.8 | 233052.42 | 0 | 124300.8 | 0 | 339768 | 261360 | 50961.24 | 0 | 10548720 | 26025079 | 0 | 1383270 | 3945192.24 | 0 | 0 | 0 | 1898967.21 | 0 | 3842351.92 | 0 | 6723935.1 | 11456438.4 | 0 | 4710074.4 | 2050297.92 | 2958912 | 0 | 0 | 0 |  | 201358519.83 | 129170911.33 | 330529431.16 | 76276228.23 | 36087708.6 | 40189918.45 | 111545075.66 | 36573799 | 485403.36 | 8559137.96 | 19355190 | 1456969.9 | 0
Yesterday Day Peak | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 52 | 357 |  | 0 | 430 | 260 | 12 | 0 | 9 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 22 | 25 | 28 | 25 | 29 | 0 | 0 | 32 | 50 | 100 | 0 | 0 | 204 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 4 | 80 | 100 | 0 | 370 | 0 | 202 | 112 | 127 | 33 | 45 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 120 | 156 | 0 | 22 | 1 | 60 | 22 | 32 | 18 | 130 | 98 | 65 | 5 | 40 | 0 | 0 | 28 | 9 | 315 | 0 | 2 | 0 | 30 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 34 | 68 | 4.1 | 0 | 0 | 0 |  | 390 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 13 | 0 | 0 | 50 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 67 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 57 | 0 | 205 | 0 | 432 | 109 | 0 | 0 | 0 | 0 | 0 | 5.3 | 26 |  | 7227.4 | DayPeak
Yesterday Evening Peak | 35 | 0 | 199 | 0 | 350 | 0 | 0 | 342 | 357 | 0 | 0 | 430 | 230 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 47 | 0 | 35 | 17 | 22 | 25 | 30 | 33 | 29 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 206 | 0 | 134 | 0 | 0 | 0 | 0 | 51 | 100 | 97 | 50 | 19 | 10 | 80 | 100 | 0 | 320 | 0 | 191 | 112 | 126 | 30 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 150 | 145 | 0 | 22 | 0 | 60 | 22 | 28 | 47 | 163 | 99 | 66 | 78 | 40 | 0 | 18 | 36 | 10 | 280 | 24 | 11 | 0 | 143 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 130 | 10 | 0 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 929 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 45 | 0 | 0 | 174 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 70 | 290 | 0 | 17 | 182 | 0 | 0 | 0 | 97 | 0 | 190 | 0 | 394 | 70 | 0 | 72 | 50 | 70 | 0 | 0 | 0 |  | 9282 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 230 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 50 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 96 | 50 | 22 | 30 | 100 | 0 | 0 | 360 | 360 | 225 | 112 | 141 | 33 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 169 | 160 | 95 | 22 | 0 | 60 | 72 | 51 | 50 | 163 | 100 | 68 | 79 | 40 | 0 | 20 | 41 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 88 | 100 | 0 | 260 | 54 | 110 |  | 944 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 33 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 35 | 22 | 12 | 11 | 0 | 68 | 280 | 17 | 17 | 225 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 230 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 45 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 50 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 95 | 50 | 22 | 10 | 100 | 0 | 0 | 360 | 360 | 225 | 112 | 140 | 33 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 129 | 160 | 95 | 22 | 1.6 | 60 | 72 | 51 | 50 | 163 | 100 | 68 | 76 | 40 | 0 | 20 | 41 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 88 | 0 | 4.4 | 230 | 54 | 110 |  | 944 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 12 | 11 | 0 | 68 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 280 | 0 | 0 | 377 | 263 | 0 | 0 | 340 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 29 | 33 | 0 | 0 | 43 | 50 | 100 | 0 | 0 | 217 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 4 | 60 | 100 | 0 | 295 | 135 | 201 | 8 | 126 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 12 | 94 | 124 | 0 | 0 | 0.4 | 59 | 22 | 5 | 5 | 130 | 108 | 40 | 5 | 5 | 0 | 0 | 8 | 0 | 320 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.94 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 1.42 | 0 | 0 | 0 | 0 | 637 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 68 | 280 | 0 | 0 | 178 | 0 | 0 | 0 | 11 | 0 | 178 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0
199
| Minimum Generation |  | 5208 | 5:00
| Highest Generation |  | 9282 | 19:00
| Day Peak Generation |  | 7227.4 | 12:00
| Evening Peak Generation |  | 9282 | 19:00
| HVDC Max Flow |  | 929 | 19:00
| HVDC EvPeak Flow |  | 929 | 19:00
| Load factor L.F |  | 76.92%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7227.4 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 6192.91 | MW
Evening Peak Generation : |  | 9282 | MW Hour : | 19:00 | Available Max Generation : |  | 14624 | MW
E.P. Demand (at gen end) : |  | 9282 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 9282 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4124 | MW
Total Gen. (MKWH) : |  | 171.3509 | System Load Factor : | 76.92% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 242 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-27
Actual : | 102.37 | Ft.(MSL) , | Rule curve : | 108.5 | Ft.( MSL )
Gas Consumed : | Total = | 1109.88 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 116466146.68
: |  | Coal : | 36573799 | Oil : | 120104213.62 | Total : | 273144159.3
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3725.7124 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1265.3372 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1133.4131 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1024.0324 |  |  | 0 | 0%
) | 0 | 0:00 | 925.4595 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 746.809 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 419.6522 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 192.3381 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 575.9663 |  |  | 0 | 0%
Total | 0 |  | 10008.7202 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-1,3 & 5
4) Sirajganj 225 MW Unit-2
5) Raozan #2
6) Siddirganj-335 MW
7) Ashuganj unit-4
8) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Joydebpur 132/33 kV T2 transformer was under shut down from 08:43 to 14:56 for A/M.
b) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 09:03 to 12:28 for A/M.
c) Aminbazar-Hasnabad 230 kV Ckt-1 was under shut down from 09:17 to 20:16 for A/M.
d) Rangpur 132/33 kV T1 transformer was shut down at 08:25 for D/W.
e) Barishal(N) 132/33 kV T4 transformer and its 33 kV bus was under shut down from 09:42 to 17:07 for |  |  |  |  | About 30 MW power interruption occurred under Barishal(N) S/S area
A/M. |  |  |  |  | from 09:42 to 17:07.
f) Magura 132/33 kV T2 transformer tripped at 11:21 showing differential oil temperature protection and
was switched on at 12:10.
g) Khulna(S) 230/132 kV T02 transformer was under shut down from 10:55 to 11:28 for oil refill on auxiliary.
h) Shahjadpur 132/33 kV T1 transformer was under shut down from 10:20 to 11:33 for work on NGR |  |  |  |  | About 16 MW power interruption occurred under Shahjadpur S/S area
problem. |  |  |  |  | from 10:20 to 11:33.
i) Baghabari 100 MW GT tripped at 12:43 due to low gas pressure.
j) Mohastangor 132/33 T2 transformer was under shut down from 10:05 to 16:26 for A/M.
k) Haripur 412 MW EGCB ST was synchronized at 14:18.
l) Barapukuria 132/33 kV T3 transformer was under shut down from 21:19 to 22:50 due to R/H at 33 kV
isolator Y-phase.
m) After maintenance Ashuganj(S) CCPP GT was synchronized at 22:51.
n) Chandraghona-Madunaghat 132 kV Ckt-2 was shut down at 07:18(27/10/2019) for A/M.
o) Sikalbaha(New)-Sikalbaha(Old) 132 kV Ckt-1 was shut down at 07:42(27/10/2019) for C/M.
p) Sikalbaha(Old) 132 kV bus-A was shut down at 07:42(27/10/2019) for C/M.
q) Barishal(N) 132/33 kV T4 transformer was shut down at 07:42(27/10/2019) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 805000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 199 | 3612000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 7438009
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 6196230 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 357 | 7542000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 430 | 8979625 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 47040 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 5899375 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 191172 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 357732
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 26880 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 504528
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 79200 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 31200 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 149659 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 138836 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 68 | 477120 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1253760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 440700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 758100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 143 | 853091 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 34560 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 712980 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 2495 | 46528797
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 118935
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 387360
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 1866936 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 206 | 4969430
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 134 | 3030676 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1416799
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 447150 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 738360
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 133440 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 428160
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 456000
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 691200 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 31928 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 974 | 17044814
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1660848 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2384695 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4422000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7686000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 528264 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 653280
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 112 | 1572363 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 469704 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 185434 | Low demand
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 126 | 2976960
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 130 | 451200 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 339516
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 132300 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 2805100
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 450600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 10469 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 324680 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1409 | 27053413
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3263080 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 312696
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 64320 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 1137600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 317 | 4782846
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1005000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 977679
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3151857
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 99 | 1931000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 28 | 462000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 533376
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 207696
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1227264 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 843840 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 600480 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 207000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 36 | 413820 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 247656
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7298700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 113220
| Sylhet Area Total |  |  |  | 1949 | 982 | 19220588
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 929 | 13365818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 47040 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 45 | 94080
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 290 | 7261344 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 89250 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1211040 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 230112 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1400 | 22298684
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 68160 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 23 | 393400 | Machine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 174 | 4045225 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1194319
| Barisal Area Total |  |  |  | 462 | 326 | 5701104
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 639300 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 52559 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 151840
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 19902 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 182 | 4483173 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4366309 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 394 | 9210870 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 308880
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 158400
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 67320 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 12480 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 50428 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 72 | 513080 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 264960 | On test
| Rajshahi Area Total |  |  |  | 2183 | 932 | 20299501
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 70 | 1656000
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 290 | 6363100
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 49000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 316800 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36275
| Rangpur Area Total |  |  |  | 605 | 447 | 8421175
| Total |  |  |  | 19018 | 9282 | 171350922
| Eastern Grid Total |  |  |  | 13454 | 6177 | 114630458
| Western Grid Total |  |  |  | 5564 | 3105 | 56720464
| National Grid Total |  |  |  | 19018 | 9282 | 171350922
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-26
(a) ENTIRE EASTERN GRID : |  | 6174 | MW | (b) ENTIRE WESTERN GRID : |  | 2664 | MW
i) Dhaka area |  | 3340 | MW | i) Khulna area |  | 1046 | MW
ii) Chittagong area |  | 1092 | MW | ii) Rajshahi area |  | 810 | MW
iii) Comilla area |  | 822 | MW | iii) Barisal area |  | 264 | MW
iv) Mymensingh area |  | 579 | MW | iv) Rangpur area |  | 544 | MW
v) Sylhet area |  | 341 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8838 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1200 | Srimongal | 29 | 1800 | Bottail | 92 | 1800
Munsiganj | 88 | 2000 | Shahjibazar | 86 | 2100 | G.K Project | 39 | 1800
Sonargaon | 65 | 1700 | Fenchuganj | 27 | 1800 | Faridpur | 130 | 1830
Shyampur | 176 | 1300 | Kulawara | 31 | 19* | Madaripur | 68 | 2000
Bhulta | 163 | 1100 | Sylhet | 95 | 1800 | Sariatpur | 44 | 2000
Madanganj | 54 | 1900 | Chatak | 21 | 1900 | Gopalganj | 70 | 1830
Shitalakhya | 102 | 1700 | Sunamganj | 28 | 1800 | Bagerhat | 70 | 1800
Rahim steel | 21 | 900 | Biani Bazar | 37 | 1830 | Mongla | 30 | 900
Matuail | 54 | 1300 | Comilla (S) | 150 | 1800 | Satkhira | 70 | 1800
Ghorasal | 68 | 1900 | Comilla(N) | 97 | 1800 | Gallamari | 40 | 1300
Narsingdi | 120 | 1900 | Chandpur | 74 | 1930 | Magura | 36 | 1800
Haripur (SBU) | 87 | 1900 | Feni | 110 | 1900 | Norail | 17 | 1830
Ullon | 71 | 1400 | Chowmuhani | 128 | 1800 | Chuadanga | 60 | 1800
Hasnabad | 160 | 1800 | Ashuganj | 44 | 2000 | Barisal(N) | 32 | 2000
Magbazar | 84 | 1800 | Daudkandi | 96 | 1930 | Barisal (S) | 80 | 1830
Maniknagar | 88 | 1800 | B.Baria | 104 | 1930 | Patuakhali | 83 | 1900
Bangabhaban | 10 | 1100 | Ramganj | 66 | 1830 | Bhandaria | 44 | 2000
Narinda | 78 | 1900 | Madunaghat | 62 | 1400 | Borhan Uddin | 32 | 2100
Dhanmondi | 117 | 1800 | Hathazari | 91 | 1800 | Ishurdi | 46 | 1830
Lalbag | 75 | 1800 | Khulshi | 200 | 1800 | Ruppur Paromanobik | 1 | 100
Madartek | 46 | 1830 | Halishahar | 144 | 1800 | Natore | 82 | 1930
Mirpur | 85 | 1800 | Baraulia | 144 | 900 | Bogra | 142 | 1800
Kalyanpur | 81 | 1800 | Sikalbaha | 30 | 1900 | Noagaon | 75 | 2000
Gulshan | 102 | 1800 | Dohazari | 87 | 2100 | Rajshahi | 92 | 1900
Uttara | 45 | 1800 | Cox'sbazar | 93 | 1800 | Rajshahi New | 9 | 2000
Uttara New | 30 | 1830 | Chandraghona | 30 | 2000 | C.Nawabganj | 50 | 1930
Kamrangirchar | 60 | 1300 | Kaptai | 5 | 1800 | Amnura | 22 | 1830
Savar | 111 | 1800 | A. Khaer Stl. | 7 | 1600 | Pabna | 72 | 1930
Bhasantec | 120 | 1800 | Bakulia | 111 | 1830 | Shahjadpur | 66 | 1800
Agargaon | 40 | 1800 | Julda | 20 | 1300 | Serajganj | 65 | 1930
Satmosjid | 87 | 1800 | TK chemical | 18 | 1830 | Niyamatpur | 41 | 1930
Tongi | 122 | 1800 | Modern Steel | 11 | 1100 | Joypurhat | 41 | 2000
Kabirpur | 170 | 1800 | Shahmirpur | 25 | 100 | Sherpur(Bogura) | 33 | 1800
Basundhara | 85 | 1800 | Khagrachhari | 16 | 1800 | Mohastangor | 7 | 800
Manikganj | 66 | 1800 | Matarbari | 29 | 1930 | Rangpur | 101 | 1800
Joydevpur | 171 | 1800 | Baroiar Hat | 22 | 1800 | Lalmonirhat | 45 | 1800
New Tongi | 88 | 1830 | Rangamati | 12 | 1800 | Saidpur | 81 | 1800
Korda | 212 | 1800 | Abul Khair 230 | 5 | 800 | Purbasadipur | 77 | 1900
Dhamrai | 44 | 1800 | BSRM | 104 | 100 | Thakurgaon | 55 | 1930
Valuka | 80 | 2000 | GPH Ispat | 0 | 0 | Palashbari | 75 | 1830
Tangail | 134 | 2000 | Goalpara | 9 | 1300 | Barapukuria | 42 | 1800
Mymensing | 145 | 1800 | Central s/s | 11 | 1800 | Panchagar | 38 | 1800
Kishorganj | 82 | 2000 | Noapara | 87 | 1830 | Joldhaka | 20 | 1830
Netrokona | 64 | 1900 | Jessore | 58 | 1800 | Kurigram | 36 | 1800
Jamalpur | 87 | 2000 | Benapol | 84 | 1830
Sherpur | 70 | 1930 | Jhenida | 74 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-26 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 393 | 4:00 | 382 | 11:00 | Kaliakoir | 376 | 4:00 | 362 | 11:00
Bheramara | 407 | 3:00 | 389 | 18:30 | Bhulta | 377 | 2:00 | 367 | 15:00
Ashuganj(N) | 380 | 2:00 | 372 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal | 230 | 7:00 | 222 | 11:00 | Hathazari | 217 | 8:00 | 211 | 12:00
Ishurdi | 236 | 2:00 | 227 | 19:30 | Megnaghat | 223 | 3:00 | 215 | 13:00
Ashuganj | 230 | 7:00 | 225 | 9:00 | Fenchuganj | 237 | 3:00 | 231 | 9:00
Serajganj | 232 | 3:00 | 230 | 1:00 | Siddhirganj | 224 | 4:00 | 214 | 12:00
Baghabari | 237 | 1:00 | 232 | 21:00 | Maniknagar | 222 | 4:00 | 212 | 12:00
Barapukuria | 233 | 3:00 | 226 | 18:00 | Old Airport | 223 | 4:00 | 212 | 12:00
Bogra | 233 | 4:00 | 228 | 18:00 | Barisal | 233 | 3:00 | 222 | 18:00
Khulna South | 238 | 2:00 | 215 | 18:30 | AKSML | 215 | 17:00 | 208 | 12:00
Rampura | 222 | 4:00 | 215 | 12:00 | BSRM | 217 | 2:00 | 209 | 16:00
Haripur | 221 | 4:00 | 214 | 12:00 | Bibiyana | 234 | 6:00 | 227 | 24:00
Hasnabad | 222 | 3:00 | 212 | 12:00 | Bhulta | 225 | 2:00 | 215 | 12:00
Aminbazar | 223 | 4:00 | 213 | 12:00 | Ashuganj (S) | 229 | 17:00 | 223 | 10:00
Tongi | 222 | 6:00 | 210 | 9:00 | Kaliakoir | 227 | 3:00 | 216 | 14:00
Comilla (N) | 228 | 7:00 | 220 | 12:00 | GPH | 213 | 3:00 | 207 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 1500 | 131 | 100 | Halishahar | 129 | 1800 | 125 | 800
Munsiganj | 134 | 1800 | 128 | 300 | Baraulia | 128 | 400 | 124 | 1200
Megnaghat | 131 | 1300 | 128 | 100 | Sikalbaha | 129 | 700 | 125 | 2200
Shyampur | 136 | 1900 | 132 | 400 | Dohazari | 127 | 800 | 122 | 2100
Bhulta | 128 | 1300 | 125 | 100 | Cox'sbazar | 124 | 800 | 111 | 2000
Madanganj | 132 | 100 | 129 | 1000 | Chandraghona | 130 | 800 | 125 | 2200
Shitalakhya | 137 | 1800 | 134 | 100 | Kaptai | 130 | 100 | 127 | 2000
Rahim steal | 134 | 1300 | 130 | 100 | A. Khaer Stl. | 127 | 900 | 125 | 300
Matuail | 133 | 1300 | 130 | 100 | Bakulia | 128 | 800 | 123 | 2200
Ghorasal | 137 | 1800 | 135 | 100 | Julda | 129 | 700 | 124 | 1400
Narsinghdi | 134 | 1500 | 130 | 100 | TK Chemical | 128 | 800 | 127 | 100
Haripur (SBU) | 135 | 1930 | 130 | 400 | Modern Steel | 131 | 600 | 124 | 500
Ullon | 137 | 700 | 135 | 1200 | Shahmirpur | 129 | 700 | 124 | 1600
Hasnabad | 136 | 1300 | 134 | 100 | Khagrachhari | 129 | 800 | 125 | 1600
Magbazar | 137 | 600 | 135 | 1200 | Matarbari | 124 | 900 | 114 | 2200
Maniknagar | 138 | 800 | 134 | 1500 | Baroiar Hat | 128 | 700 | 124 | 2100
Bangabhaban | 138 | 800 | 134 | 1500 | Rangamati | 129 | 800 | 126 | 1200
Narinda | 138 | 800 | 134 | 1500 | Goalpara | 139 | 1400 | 128 | 1830
Dhanmondi | 137 | 700 | 135 | 1200 | Central s/s | 137 | 600 | 127 | 1830
Lalbag | 136 | 1800 | 132 | 100 | Noapara | 136 | 600 | 126 | 1830
Madartek | 137 | 700 | 135 | 1200 | Jessore | 134 | 1400 | 120 | 1830
Mirpur | 134 | 100 | 132 | 1200 | Benapol | 135 | 600 | 124 | 1830
Kalyanpur | 138 | 300 | 135 | 1100 | Jhenida | 135 | 200 | 124 | 1830
Gulshan | 136 | 400 | 134 | 1700 | Bottail | 138 | 500 | 131 | 1830
Uttara | 135 | 500 | 131 | 1100 | G.K Project | 142 | 300 | 137 | 1830
Uttara New | 135 | 600 | 130 | 1000 | Faridpur | 134 | 500 | 127 | 1930
Kamrangirchar | 135 | 500 | 133 | 1200 | Madaripur | 135 | 1400 | 129 | 100
Savar | 136 | 500 | 130 | 1100 | Sariatpur | 133 | 700 | 129 | 100
Bhasantec | 136 | 600 | 134 | 1300 | Gopalganj | 135 | 600 | 130 | 100
Agargaon | 137 | 200 | 135 | 1100 | Bagerhat | 135 | 400 | 126 | 1830
Satmosjid | 137 | 500 | 134 | 1100 | Mongla | 134 | 1100 | 125 | 1900
Tongi | 132 | 1300 | 130 | 1930 | Satkhira | 134 | 600 | 126 | 1830
Kabirpur | 137 | 1900 | 124 | 900 | Gallamari | 138 | 1400 | 127 | 1830
Basundhara | 131 | 1500 | 128 | 1000 | Magura | 135 | 500 | 123 | 1830
Manikganj | 135 | 1900 | 130 | 1930 | Norail | 134 | 600 | 122 | 1830
Joydevpur | 137 | 1800 | 133 | 300 | Chuadanga | 133 | 300 | 120 | 1830
New Tongi | 133 | 1900 | 128 | 1930 | Barisal(N) | 137 | 1400 | 131 | 1930
Kodda | 130 | 1900 | 123 | 1930 | Barisal (S) | 136 | 1500 | 130 | 1930
Dhamrai | 135 | 1800 | 132 | 1000 | Patuakhali | 137 | 1500 | 130 | 100
Valuka | 133 | 1900 | 124 | 1200 | Bhandaria | 137 | 1400 | 129 | 1830
Tangail | 135 | 600 | 130 | 1000 | Ishurdi | 140 | 200 | 135 | 1800
Mymensing | 137 | 1900 | 127 | 1200 | Ruppur Paromanobik | 140 | 100 | 135 | 1830
Kishorganj | 135 | 1930 | 130 | 900 | Natore | 138 | 200 | 132 | 1900
Netrokona | 136 | 1900 | 129 | 100 | Bogra | 140 | 500 | 133 | 1900
Jamalpur | 136 | 1900 | 124 | 1200 | Noagaon | 136 | 500 | 130 | 1800
Sherpur | 138 | 1900 | 123 | 1200 | Rajshahi | 134 | 1800 | 129 | 1930
Srimongal | 140 | 1900 | 134 | 100 | Rajshahi New | 134 | 200 | 129 | 1930
Shahjibazar | 139 | 1900 | 133 | 300 | C.Nawabganj | 133 | 1800 | 127 | 900
Fenchuganj | 136 | 1900 | 132 | 1100 | Amnura | 136 | 1800 | 128 | 800
Khulawara | 136 | 1830 | 132 | 100 | Pabna | 140 | 100 | 134 | 1830
Sylhet | 134 | 1800 | 130 | 1100 | Shahjadpur | 143 | 1500 | 140 | 1300
Chatak | 134 | 1900 | 130 | 1600 | Serajganj | 138 | 300 | 134 | 1830
Sunamganj | 132 | 1800 | 129 | 100 | Niyamatpur | 136 | 700 | 129 | 1800
Biani Bazar | 133 | 1800 | 130 | 100 | Joypurhat | 139 | 600 | 131 | 1830
Comilla(s) | 127 | 600 | 122 | 1800 | Sherpur(Bogura) | 139 | 500 | 133 | 1830
Comilla(n) | 134 | 900 | 132 | 1600 | Mohastangor | 139 | 500 | 130 | 1830
Chandpur | 131 | 300 | 128 | 2200 | Rangpur | 131 | 1500 | 123 | 100
Feni | 128 | 900 | 123 | 2300 | Lalmonirhat | 128 | 1500 | 120 | 1830
Chowmuhani | 125 | 1000 | 121 | 1930 | Saidpur | 130 | 1500 | 124 | 1800
Ashuganj | 140 | 1900 | 135 | 100 | Purbasadipur | 131 | 500 | 123 | 1100
Daudkandi | 132 | 900 | 128 | 1930 | Thakurgaon | 128 | 1500 | 119 | 1800
B.Baria | 134 | 700 | 132 | 2200 | Palashbari | 138 | 500 | 125 | 1800
Ramganj | 126 | 800 | 122 | 1100 | Barapukuria | 132 | 1400 | 126 | 1830
Madanhat | 130 | 100 | 127 | 500 | Panchagar | 126 | 1500 | 114 | 1830
Hathazari | 131 | 800 | 126 | 1600 | Joldhaka | 130 | 1500 | 122 | 1900
Khulshi | 127 | 200 | 123 | 1200 | Kurigram | 130 | 900 | 121 | 1900
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 556 | 4915 | 2608 | 7523 |  |  |  | QF-LDC-12
0:30 | 608 | 4394.5 | 2339.5 | 6734 | Date: | 2019-10-26
1:00 | 660 | 3874 | 2071 | 5945
1:30 | 670 | 3921 | 1957 | 5878
2:00 | 680 | 3968 | 1843 | 5811
2:30 | 595 | 3893 | 1816.5 | 5709.5 | [5 empty] | Gen. at Eve. Peak | 9282 | 9666 MW (21:00 )
3:00 | 510 | 3818 | 1790 | 5608 | [6 empty] | 19:00
3:30 | 500 | 3713.5 | 1778 | 5491.5 | [5 empty] | Gen. at Day Peak | 7227.4 | 6456.31 MW (11:00 )
4:00 | 490 | 3609 | 1766 | 5375 | [6 empty] | 12:00
4:30 | 502 | 3526 | 1765.5 | 5291.5 | [5 empty] | Highest Generation | 9282
5:00 | 514 | 3443 | 1765 | 5208 | [6 empty] | 19:00
5:30 | 521 | 3441 | 1789.5 | 5230.5
6:00 | 528 | 3439 | 1814 | 5253
6:30 | 489 | 3499.55 | 1896.5 | 5396.05
7:00 | 450 | 3560.1 | 1979 | 5539.1
7:30 | 495 | 3660.44 | 2095.4 | 5755.84
8:00 | 540 | 3760.78 | 2211.8 | 5972.58
8:30 | 590 | 4010.94 | 2228.55 | 6239.49
9:00 | 640 | 4261.1 | 2245.3 | 6506.4
9:30 | 655 | 4326.95 | 2296.55 | 6623.5
10:00 | 670 | 4392.8 | 2347.8 | 6740.6
10:30 | 660 | 4468.35 | 2343.6 | 6811.95
11:00 | 650 | 4543.9 | 2339.4 | 6883.3
11:30 | 610 | 4694 | 2361.35 | 7055.35
12:00 | 570 | 4844.1 | 2383.3 | 7227.4
12:30 | 445 | 4978.85 | 2330.9 | 7309.75
13:00 | 320 | 5113.6 | 2278.5 | 7392.1
13:30 | 370 | 4990.6 | 2260.2 | 7250.8
14:00 | 420 | 4867.6 | 2241.9 | 7109.5
14:30 | 394 | 4960.05 | 2204.55 | 7164.6
15:00 | 368 | 5052.5 | 2167.2 | 7219.7
15:30 | 364 | 5090.05 | 2132.2 | 7222.25
16:00 | 360 | 5127.6 | 2097.2 | 7224.8
16:30 | 302 | 5224.8 | 2120.15 | 7344.95
17:00 | 244 | 5322 | 2143.1 | 7465.1
17:30 | 248 | 5765 | 2572.05 | 8337.05
18:00 | 252 | 6208 | 3001 | 9209
18:30 | 279 | 6192.5 | 3053 | 9245.5
19:00 | 306 | 6177 | 3105 | 9282
19:30 | 294 | 6097 | 3066 | 9163
20:00 | 276 | 6054 | 3070 | 9124 |  |  |  | Executive Engineer
20:30 | 303 | 5994.5 | 3040 | 9034.5 |  |  |  | Network Operation Division
21:00 | 330 | 5935 | 3010 | 8945
21:30 | 325 | 5839.5 | 2884.5 | 8724
22:00 | 320 | 5744 | 2759 | 8503 |  |  |  |  | Page 6 of 7
22:30 | 395 | 5477 | 2716.5 | 8193.5
23:00 | 470 | 5210 | 2674 | 7884
23:30 | 513 | 5062.5 | 2641 | 7703.5
24:00 | 556 | 4915 | 2608 | 7523
9666 MW (21:00 )
6456.31 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-26 |  | Energy | 171350922
[10 empty] | 2019-10-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3540 | 926 | 1902 | 536 | 346 | 94 | 51 | 0 | 128
0:30 | 3344 | 773 | 1627.5 | 426 | 321.5 | 83.5 | 42.5 | 0 | 116 | Date: | 2019-10-26
1:00 | 3148 | 620 | 1353 | 316 | 297 | 73 | 34 | 0 | 104
1:30 | 3197.5 | 505.5 | 1353 | 316 | 297 | 73 | 34 | 0 | 102 | [7 empty] | Total Energy | 171.3509 | Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
2:00 | 3247 | 391 | 1353 | 316 | 297 | 73 | 34 | 0 | 100 | [7 empty] | Energy not Served | 0
2:30 | 3201.5 | 391 | 1350 | 273 | 297 | 73.5 | 25.5 | 0 | 98 | [7 empty] | Energy Requirement | 171.3509
3:00 | 3156 | 391 | 1347 | 230 | 297 | 74 | 17 | 0 | 96
3:30 | 3056 | 391 | 1342 | 230 | 297 | 74 | 8.5 | 0 | 93 | [6 empty] | Shortage
4:00 | 2956 | 391 | 1337 | 230 | 297 | 74 | 0 | 0 | 90
4:30 | 2875 | 390.5 | 1335 | 230 | 297 | 75 | 0 | 0 | 89
5:00 | 2794 | 390 | 1333 | 230 | 297 | 76 | 0 | 0 | 88
5:30 | 2777.5 | 390.5 | 1371.5 | 230 | 297 | 76 | 0 | 0 | 88
6:00 | 2761 | 391 | 1410 | 230 | 297 | 76 | 0 | 0 | 88
6:30 | 2830.5 | 390.5 | 1432.5 | 280 | 298 | 76 | 0 | 0 | 87 |  |  |  |  | Coal
7:00 | 2900 | 390 | 1455 | 330 | 299 | 76 | 0 | 0 | 86
7:30 | 3044 | 390 | 1517 | 337.5 | 298 | 76.5 | 0 | 0 | 84 |  |  |  | Oil |  |  |  | ,
8:00 | 3188 | 390 | 1579 | 345 | 297 | 77 | 0 | 0 | 82
8:30 | 3365 | 390.5 | 1649.5 | 368.5 | 297 | 62 | 0 | 0 | 90
9:00 | 3542 | 391 | 1720 | 392 | 297 | 47 | 0 | 0 | 98
9:30 | 3591.5 | 391 | 1736 | 414 | 322 | 47 | 0 | 0 | 101
10:00 | 3641 | 391 | 1752 | 436 | 347 | 47 | 0 | 0 | 104
10:30 | 3645.5 | 391 | 1776 | 450.5 | 346.5 | 69.5 | 0 | 0 | 107
11:00 | 3650 | 391 | 1800 | 465 | 346 | 92 | 0 | 0 | 110
11:30 | 3618 | 390.5 | 1934 | 538.5 | 346.5 | 87 | 4.5 | 0 | 115
12:00 | 3586 | 390 | 2068 | 612 | 347 | 82 | 9 | 0 | 120
12:30 | 3518 | 390.5 | 2133.5 | 689 | 348.5 | 86 | 4.5 | 0 | 119
13:00 | 3450 | 391 | 2199 | 766 | 350 | 90 | 0 | 0 | 118
13:30 | 3450 | 391 | 2199 | 766 | 350 | 90 | 0 | 0 | 118
14:00 | 3450 | 391 | 2199 | 766 | 350 | 90 | 0 | 0 | 118
14:30 | 3440 | 391 | 2170.5 | 714.5 | 354.5 | 90 | 0 | 0 | 123
15:00 | 3430 | 391 | 2142 | 663 | 359 | 90 | 0 | 0 | 128
15:30 | 3540 | 391 | 2018 | 688 | 359 | 90 | 0 | 0 | 124
16:00 | 3650 | 391 | 1894 | 713 | 359 | 90 | 0 | 0 | 120
16:30 | 3577.5 | 391 | 1812 | 968 | 358.5 | 90 | 22.5 | 0 | 121
17:00 | 3505 | 391 | 1730 | 1223 | 358 | 90 | 45 | 0 | 122
17:30 | 3598 | 659.5 | 1931 | 1461.5 | 358.5 | 90.5 | 101.5 | 0 | 136
18:00 | 3691 | 928 | 2132 | 1700 | 359 | 91 | 158 | 0 | 150
18:30 | 3724 | 928.5 | 2179 | 1677.5 | 359.5 | 91.5 | 135.5 | 0 | 150
19:00 | 3757 | 929 | 2226 | 1655 | 360 | 92 | 113 | 0 | 150
19:30 | 3826 | 928 | 2267 | 1477 | 359 | 92 | 68 | 0 | 146
20:00 | 3785 | 929 | 2260 | 1483 | 359 | 92 | 68 | 0 | 148
20:30 | 3756.5 | 928 | 2286.5 | 1397 | 359 | 92.5 | 68 | 0 | 147
21:00 | 3728 | 927 | 2313 | 1311 | 359 | 93 | 68 | 0 | 146
21:30 | 3725 | 926.5 | 2270 | 1149 | 358 | 93 | 59.5 | 0 | 143
22:00 | 3722 | 926 | 2227 | 987 | 357 | 93 | 51 | 0 | 140
22:30 | 3704.5 | 925.5 | 2117.5 | 812.5 | 352 | 93.5 | 51 | 0 | 137
23:00 | 3687 | 925 | 2008 | 638 | 347 | 94 | 51 | 0 | 134
23:30 | 3613.5 | 925.5 | 1955 | 587 | 346.5 | 94 | 51 | 0 | 131 | Max Temp. in Dhaka |  | 26.8° C
24:00 | 3540 | 926 | 1902 | 536 | 346 | 94 | 51 | 0 | 128
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
Note on W13: Author:

## Generation
2019-10-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 73 | 73 | 74 | 74 | 76 | 76 | 76 | 77 | 47 | 47 | 42 | 32 | 40 | 40 | 40 | 40 | 40 | 41 |  | 42 | 42 | 42 | 43 | 43 | 44 | 44 | 1210936
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 656000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 8.5 | 12.1 | 12.4 | 17.3 | 3 | 14.5 | 16.8 | 12.5 | 6.1 | 0.9 | [9 empty] | 118935
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 218 | 204 | 217 | 219 | 229 | 205 | 205 | 204 | 205 | 204 | 205 | 211 | 204 | 204 |  | 206 | 217 | 207 | 204 | 204 | 204 | 204 | 4969430
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 145 | 146 | 147 | 80 | 100 | 114 | 120 | 127 | 114 | 134 | 134 | 143 | 141 | 140 | 140 | 140 | 104 | 134 |  | 134 | 135 | 135 | 133 | 134 | 109 | 109 | 3030676
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 17 | 0 | [12 empty] | 0 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 447150
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | [8 empty] | 22 | 68 | 80 | 85 | 103 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1416799
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 2 | 30 | 30 | 30 | 35 | 45 | 62 | 95 |  | 143 | 145 | 145 | 132 | 45 | 0 |  | 853091
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 35 | 63 | 112 | 112 | 112 | 105 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 1572363
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 805000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 101 | 101 | 101 | 101 | 98 | 100 | 100 | 100 | 100 | 100 | 150 | 200 | 201 | 200 | 200 | 200 | 200 |  | 199 | 200 | 200 | 200 | 200 | 200 | 148 | 3612000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 230 | 230 | 230 | 210 | 210 | 220 | 250 | 280 | 320 | 350 | 380 | 380 | 380 | 370 | 370 | 370 | 320 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 7438009
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 60 | 60 | 60 | 60 | 60 | 1660848
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384695
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 528264
33 | Ashuganj 225 MW CCPP | 161 | 161 | 160 | 160 | 180 | 162 | 182 | 183 | 199 | 193 | 184 | 202 | 179 | 180 | 181 | 198 | 180 | 181 |  | 191 | 197 | 188 | 181 | 179 | 179 | 180 | 4422000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 230 | 230 | 230 | 280 | 325 | 365 | 350 | 340 | 370 | 340 | 340 | 340 | 360 | 280 | 315 |  | 320 | 335 | 335 | 320 | 320 | 320 | 320 | 7686000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 45 | 44 | 44 | 45 | 10 | 10 | 10 |  | 50 | 50 | 50 | 50 | 48 | 47 | 50 | 653280
36 | Chandpur 150 MW CCPP | 121 | 127 | 121 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 126 | 126 | 126 | 126 | 121 | 126 |  | 126 | 126 | 126 | 126 | 122 | 126 | 122 | 2976960
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 207 | 290 | 294 | 295 | 225 | 205 | 205 | 230 | 279 | 287 | 280 | 52 | 28 | 63 | 120 | 300 | 300 | 324 |  | 342 | 361 | 358 | 345 | 342 | 341 | 343 | 6196230
40 | Meghnaghat 450 MW CCPP(MPL) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 360 | 400 | 400 | 400 | 430 | 430 | 360 | 360 | 360 | 360 | 430 |  | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 8979625
41 | Haripur 360MW CCPP(HPL) | 242 | 242 | 242 | 242 | 262 | 262 | 282 | 282 | 356 | 358 | 359 | 357 | 358 | 305 | 356 | 355 | 302 | 345 |  | 357 | 358 | 358 | 359 | 359 | 362 | 362 | 7542000
42 | RPCL 210MW CCPP | 161 | 161 | 124 | 105 | 104 | 104 | 104 | 105 | 159 | 159 | 155 | 156 | 136 | 127 | 126 | 144 | 145 | 145 |  | 145 | 145 | 143 | 145 | 147 | 159 | 159 | 3263080
43
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 60 | 60 | 60 | 59 | 60 | 60 | 60 |  | 60 | 60 | 59 | 59 | 60 | 60 | 60 | 1005000
45 | Fenchugonj CCPP Phase-2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 977679
46 | Shajibazar 330 MW CCPP | 100 | 100 | 100 | 100 | 20 | 20 | 20 | 20 | 100 | 96 | 97 | 98 | 95 | 98 | 100 | 105 | 101 | 100 |  | 99 | 101 | 101 | 102 | 99 | 101 | 101 | 1931000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 45 | 45 | 45 | 32 | 32 | 32 | 32 | 40 | 40 | 40 | 65 | 53 | 54 | 60 | 65 | 65 | 66 |  | 66 | 66 | 66 | 66 | 67 | 67 | 40 | 1227264
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 79 | 79 | 78 | 40 | 40 | 78 |  | 78 | 78 | 78 | 78 | 78 | 40 | 5 | 843840
49 | Shahjibazar 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 10 | 10 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 5 | 600480
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [12 empty] | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 207000
52 | Sylhet 50MW PP (EPL) | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 5 | 5 | 6 | 6 | 28 | 29 | 30 | 32 | 13 | 13 | 31 |  | 36 | 35 | 35 | 35 | 35 | 8 | 8 | 413820
53 | Sylhet 10MW PP (Desh) | [11 empty] | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 113220
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 8 | 8 | 8 | 2 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 207696
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 32 | 47 | 50 | 47 | 11 | 11 | 53 |  | 28 | 28 | 28 | 53 | 53 | 5 | 5 | 462000
56 | Shahjahanulla 25 MW PP | [12 empty] | 24 | 24 | 23 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 247656
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 275 | 270 | 260 | 270 | 300 | 300 | 325 | 320 | 315 | 310 | 315 | 280 | 270 | 300 | 290 | 290 | 270 |  | 280 | 315 | 305 | 290 | 275 | 270 | 290 | 7298700
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 17 | 55 | 55 |  | 17 | 17 | 17 |  |  |  | 0 | 138836
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 428160
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | [6 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 357732
62 | Tangail 22 MW PP (Doreen) | [8 empty] | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 312696
63 | Impoprt (Tripura) | 104 | 100 | 96 | 90 | 88 | 88 | 86 | 82 | 98 | 104 | 110 | 120 | 118 | 126 | 128 | 120 | 122 | 150 |  | 150 | 146 | 148 | 146 | 140 | 134 | 128 | 2805100
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 7 | 6 | 6 | 2 | 2 | 2 | 2 | 4 | 9 | 4 | 4 | 4 | 4 | 8 |  | 10 | 17 | 20 | 28 | 38 | 40 | 41 | 456000
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | [5 empty] | 13 | 16 | 16 | 19 | 16 | 16 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 339516
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | [7 empty] | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 132300
67 | Jangalia 33MW PP (Summit) | [9 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  | 0 | 450600
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 10 | 10 | 12 | 15 | 18 | 18 | 18 | 18 |  |  |  |  | 15 | 15 | 15 |  | 17 | 17 | 17 | 324680
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 25 | 25 | 0 |  | 30 | 19 |  | 30 | 21 | 21 | 30 | 30 | 31 | 31 | 653760
71 | Maona 33 MW PP(Summit) | [8 empty] | 0 |  | 23 | 25 | 30 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 440700
72 | Rupganj 33 MW PP(Summit) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 31 | 31 | 31 | 33 | 758100
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 10 | 14 | [12 empty] | 0 | 26880
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [16 empty] | 16 | 16 | [7 empty] | 0 | 31200
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 18 | 40 |  | 0 | 0 | [5 empty] | 64320
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 10469
| Gazipur 100 MW PP | [8 empty] | 34 | 35 | 35 | 34 | 35 | 35 | 52 | 52 | 88 | 88 |  | 88 | 52 | 35 | 35 | 35 | 35 | 35 | 712980
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 3.08 | 2.2 | 4.4 | 4.8 | 4.1 | 4.5 | 1.3 | 2.5 | 1.4 | 0.1 | 0 | [8 empty] | 28440
| Jodiac Power | [16 empty] | 9 | 17 | [7 empty] | 0 | 31928
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 260 | 260 | 260 | 260 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5899375
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 12 | 10 |  |  |  | 7 | 7 | [7 empty] | 0 | 47040
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 0 | [10 empty] | 10 | 10 | 10 | 90 | 100 |  | 100 | 100 | 100 | 90 | 90 | 90 | 70 | 738360
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 18 | 46 | 46 | 47 | 10 | 10 | 33 |  | 47 | 47 | 47 | 47 | 47 | 5 | 5 | 533376
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 5 | 5 | 469704
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | 6 | 6 | [5 empty] | 5 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 22 | 50 |  | 50 | 18 | 18 | 18 | 18 | 18 | 18 | 387360
96 | Chattogram 108 MW PP (ECPV) | 24 | 24 | [12 empty] | 1 | 10 | 27 | 85 |  | 97 | 97 | 97 | 97 | 97 | 51 | 30 | 691200
97 | Katpotti 52 MW PP (Sinha) | 12 | 12 | [9 empty] | 17 | 41 | 18 | 18 | 15 | 23 | 47 |  | 47 | 47 | 46 | 46 | 46 | 32 | 32 | 504528
98 | Bosila 108MW PP(CLC) | [12 empty] | 24 | 24 | 24 | 48 | 70 | 69 |  | 68 | 68 | 68 | 69 | 41 |  | 0 | 477120
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 9 | 15 | 15 | 15 | 15 | 17 | 45 |  | 15 | 15 | 15 | 0 | 0 |  |  | 191172
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 35 | 55 |  | 35 | 17 | 17 |  |  |  | 0 | 149659
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 163 | 100 | 130 | 130 | 100 | 163 |  | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 3151857
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.2 | 0.8 | 1 | 0.8 | 1 | 0.6 | 0.5 | 0.5 | 0.1 | 0 | 0 | [8 empty] | 5150
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 |  |  |  | 17 | 17 | [7 empty] | 0 | 79200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [11 empty] | 2 | 50 | 50 | 50 | 50 | 65 | 102 |  | 150 | 150 | 150 | 150 | 150 | 50 | 0 | 1137600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [16 empty] | 8 | 15 |  | 0 | 0 | [5 empty] | 34560
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 40 | 40 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 133440
116 | Chandpur 200MW (Desh energy) | [16 empty] | 47 | 105 |  | 130 | 50 | 75 | 50 | 17 | 0 |  | 451200
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 11 | 50 |  | 10 | 10 | 10 | 10 |  |  | 0 | 185434
118 | Bibiyana-III 400 MW CCPP
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [8 empty] | 0 | [16 empty] | 0 | 0
120 | Eastern Zone Total | 3874 | 3968 | 3818 | 3609 | 3443 | 3439 | 3560.1 | 3760.78 | 4261.1 | 4392.8 | 4543.9 | 4844.1 | 5113.6 | 4867.6 | 5052.5 | 5127.6 | 5322 | 6208 | 0 | 6177 | 6097 | 6054 | 5935 | 5744 | 5210 | 4915 | 114630458
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 16 |  | 16 | 0 | [5 empty] | 47040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 29 | 41 |  | 45 | 0 | [5 empty] | 94080
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 100 | 110 | 110 | 108 | 109 | 109 | 109 | 109 | 35 | 17 | 17 | 45 |  | 70 | 70 | 70 | 70 | 35 | 0 |  | 1211040
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 0 | 16 |  | 32 | 32 | 16 | 0 |  |  |  | 68160
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 57 | 89 | 97 | 95 | 60 | 41 | 91 |  | 97 | 96 | 96 | 94 | 95 | 96 | 83 | 1194319
| Bhola 225 MW CCPP | 180 | 180 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 174 | 174 | 174 | 165 | 167 | 173 | 173 | 173 | 174 |  | 174 | 174 | 174 | 174 | 165 | 174 | 168 | 4045225
140 | Bhola 33 MW PP (Venture) | 19 | 19 | 18 | 18 | 18 | 10 | 11 | 11 | 12 | 13 | 14 | 13 | 16 | 15 | 15 | 14 | 14 | 20 |  | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 393400
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 0 | 0 | 32 | 32 | 0 |  |  | 89250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 17 | 23 |  | 50 | 50 | 33 | 33 | 33 | 27 | 16 | 230112
146 | Bheramara HVDC | 620 | 391 | 391 | 391 | 390 | 391 | 390 | 390 | 391 | 391 | 391 | 390 | 391 | 391 | 391 | 391 | 391 | 928 |  | 929 | 928 | 929 | 927 | 926 | 925 | 926 | 13365818
147 | Bheramara 360 MW CCPP | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 410 | 385 | 365 | 365 | 325 | 270 | 245 | 235 | 240 | 255 | 275 |  | 290 | 295 | 295 | 285 | 290 | 290 | 290 | 7261344
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 67 | 67 | 67 | 67 | 67 | 67 | 69 | 67 | 67 | 67 | 66 | 67 | 70 | 70 | 69 | 69 | 68 | 69 |  | 70 | 69 | 69 | 68 | 67 | 66 | 66 | 1656000
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 280 | 280 | 280 | 280 | 280 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 291 | 290 | 281 | 280 | 6363100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 0 |  |  |  | 50 |  | 0 | 0 | 0 |  |  |  |  | 639300
| Baghabari 50 MW Peaking PP | [26 empty] | 52559
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 154 | 160 | 153 | 135 | 135 | 135 | 142 | 200 | 205 | 204 | 193 | 200 | 205 | 174 | 175 | 167 | 173 | 165 |  | 182 | 192 | 196 | 190 | 184 | 181 | 183 | 4483173
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 155 | 155 | 140 | 134 | 134 | 134 | 134 | 135 | 181 | 210 | 208 | 205 | 195 | 167 | 170 | 162 | 161 | 165 |  | 190 | 198 | 198 | 198 | 192 | 191 | 190 | 4366309
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 313 | 310 | 310 | 310 | 310 | 366 | 392 | 433 | 432 | 430 | 433 | 432 | 376 | 401 | 407 | 394 | 332 | 367 |  | 394 | 394 | 394 | 430 | 383 | 398 | 378 | 9210870
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [7 empty] | 12 | 14 | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 3 | 3 | 308880
163 | Bogura 20 MW PP (Energyprima) | [11 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 158400
164 | Ullapara 11 MW PP (Summit) | [8 empty] | 3 | 3 | 0 | 5 | 5 | 5 | 3 | 3 | 3 | 5 |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 67320
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 12 | 12 |  | 50 | 50 | 50 | 25 | 0 |  |  | 151840
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 0 | 0 | 0 |  |  |  |  | 19902
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 0 |  | 0 | [6 empty] | 12480
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 9 | 0 | 0 |  |  |  | 50 |  | 0 | 0 | 0 |  |  |  |  | 50428
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence) | [12 empty] | 18 | 35 | 35 | 35 | 35 | 45 |  | 72 | 74 | 74 | 74 | 35 |  | 0 | 513080
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 15 | 19 | 26 | 45 | 47 | 37 | 46 | 22 | 0 |  | 0 | [6 empty] | 264960
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 17 | 17 | 17 | 17 | 0 |  |  | 49000
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 50 | 70 |  | 70 | 70 | 70 | 35 | 0 |  |  | 316800
177 | Sympa Solar Power 8MW | [7 empty] | 2.8 | 4.3 | 4.8 | 6.4 | 5.3 | 8.5 | 2.9 | 1.2 | 0.2 | 0.1 | 0 | [8 empty] | 36275
178
178