## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-24 | Thursday
|  | Date (day): | 2019-10-24 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13340 | MW |  |  | (b) At Evening Peak Hour : |  | 14545 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-23 | 2019-10-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 350 | 350 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 369 | 358 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 352 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 93 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 230 | 230 | 230 | 75 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 81 | 81 | 81 |  | 21 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 48 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under shut down
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 25 | 45 | 46
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 69 | 69 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 300 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2581 | 3311 | 3848 | 4251 | 576 | 994
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 84 | 84 | 84 | 84 | 146 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 219 | 209 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 124 | 104 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 15 | 51 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 6 | 10 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 91 | 95 | 95 | 95 |  | 13 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.509 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 142 | 142 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 113 | 113
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 916.509 | 1085 | 1462.4 | 1568 | 406 | 111
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 194 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 345 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 275 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 33 | 30 | 30 |  | 15 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 48 | 48 | 48 |  | 7 | Engine problem
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 68 | 68 | 68 | 127 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 17 | 27 | 27 | 27 |  | 24 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 127 | 127 | 140 | 141
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 100 | 200 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 144 | 178 | 131 | 172
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1497 | 1730 | 1978 | 2270 | 425 | 50
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 136 | 126 | 140 | 140 | 62 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 88 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 248.1 | 458 | 573.6 | 572 | 62 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 73 | 73 | 73 | 73
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 102 | 100 | 100 | 100 |  | 230 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 43 | 46 | 50 | 50
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 68 | 68 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 35 | 42 | 42 | 42 |  | 8 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 295 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1051 | 1072 | 1128 | 1128 | 0 | 800
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 927 | 929 | 936 | 936
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 6 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 360 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 53 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 33 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1357 | 1453 | 1986 | 2146 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 19 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 173 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 286 | 351 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 50 | 50 | 50 | 50 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 17 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 32 | 42 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 196 | 181 | 225 | 225 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 172 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 411 | 383 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 12 | 12
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 26 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 12 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 941 | 1131 | 1517 | 1667 | 270 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 69 | 67 | 68 | 68
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 108 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 351.8 | 472 | 469 | 495 | 0 | 85
| Total |  |  |  |  | 19541 | 19018 | 9229.409 | 11063 | 13340 | 14545 | 1739 | 2119
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8765.5609 | 10507 | 12669.5634 | 13814.003
A. |  | 2019-10-23 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 11063 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7845 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11063 | MW
3 | Day peak Generation : |  |  | 9229.409 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10507 | MW
4 | Evening peak Generation : |  |  | 11063 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 224.083 | MKWHr | By Solar | 0.18485 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 147.3838 | MKWHr |  | By Oil: | 40.3734 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.4275 | MKWHr |  | By Hydro: | 1.8696 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1739 | MW | Dhaka | 3981 | 3981 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2119 | MW | Chittagong | 1161 | 1161 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3858 | MW | Khulna | 1116 | 1116 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1210.02 | MMCFD |  |  | Rajshahi | 1054 | 1054 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 135674557.792 | ii) Oil : | Taka | 341700217.43 | Comilla | 1063 | 1063 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 38129813.66 | Total | Taka | 515504588.882 | Mymensingh | 830 | 830 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 447 | 447 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 180 | MW (E to W) at | 19:30 | hrs | Barisal | 246 | 246 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 90 | MW at | 20:00 | hrs | Rangpur | 609 | 609 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31° C |  |  | Total | 10507 | 10507 |  | 0
B. |  | 2019-10-24 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 25.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14545 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 4045 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 212.6793 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6914.9 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2611 | MKWHr. | ii) HVDC Flow at Peak Time |  | 929 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5827 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 102.63 | 102.72 |  | (b) Today: | 102.63 |  | (c) Rule Curve: |  | 108.2
.

## YesterdayGen
2019-10-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 355 |  | 0 | 420 | 230 | 0 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 69 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 17 | 100 | 97 | 0 | 19 | 40 | 0 | 100 | 0 | 320 | 315 | 180 | 63 | 120 | 30 | 53 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 156 | 126 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 100 | 65 | 79 | 40 | 0 | 18 | 28 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 141 | 0 | 100 | 200 | 0 | 0 | 115 | 0 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 174 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 25 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 98 | 0 | 193 | 0 | 394 | 35 | 0 | 0 | 17 | 53 | 0 | 0 | 0 |  | 6521 | 2995 | 9516 | 4071 | 927 | 2220 | 1684 | 347 | 84 | 27 | 156 | 0 | 0 | 102.73
2:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 355 |  | 0 | 420 | 230 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 203 | 0 | 133 | 0 |  | 0 | 0 | 17 | 60 | 97 | 0 | 19 | 38 | 0 | 100 | 0 | 320 | 315 | 180 | 63 | 125 | 30 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 150 | 127 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 100 | 66 | 79 | 41 | 0 | 18 | 28 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 95 | 0 | 100 | 160 | 0 | 0 | 80 | 0 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 181 | 0 | 0 | 0 | 97 | 0 | 190 | 0 | 393 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 6305 | 2856 | 9161 | 4094 | 927 | 2220 | 1322 | 347 | 84 | 17 | 150 | 0 | 0 | 102.73
3:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 346 | 355 |  | 0 | 420 | 230 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 17 | 20 | 97 | 0 | 16 | 40 | 0 | 100 | 0 | 320 | 315 | 180 | 63 | 125 | 30 | 53 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 144 | 127 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 102 | 66 | 79 | 41 | 0 | 18 | 28 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 60 | 105 | 0 | 0 | 60 | 0 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 190 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6088 | 2826 | 8914 | 4105 | 927 | 2227 | 1063 | 347 | 84 | 17 | 144 | 0 | 0 | 102.73
4:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 355 |  | 0 | 420 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 17 | 10 | 97 | 0 | 16 | 40 | 0 | 100 | 0 | 320 | 315 | 179 | 63 | 126 | 30 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 140 | 144 | 95 | 22 | 0 | 50 | 73 | 39 | 49 | 163 | 100 | 66 | 79 | 41 | 0 | 18 | 28 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 |  | 927 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 187 | 0 | 0 | 0 | 97 | 0 | 190 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5852 | 2758 | 8610 | 4121 | 927 | 2191 | 783 | 347 | 84 | 17 | 140 | 0 | 0 | 102.72
5:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 349 | 355 |  | 0 | 420 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 97 | 0 | 16 | 40 | 0 | 100 | 0 | 280 | 280 | 187 | 63 | 126 | 30 | 52 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 138 | 144 | 48 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 102 | 66 | 79 | 41 | 0 | 18 | 28 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 |  | 927 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 175 | 0 | 0 | 0 | 96 | 0 | 178 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5630 | 2749 | 8379 | 4014 | 927 | 2185 | 667 | 347 | 84 | 17 | 138 | 0 | 0 | 102.72
6:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 346 | 328 |  | 0 | 380 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 97 | 0 | 16 | 41 | 0 | 100 | 0 | 270 | 280 | 179 | 63 | 127 | 30 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 124 | 156 | 48 | 22 | 0 | 60 | 73 | 39 | 49 | 100 | 101 | 67 | 79 | 42 | 0 | 18 | 28 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 |  | 926 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 0 | 0 | 67 | 280 | 0 | 0 | 165 | 0 | 0 | 0 | 97 | 0 | 164 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5474 | 2641 | 8115 | 3980 | 926 | 1970 | 667 | 347 | 84 | 17 | 124 | 0 | 0 | 102.72
7:00 | 35 | 0 | 160 | 0 | 350 | 0 | 0 | 345 | 300 |  | 0 | 350 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 80 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 97 | 0 | 16 | 31 | 0 | 100 | 0 | 270 | 280 | 180 | 63 | 126 | 30 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 114 | 156 | 48 | 22 | 0 | 60 | 73 | 11 | 10 | 100 | 100 | 66 | 10 | 42 | 0 | 18 | 27 | 10 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 |  | 928 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 0 | 0 | 67 | 280 | 0 | 0 | 154 | 0 | 0 | 0 | 53 | 0 | 160 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5202 | 2643 | 7845 | 3950 | 928 | 1762 | 644 | 347 | 80 | 17 | 114 | 3 | 0 | 102.71
8:00 | 35 | 0 | 150 | 0 | 350 | 0 | 0 | 345 | 300 |  | 0 | 350 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 16 | 0 | 91 | 0 | 16 | 7 | 0 | 100 | 0 | 270 | 280 | 180 | 63 | 127 | 30 | 52 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 116 | 155 | 48 | 22 | 0.8 | 58 | 73 | 11 | 10 | 100 | 101 | 66 | 10 | 40 | 0 | 18 | 21 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 8 | 30 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 106 | 0 | 0 |  | 927 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 25 | 0 | 22 | 12 | 8 | 0 | 68 | 280 | 0 | 0 | 156 | 0 | 0 | 0 | 52 | 0 | 164 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5326.8 | 2677 | 8003.8 | 3948 | 927 | 1718 | 836 | 348 | 84 | 16 | 116 | 10.8 | 0 | 102.71
9:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 375 | 333 |  | 0 | 380 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 42 | 0 | 100 | 0 | 0 | 216 | 0 | 105 | 0 |  | 0 | 0 | 16 | 0 | 91 | 18 | 16 | 3 | 0 | 100 | 0 | 295 | 310 | 217 | 63 | 126 | 30 | 53 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 118 | 140 | 48 | 22 | 1.4 | 60 | 73 | 16 | 18 | 130 | 102 | 64 | 10 | 40 | 0 | 18 | 21 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 13 | 30 | 0 | 0 | 0 | 0 | 80 | 0 | 3.05 | 106 | 0 | 0 |  | 927 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 42 | 0 | 22 | 12 | 11 | 0 | 68 | 280 | 0 | 0 | 171 | 0 | 0 | 0 | 52 | 0 | 165 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 |  | 5652.45 | 2737.6 | 8390.05 | 4115 | 927 | 1872 | 933 | 348 | 42 | 16 | 118 | 19.05 | 0 | 102.71
10:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 375 | 333 |  | 0 | 380 | 230 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 0 | 100 | 0 | 0 | 213 | 0 | 104 | 0 |  | 0 | 0 | 15 | 0 | 91 | 50 | 16 | 3 | 0 | 110 | 0 | 295 | 330 | 200 | 63 | 127 | 30 | 53 | 0 | 14 | 0 | 0 | 0 | 19 | 8 | 16 | 20 | 134 | 138 | 58 | 22 | 1.4 | 60 | 73 | 36 | 49 | 130 | 102 | 64 | 50 | 40 | 0 | 18 | 21 | 10 | 320 | 23 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 149 | 16 | 30 | 25 | 0 | 0 | 0 | 88 | 0 | 3.92 | 142 | 0 | 0 |  | 927 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 43 | 0 | 22 | 9 | 11 | 0 | 68 | 280 | 0 | 0 | 173 | 0 | 0 | 0 | 51 | 0 | 171 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 18 |  | 5910.32 | 2752.8 | 8663.12 | 4112 | 927 | 1979 | 1082 | 348 | 42 | 15 | 134 | 24.12 | 0 | 102.7
11:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 370 | 350 |  | 0 | 420 | 230 | 0 | 48 | 35 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 210 | 0 | 104 | 0 |  | 0 | 0 | 15 | 0 | 91 | 50 | 16 | 2 | 0 | 110 | 0 | 285 | 320 | 195 | 63 | 127 | 30 | 49 | 0 | 17 | 0 | 0 | 0 | 0 | 8 | 16 | 20 | 140 | 138 | 68 | 22 | 1 | 60 | 73 | 39 | 49 | 130 | 103 | 63 | 79 | 40 | 0 | 18 | 32 | 10 | 315 | 23 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 149 | 17 | 30 | 68 | 0 | 0 | 0 | 88 | 0 | 4 | 142 | 0 | 0 |  | 927 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 43 | 0 | 22 | 12 | 11 | 0 | 68 | 280 | 0 | 0 | 177 | 0 | 0 | 0 | 51 | 0 | 174 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 25 |  | 6135 | 2788 | 8923 | 4064 | 927 | 2076 | 1243 | 348 | 84 | 15 | 140 | 26 | 0 | 102.7
12:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 369 | 347 |  | 0 | 420 | 230 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 0 | 120 | 0 | 0 | 219 | 0 | 124 | 0 |  | 0 | 0 | 15 | 0 | 91 | 50 | 16 | 3 | 0 | 100 | 0 | 270 | 350 | 202 | 63 | 127 | 30 | 49 | 0 | 17 | 0 | 0 | 0 | 0 | 8 | 16 | 21 | 144 | 136 | 88 | 22 | 2.1 | 60 | 73 | 43 | 49 | 130 | 102 | 63 | 78 | 40 | 0 | 18 | 35 | 10 | 315 | 24 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 149 | 18 | 30 | 100 | 0 | 0 | 0 | 88 | 0 | 4.509 | 142 | 0 | 0 |  | 927 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 43 | 0 | 22 | 12 | 11 | 0 | 69 | 280 | 0 | 0 | 196 | 0 | 0 | 0 | 92 | 0 | 190 | 0 | 411 | 35 | 0 | 0 | 0 | 0 | 0 | 2.8 | 12 |  | 6293.609 | 2935.8 | 9229.409 | 4170 | 927 | 2156 | 1357 | 349 | 84 | 15 | 144 | 27.409 | 0 | 102.7
13:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 360 | 349 |  | 0 | 420 | 230 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 0 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 91 | 50 | 19 | 2 | 0 | 100 | 0 | 325 | 305 | 182 | 63 | 127 | 30 | 48 | 0 | 17 | 0 | 0 | 0 | 0 | 8 | 16 | 21 | 146 | 125 | 91 | 22 | 1 | 60 | 73 | 42 | 49 | 130 | 99 | 63 | 78 | 40 | 0 | 18 | 38 | 10 | 310 | 24 | 11 | 0 | 20 | 0 | 0 | 0 | 0 | 149 | 17 | 30 | 125 | 0 | 0 | 15 | 88 | 0 | 4 | 142 | 0 | 0 |  | 927 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 43 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 191 | 0 | 0 | 0 | 91 | 0 | 205 | 0 | 420 | 35 | 0 | 0 | 0 | 0 | 0 | 4 | 4 |  | 6279 | 2943 | 9222 | 4100 | 927 | 2162 | 1429 | 347 | 85 | 0 | 146 | 26 | 0 | 102.69
14:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 350 | 302 |  | 0 | 390 | 230 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 22 | 3 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 178 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 96 | 50 | 19 | 2 | 0 | 100 | 0 | 260 | 265 | 185 | 63 | 127 | 27 | 47 | 0 | 17 | 0 | 0 | 0 | 0 | 8 | 16 | 21 | 154 | 122 | 90 | 22 | 0.7 | 60 | 73 | 44 | 49 | 100 | 101 | 64 | 78 | 40 | 0 | 18 | 39 | 10 | 300 | 24 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 149 | 14.29 | 30 | 140 | 0 | 0 | 28 | 88 | 0 | 3.475 | 143 | 0 | 0 |  | 929 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 32 | 0 | 30 | 0 | 0 | 0 | 0 | 40 | 42 | 0 | 43 | 0 | 22 | 12 | 11 | 0 | 68 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 95 | 0 | 180 | 0 | 414 | 35 | 0 | 0 | 0 | 0 | 0 | 2.2 | 15 |  | 5996.465 | 2986.2 | 8982.665 | 3880 | 929 | 2046 | 1521 | 348 | 84 | 0 | 154 | 20.665 | 0 | 102.69
15:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 355 | 303 |  | 0 | 390 | 230 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 0 | 100 | 0 | 0 | 178 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 95 | 50 | 19 | 2 | 0 | 100 | 0 | 270 | 275 | 193 | 63 | 127 | 30 | 47 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 33 | 21 | 154 | 121 | 90 | 22 | 0.4 | 60 | 73 | 44 | 49 | 100 | 102 | 63 | 78 | 40 | 0 | 18 | 40 | 10 | 310 | 24 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 149 | 10.18 | 30 | 140 | 0 | 0 | 28 | 88 | 0 | 2.653 | 143 | 0 | 0 |  | 929 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 32 | 0 | 30 | 0 | 0 | 0 | 0 | 40 | 42 | 0 | 51 | 0 | 22 | 12 | 11 | 0 | 68 | 280 | 0 | 0 | 166 | 0 | 0 | 0 | 95 | 0 | 174 | 0 | 418 | 35 | 0 | 0 | 0 | 0 | 0 | 1.8 | 20 |  | 6096.233 | 2987.8 | 9084.033 | 3953 | 929 | 2070 | 1533 | 348 | 82 | 0 | 154 | 15.033 | 0 | 102.69
16:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 303 |  | 0 | 390 | 230 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 0 | 100 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 95 | 50 | 19 | 2 | 0 | 100 | 0 | 260 | 260 | 180 | 63 | 126 | 30 | 48 | 0 | 27 | 0 | 0 | 0 | 0 | 8 | 16 | 21 | 150 | 123 | 90 | 22 | 0.4 | 59 | 73 | 44 | 49 | 100 | 100 | 65 | 78 | 40 | 0 | 18 | 40 | 10 | 290 | 24 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 149 | 4.26 | 30 | 140 | 0 | 0 | 28 | 88 | 0 | 0.564 | 143 | 0 | 0 |  | 929 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 164 | 20 | 32 | 0 | 30 | 0 | 0 | 0 | 0 | 40 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 158 | 0 | 0 | 0 | 97 | 0 | 159 | 0 | 389 | 35 | 0 | 0 | 0 | 0 | 0 | 0.8 | 24 |  | 6029.224 | 2925.8 | 8955.024 | 3857 | 929 | 2024 | 1538 | 347 | 82 | 22 | 150 | 6.024 | 0 | 102.68
17:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 344 | 303 |  | 0 | 390 | 230 | 0 | 48 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 95 | 50 | 19 | 2 | 0 | 100 | 0 | 260 | 260 | 178 | 68 | 127 | 30 | 48 | 0 | 27 | 0 | 0 | 0 | 0 | 8 | 16 | 18 | 148 | 125 | 90 | 22 | 0 | 58 | 73 | 46 | 20 | 100 | 99 | 65 | 79 | 40 | 0 | 18 | 42 | 10 | 285 | 24 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 149 | 0 | 30 | 140 | 0 | 0 | 28 | 88 | 0 | 0.121 | 143 | 0 | 0 |  | 928 | 0 | 345 | 0 | 2 | 0 | 0 | 0 | 26 | 31 | 0 | 173 | 21 | 16 | 0 | 40 | 0 | 3 | 0 | 9 | 50 | 42 | 6 | 52 | 7 | 22 | 12 | 8 | 0 | 67 | 280 | 0 | 18 | 167 | 0 | 0 | 0 | 97 | 0 | 156 | 0 | 356 | 17 | 0 | 0 | 0 | 0 | 0 | 0.1 | 4 |  | 6004.121 | 2955.1 | 8959.221 | 3882 | 928 | 1968 | 1503 | 347 | 83 | 100 | 148 | 0.221 | 0 | 0
18:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 354 | 352 |  | 0 | 420 | 230 | 16 | 50 | 55 | 0 | 0 | 0 | 0 | 50 | 7 | 100 | 11 | 69 | 0 | 0 | 53 | 30 | 55 | 22 | 25 | 30 | 0 | 33 | 14 | 0 | 83 | 0 | 100 | 0 | 7 | 205 | 0 | 104 | 0 |  | 0 | 0 | 51 | 80 | 95 | 50 | 19 | 10 | 0 | 100 | 0 | 320 | 260 | 181 | 68 | 126 | 33 | 48 | 0 | 27 | 0 | 0 | 7 | 0 | 8 | 33 | 21 | 176 | 125 | 91 | 22 | 0 | 59 | 73 | 46 | 38 | 163 | 100 | 65 | 79 | 40 | 0 | 18 | 40 | 10 | 300 | 24 | 11 | 0 | 95 | 0 | 0 | 43 | 0 | 149 | 0 | 100 | 170 | 10 | 0 | 78 | 88 | 0 | 0 | 143 | 0 | 0 |  | 929 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 43 | 31 | 40 | 173 | 31 | 64 | 0 | 40 | 0 | 50 | 0 | 60 | 50 | 42 | 48 | 52 | 32 | 22 | 12 | 8 | 0 | 66 | 280 | 0 | 17 | 188 | 0 | 0 | 0 | 53 | 0 | 165 | 0 | 361 | 100 | 0 | 40 | 85 | 108 | 0 | 0 | 0 |  | 6953 | 3601 | 10554 | 3975 | 929 | 2120 | 2493 | 346 | 83 | 432 | 176 | 0 | 0 | 102.68
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 344 | 352 |  | 0 | 420 | 230 | 100 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 16 | 100 | 18 | 69 | 0 | 37 | 53 | 55 | 55 | 22 | 25 | 30 | 22 | 33 | 25 | 0 | 84 | 0 | 100 | 0 | 25 | 204 | 0 | 104 | 0 |  | 0 | 0 | 51 | 100 | 95 | 50 | 19 | 10 | 0 | 100 | 0 | 330 | 260 | 180 | 68 | 127 | 33 | 48 | 0 | 27 | 0 | 0 | 51 | 21 | 8 | 33 | 21 | 176 | 126 | 96 | 22 | 0 | 60 | 73 | 46 | 49 | 163 | 101 | 66 | 76 | 40 | 0 | 18 | 43 | 10 | 280 | 24 | 11 | 0 | 285 | 0 | 0 | 84 | 0 | 149 | 0 | 100 | 200 | 10 | 0 | 115 | 88 | 0 | 0 | 143 | 0 | 0 |  | 928 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 27 | 6 | 40 | 170 | 32 | 64 | 0 | 40 | 0 | 34 | 0 | 60 | 50 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 66 | 280 | 0 | 17 | 167 | 0 | 0 | 0 | 97 | 0 | 155 | 0 | 369 | 53 | 0 | 110 | 33 | 108 | 0 | 0 | 0 |  | 7629 | 3417 | 11046 | 3985 | 928 | 2164 | 3068 | 346 | 84 | 295 | 176 | 0 | 0 | 102.67
19:30 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 358 | 352 |  | 0 | 420 | 230 | 93 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 69 | 0 | 25 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 25 | 209 | 0 | 104 | 0 |  | 0 | 0 | 51 | 100 | 95 | 50 | 19 | 6 | 0 | 100 | 0 | 345 | 275 | 194 | 68 | 127 | 33 | 48 | 0 | 27 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 178 | 126 | 95 | 22 | 0 | 60 | 73 | 46 | 49 | 163 | 100 | 65 | 76 | 40 | 0 | 18 | 42 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 142 | 0 | 0 |  | 929 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 6 | 0 | 40 | 173 | 19 | 64 | 0 | 50 | 0 | 17 | 0 | 26 | 50 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 17 | 181 | 0 | 0 | 0 | 95 | 0 | 172 | 0 | 383 | 53 | 0 | 113 | 33 | 108 | 0 | 0 | 0 |  | 7656 | 3407 | 11063 | 4121 | 929 | 2173 | 3014 | 347 | 84 | 217 | 178 | 0 | 0 | 0
20:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 347 | 355 |  | 0 | 420 | 230 | 95 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 69 | 0 | 25 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 25 | 204 | 0 | 104 | 0 |  | 0 | 0 | 50 | 100 | 95 | 50 | 19 | 19 | 0 | 100 | 0 | 330 | 260 | 180 | 68 | 127 | 33 | 49 | 0 | 27 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 176 | 125 | 95 | 22 | 0 | 60 | 73 | 46 | 49 | 163 | 102 | 66 | 78 | 40 | 0 | 18 | 43 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 143 | 0 | 0 |  | 928 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 6 | 0 | 40 | 159 | 2 | 64 | 0 | 50 | 0 | 0 | 0 | 26 | 50 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 17 | 180 | 0 | 0 | 0 | 97 | 0 | 171 | 0 | 337 | 53 | 0 | 113 | 33 | 113 | 0 | 0 | 0 |  | 7614 | 3297 | 10911 | 4028 | 928 | 2127 | 3022 | 347 | 84 | 199 | 176 | 0 | 0 | 102.67
21:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 344 | 357 |  | 0 | 420 | 230 | 55 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 69 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 8 | 205 | 0 | 134 | 0 |  | 0 | 0 | 36 | 100 | 95 | 50 | 19 | 28 | 0 | 100 | 0 | 330 | 260 | 180 | 68 | 126 | 33 | 49 | 0 | 27 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 170 | 108 | 95 | 22 | 0 | 60 | 73 | 47 | 49 | 163 | 100 | 66 | 78 | 40 | 0 | 18 | 43 | 10 | 290 | 24 | 11 | 0 | 65 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 143 | 0 | 0 |  | 929 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 6 | 0 | 40 | 174 | 21 | 64 | 0 | 50 | 0 | 0 | 0 | 0 | 30 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 17 | 181 | 0 | 0 | 0 | 97 | 0 | 187 | 0 | 356 | 53 | 0 | 113 | 17 | 113 | 0 | 0 | 0 |  | 7297 | 3311 | 10608 | 4073 | 929 | 2177 | 2669 | 347 | 84 | 159 | 170 | 0 | 0 | 102.67
22:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 344 | 359 |  | 0 | 420 | 230 | 0 | 81 | 55 | 0 | 0 | 0 | 0 | 92 | 0 | 100 | 0 | 69 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 51 | 90 | 93 | 46 | 19 | 28 | 0 | 100 | 0 | 330 | 260 | 180 | 68 | 121 | 33 | 50 | 0 | 27 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 168 | 109 | 92 | 22 | 0 | 60 | 73 | 47 | 49 | 163 | 100 | 66 | 79 | 42 | 0 | 18 | 43 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 143 | 0 | 0 |  | 929 | 0 | 345 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 40 | 166 | 23 | 64 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 344 | 35 | 0 | 113 | 17 | 113 | 0 | 0 | 0 |  | 7053 | 3220 | 10273 | 4060 | 929 | 2157 | 2378 | 347 | 83 | 151 | 168 | 0 | 0 | 102.66
23:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 359 |  | 0 | 380 | 230 | 0 | 81 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 8 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 90 | 96 | 13 | 19 | 36 | 0 | 100 | 0 | 345 | 280 | 191 | 68 | 126 | 33 | 52 | 0 | 27 | 0 | 0 | 25 | 22 | 8 | 33 | 21 | 166 | 126 | 92 | 22 | 0 | 60 | 73 | 47 | 49 | 130 | 101 | 65 | 79 | 42 | 0 | 18 | 43 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 143 | 0 | 0 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 25 | 64 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 181 | 0 | 0 | 0 | 96 | 0 | 188 | 0 | 382 | 35 | 0 | 100 | 0 | 71 | 0 | 0 | 0 |  | 6580 | 3126 | 9706 | 4138 | 929 | 2129 | 1851 | 347 | 81 | 65 | 166 | 0 | 0 | 102.66
24:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 348 | 356 |  | 0 | 380 | 230 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 81 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 19 | 39 | 0 | 100 | 0 | 330 | 260 | 181 | 68 | 126 | 33 | 53 | 0 | 27 | 0 | 0 | 25 | 22 | 8 | 33 | 21 | 164 | 126 | 95 | 22 | 0 | 59 | 73 | 47 | 49 | 130 | 100 | 65 | 79 | 41 | 0 | 18 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 60 | 55 | 0 | 0 | 143 | 0 | 0 |  | 923 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 24 | 64 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 24 | 0 | 22 | 12 | 8 | 0 | 67 | 280 | 0 | 0 | 188 | 0 | 0 | 0 | 96 | 0 | 197 | 0 | 377 | 0 | 0 | 62 | 0 | 35 | 0 | 0 | 0 |  | 6364 | 2989 | 9353 | 4107 | 923 | 2153 | 1546 | 347 | 81 | 32 | 164 | 0 | 0 | 102.66
KWH | 775000 | 0 | 4685000 | 0 | 8047745 | 0 | 0 | 8623920 | 8061000 |  | 0 | 9662500 | 5853207 | 271680 | 1171632 | 706925 | 0 | 0 | 0 | 0 | 637440 | 32976 | 600480 | 36407 | 1274880 | 0 | 0 | 654120 | 445216 | 397546 | 481212 | 600000 | 673920 | 746700 | 823300 | 41964 | 0 | 1869573 | 0 | 2400000 | 0 | 69645 | 4858736 | 0 | 2792352 | 0 |  | 0 | 0 | 483463 | 817080 | 2275200 | 685440 | 416160 | 111240 | 0 | 2453960 | 0 | 7607500 | 7069000 | 4529000 | 1589090 | 2991380 | 693432 | 1215840 | 0 | 541736 | 0 | 0 | 278746 | 335880 | 182520 | 681100 | 498580 | 3582720 | 3036520 | 1992960 | 464654 | 10150 | 1428000 | 1722000 | 918000 | 1075032 | 3415124 | 2291000 | 1576320 | 1654080 | 928080 | 0 | 444000 | 790760 | 250560 | 7303300 | 581472 | 256992 | 0 | 1111717 | 0 | 0 | 530400 | 0 | 3160800 | 122580 | 1403520 | 2933760 | 16727 | 0 | 1201200 | 1359480 | 0 | 28440 | 3312000 | 0 | 0 |  | 22261091 | 0 | 8808192 | 0 | 172800 | 0 | 0 | 0 | 96000 | 92416 | 225750 | 4178550 | 529581 | 967392 | 0 | 449000 | 0 | 91395 | 0 | 134568 | 468700 | 623003 | 70851 | 824160 | 30073 | 511440 | 273276 | 235026 | 0 | 1605818 | 6821700 | 0 | 84000 | 4492564 | 0 | 0 | 0 | 2041589 | 0 | 4493764 | 0 | 9087091 | 949920 | 0 | 694080 | 176832 | 788160 | 0 | 23679 | 126720 |  | 151653771 | 72429181 | 224082952 | 97424451 | 22261091 | 49959319 | 38690185 | 8427518 | 1869573 | 1683246 | 3582720 | 184849 | 0
Fuel Cost | 868000 | 0 | 5012950 | 0 | 5955331.3 | 0 | 0 | 6209222.4 | 6126360 |  | 0 | 7730000 | 5267886.3 | 2771136 | 12688774.56 | 7253050.5 | 0 | 0 | 0 | 0 | 7075584 | 335036.16 | 5950756.8 | 381545.36 | 11601408 | 0 | 0 | 6273010.8 | 4247360.64 | 3959558.16 | 360909 | 450000 | 0 | 0 | 0 | 402015.12 | 0 | 486088.98 | 0 | 3672000 | 0 | 669288.45 | 5101672.8 | 0 | 3546287.04 | 0 |  | 0 | 0 | 5071526.87 | 8407753.2 | 21637152 | 6415718.4 | 382867.2 | 309247.2 | 0 | 2576658 | 0 | 5629550 | 5937960 | 4166680 | 1557308.2 | 3978535.4 | 568614.24 | 1252315.2 | 0 | 774682.48 | 0 | 0 | 2620212.4 | 342597.6 | 136890 | 1287279 | 373935 | 24720768 | 2489946.4 | 18953049.6 | 473947.08 | 166460 | 1942080 | 2341920 | 1248480 | 1343790 | 4234753.76 | 2107720 | 2348716.8 | 2911180.8 | 1030168.8 | 0 | 705960 | 925189.2 | 588816 | 5185343 | 436104 | 195313.92 | 0 | 11639676.99 | 0 | 0 | 5102448 | 0 | 31892472 | 1414573.2 | 13080806.4 | 27518668.8 | 156731.99 | 0 | 10534524 | 12112966.8 | 0 | 0 | 30536640 | 0 | 0 |  | 60104945.7 | 0 | 6870389.76 | 0 | 1665792 | 0 | 0 | 0 | 1113600 | 1210649.6 | 2232667.5 | 3342840 | 820850.55 | 10389790.08 | 0 | 844120 | 0 | 1018140.3 | 0 | 1332223.2 | 4860419 | 7295365.13 | 853754.55 | 8208633.6 | 296219.05 | 562584 | 450905.4 | 177914.682 | 0 | 10229060.66 | 27900753 | 0 | 2371320 | 3953456.32 | 0 | 0 | 0 | 3246126.51 | 0 | 3954512.32 | 0 | 6633576.43 | 8986243.2 | 0 | 6371654.4 | 1575573.12 | 7361414.4 | 0 | 0 | 0 |  | 406161930.3 | 196235494.462 | 602397424.762 | 88742880.262 | 60104945.7 | 46931677.53 | 322482027.06 | 38129813.66 | 486088.98 | 19218190.37 | 24720768 | 1581033.2 | 0
Yesterday Day Peak | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 369 | 347 |  | 0 | 420 | 230 | 0 | 48 | 48 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 69 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 0 | 120 | 0 | 0 | 219 | 0 | 124 | 0 |  | 0 | 0 | 15 | 0 | 91 | 50 | 16 | 3 | 0 | 100 | 0 | 270 | 350 | 202 | 63 | 127 | 30 | 49 | 0 | 17 | 0 | 0 | 0 | 0 | 8 | 16 | 21 | 144 | 136 | 88 | 22 | 2.1 | 60 | 73 | 43 | 49 | 130 | 102 | 63 | 78 | 40 | 0 | 18 | 35 | 10 | 315 | 24 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 149 | 18 | 30 | 100 | 0 | 0 | 0 | 88 | 0 | 4.509 | 142 | 0 | 0 |  | 927 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 43 | 0 | 22 | 12 | 11 | 0 | 69 | 280 | 0 | 0 | 196 | 0 | 0 | 0 | 92 | 0 | 190 | 0 | 411 | 35 | 0 | 0 | 0 | 0 | 0 | 2.8 | 12 |  | 9229.409 | DayPeak
Yesterday Evening Peak | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 358 | 352 | 0 | 0 | 420 | 230 | 93 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 69 | 0 | 25 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 25 | 209 | 0 | 104 | 0 | 0 | 0 | 0 | 51 | 100 | 95 | 50 | 19 | 6 | 0 | 100 | 0 | 345 | 275 | 194 | 68 | 127 | 33 | 48 | 0 | 27 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 178 | 126 | 95 | 22 | 0 | 60 | 73 | 46 | 49 | 163 | 100 | 65 | 76 | 40 | 0 | 18 | 42 | 10 | 295 | 24 | 11 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 88 | 0 | 0 | 142 | 0 | 0 |  | 929 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 6 | 0 | 40 | 173 | 19 | 64 | 0 | 50 | 0 | 17 | 0 | 26 | 50 | 42 | 0 | 52 | 0 | 22 | 12 | 11 | 0 | 67 | 280 | 0 | 17 | 181 | 0 | 0 | 0 | 95 | 0 | 172 | 0 | 383 | 53 | 0 | 113 | 33 | 108 | 0 | 0 | 0 |  | 11063 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 230 | 100 | 81 | 55 | 0 | 0 |  | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 84 | 0 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 95 | 50 | 22 | 10 | 0 | 100 | 0 | 360 | 360 | 225 | 68 | 141 | 30 | 48 | 0 | 27 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 172 | 140 | 95 | 22 | 0 | 60 | 73 | 50 | 50 | 163 | 100 | 68 | 76 | 40 | 0 | 20 | 42 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 88 | 100 | 0 | 260 | 54 | 113 |  | 936 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 33 | 110 | 30 | 50 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 35 | 22 | 12 | 11 | 0 | 68 | 280 | 17 | 17 | 225 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 230 | 100 | 81 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 45 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 84 | 0 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 95 | 50 | 22 | 10 | 0 | 100 | 0 | 360 | 360 | 225 | 68 | 140 | 30 | 48 | 0 | 27 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 131 | 140 | 95 | 22 | 1.6 | 60 | 73 | 50 | 50 | 163 | 100 | 68 | 76 | 40 | 0 | 20 | 42 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 88 | 0 | 4.4 | 230 | 54 | 113 |  | 936 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 50 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 12 | 11 | 0 | 68 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 130 | 0 | 280 | 0 | 0 | 364 | 305 | 0 | 0 | 330 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 0 | 25 | 0 | 0 | 85 | 85 | 100 | 0 | 0 | 216 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 19 | 6 | 0 | 100 | 0 | 290 | 290 | 198 | 16 | 127 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 102 | 159 | 0 | 0 | 0.3 | 60 | 73 | 11 | 10 | 100 | 101 | 67 | 10 | 10 | 0 | 0 | 17 | 0 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 9.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 16 | 0 | 0 | 0 | 679 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5 | 0 | 67 | 280 | 0 | 0 | 177 | 0 | 0 | 0 | 12 | 0 | 177 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0
199
| Minimum Generation |  | 7845 | 7:00
| Highest Generation |  | 11063 | 19:30
| Day Peak Generation |  | 9229.409 | 12:00
| Evening Peak Generation |  | 11063 | 19:30
| HVDC Max Flow |  | 929 | 14:00
| HVDC EvPeak Flow |  | 929 | 19:30
| Load factor L.F |  | 84.4%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9229.409 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6914.9 | MW
Evening Peak Generation : |  | 11063 | MW Hour : | 19:30 | Available Max Generation : |  | 14545 | MW
E.P. Demand (at gen end) : |  | 11063 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 11063 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4045 | MW
Total Gen. (MKWH) : |  | 224.083 | System Load Factor : | 84.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 90 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-24
Actual : | 102.63 | Ft.(MSL) , | Rule curve : | 108.2 | Ft.( MSL )
Gas Consumed : | Total = | 1210.02 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 135674557.792
: |  | Coal : | 38129813.66 | Oil : | 341700217.43 | Total : | 515504588.882
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3716.5874 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1262.1681 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1130.5619 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1021.4519 |  |  | 0 | 0%
) | 0 | 0:00 | 923.1298 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 744.9289 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 418.686 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 191.8563 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 574.5158 |  |  | 0 | 0%
Total | 0 |  | 9983.886 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1. | 6) Sirajganj 225 MW Unit-2
|  |  |  | 2) Khulna ST 110 MW | 7) Raozan #2
|  |  |  | 3) Sikalbaha ST 60 MW | 8) Siddirganj-335 MW
|  |  |  | 4) Sylhet-150 MW. | 9) Ashuganj unit-3
5) Ghorasal Unit-1,3 & 5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sikalbaha 132/33 kV T-4 transformer tripped at 07:45 from both end showing O/C & E/F relays at 132
kV end & O/C relay at 33 kV end and was switched on at 08:10.
b) Aminbazar-Kaliakoir 230 kV Ckt-1 was under shut down from 09:02 to 16:14 for A/M.
c) Julda-Halishahar 132 kV Ckt was under shut down from 08:42 to 13:43 for D/W.
d) After maintenance Baghabari-100 MW was synchronized at 13:25.
e) Daudkandi 132/33 kV T-1 transformer was under shut down from 12:24 to 13:04 for A/M.
f) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 08:07 to 11:30 for C/M.
g) Palashbari 132 kV Bus-A was under shut down from 08:30 to 15:35 for A/M.
h) Chapainawabganj 132/33 kV T-1 transformer was under shut down from 07:56 to 15:02 for A/M.
i) Bagura-Sherpur 132 kV Ckt-1 was under shut down from 09:18 to 17:03 for A/M.
j) Sherpur-Sirajganj 132 kV Ckt-1 was under shut down from 08:15 to 15:18 for A/M.
k) Mohastangarh 132/33 kV T-1 transformer was under shut down from 09:10 to 15:20 for A/M.
l) Joypurhat 132/33 kV T-1 transformer was under shut down from 08:58 to 15:37 for A/M.
m) Bheramara HVDC 20DF-11 Bay was under shut down from 09:45 to 16:15 for C/M.
n) Rangpur 132/33 kV T-2 transformer is under shut down since 06:50(24/10/19) for D/W. |  |  |  |  | About 05 MW power interruption occurred under Rangpur S/S area
since 06:50(24/10/19).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 775000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4685000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 8047745
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 358 | 8623920 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 352 | 8061000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9662500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 271680 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 5853207 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 81 | 1171632 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 706925
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 36407 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 481212
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 637440
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 32976 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 25 | 0 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 654120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 600480 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 445216
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 397546
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 69 | 1274880 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1273920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 746700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 823300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 41964 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 1111717
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3160800
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1359480 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 3311 | 60936767
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 69645
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122580
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 685440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 84 | 1869573 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 209 | 4858736
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2792352 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 483463 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 817080
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1403520
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 416160
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 6 | 111240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 2275200 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 142 | 3312000 | Transformer & Line overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer & Line overload
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer & Line overload
| Chattogram area Total |  |  |  | 2166 | 1085 | 21645429
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2453960 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 4529000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7607500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7069000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 693432 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 48 | 1215840 | Engine problem
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1589090 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 27 | 541736 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 16727 | Transformer & Line overload
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 127 | 2991380
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2933760
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 335880
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 182520 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 178 | 3582720
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 681100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 278746
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 498580 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1730 | 37200971
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3036520 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 464654
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1992960
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 530400 | High Voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1201200
| Mymensingh Area Total |  |  |  | 637 | 458 | 7235884
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1428000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 73 | 1722000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3415124
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2291000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 46 | 918000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1075032
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 256992
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1576320 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1654080
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 928080 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 444000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 42 | 790760 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 581472
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7303300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250560
| Sylhet Area Total |  |  |  | 1949 | 1072 | 24634720
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 929 | 22261091
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 172800 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 6 | 96000 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 92416 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8808192 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 225750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 949920 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 33 | 176832 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1453 | 32783001
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 967392 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 19 | 529581 | Machine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 4178550 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 2041589
| Barisal Area Total |  |  |  | 462 | 351 | 7717112
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 449000
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 17 | 91395 | Low demand
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 468700
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 623003 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 70851 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 181 | 4492564 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 172 | 4493764 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 383 | 9087091 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 30073 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 511440
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 12 | 273276
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235026
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 824160
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 26 | 134568 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 694080
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 126720 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1131 | 22605711
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 67 | 1605818
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6821700
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 84000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 108 | 788160
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23679
| Rangpur Area Total |  |  |  | 605 | 472 | 9323357
| Total |  |  |  | 19018 | 11063 | 224082952
| Eastern Grid Total |  |  |  | 13454 | 7656 | 151653771
| Western Grid Total |  |  |  | 5564 | 3407 | 72429181
| National Grid Total |  |  |  | 19018 | 11063 | 224082952
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-23
(a) ENTIRE EASTERN GRID : |  | 7482 | MW | (b) ENTIRE WESTERN GRID : |  | 3025 | MW
i) Dhaka area |  | 3981 | MW | i) Khulna area |  | 1116 | MW
ii) Chittagong area |  | 1161 | MW | ii) Rajshahi area |  | 1054 | MW
iii) Comilla area |  | 1063 | MW | iii) Barisal area |  | 246 | MW
iv) Mymensingh area |  | 830 | MW | iv) Rangpur area |  | 609 | MW
v) Sylhet area |  | 447 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10507 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 1800 | Srimongal | 36 | 1830 | Bottail | 110 | 1830
Munsiganj | 98 | 1830 | Shahjibazar | 112 | 1800 | G.K Project | 53 | 1830
Sonargaon | 76 | 2000 | Fenchuganj | 37 | 1800 | Faridpur | 160 | 1830
Shyampur | 196 | 900 | Kulawara | 41 | 1800 | Madaripur | 70 | 100
Bhulta | 184 | 1000 | Sylhet | 127 | 1830 | Sariatpur | 50 | 1830
Madanganj | 51 | 100 | Chatak | 25 | 1800 | Gopalganj | 65 | 100
Shitalakhya | 98 | 1000 | Sunamganj | 36 | 2000 | Bagerhat | 62 | 1930
Rahim steel | 18 | 900 | Biani Bazar | 50 | 1800 | Mongla | 38 | 1200
Matuail | 98 | 900 | Comilla (S) | 178 | 1930 | Satkhira | 68 | 1930
Ghorasal | 80 | 1930 | Comilla(N) | 113 | 1900 | Gallamari | 45 | 1200
Narsingdi | 141 | 1900 | Chandpur | 91 | 1830 | Magura | 46 | 1800
Haripur (SBU) | 92 | 1930 | Feni | 136 | 1900 | Norail | 20 | 1800
Ullon | 81 | 2000 | Chowmuhani | 164 | 1900 | Chuadanga | 81 | 1830
Hasnabad | 187 | 1830 | Ashuganj | 55 | 2100 | Barisal(N) | 32 | 100
Magbazar | 129 | 1100 | Daudkandi | 124 | 1830 | Barisal (S) | 90 | 1500
Maniknagar | 112 | 1300 | B.Baria | 132 | 2100 | Patuakhali | 94 | 1830
Bangabhaban | 22 | 1200 | Ramganj | 86 | 1930 | Bhandaria | 38 | 1830
Narinda | 100 | 1300 | Madunaghat | 60.5 | 1930 | Borhan Uddin | 33 | 1930
Dhanmondi | 179 | 1200 | Hathazari | 102 | 1830 | Ishurdi | 57 | 1800
Lalbag | 86 | 1300 | Khulshi | 190 | 1800 | Ruppur Paromanobik | 2 | 1800
Madartek | 58 | 2000 | Halishahar | 143 | 1500 | Natore | 108 | 1830
Mirpur | 105 | 1830 | Baraulia | 162 | 600 | Bogra | 169 | 1830
Kalyanpur | 99 | 1830 | Sikalbaha | 25 | 1830 | Noagaon | 96 | 1830
Gulshan | 146 | 1100 | Dohazari | 88 | 1900 | Rajshahi | 118 | 1930
Uttara | 56 | 1800 | Cox'sbazar | 92 | 1900 | Rajshahi New | 12 | 2000
Uttara New | 43 | 1100 | Chandraghona | 28 | 1900 | C.Nawabganj | 67 | 1830
Kamrangirchar | 72 | 1800 | Kaptai | 4.5 | 1800 | Amnura | 28 | 1830
Savar | 122 | 1900 | A. Khaer Stl. | 7 | 1100 | Pabna | 104 | 1900
Bhasantec | 154 | 1800 | Bakulia | 106 | 1800 | Shahjadpur | 98 | 2000
Agargaon | 58 | 1000 | Julda | 24 | 1100 | Serajganj | 85 | 1900
Satmosjid | 111 | 1800 | TK chemical | 17 | 1800 | Niyamatpur | 52 | 1800
Tongi | 144 | 900 | Modern Steel | 12 | 600 | Joypurhat | 48 | 1900
Kabirpur | 208 | 1800 | Shahmirpur | 30 | 1830 | Sherpur(Bogura) | 36 | 2000
Basundhara | 119 | 1600 | Khagrachhari | 20 | 2000 | Mohastangor | 12 | 2000
Manikganj | 82 | 1900 | Matarbari | 28.5 | 2000 | Rangpur | 116 | 1800
Joydevpur | 211 | 1900 | Baroiar Hat | 24 | 1800 | Lalmonirhat | 46 | 1830
New Tongi | 105 | 1830 | Rangamati | 12 | 1800 | Saidpur | 89 | 1800
Korda | 226 | 1830 | Abul Khair 230 | 11 | 900 | Purbasadipur | 86 | 1830
Dhamrai | 54 | 1930 | BSRM | 109 | 100 | Thakurgaon | 56 | 1930
Valuka | 102 | 1830 | GPH Ispat | 0.13 | 700 | Palashbari | 98 | 1830
Tangail | 164 | 1830 | Goalpara | 21 | 700 | Barapukuria | 43 | 1830
Mymensing | 201 | 1930 | Central s/s | 87 | 1300 | Panchagar | 38 | 1930
Kishorganj | 104 | 1900 | Noapara | 65 | 1800 | Joldhaka | 20 | 1800
Netrokona | 82 | 1900 | Jessore | 108 | 1800 | Kurigram | 40 | 1800
Jamalpur | 106 | 1930 | Benapol | 34 | 1830 | 0 | 0 | 0
Sherpur | 84 | 1830 | Jhenida | 98 | 1800 | 0 | 0 | 0
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-23 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 387 | 20:00 | 376 | 12:00 | Kaliakoir | 367 | 19:00 | 354 | 12:00
Bheramara | 396 | 24:00 | 390 | 19:00 | Bhulta | 376 | 20:00 | 356 | 12:00
Ashuganj(N) | 381 | 20:00 | 362 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
Ghorasal | 228 | 18:30 | 220 | 15:00 | Hathazari | 219 | 19:30 | 215 | 7:00
Ishurdi | 235 | 17:00 | 225 | 11:00 | Megnaghat | 221 | 19:00 | 210 | 12:00
Ashuganj | 232 | 20:00 | 223 | 10:00 | Fenchuganj | 234 | 20:00 | 227 | 12:00
Serajganj | 231 | 22:00 | 227 | 10:00 | Siddhirganj | 219 | 18:30 | 207 | 12:00
Baghabari | 236 | 7:00 | 231 | 9:00 | Maniknagar | 217 | 19:00 | 205 | 12:00
Barapukuria | 230 | 1:00 | 223 | 12:00 | Old Airport | 217 | 20:00 | 205 | 11:00
Bogra | 228 | 5:00 | 223 | 11:00 | Barisal | 235 | 18:00 | 221 | 11:00
Khulna South | 228 | 17:00 | 210 | 11:00 | AKSML | 215 | 1:00 | 209 | 16:00
Rampura | 220 | 19:30 | 209 | 12:00 | BSRM | 217 | 20:00 | 211 | 12:00
Haripur | 218 | 21:00 | 207 | 12:00 | Bibiyana | 231 | 21:00 | 218 | 18:00
Hasnabad | 216 | 19:00 | 209 | 11:00 | Bhulta | 221 | 21:00 | 208 | 12:00
Aminbazar | 218 | 5:00 | 205 | 12:00 | Ashuganj (S) | 231 | 20:00 | 221 | 12:00
Tongi | 220 | 20:00 | 206 | 11:00 | Kaliakoir | 223 | 20:00 | 210 | 10:00
Comilla (N) | 227 | 20:00 | 219 | 12:00 | GPH | 216 | 20:00 | 210 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 2000 | 123 | 1100 | Halishahar | 131 | 300 | 126 | 1800
Munsiganj | 134 | 1830 | 124 | 900 | Baraulia | 130 | 2000 | 125 | 1500
Megnaghat | 130 | 2000 | 122 | 1100 | Sikalbaha | 132 | 2000 | 129 | 400
Shyampur | 132 | 1900 | 124 | 1200 | Dohazari | 130 | 700 | 125 | 1400
Bhulta | 125 | 1800 | 118 | 1100 | Cox'sbazar | 126 | 800 | 115 | 1830
Madanganj | 132 | 1830 | 124 | 1200 | Chandraghona | 131 | 800 | 127 | 1500
Shitalakhya | 134 | 1830 | 124 | 1200 | Kaptai | 131 | 2100 | 127 | 1200
Rahim steal | 131 | 1930 | 124 | 1300 | A. Khaer Stl. | 129 | 100 | 125 | 1200
Matuail | 131 | 2000 | 121 | 1200 | Bakulia | 130 | 700 | 126 | 1500
Ghorasal | 135 | 100 | 130 | 1200 | Julda | 132 | 2000 | 127 | 1500
Narsinghdi | 131 | 600 | 126 | 1830 | TK Chemical | 131 | 2000 | 127 | 1600
Haripur (SBU) | 132 | 2000 | 125 | 900 | Modern Steel | 130 | 100 | 126 | 1500
Ullon | 135 | 700 | 126 | 1200 | Shahmirpur | 132 | 2000 | 127 | 1600
Hasnabad | 132 | 600 | 125 | 1200 | Khagrachhari | 130 | 800 | 126 | 1500
Magbazar | 135 | 700 | 126 | 1200 | Matarbari | 126 | 900 | 119 | 1900
Maniknagar | 134 | 600 | 129 | 1200 | Baroiar Hat | 126 | 1930 | 124 | 1200
Bangabhaban | 134 | 600 | 129 | 1200 | Rangamati | 130 | 700 | 126 | 1500
Narinda | 134 | 600 | 129 | 1200 | Goalpara | 138 | 1800 | 125 | 1100
Dhanmondi | 135 | 700 | 126 | 1200 | Central s/s | 138 | 1800 | 128 | 100
Lalbag | 130 | 2000 | 120 | 1200 | Noapara | 133 | 1700 | 124 | 1100
Madartek | 136 | 600 | 125 | 1200 | Jessore | 131 | 1700 | 120 | 100
Mirpur | 134 | 500 | 126 | 1100 | Benapol | 132 | 600 | 123 | 100
Kalyanpur | 135 | 600 | 127 | 1200 | Jhenida | 131 | 600 | 121 | 100
Gulshan | 135 | 600 | 125 | 1200 | Bottail | 135 | 600 | 129 | 1100
Uttara | 132 | 100 | 121 | 1200 | G.K Project | 143 | 1700 | 138 | 1000
Uttara New | 130 | 300 | 123 | 1100 | Faridpur | 134 | 1700 | 125 | 100
Kamrangirchar | 130 | 300 | 123 | 1200 | Madaripur | 138 | 1800 | 124 | 2300
Savar | 131 | 600 | 122 | 1200 | Sariatpur | 136 | 1800 | 123 | 2100
Bhasantec | 136 | 600 | 125 | 1200 | Gopalganj | 143 | 1800 | 126 | 2100
Agargaon | 137 | 700 | 128 | 1100 | Bagerhat | 139 | 1800 | 124 | 1100
Satmosjid | 136 | 600 | 127 | 1200 | Mongla | 135 | 1800 | 120 | 1100
Tongi | 133 | 2000 | 125 | 1100 | Satkhira | 138 | 1800 | 125 | 1100
Kabirpur | 131 | 1900 | 124 | 100 | Gallamari | 139 | 1800 | 126 | 1100
Basundhara | 133 | 2000 | 121 | 1200 | Magura | 130 | 1600 | 121 | 1830
Manikganj | 136 | 1900 | 128 | 1200 | Norail | 130 | 600 | 120 | 1830
Joydevpur | 135 | 2000 | 126 | 1200 | Chuadanga | 130 | 1300 | 115 | 1930
New Tongi | 132 | 1900 | 123 | 1200 | Barisal(N) | 141 | 1800 | 130 | 1100
Kodda | 134 | 1930 | 122 | 500 | Barisal (S) | 137 | 1700 | 128 | 1100
Dhamrai | 131 | 2000 | 126 | 1200 | Patuakhali | 135 | 600 | 130 | 1100
Valuka | 125 | 200 | 116 | 1200 | Bhandaria | 137 | 1800 | 125 | 1100
Tangail | 130 | 200 | 124 | 1200 | Ishurdi | 139 | 1800 | 134 | 1100
Mymensing | 127 | 100 | 120 | 1100 | Ruppur Paromanobik | 138 | 1700 | 134 | 1200
Kishorganj | 129 | 400 | 125 | 1200 | Natore | 139 | 1600 | 131 | 300
Netrokona | 126 | 100 | 118 | 1100 | Bogra | 138 | 600 | 134 | 1100
Jamalpur | 138 | 2000 | 123 | 1200 | Noagaon | 133 | 600 | 130 | 1930
Sherpur | 138 | 2000 | 121 | 800 | Rajshahi | 135 | 1500 | 125 | 200
Srimongal | 135 | 300 | 133 | 1900 | Rajshahi New | 136 | 1700 | 125 | 200
Shahjibazar | 136 | 500 | 132 | 1800 | C.Nawabganj | 132 | 1600 | 122 | 100
Fenchuganj | 134 | 700 | 130 | 1830 | Amnura | 137 | 1800 | 123 | 300
Khulawara | 133 | 500 | 130 | 1500 | Pabna | 137 | 1700 | 131 | 1100
Sylhet | 132 | 600 | 127 | 1800 | Shahjadpur | 140 | 100 | 136 | 1000
Chatak | 131 | 600 | 16 | 1800 | Serajganj | 136 | 500 | 130 | 1100
Sunamganj | 130 | 700 | 125 | 1900 | Niyamatpur | 134 | 1600 | 126 | 1100
Biani Bazar | 131 | 800 | 125 | 1800 | Joypurhat | 135 | 600 | 130 | 1930
Comilla(s) | 126 | 600 | 120 | 1800 | Sherpur(Bogura) | 137 | 500 | 131 | 1200
Comilla(n) | 134 | 700 | 129 | 1200 | Mohastangor | 136 | 600 | 132 | 1200
Chandpur | 135 | 2300 | 130 | 900 | Rangpur | 127 | 100 | 118 | 1200
Feni | 125 | 700 | 122 | 1800 | Lalmonirhat | 124 | 400 | 115 | 1200
Chowmuhani | 124 | 1300 | 120 | 1930 | Saidpur | 125 | 700 | 118 | 1200
Ashuganj | 136 | 700 | 132 | 1200 | Purbasadipur | 123 | 300 | 114 | 1200
Daudkandi | 127 | 1830 | 122 | 1200 | Thakurgaon | 120 | 100 | 112 | 1800
B.Baria | 132 | 600 | 128 | 1830 | Palashbari | 133 | 600 | 127 | 1000
Ramganj | 124 | 2200 | 120 | 1900 | Barapukuria | 130 | 100 | 123 | 1300
Madanhat | 132 | 1930 | 127 | 1500 | Panchagar | 120 | 400 | 109 | 1800
Hathazari | 130 | 300 | 127 | 1500 | Joldhaka | 125 | 400 | 116 | 1200
Khulshi | 129 | 2000 | 125 | 1300 | Kurigram | 124 | 100 | 115 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 400 | 6364 | 2989 | 9353 |  |  |  | QF-LDC-12
0:30 | 338 | 6442.5 | 2992 | 9434.5 | Date: | 2019-10-23
1:00 | 276 | 6521 | 2995 | 9516
1:30 | 293 | 6413 | 2925.5 | 9338.5
2:00 | 310 | 6305 | 2856 | 9161
2:30 | 325 | 6196.5 | 2841 | 9037.5 | [5 empty] | Gen. at Eve. Peak | 11063 | 11063 MW (19:30 )
3:00 | 340 | 6088 | 2826 | 8914 | [6 empty] | 19:30
3:30 | 360 | 5970 | 2792 | 8762 | [5 empty] | Gen. at Day Peak | 9229.409 | 9229.409 MW (12:00 )
4:00 | 380 | 5852 | 2758 | 8610 | [6 empty] | 12:00
4:30 | 432 | 5741 | 2753.5 | 8494.5 | [5 empty] | Highest Generation | 11063
5:00 | 484 | 5630 | 2749 | 8379 | [6 empty] | 19:30
5:30 | 457 | 5552 | 2695 | 8247
6:00 | 430 | 5474 | 2641 | 8115
6:30 | 410 | 5338 | 2642 | 7980
7:00 | 390 | 5202 | 2643 | 7845
7:30 | 390 | 5264.4 | 2660 | 7924.4
8:00 | 390 | 5326.8 | 2677 | 8003.8
8:30 | 432.5 | 5489.625 | 2707.3 | 8196.925
9:00 | 475 | 5652.45 | 2737.6 | 8390.05
9:30 | 510 | 5781.385 | 2745.2 | 8526.585
10:00 | 545 | 5910.32 | 2752.8 | 8663.12
10:30 | 507.5 | 6022.66 | 2770.4 | 8793.06
11:00 | 470 | 6135 | 2788 | 8923
11:30 | 482.5 | 6214.3045 | 2861.9 | 9076.2045
12:00 | 495 | 6293.609 | 2935.8 | 9229.409
12:30 | 460 | 6286.3045 | 2939.4 | 9225.7045
13:00 | 425 | 6279 | 2943 | 9222
13:30 | 457.5 | 6137.7325 | 2964.6 | 9102.3325
14:00 | 490 | 5996.465 | 2986.2 | 8982.665
14:30 | 557.5 | 6046.349 | 2987 | 9033.349
15:00 | 625 | 6096.233 | 2987.8 | 9084.033
15:30 | 622.5 | 6062.7285 | 2956.8 | 9019.5285
16:00 | 620 | 6029.224 | 2925.8 | 8955.024
16:30 | 615 | 6016.6725 | 2940.45 | 8957.1225
17:00 | 610 | 6004.121 | 2955.1 | 8959.221
17:30 | 491 | 6478.5605 | 3278.05 | 9756.6105
18:00 | 372 | 6953 | 3601 | 10554
18:30 | 301 | 7291 | 3509 | 10800
19:00 | 230 | 7629 | 3417 | 11046
19:30 | 180 | 7656 | 3407 | 11063
20:00 | 90 | 7614 | 3297 | 10911 |  |  |  | Executive Engineer
20:30 | 130 | 7455.5 | 3304 | 10759.5 |  |  |  | Network Operation Division
21:00 | 170 | 7297 | 3311 | 10608
21:30 | 250 | 7175 | 3265.5 | 10440.5
22:00 | 330 | 7053 | 3220 | 10273 |  |  |  |  | Page 6 of 7
22:30 | 375 | 6816.5 | 3173 | 9989.5
23:00 | 420 | 6580 | 3126 | 9706
23:30 | 410 | 6472 | 3057.5 | 9529.5
24:00 | 400 | 6364 | 2989 | 9353
11063 MW (19:30 )
9229.409 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-23 |  | Energy | 224082952
[10 empty] | 2019-10-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4107 | 923 | 2153 | 1546 | 347 | 81 | 32 | 0 | 164
0:30 | 4089 | 925 | 2186.5 | 1615 | 347 | 82.5 | 29.5 | 0 | 160 | Date: | 2019-10-23
1:00 | 4071 | 927 | 2220 | 1684 | 347 | 84 | 27 | 0 | 156
1:30 | 4082.5 | 927 | 2220 | 1503 | 347 | 84 | 22 | 0 | 153 | [7 empty] | Total Energy | 224.083 | Total Energy Gen 224.083 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 224.083 MKWHr
2:00 | 4094 | 927 | 2220 | 1322 | 347 | 84 | 17 | 0 | 150 | [7 empty] | Energy not Served | 0
2:30 | 4099.5 | 927 | 2223.5 | 1192.5 | 347 | 84 | 17 | 0 | 147 | [7 empty] | Energy Requirement | 224.083
3:00 | 4105 | 927 | 2227 | 1063 | 347 | 84 | 17 | 0 | 144
3:30 | 4113 | 927 | 2209 | 923 | 347 | 84 | 17 | 0 | 142 | [6 empty] | Shortage
4:00 | 4121 | 927 | 2191 | 783 | 347 | 84 | 17 | 0 | 140
4:30 | 4067.5 | 927 | 2188 | 725 | 347 | 84 | 17 | 0 | 139
5:00 | 4014 | 927 | 2185 | 667 | 347 | 84 | 17 | 0 | 138
5:30 | 3997 | 926.5 | 2077.5 | 667 | 347 | 84 | 17 | 0 | 131
6:00 | 3980 | 926 | 1970 | 667 | 347 | 84 | 17 | 0 | 124
6:30 | 3965 | 927 | 1866 | 655.5 | 347 | 82 | 17 | 0 | 119 |  |  |  |  | Coal
7:00 | 3950 | 928 | 1762 | 644 | 347 | 80 | 17 | 0 | 114
7:30 | 3949 | 927.5 | 1740 | 740 | 347.5 | 82 | 16.5 | 0 | 115 |  |  |  | Oil |  |  |  | ,
8:00 | 3948 | 927 | 1718 | 836 | 348 | 84 | 16 | 0 | 116
8:30 | 4031.5 | 927 | 1795 | 884.5 | 348 | 63 | 16 | 0 | 117
9:00 | 4115 | 927 | 1872 | 933 | 348 | 42 | 16 | 0 | 118
9:30 | 4113.5 | 927 | 1925.5 | 1007.5 | 348 | 42 | 15.5 | 0 | 126
10:00 | 4112 | 927 | 1979 | 1082 | 348 | 42 | 15 | 0 | 134
10:30 | 4088 | 927 | 2027.5 | 1162.5 | 348 | 63 | 15 | 0 | 137
11:00 | 4064 | 927 | 2076 | 1243 | 348 | 84 | 15 | 0 | 140
11:30 | 4117 | 927 | 2116 | 1300 | 348.5 | 84 | 15 | 0 | 142
12:00 | 4170 | 927 | 2156 | 1357 | 349 | 84 | 15 | 0 | 144
12:30 | 4135 | 927 | 2159 | 1393 | 348 | 84.5 | 7.5 | 0 | 145
13:00 | 4100 | 927 | 2162 | 1429 | 347 | 85 | 0 | 0 | 146
13:30 | 4100 | 927 | 2162 | 1429 | 347 | 85 | 0 | 0 | 146
14:00 | 4100 | 927 | 2162 | 1429 | 347 | 85 | 0 | 0 | 146
14:30 | 4026.5 | 928 | 2116 | 1481 | 347.5 | 83.5 | 0 | 0 | 150
15:00 | 3953 | 929 | 2070 | 1533 | 348 | 82 | 0 | 0 | 154
15:30 | 3905 | 929 | 2047 | 1535.5 | 347.5 | 82 | 11 | 0 | 152
16:00 | 3857 | 929 | 2024 | 1538 | 347 | 82 | 22 | 0 | 150
16:30 | 3869.5 | 928.5 | 1996 | 1520.5 | 347 | 82.5 | 61 | 0 | 149
17:00 | 3882 | 928 | 1968 | 1503 | 347 | 83 | 100 | 0 | 148
17:30 | 3928.5 | 928.5 | 2044 | 1998 | 346.5 | 83 | 266 | 0 | 162
18:00 | 3975 | 929 | 2120 | 2493 | 346 | 83 | 432 | 0 | 176
18:30 | 3980 | 928.5 | 2142 | 2780.5 | 346 | 83.5 | 363.5 | 0 | 176
19:00 | 3985 | 928 | 2164 | 3068 | 346 | 84 | 295 | 0 | 176
19:30 | 4121 | 929 | 2173 | 3014 | 347 | 84 | 217 | 0 | 178
20:00 | 4028 | 928 | 2127 | 3022 | 347 | 84 | 199 | 0 | 176
20:30 | 4050.5 | 928.5 | 2152 | 2845.5 | 347 | 84 | 179 | 0 | 173
21:00 | 4073 | 929 | 2177 | 2669 | 347 | 84 | 159 | 0 | 170
21:30 | 4066.5 | 929 | 2167 | 2523.5 | 347 | 83.5 | 155 | 0 | 169
22:00 | 4060 | 929 | 2157 | 2378 | 347 | 83 | 151 | 0 | 168
22:30 | 4099 | 929 | 2143 | 2114.5 | 347 | 82 | 108 | 0 | 167
23:00 | 4138 | 929 | 2129 | 1851 | 347 | 81 | 65 | 0 | 166
23:30 | 4122.5 | 926 | 2141 | 1698.5 | 347 | 81 | 48.5 | 0 | 165 | Max Temp. in Dhaka |  | 31° C
24:00 | 4107 | 923 | 2153 | 1546 | 347 | 81 | 32 | 0 | 164
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 224.083 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 224.083 MKWHr
Note on W13: Author:

## Generation
2019-10-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 84 | 84 | 84 | 84 | 84 | 84 | 80 | 84 | 42 | 42 | 84 | 84 | 85 | 84 | 82 | 82 | 83 | 83 |  | 84 | 84 | 84 | 84 | 83 | 81 | 81 | 1869573
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 0 | 7 |  | 25 | 25 | 25 | 8 | 0 |  | 0 | 69645
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 8 | 13 | 16 | 17 | 18 | 17 | 14.29 | 10.18 | 4.26 | 0 | [9 empty] | 122580
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 204 | 204 | 204 | 204 | 204 | 204 | 216 | 213 | 210 | 219 | 205 | 178 | 178 | 205 | 205 | 205 |  | 204 | 209 | 204 | 205 | 205 | 204 | 205 | 4858736
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 134 | 133 | 134 | 134 | 104 | 104 | 104 | 104 | 105 | 104 | 104 | 124 | 140 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 134 | 134 | 134 | 134 | 2792352
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 15 | 15 | 15 | 0 |  |  |  | 0 | 51 |  | 51 | 51 | 50 | 36 | 51 | 0 |  | 483463
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [9 empty] | 1 | 15 | 15 | 20 | 30 | 30 | 30 | 30 | 95 |  | 285 | 300 | 300 | 65 | 0 | 0 |  | 1111717
19 | Ashuganj 195MW PP (APSCL-United) | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1589090
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 775000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 160 | 150 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4685000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8047745
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 110 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2453960
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 30 | 30 | 30 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 693432
33 | Ashuganj 225 MW CCPP | 180 | 180 | 180 | 179 | 187 | 179 | 180 | 180 | 217 | 200 | 195 | 202 | 182 | 185 | 193 | 180 | 178 | 181 |  | 180 | 194 | 180 | 180 | 180 | 191 | 181 | 4529000
34 | Ashuganj 450 MW CCPP(South) | 315 | 315 | 315 | 315 | 280 | 280 | 280 | 280 | 310 | 330 | 320 | 350 | 305 | 265 | 275 | 260 | 260 | 260 |  | 260 | 275 | 260 | 260 | 260 | 280 | 260 | 7069000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 280 | 270 | 270 | 270 | 295 | 295 | 285 | 270 | 325 | 260 | 270 | 260 | 260 | 320 |  | 330 | 345 | 330 | 330 | 330 | 345 | 330 | 7607500
35 | Ashuganj 55 MW PP (Precision) | 53 | 54 | 53 | 54 | 52 | 53 | 53 | 52 | 53 | 53 | 49 | 49 | 48 | 47 | 47 | 48 | 48 | 48 |  | 48 | 48 | 49 | 49 | 50 | 52 | 53 | 1215840
36 | Chandpur 150 MW CCPP | 120 | 125 | 125 | 126 | 126 | 127 | 126 | 127 | 126 | 127 | 127 | 127 | 127 | 127 | 127 | 126 | 127 | 126 |  | 127 | 127 | 127 | 126 | 121 | 126 | 126 | 2991380
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 345 | 346 | 345 | 349 | 346 | 345 | 345 | 375 | 375 | 370 | 369 | 360 | 350 | 355 | 345 | 344 | 354 |  | 344 | 358 | 347 | 344 | 344 | 345 | 348 | 8623920
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 380 | 350 | 350 | 380 | 380 | 420 | 420 | 420 | 390 | 390 | 390 | 390 | 420 |  | 420 | 420 | 420 | 420 | 420 | 380 | 380 | 9662500
41 | Haripur 360MW CCPP(HPL) | 355 | 355 | 355 | 355 | 355 | 328 | 300 | 300 | 333 | 333 | 350 | 347 | 349 | 302 | 303 | 303 | 303 | 352 |  | 352 | 352 | 355 | 357 | 359 | 359 | 356 | 8061000
42 | RPCL 210MW CCPP | 126 | 127 | 127 | 144 | 144 | 156 | 156 | 155 | 140 | 138 | 138 | 136 | 125 | 122 | 121 | 123 | 125 | 125 |  | 126 | 126 | 125 | 108 | 109 | 126 | 126 | 3036520
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 50 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 58 | 59 |  | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 1428000
45 | Fenchugonj CCPP Phase-2 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1722000
46 | Shajibazar 330 MW CCPP | 100 | 100 | 102 | 100 | 102 | 101 | 100 | 101 | 102 | 102 | 103 | 102 | 99 | 101 | 102 | 100 | 99 | 100 |  | 101 | 100 | 102 | 100 | 100 | 101 | 100 | 2291000
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 66 | 66 | 66 | 66 | 67 | 66 | 66 | 64 | 64 | 63 | 63 | 63 | 64 | 63 | 65 | 65 | 65 |  | 66 | 65 | 66 | 66 | 66 | 65 | 65 | 1576320
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 79 | 79 | 79 | 10 | 10 | 10 | 50 | 79 | 78 | 78 | 78 | 78 | 78 | 79 | 79 |  | 76 | 76 | 78 | 78 | 79 | 79 | 79 | 1654080
49 | Shahjibazar 50MW PP (EPL) | 40 | 41 | 41 | 41 | 41 | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 42 | 42 | 41 | 928080
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 444000
52 | Sylhet 50MW PP (EPL) | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 21 | 21 | 21 | 32 | 35 | 38 | 39 | 40 | 40 | 42 | 40 |  | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 790760
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250560
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256992
55 | Fenchugonj 51 MW PP (Barakatullah) | 39 | 39 | 39 | 39 | 39 | 39 | 11 | 11 | 16 | 36 | 39 | 43 | 42 | 44 | 44 | 44 | 46 | 46 |  | 46 | 46 | 46 | 47 | 47 | 47 | 47 | 918000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 581472
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 300 | 295 | 290 | 280 | 280 | 290 | 310 | 320 | 315 | 315 | 310 | 300 | 310 | 290 | 285 | 300 |  | 280 | 295 | 290 | 290 | 275 | 270 | 300 | 7303300
58 | Nababganj 55 MW PP (Southern power ) | 0 | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 | 17 |  | 0 | 397546
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 416160
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 481212
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 464654
63 | Impoprt (Tripura) | 156 | 150 | 144 | 140 | 138 | 124 | 114 | 116 | 118 | 134 | 140 | 144 | 146 | 154 | 154 | 150 | 148 | 176 |  | 176 | 178 | 176 | 170 | 168 | 166 | 164 | 3582720
64 | Malancha, Ctg. EPZ (United) | 40 | 38 | 40 | 40 | 40 | 41 | 31 | 7 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 10 |  | 10 | 6 | 19 | 28 | 28 | 36 | 39 | 111240
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 0 | [6 empty] | 0 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 335880
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 182520
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 16 | 33 | 16 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 681100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 498580
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 28 | 31 | 31 | 30 | 27 | 31 | 28 | 28 | 28 | 22 | 28 | 28 | 31 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 673920
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 3 | 33 | 33 | 33 | 0 |  | 22 | 33 | 33 | 33 | 33 | 33 | 33 | 746700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823300
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 14 | 24 | 24 | 24 | 24 | 24 | 24 | 50 |  | 100 | 100 | 100 | 100 | 92 |  | 0 | 637440
78 | Gazipur 52 MW PP | [16 empty] | 0 | 14 |  | 25 | 0 |  |  |  |  | 0 | 41964
79 | Kodda 150MW PP | 10 | 0 | [14 empty] | 0 | 100 |  | 100 | 100 | 100 | 100 | 100 | 65 | 32 | 600480
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 48 | 48 | 48 | 48 | 48 | 58 | 68 | 88 | 91 | 90 | 90 | 90 | 90 | 91 |  | 96 | 95 | 95 | 95 | 92 | 92 | 95 | 1992960
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 0 | 7 |  | 51 | 52 | 52 | 52 | 52 | 25 | 25 | 278746
| Gazipur 100 MW PP | [7 empty] | 34 | 80 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 55 | 1359480
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3.05 | 3.92 | 4 | 4.509 | 4 | 3.475 | 2.653 | 0.564 | 0.121 | [9 empty] | 28440
Jodiac Power
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 64 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 50 |  | 80 | 81 | 81 | 81 | 81 | 81 | 60 | 1171632
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 0 | 11 |  | 18 | 0 |  |  |  |  | 0 | 36407
86 | Meghnaghat CCPP(Summit) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5853207
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 0 | 16 |  | 100 | 93 | 95 | 55 | 0 |  | 0 | 271680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 60 | 20 | 10 | 0 | [11 empty] | 0 | 80 |  | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 817080
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 18 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 20 | 38 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1075032
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 5 | 5 | 5 | 5 | 5 | 14 | 17 | 17 | 17 | 17 | 25 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 541736
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 0 | 7 |  | 16 | 0 | [5 empty] | 32976
95 | Patenga 50MW PP (Baraka) | 0 | [7 empty] | 18 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 46 | 13 | 0 | 685440
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 91 | 91 | 91 | 91 | 91 | 91 | 96 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 93 | 96 | 97 | 2275200
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 0 |  | 37 | 25 | 25 | 0
98 | Bosila 108MW PP(CLC) | 69 | 69 | 24 | 24 | 24 | 24 | 24 | 58 | 62 | 65 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 |  | 69 | 69 | 69 | 69 | 69 | 8 | 8 | 1274880
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [6 empty] | 0 | 10 | 35 | 48 | 48 | 48 | 48 | 48 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 15 | 0 | 706925
100 | Manikganj 55 MW PP (Northern) | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 |  | 55 | 55 | 55 | 55 | 55 | 0 | 0 | 445216
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3415124
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.8 | 1.4 | 1.4 | 1 | 2.1 | 1 | 0.7 | 0.4 | 0.4 | 0 | [9 empty] | 10150
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 35 | 0 | 654120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 7 | 7 | 0 | [13 empty] | 0 | 43 |  | 84 | 100 | 100 | 100 | 50 | 7 | 7 | 530400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 141 | 95 | 83 | 76 | 67 | 67 | 77 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3160800
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1403520
116 | Chandpur 200MW (Desh energy) | 200 | 160 | 105 | 50 | 17 | 17 | 0 | 0 | 0 | 25 | 68 | 100 | 125 | 140 | 140 | 140 | 140 | 170 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2933760
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 0 | 10 |  | 10 | 0 |  |  |  |  | 0 | 16727
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 80 | 60 | 0 | [8 empty] | 15 | 28 | 28 | 28 | 28 | 78 |  | 115 | 115 | 115 | 115 | 115 | 115 | 60 | 1201200
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 107 | 106 | 106 | 106 | 106 | 106 | 142 | 142 | 142 | 142 | 143 | 143 | 143 | 143 | 143 |  | 143 | 142 | 143 | 143 | 143 | 143 | 143 | 3312000
120 | Eastern Zone Total | 6521 | 6305 | 6088 | 5852 | 5630 | 5474 | 5202 | 5326.8 | 5652.45 | 5910.32 | 6135 | 6293.609 | 6279 | 5996.465 | 6096.233 | 6029.224 | 6004.121 | 6953 |  | 7629 | 7656 | 7614 | 7297 | 7053 | 6580 | 6364 | 151653771
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [15 empty] | 0 | 2 | 66 |  | 32 | 32 | 32 | 32 | 14 | 0 |  | 172800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 0 | 26 | 43 |  | 27 | 6 | 6 | 6 | 0 |  |  | 96000
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 | [9 empty] | 35 | 35 | 35 | 35 | 35 | 17 | 100 |  | 53 | 53 | 53 | 53 | 35 | 35 | 0 | 949920
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 80 | 32 | 16 | 16 | 0 |  |  |  |  | 0 | 32 | 32 | 32 | 32 | 16 | 64 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 967392
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 98 | 97 | 97 | 97 | 96 | 97 | 53 | 52 | 52 | 51 | 51 | 92 | 91 | 95 | 95 | 97 | 97 | 53 |  | 97 | 95 | 97 | 97 | 96 | 96 | 96 | 2041589
| Bhola 225 MW CCPP | 174 | 174 | 174 | 174 | 174 | 155 | 174 | 173 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 164 | 173 | 173 |  | 170 | 173 | 159 | 174 | 166 | 174 | 173 | 4178550
140 | Bhola 33 MW PP (Venture) | 30 | 27 | 26 | 26 | 26 | 20 | 20 | 20 | 19 | 20 | 20 | 20 | 21 | 22 | 22 | 20 | 21 | 31 |  | 32 | 19 | 2 | 21 | 23 | 25 | 24 | 529581
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 0 | [14 empty] | 0 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 225750
143 | Gopalganj 100 MW Peaking PP | [14 empty] | 0 | 22 | 31 | 31 |  | 6 | 0 | [5 empty] | 92416
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 17 | 0 | [14 empty] | 0 | 85 |  | 33 | 33 | 33 | 17 | 17 | 0 |  | 176832
146 | Bheramara HVDC | 927 | 927 | 927 | 927 | 927 | 926 | 928 | 927 | 927 | 927 | 927 | 927 | 927 | 929 | 929 | 929 | 928 | 929 |  | 928 | 929 | 928 | 929 | 929 | 929 | 923 | 22261091
147 | Bheramara 360 MW CCPP | 335 | 355 | 355 | 370 | 370 | 395 | 410 | 410 | 390 | 380 | 380 | 395 | 360 | 370 | 365 | 340 | 345 | 345 |  | 340 | 360 | 340 | 345 | 345 | 345 | 345 | 8808192
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 68 | 68 | 68 | 68 | 69 | 67 | 68 | 68 | 67 | 67 | 66 |  | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 1605818
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6821700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [13 empty] | 30 | 30 | 30 | 40 | 40 |  | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 449000
| Baghabari 50 MW Peaking PP | [15 empty] | 0 | 3 | 50 |  | 34 | 17 | 0 |  |  |  |  | 91395
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 181 | 190 | 187 | 175 | 165 | 154 | 156 | 171 | 173 | 177 | 196 | 191 | 170 | 166 | 158 | 167 | 188 |  | 167 | 181 | 180 | 181 | 180 | 181 | 188 | 4492564
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 193 | 190 | 190 | 190 | 178 | 164 | 160 | 164 | 165 | 171 | 174 | 190 | 205 | 180 | 174 | 159 | 156 | 165 |  | 155 | 172 | 171 | 187 | 187 | 188 | 197 | 4493764
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 394 | 393 | 395 | 363 | 395 | 322 | 363 | 343 | 375 | 375 | 376 | 411 | 420 | 414 | 418 | 389 | 356 | 361 |  | 369 | 383 | 337 | 356 | 344 | 382 | 377 | 9087091
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511440
163 | Bogura 20 MW PP (Energyprima) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 273276
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 0 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 235026
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 0 | 12 | 12 | 12 | 12 | 12 | 40 | 40 | 40 | 50 | 50 |  | 50 | 50 | 50 | 30 | 18 | 0 |  | 468700
166 | Katakhali 50 MW PP (Northern) | 16 | 0 | [5 empty] | 16 | 16 | 16 | 32 | 32 | 32 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 623003
167 | Katakhali 50 MW Peaking PP | [15 empty] | 0 | 6 | 48 |  | 0 | [6 empty] | 70851
168 | Santahar 50 MW Peaking PP | [15 empty] | 0 | 7 | 32 |  | 0 | [6 empty] | 30073
169 | Natore 52 MW PP (Rajlanka) | 25 | 0 | [5 empty] | 25 | 42 | 43 | 43 | 43 | 43 | 43 | 51 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 24 | 824160
170 | Chapainawabganj 100 MW Peaking PP | [15 empty] | 0 | 9 | 60 |  | 60 | 26 | 26 | 0 |  |  |  | 134568
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence) | [16 empty] | 0 | 40 |  | 110 | 113 | 113 | 113 | 113 | 100 | 62 | 694080
172 | Confidence Power Bogura Unit-1 113 MW | [8 empty] | 0 | 18 | 25 | 12 | 4 | 15 | 20 | 24 | 4 | 0 | [8 empty] | 126720
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [15 empty] | 0 | 18 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 84000
176 | Rangpur 113 MW PP (Confidence) | 53 | 10 | 0 | [13 empty] | 0 | 108 |  | 108 | 108 | 113 | 113 | 113 | 71 | 35 | 788160
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 1.6 | 2.8 | 4 | 2.8 | 4 | 2.2 | 1.8 | 0.8 | 0.1 | [9 empty] | 23679
178
178