## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-22 | Tuesday
|  | Date (day): | 2019-10-22 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13586 | MW |  |  | (b) At Evening Peak Hour : |  | 14823 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-21 | 2019-10-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 199 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 370 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 353 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 351 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 230 | 230 | 230
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 53 | 81 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 32 | 46 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 90 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under shut down
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 64 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 14 | 47 | 47
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 70 | 68 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 48 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 145 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 68 | 87 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2579 | 3303 | 3872 | 4272 | 501 | 965
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 46 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 83 | 89 | 170 | 170 | 60 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 205 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 134 | 145 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 71 | 85 | 85
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 88 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 12 | 15 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 89 | 95 | 95 | 95 |  | 13 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.7 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 120 | 161 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 113 | 113
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 848.2 | 1156 | 1538.4 | 1649 | 320 | 111
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 0 | 0 | 0 |  |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 90 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 214 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 340 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 280 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 27 | 27 | 27 |  | 18 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 52 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 68 | 68 | 68 | 127 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 127 | 128 | 140 | 141
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 61 | 200 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 180 | 128 | 170
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 32 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 50 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 20 | 20 |  | 5 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1560 | 1807 | 1986 | 2279 | 290 | 39
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 69 | 89 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 91 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 150 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 309.2 | 471 | 583.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 44 | 73 | 73 | 73
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 100 | 101 | 154 | 155 |  | 175 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 36 | 39 | 50 | 50
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 45 | 49 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 65 | 68 | 68 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 80 | 80 |  | 6 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 77 | 119 | 110 | 130
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 35 | 37 | 42 | 42 |  | 8 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1070 | 1198 | 1296 | 1317 | 0 | 599
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 927 | 926 | 936 | 936
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 35 | 66 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 75
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 265 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 48 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1342 | 1554 | 1986 | 2156 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 8 | 30 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 174 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 307 | 412 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 46 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 50 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 48 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 186 | 190 | 225 | 225 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 188 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 424 | 395 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 9 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 68 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 102 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 868 | 1316 | 1477 | 1627 | 220 | 171
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 67 | 68 | 68
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 284 | 283 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 15
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 107 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.6 | 0 | 8 | 0
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 0 | 0 |  |  | On test
| Rangpur Area Total |  |  |  |  | 798 | 718 | 388.6 | 490 | 469 | 493 | 0 | 85
| Total |  |  |  |  | 19541 | 19018 | 9272 | 11707 | 13586 | 14823 | 1383 | 1970
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8716.0126 | 11005 | 12771.3274 | 13934.1518
A. |  | 2019-10-21 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11707 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8102.34 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11707 | MW
3 | Day peak Generation : |  |  | 9272 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11005 | MW
4 | Evening peak Generation : |  |  | 11707 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 234.5714 | MKWHr | By Solar | 0.20454 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 151.6488 | MKWHr |  | By Oil: | 47.2916 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 7.4782 | MKWHr |  | By Hydro: | 1.9418 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1383 | MW | Dhaka | 4232 | 4232 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1970 | MW | Chittagong | 999 | 999 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3353 | MW | Khulna | 1362 | 1362 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1248.06 | MMCFD |  |  | Rajshahi | 1075 | 1075 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 142265351.734 | ii) Oil : | Taka | 412350094.72 | Comilla | 1098 | 1098 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 32050453.99 | Total | Taka | 586665900.444 | Mymensingh | 811 | 811 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 475 | 475 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 110 | MW (E to W) at | 19:00 | hrs | Barisal | 315 | 315 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 40 | MW at | 20:00 | hrs | Rangpur | 638 | 638 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.7° C |  |  | Total | 11005 | 11005 |  | 0
B. |  | 2019-10-22 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14823 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9100 | MW
4 | Reserve(Generation end) |  |  |  | 3123 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 234.4312 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7768.1 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3615 | MKWHr. | ii) HVDC Flow at Peak Time |  | 926 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6451 | MKWHr. | iii) Maximum HVDC Flow : |  | 939 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 102.8 | 102.88 |  | (b) Today: | 102.8 |  | (c) Rule Curve: |  | 108
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-10-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 357 | 353 |  | 0 | 400 | 230 | 0 | 97 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 208 | 0 | 134 | 0 |  | 0 | 0 | 79 | 90 | 90 | 12 | 19 | 25 | 80 | 90 | 0 | 320 | 325 | 193 | 16 | 126 | 27 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 152 | 123 | 95 | 22 | 0 | 60 | 44 | 42 | 49 | 163 | 101 | 66 | 78 | 40 | 122 | 17 | 43 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 34 | 0 | 0 | 197 | 0 | 0 |  | 938 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 279 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 201 | 0 | 426 | 70 | 0 | 35 | 33 | 42 | 0 | 0 | 0 |  | 6843 | 3108 | 9951 | 4321 | 938 | 2208 | 1905 | 279 | 37 | 111 | 152 | 0 | 0 | 102.9
2:00 | 35 | 0 | 201 | 0 | 370 | 0 | 0 | 353 | 355 |  | 0 | 400 | 230 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 17 | 90 | 90 | 0 | 19 | 20 | 80 | 90 | 0 | 310 | 315 | 179 | 16 | 127 | 27 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 148 | 123 | 95 | 22 | 0 | 60 | 44 | 42 | 49 | 163 | 102 | 67 | 78 | 40 | 113 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 0 | 0 | 0 | 197 | 0 | 0 |  | 937 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 186 | 0 | 0 | 0 | 96 | 0 | 196 | 0 | 415 | 70 | 0 | 0 | 11 | 32 | 0 | 0 | 0 |  | 6635 | 2962 | 9597 | 4250 | 937 | 2177 | 1735 | 280 | 37 | 33 | 148 | 0 | 0 | 102.9
3:00 | 35 | 0 | 202 | 0 | 370 | 0 | 0 | 350 | 355 |  | 0 | 400 | 230 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 40 | 90 | 0 | 19 | 39 | 80 | 90 | 0 | 310 | 315 | 179 | 16 | 126 | 27 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 144 | 144 | 95 | 22 | 0 | 60 | 44 | 42 | 49 | 163 | 103 | 67 | 78 | 40 | 113 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 93 | 0 | 100 | 160 | 0 | 0 | 115 | 0 | 0 | 0 | 197 | 0 | 0 |  | 938 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 24 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 24 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 187 | 0 | 0 | 0 | 97 | 0 | 193 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6401 | 2820 | 9221 | 4268 | 938 | 2212 | 1342 | 280 | 37 | 0 | 144 | 0 | 0 | 102.89
4:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 349 | 356 |  | 0 | 400 | 230 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 90 | 0 | 19 | 39 | 80 | 90 | 0 | 310 | 315 | 183 | 16 | 127 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 140 | 145 | 95 | 22 | 0 | 60 | 44 | 42 | 49 | 163 | 101 | 66 | 78 | 40 | 113 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 100 | 105 | 0 | 0 | 115 | 0 | 0 | 0 | 197 | 0 | 0 |  | 938 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 188 | 0 | 0 | 0 | 95 | 0 | 194 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6246 | 2805 | 9051 | 4269 | 938 | 2213 | 1126 | 280 | 85 | 0 | 140 | 0 | 0 | 102.89
5:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 354 | 355 |  | 0 | 400 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 60 | 0 | 19 | 40 | 80 | 90 | 0 | 325 | 330 | 194 | 16 | 126 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 136 | 144 | 95 | 22 | 0 | 60 | 44 | 42 | 49 | 163 | 101 | 66 | 78 | 40 | 115 | 17 | 43 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 70 | 34 | 0 | 0 | 50 | 0 | 0 | 0 | 143 | 0 | 0 |  | 938 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 280 | 0 | 0 | 187 | 0 | 0 | 0 | 95 | 0 | 199 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6039 | 2739 | 8778 | 4318 | 938 | 2219 | 802 | 280 | 85 | 0 | 136 | 0 | 0 | 102.88
6:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 370 | 356 |  | 0 | 400 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 85 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 19 | 40 | 80 | 90 | 0 | 300 | 275 | 161 | 16 | 126 | 27 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 130 | 145 | 95 | 22 | 0 | 59 | 44 | 42 | 49 | 163 | 101 | 66 | 78 | 40 | 76 | 17 | 43 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 10 | 17 | 0 | 0 | 50 | 0 | 0 | 0.022 | 71 | 0 | 0 |  | 938 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 280 | 0 | 0 | 185 | 0 | 0 | 0 | 97 | 0 | 200 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5658.022 | 2732 | 8390.022 | 4139 | 938 | 2213 | 605 | 280 | 85 | 0 | 130 | 0.022 | 0 | 102.88
7:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 348 | 320 |  | 0 | 400 | 230 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 34 | 80 | 90 | 0 | 260 | 265 | 165 | 16 | 126 | 27 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 114 | 144 | 95 | 22 | 0.3 | 60 | 44 | 42 | 49 | 100 | 102 | 66 | 75 | 40 | 70 | 17 | 43 | 10 | 300 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 4 | 10 | 17 | 0 | 0 | 50 | 0 | 0 | 0.96 | 71 | 0 | 0 |  | 937 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 280 | 0 | 0 | 181 | 0 | 0 | 0 | 95 | 0 | 163 | 0 | 425 | 0 | 0 | 0 | 0 | 60 | 0 | 0.2 | 0 |  | 5484.26 | 2750.2 | 8234.46 | 4034 | 937 | 2092 | 690 | 280 | 82 | 0 | 114 | 5.46 | 0 | 102.87
8:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 346 | 278 |  | 0 | 330 | 230 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 0 | 100 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 14 | 0 | 19 | 7 | 80 | 90 | 0 | 270 | 275 | 172 | 16 | 126 | 23 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 112 | 143 | 95 | 22 | 0.4 | 60 | 44 | 42 | 49 | 100 | 100 | 66 | 75 | 40 | 84 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 10.64 | 10 | 17 | 0 | 0 | 50 | 0 | 0 | 2.2 | 71 | 0 | 0 |  | 938 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 280 | 0 | 0 | 177 | 0 | 0 | 0 | 94 | 0 | 160 | 0 | 370 | 0 | 0 | 0 | 0 | 100 | 0 | 1.1 | 0 |  | 5380.24 | 2722.1 | 8102.34 | 3986 | 938 | 1893 | 797 | 280 | 82 | 0 | 112 | 14.34 | 0 | 102.87
9:00 | 35 | 0 | 201 | 0 | 300 | 0 | 0 | 361 | 355 |  | 0 | 360 | 230 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 17 | 26 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 54 | 3 | 19 | 2 | 80 | 90 | 0 | 340 | 315 | 179 | 16 | 120 | 23 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 124 | 71 | 91 | 22 | 1.5 | 60 | 44 | 39 | 49 | 130 | 100 | 65 | 75 | 40 | 70 | 17 | 42 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 15.6 | 10 | 17 | 0 | 0 | 80 | 68 | 0 | 3.6 | 120 | 0 | 0 |  | 938 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 94 | 0 | 168 | 0 | 383 | 0 | 0 | 0 | 0 | 100 | 0 | 1.1 | 0 |  | 5878.7 | 2735.1 | 8613.8 | 4051 | 938 | 2016 | 1100 | 280 | 83 | 0 | 124 | 21.8 | 0 | 102.87
10:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 346 | 325 |  | 0 | 360 | 230 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 71 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 0 | 0 | 205 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 90 | 12 | 19 | 2 | 80 | 90 | 0 | 280 | 290 | 179 | 16 | 126 | 23 | 54 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 126 | 71 | 91 | 22 | 1.8 | 60 | 44 | 39 | 49 | 100 | 100 | 64 | 75 | 40 | 72 | 17 | 40 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 18 | 10 | 17 | 0 | 0 | 80 | 68 | 0 | 4.4 | 120 | 0 | 0 |  | 939 | 0 | 315 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 24 | 174 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 167 | 0 | 0 | 0 | 92 | 0 | 155 | 0 | 396 | 35 | 0 | 0 | 0 | 100 | 0 | 2.2 | 0 |  | 5791.2 | 2811.2 | 8602.4 | 3881 | 939 | 1952 | 1314 | 280 | 84 | 0 | 126 | 26.4 | 0 | 102.86
11:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 362 | 346 |  | 0 | 400 | 230 | 0 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 35 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 0 | 100 | 0 | 0 | 208 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 90 | 12 | 19 | 2 | 80 | 90 | 0 | 300 | 305 | 194 | 40 | 127 | 23 | 53 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 134 | 70 | 91 | 22 | 1.8 | 60 | 44 | 36 | 45 | 100 | 100 | 63 | 78 | 40 | 79 | 17 | 40 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 5 | 0 | 149 | 4 | 15 | 17 | 0 | 0 | 99 | 68 | 0 | 4.8 | 120 | 0 | 0 |  | 938 | 0 | 315 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 24 | 174 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 18 | 14 | 8 | 0 | 0 | 280 | 0 | 0 | 181 | 0 | 0 | 0 | 93 | 0 | 169 | 0 | 423 | 35 | 0 | 0 | 0 | 100 | 0 | 3 | 0 |  | 6077.6 | 2855 | 8932.6 | 4051 | 938 | 2081 | 1353 | 280 | 82 | 0 | 134 | 13.6 | 0 | 102.86
12:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 351 | 348 |  | 0 | 400 | 230 | 0 | 53 | 32 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 89 | 12 | 19 | 2 | 80 | 90 | 0 | 315 | 315 | 180 | 63 | 127 | 27 | 51 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 33 | 17 | 142 | 69 | 91 | 22 | 2.2 | 60 | 44 | 36 | 45 | 130 | 100 | 61 | 80 | 40 | 77 | 17 | 35 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 19.5 | 50 | 61 | 0 | 0 | 109 | 68 | 0 | 4.7 | 120 | 0 | 0 |  | 927 | 0 | 305 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 284 | 0 | 0 | 186 | 0 | 0 | 0 | 93 | 0 | 190 | 0 | 424 | 35 | 0 | 0 | 0 | 100 | 0 | 4.6 | 0 |  | 6366.4 | 2905.6 | 9272 | 4066 | 927 | 2136 | 1603 | 284 | 83 | 0 | 142 | 31 | 0 | 102.86
13:00 | 35 | 0 | 197 | 0 | 330 | 0 | 0 | 348 | 347 |  | 0 | 400 | 230 | 0 | 64 | 44 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 69 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 89 | 12 | 19 | 2 | 80 | 90 | 0 | 340 | 315 | 179 | 63 | 126 | 27 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 152 | 69 | 83 | 22 | 2.1 | 60 | 44 | 42 | 45 | 130 | 101 | 62 | 80 | 40 | 107 | 17 | 35 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 150 | 18.6 | 50 | 120 | 0 | 0 | 115 | 68 | 0 | 4.3 | 124 | 0 | 0 |  | 926 | 0 | 295 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 285 | 0 | 0 | 197 | 0 | 0 | 0 | 91 | 0 | 195 | 0 | 412 | 35 | 0 | 0 | 0 | 107 | 0 | 5.2 | 0 |  | 6528 | 2946.2 | 9474.2 | 4124 | 926 | 2137 | 1721 | 285 | 83 | 16 | 152 | 30.2 | 0 | 102.85
14:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 348 | 324 |  | 0 | 350 | 230 | 0 | 64 | 43 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 68 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 89 | 12 | 19 | 5 | 80 | 90 | 0 | 340 | 315 | 179 | 63 | 126 | 27 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 156 | 90 | 91 | 22 | 1.9 | 60 | 44 | 42 | 45 | 100 | 100 | 61 | 80 | 40 | 71 | 17 | 35 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 16.3 | 50 | 122 | 0 | 0 | 115 | 70 | 0 | 3.5 | 140 | 0 | 0 |  | 927 | 0 | 285 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 173 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 49 | 280 | 0 | 0 | 161 | 0 | 0 | 0 | 92 | 0 | 161 | 0 | 400 | 35 | 0 | 0 | 0 | 107 | 0 | 5.3 | 0 |  | 6384.7 | 2921.3 | 9306 | 4000 | 927 | 2003 | 1765 | 329 | 83 | 16 | 156 | 27 | 0 | 102.85
15:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 373 | 324 |  | 0 | 350 | 230 | 0 | 64 | 43 | 0 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 68 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 85 | 0 | 100 | 0 | 0 | 218 | 0 | 135 | 0 |  | 0 | 0 | 3 | 20 | 89 | 12 | 19 | 2 | 0 | 90 | 0 | 360 | 290 | 173 | 63 | 126 | 27 | 47 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 156 | 79 | 91 | 22 | 0.7 | 60 | 42 | 39 | 45 | 130 | 102 | 62 | 80 | 40 | 122 | 17 | 37 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 11 | 70 | 120 | 0 | 0 | 115 | 70 | 0 | 2.4 | 161 | 0 | 0 |  | 926 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 60 | 285 | 0 | 0 | 181 | 0 | 0 | 0 | 92 | 0 | 177 | 0 | 399 | 53 | 0 | 0 | 0 | 107 | 0 | 3.6 | 0 |  | 6507.1 | 2992.6 | 9499.7 | 4059 | 926 | 2051 | 1841 | 345 | 85 | 19 | 156 | 17.7 | 0 | 102.85
16:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 362 | 346 |  | 0 | 350 | 230 | 0 | 64 | 43 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 69 | 0 | 0 | 17 | 35 | 55 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 75 | 0 | 100 | 0 | 0 | 204 | 0 | 143 | 0 |  | 0 | 0 | 6 | 30 | 95 | 12 | 19 | 8 | 0 | 100 | 0 | 340 | 260 | 186 | 63 | 127 | 27 | 48 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 0 | 19 | 152 | 76 | 91 | 20 | 0.4 | 60 | 53 | 42 | 48 | 130 | 100 | 63 | 80 | 40 | 114 | 17 | 36 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 6.5 | 100 | 120 | 4 | 0 | 115 | 70 | 0 | 1 | 161 | 0 | 0 |  | 927 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 8 | 173 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 67 | 285 | 0 | 0 | 202 | 0 | 0 | 0 | 91 | 0 | 199 | 0 | 398 | 53 | 0 | 0 | 0 | 107 | 0 | 1.1 | 0 |  | 6449.9 | 2972.1 | 9422 | 4012 | 927 | 2083 | 1770 | 352 | 75 | 42 | 152 | 9 | 0 | 102.84
17:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 350 | 311 |  | 0 | 350 | 230 | 0 | 64 | 43 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 69 | 0 | 0 | 17 | 35 | 55 | 19 | 25 | 27 | 33 | 16 | 0 | 0 | 75 | 0 | 100 | 0 | 0 | 205 | 0 | 110 | 0 |  | 0 | 0 | 4 | 30 | 95 | 12 | 19 | 9 | 0 | 100 | 0 | 290 | 280 | 179 | 63 | 120 | 27 | 49 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 146 | 74 | 91 | 22 | 0.1 | 59 | 72 | 11 | 10 | 130 | 102 | 65 | 50 | 20 | 71 | 17 | 19 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 0.7 | 100 | 120 | 4 | 0 | 78 | 70 | 0 | 0.1 | 161 | 0 | 0 |  | 926 | 0 | 275 | 0 | 16 | 0 | 0 | 0 | 15 | 53 | 8 | 173 | 21 | 64 | 0 | 0 | 0 | 5 | 10 | 15 | 6 | 8 | 0 | 8 | 9 | 22 | 9 | 11 | 0 | 58 | 283 | 0 | 0 | 188 | 0 | 0 | 0 | 92 | 0 | 188 | 0 | 346 | 35 | 0 | 0 | 0 | 107 | 0 | 0.1 | 4 |  | 6130.9 | 2955.1 | 9086 | 3899 | 926 | 1852 | 1719 | 341 | 75 | 127 | 146 | 1 | 0 | 102.84
18:00 | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 364 | 349 |  | 0 | 420 | 230 | 22 | 66 | 43 | 0 | 0 | 0 | 0 | 30 | 65 | 85 | 25 | 69 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 5 | 0 | 88 | 0 | 100 | 0 | 5 | 206 | 0 | 143 | 0 |  | 0 | 0 | 78 | 85 | 95 | 19 | 19 | 9 | 0 | 100 | 0 | 340 | 285 | 213 | 68 | 126 | 27 | 51 | 0 | 35 | 0 | 0 | 12 | 22 | 8 | 33 | 18 | 182 | 79 | 91 | 22 | 0 | 60 | 73 | 41 | 33 | 163 | 101 | 65 | 80 | 40 | 120 | 17 | 37 | 10 | 305 | 24 | 11 | 0 | 30 | 0 | 0 | 86 | 0 | 149 | 0 | 100 | 155 | 22 | 0 | 86 | 87 | 0 | 0 | 161 | 0 | 0 |  | 927 | 0 | 265 | 0 | 49 | 0 | 0 | 0 | 44 | 59 | 40 | 173 | 30 | 96 | 0 | 0 | 0 | 50 | 46 | 60 | 50 | 50 | 45 | 39 | 34 | 22 | 9 | 11 | 0 | 59 | 283 | 0 | 18 | 191 | 0 | 0 | 0 | 96 | 0 | 181 | 0 | 402 | 90 | 0 | 42 | 16 | 107 | 0 | 0 | 0 |  | 7281 | 3584 | 10865 | 4127 | 927 | 2200 | 2480 | 342 | 88 | 519 | 182 | 0 | 0 | 102.84
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 199 | 0 | 370 | 0 | 0 | 353 | 351 |  | 0 | 420 | 230 | 100 | 81 | 46 | 0 | 0 | 0 | 0 | 90 | 64 | 100 | 50 | 68 | 0 | 14 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 48 | 0 | 89 | 0 | 100 | 0 | 25 | 205 | 0 | 145 | 0 |  | 0 | 0 | 71 | 88 | 95 | 46 | 19 | 12 | 0 | 100 | 0 | 340 | 280 | 214 | 68 | 128 | 27 | 52 | 0 | 35 | 0 | 0 | 50 | 22 | 8 | 32 | 21 | 180 | 89 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 101 | 65 | 80 | 40 | 119 | 17 | 37 | 10 | 310 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 87 | 0 | 0 | 161 | 0 | 0 |  | 926 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 44 | 60 | 40 | 174 | 30 | 110 | 0 | 0 | 0 | 50 | 46 | 68 | 50 | 50 | 48 | 52 | 35 | 22 | 9 | 11 | 0 | 67 | 283 | 16 | 17 | 190 | 0 | 0 | 0 | 98 | 0 | 188 | 0 | 395 | 105 | 0 | 102 | 48 | 107 | 0 | 0 | 0 |  | 7935 | 3772 | 11707 | 4147 | 926 | 2220 | 3240 | 350 | 89 | 555 | 180 | 0 | 0 | 102.83
19:30 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 345 | 355 |  | 0 | 420 | 230 | 100 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 64 | 100 | 50 | 72 | 0 | 47 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 89 | 0 | 100 | 0 | 25 | 205 | 0 | 144 | 0 |  | 0 | 0 | 73 | 88 | 95 | 50 | 19 | 24 | 0 | 100 | 0 | 340 | 280 | 213 | 68 | 126 | 27 | 52 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 184 | 74 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 101 | 66 | 80 | 40 | 109 | 17 | 37 | 10 | 290 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 87 | 0 | 0 | 161 | 0 | 0 |  | 927 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 44 | 53 | 40 | 173 | 30 | 110 | 0 | 0 | 0 | 50 | 20 | 68 | 50 | 50 | 48 | 52 | 34 | 22 | 9 | 11 | 0 | 67 | 283 | 16 | 17 | 181 | 0 | 0 | 0 | 98 | 0 | 188 | 0 | 372 | 105 | 0 | 113 | 50 | 107 | 0 | 0 | 0 |  | 7968 | 3719 | 11687 | 4103 | 927 | 2193 | 3318 | 350 | 89 | 523 | 184 | 0 | 0 | 0
20:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 346 | 352 |  | 0 | 420 | 230 | 100 | 84 | 55 | 0 | 0 | 0 | 0 | 100 | 7 | 100 | 10 | 69 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 16 | 0 | 88 | 0 | 100 | 0 | 25 | 205 | 0 | 144 | 0 |  | 0 | 0 | 80 | 88 | 95 | 50 | 19 | 26 | 0 | 100 | 0 | 340 | 280 | 213 | 68 | 127 | 27 | 52 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 180 | 99 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 102 | 65 | 80 | 40 | 109 | 17 | 37 | 10 | 285 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 87 | 0 | 0 | 162 | 0 | 0 |  | 926 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 43 | 53 | 40 | 173 | 29 | 110 | 0 | 0 | 0 | 50 | 0 | 43 | 50 | 50 | 0 | 52 | 0 | 22 | 9 | 11 | 0 | 68 | 283 | 16 | 17 | 181 | 0 | 0 | 0 | 98 | 0 | 188 | 0 | 400 | 105 | 0 | 113 | 49 | 107 | 0 | 0 | 0 |  | 7861 | 3617 | 11478 | 4130 | 926 | 2214 | 3187 | 351 | 88 | 402 | 180 | 0 | 0 | 102.83
21:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 346 | 353 |  | 0 | 420 | 230 | 100 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 69 | 0 | 12 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 100 | 0 | 25 | 205 | 0 | 145 | 0 |  | 0 | 0 | 65 | 90 | 96 | 50 | 19 | 31 | 0 | 100 | 0 | 340 | 280 | 213 | 68 | 120 | 27 | 52 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 21 | 182 | 103 | 95 | 22 | 0 | 59 | 73 | 39 | 49 | 163 | 100 | 66 | 80 | 40 | 109 | 17 | 36 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 88 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 43 | 53 | 40 | 173 | 30 | 110 | 0 | 0 | 0 | 50 | 0 | 42 | 50 | 50 | 0 | 52 | 0 | 22 | 9 | 11 | 0 | 68 | 283 | 17 | 17 | 183 | 0 | 0 | 0 | 97 | 0 | 187 | 0 | 365 | 105 | 0 | 113 | 51 | 107 | 0 | 0 | 0 |  | 7812 | 3586 | 11398 | 4127 | 927 | 2199 | 3137 | 351 | 88 | 387 | 182 | 0 | 0 | 102.83
22:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 353 |  | 0 | 420 | 230 | 60 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 70 | 0 | 12 | 53 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 100 | 0 | 8 | 204 | 0 | 146 | 0 |  | 0 | 0 | 34 | 90 | 90 | 46 | 19 | 33 | 0 | 100 | 0 | 340 | 280 | 214 | 68 | 126 | 27 | 51 | 0 | 35 | 0 | 0 | 43 | 22 | 8 | 33 | 21 | 176 | 115 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 100 | 66 | 80 | 40 | 112 | 17 | 37 | 10 | 275 | 24 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 88 | 0 | 0 | 161 | 0 | 0 |  | 927 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 37 | 0 | 40 | 173 | 29 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 52 | 0 | 22 | 9 | 11 | 0 | 69 | 283 | 17 | 17 | 180 | 0 | 0 | 0 | 97 | 0 | 188 | 0 | 368 | 105 | 0 | 113 | 51 | 107 | 0 | 0 | 0 |  | 7539 | 3436 | 10975 | 4108 | 927 | 2178 | 2941 | 352 | 88 | 205 | 176 | 0 | 0 | 102.82
23:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 346 | 353 |  | 0 | 400 | 230 | 0 | 97 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 65 | 0 | 70 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 100 | 0 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 51 | 90 | 97 | 46 | 19 | 37 | 0 | 100 | 0 | 340 | 280 | 214 | 68 | 126 | 27 | 52 | 0 | 35 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 176 | 108 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 130 | 100 | 66 | 80 | 40 | 109 | 17 | 37 | 10 | 290 | 24 | 0 | 0 | 14 | 0 | 0 | 70 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 88 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 275 | 0 | 32 | 0 | 0 | 0 | 37 | 0 | 40 | 174 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 0 | 52 | 0 | 22 | 9 | 11 | 0 | 66 | 283 | 17 | 17 | 181 | 0 | 0 | 0 | 97 | 0 | 188 | 0 | 377 | 105 | 0 | 113 | 51 | 107 | 0 | 0 | 0 |  | 7192 | 3394 | 10586 | 4098 | 927 | 2153 | 2608 | 349 | 88 | 187 | 176 | 0 | 0 | 102.82
24:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 347 | 353 |  | 0 | 400 | 230 | 0 | 97 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 70 | 0 | 0 | 53 | 36 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 0 | 100 | 0 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 17 | 90 | 97 | 45 | 19 | 34 | 0 | 100 | 0 | 340 | 280 | 213 | 68 | 127 | 27 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 166 | 126 | 95 | 22 | 0 | 60 | 73 | 37 | 49 | 130 | 102 | 66 | 81 | 40 | 109 | 17 | 36 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 56 | 0 | 0 | 162 | 0 | 0 |  | 926 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 40 | 173 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 9 | 11 | 0 | 66 | 280 | 0 | 0 | 184 | 0 | 0 | 0 | 97 | 0 | 192 | 0 | 406 | 105 | 0 | 74 | 54 | 107 | 0 | 0 | 0 |  | 7016 | 3264 | 10280 | 4136 | 926 | 2185 | 2379 | 346 | 88 | 54 | 166 | 0 | 0 | 102.82
KWH | 767000 | 0 | 4795000 | 0 | 8620218 | 0 | 0 | 8597420 | 8177000 |  | 0 | 9218375 | 5881309 | 425280 | 1481060 | 755927 | 0 | 0 | 0 | 0 | 493440 | 463968 | 698880 | 126853 | 1386240 | 0 | 117888 | 483840 | 765916 | 803955 | 403128 | 600000 | 650880 | 793700 | 793400 | 100440 | 0 | 1941769 | 0 | 2400000 | 0 | 100854 | 4921516 | 0 | 3171788 | 0 |  | 0 | 0 | 530644 | 933120 | 1959360 | 421440 | 454608 | 462720 | 1196206 | 2216480 | 0 | 8007500 | 7290500 | 4645000 | 1053818 | 3013810 | 596016 | 1259040 | 0 | 840580 | 0 | 0 | 248323 | 498528 | 186480 | 781000 | 464710 | 3645120 | 2359440 | 2258880 | 515160 | 10850 | 1426000 | 1752000 | 908400 | 1125648 | 3438834 | 2220000 | 1555488 | 1865280 | 920160 | 2513480 | 440000 | 911500 | 248580 | 7366000 | 566160 | 235920 | 0 | 627273 | 0 | 0 | 1104000 | 0 | 3088800 | 138510 | 1661760 | 2917920 | 317818 | 0 | 2412000 | 1284420 | 0 | 31920 | 3552873 | 0 | 0 |  | 22361455 | 0 | 7326144 | 0 | 627840 | 0 | 0 | 0 | 263040 | 297728 | 480375 | 4188315 | 522732 | 1505470 | 0 | 0 | 0 | 213976 | 108703 | 239020 | 306820 | 673501 | 94132 | 593760 | 82542 | 507840 | 294660 | 240282 | 0 | 642327 | 6835900 | 83000 | 102000 | 4699245 | 0 | 0 | 0 | 2272175 | 0 | 4661527 | 0 | 9691363 | 1183680 | 0 | 755520 | 376128 | 1894080 | 0 | 23258 | 5760 |  | 160417121 | 74154298 | 234571419 | 100564049 | 22361455 | 51084705 | 44577891 | 7478227 | 1941769 | 2713665 | 3645120 | 204538 | 0
Fuel Cost | 859040 | 0 | 5130650 | 0 | 6378961.32 | 0 | 0 | 6190142.4 | 6214520 |  | 0 | 7374700 | 5293178.1 | 4337856 | 16039879.8 | 7755811.02 | 0 | 0 | 0 | 0 | 5477184 | 4713914.88 | 6925900.8 | 1329419.44 | 12614784 | 0 | 1103431.68 | 4640025.6 | 7306838.64 | 8007391.8 | 302346 | 450000 | 0 | 0 | 0 | 962215.2 | 0 | 504859.94 | 0 | 3672000 | 0 | 969206.94 | 5167591.8 | 0 | 4028170.76 | 0 |  | 0 | 0 | 5566455.56 | 9601804.8 | 18633513.6 | 3944678.4 | 418239.36 | 1286361.6 | 1256016.3 | 2327304 | 0 | 5925550 | 6124020 | 4273400 | 1032741.64 | 4008367.3 | 488733.12 | 1296811.2 | 0 | 1202029.4 | 0 | 0 | 2334236.2 | 508498.56 | 139860 | 1476090 | 348532.5 | 25151328 | 1934740.8 | 21481948.8 | 525463.2 | 177940 | 1939360 | 2382720 | 1235424 | 1407060 | 4264154.16 | 2042400 | 2317677.12 | 3282892.8 | 1021377.6 | 3820489.6 | 699600 | 1066455 | 584163 | 5229860 | 424620 | 179299.2 | 0 | 6567548.31 | 0 | 0 | 10620480 | 0 | 31165992 | 1598405.4 | 15487603.2 | 27370089.6 | 2977954.66 | 0 | 21153240 | 11444182.2 | 0 | 0 | 32757489.06 | 0 | 0 |  | 60375928.5 | 0 | 5714392.32 | 0 | 6052377.6 | 0 | 0 | 0 | 3051264 | 3900236.8 | 4750908.75 | 3350652 | 810234.6 | 16168747.8 | 0 | 0 | 0 | 2383692.64 | 1331611.75 | 2366298 | 3181723.4 | 7886696.71 | 1134290.6 | 5913849.6 | 813038.7 | 558624 | 486189 | 181893.474 | 0 | 4091622.99 | 27958831 | 2776350 | 2879460 | 4135335.6 | 0 | 0 | 0 | 3612758.25 | 0 | 4102143.76 | 0 | 7074694.99 | 11197612.8 | 0 | 6935673.6 | 3351300.48 | 17690707.2 | 0 | 0 | 0 |  | 448255221.37 | 226219140.914 | 674474362.284 | 93224300.494 | 60375928.5 | 49041051.24 | 379221495.87 | 32050453.99 | 504859.94 | 33128598.85 | 25151328 | 1776345.4 | 0
Yesterday Day Peak | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 351 | 348 |  | 0 | 400 | 230 | 0 | 53 | 32 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 89 | 12 | 19 | 2 | 80 | 90 | 0 | 315 | 315 | 180 | 63 | 127 | 27 | 51 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 33 | 17 | 142 | 69 | 91 | 22 | 2.2 | 60 | 44 | 36 | 45 | 130 | 100 | 61 | 80 | 40 | 77 | 17 | 35 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 19.5 | 50 | 61 | 0 | 0 | 109 | 68 | 0 | 4.7 | 120 | 0 | 0 |  | 927 | 0 | 305 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 284 | 0 | 0 | 186 | 0 | 0 | 0 | 93 | 0 | 190 | 0 | 424 | 35 | 0 | 0 | 0 | 100 | 0 | 4.6 | 0 |  | 9272 | DayPeak
Yesterday Evening Peak | 35 | 0 | 199 | 0 | 370 | 0 | 0 | 353 | 351 | 0 | 0 | 420 | 230 | 100 | 81 | 46 | 0 | 0 | 0 | 0 | 90 | 64 | 100 | 50 | 68 | 0 | 14 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 48 | 0 | 89 | 0 | 100 | 0 | 25 | 205 | 0 | 145 | 0 | 0 | 0 | 0 | 71 | 88 | 95 | 46 | 19 | 12 | 0 | 100 | 0 | 340 | 280 | 214 | 68 | 128 | 27 | 52 | 0 | 35 | 0 | 0 | 50 | 22 | 8 | 32 | 21 | 180 | 89 | 95 | 22 | 0 | 60 | 73 | 39 | 49 | 163 | 101 | 65 | 80 | 40 | 119 | 17 | 37 | 10 | 310 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 50 | 0 | 115 | 87 | 0 | 0 | 161 | 0 | 0 |  | 926 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 44 | 60 | 40 | 174 | 30 | 110 | 0 | 0 | 0 | 50 | 46 | 68 | 50 | 50 | 48 | 52 | 35 | 22 | 9 | 11 | 0 | 67 | 283 | 16 | 17 | 190 | 0 | 0 | 0 | 98 | 0 | 188 | 0 | 395 | 105 | 0 | 102 | 48 | 107 | 0 | 0 | 0 |  | 11707 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 230 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 85 | 85 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 95 | 50 | 22 | 20 | 0 | 100 | 0 | 360 | 360 | 225 | 68 | 141 | 27 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 170 | 150 | 95 | 22 | 0 | 60 | 73 | 50 | 50 | 163 | 155 | 68 | 80 | 40 | 130 | 20 | 42 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 | 54 | 113 |  | 936 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 75 | 40 | 180 | 33 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 50 | 40 | 52 | 35 | 22 | 14 | 11 | 0 | 68 | 280 | 17 | 15 | 225 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 230 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 85 | 85 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 95 | 50 | 22 | 15 | 0 | 100 | 0 | 360 | 360 | 225 | 68 | 140 | 27 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 128 | 150 | 95 | 22 | 1.6 | 60 | 73 | 50 | 50 | 163 | 154 | 68 | 80 | 40 | 110 | 20 | 42 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 0 | 4.4 | 230 | 54 | 113 |  | 936 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 50 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 379 | 300 | 0 | 0 | 400 | 230 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 85 | 85 | 100 | 0 | 0 | 204 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 19 | 10 | 0 | 100 | 0 | 340 | 320 | 162 | 68 | 127 | 27 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 114 | 143 | 42 | 22 | 0 | 60 | 73 | 11 | 10 | 100 | 101 | 67 | 10 | 10 | 70 | 17 | 13 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 9.6 | 0 | 0 | 0 | 0 | 8 | 52 | 0 | 2.1 | 16 | 0 | 0 | 0 | 924 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 8 | 0 | 68 | 280 | 0 | 0 | 183 | 0 | 0 | 0 | 53 | 0 | 200 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0
199
| Minimum Generation |  | 8102.34 | 8:00
| Highest Generation |  | 11707 | 19:00
| Day Peak Generation |  | 9272 | 12:00
| Evening Peak Generation |  | 11707 | 19:00
| HVDC Max Flow |  | 939 | 10:00
| HVDC EvPeak Flow |  | 926 | 19:00
| Load factor L.F |  | 83.49%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9272 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7768.1 | MW
Evening Peak Generation : |  | 11707 | MW Hour : | 19:00 | Available Max Generation : |  | 14823 | MW
E.P. Demand (at gen end) : |  | 11707 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11700 | MW
Maximum Generation : |  | 11707 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3123 | MW
Total Gen. (MKWH) : |  | 234.5714 | System Load Factor : | 83.49% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 40 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-22
Actual : | 102.8 | Ft.(MSL) , | Rule curve : | 108 | Ft.( MSL )
Gas Consumed : | Total = | 1248.06 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142265351.734
: |  | Coal : | 32050453.99 | Oil : | 412350094.72 | Total : | 586665900.444
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4094.4771 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1393.4112 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1248.6396 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1128.3184 |  |  | 0 | 0%
) | 0 | 0:00 | 1019.6079 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 822.7902 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 458.6967 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 211.8102 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 634.5832 |  |  | 0 | 0%
Total | 0 |  | 11012.3344 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1. | 6) Sirajganj 225 MW Unit-2
|  |  |  | 2) Khulna ST 110 MW | 7) Raozan #2
|  |  |  | 3) Sikalbaha ST 60 MW | 8) Siddirganj-335 MW
|  |  |  | 4) Baghabari 100 MW, | 9) Ashuganj unit-3
5) Ghorasal Unit-1,3 & 5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Chandraghona-Rangamati 132 kV Ckt-1 was under shut down from 08:43 to 15:12 for A/M.
b) Kabirpur-Kaliakoir 132 kV Ckt-1 was under shut down from 09:09 to 15:30 for A/M.
c) Ramganj 132/33 kV T2 transformer was under shut down from 10:25 to 15:16 for C/M.
d) Purbasadipur 132/33 kV MT3 transformer was under shut down from 08:54 to 15:30 for A/M.
e) Naogaon 132/33 kV T3 transformer was under shut down from 08:10 to 15:15 for A/M.
f) Bhandaria 132/33 kV T2 transformer was under shut down from 08:05 to 16:34 for A/M.
g) Bheramara HVDC 10FC16 Bay was under shut down from 09:41 to 16:26 for C/M.
h) Khulna(S)-Khulna© 132 kV Ckt-2 was under shut down from 09:22 to 15:06 for C/M.
i) Hasnabad-Shyampur 230 kV Ckt-2 was under shut down from 09:04 to 18:06 for C/M.
j) Bagerhat-Bhandaria 132 kV Ckt was under shut down from 11:47 to 13:09 for trimming trees between
tower #63 to #64.
k) Sherpur 132/33 kV T2 transformer was under shut down from 13:05 to 16:58 for SAS work.
l) After maintenance Barapukuria unit-2 was synchronized at 13:14.
m) Ashuganj unit-3 was shut down at 14:55 due to low gas pressure.
n) Sherpur 132 kV bus-B was switched on at 16:10.
o) Uttara Sector-18 132/33 kV T2 transformer was under shut down from 14:41 to 15:45 for D/W.
p) Polashbari-Rangpur Confidence 132 kV Ckt-1&2 were under shut down from 17:50 to 17:58 due to O/L
of Bogura-Mohasthangor Ckt.
q) Barapukuria S/S-Barapukuria P/S 230 kV Ckt-1 was switched on at 20:32.
r) Dohazari 33 kV bus-2 was under shut down from 22:30 to 22:57 for C/M. |  |  |  |  | About 52 MW power interruption occurred under Dohazari S/S area
from 22:30 to 22:57.
s) Chandraghona-Madunaghat 132 kV Ckt-1 was shut down at 07:20(22/10/2019) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 767000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 199 | 4795000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 370 | 8620218
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8597420 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 8177000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9218375 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 425280
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 5881309 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 81 | 1481060 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 46 | 755927 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 126853 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 403128 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 493440 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 463968 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 14 | 117888 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 483840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 698880 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 765916
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 803955
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 68 | 1386240 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1250880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 793700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 793400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 48 | 100440
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 627273 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3088800
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 87 | 1284420 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 3303 | 62401610
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 100854
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 138510
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 421440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 89 | 1941769 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4921516
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3171788 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 71 | 530644
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 88 | 933120 | Engine problem
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1661760
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 454608
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 462720
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 1959360 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31920
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 161 | 3552873 | Transformer & Line overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer & Line overload
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer & Line overload
| Chattogram area Total |  |  |  | 2166 | 1156 | 22682882
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 1196206 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2216480 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 4645000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 8007500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7290500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 27 | 596016 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1259040
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1053818 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 840580 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 317818 | Transformer & Line overload
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 128 | 3013810
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2917920
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 498528
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 186480 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 180 | 3645120
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 781000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 50 | 248323
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 464710 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1807 | 39178849
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 89 | 2359440 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 515160
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 2258880
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10850
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 1104000 | High Voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2412000
| Mymensingh Area Total |  |  |  | 637 | 471 | 8660330
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1426000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 73 | 1752000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3438834
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 101 | 2220000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 39 | 908400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1125648
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 235920
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1555488 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1865280
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 920160 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 119 | 2513480
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 440000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 37 | 911500 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 566160
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7366000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248580
| Sylhet Area Total |  |  |  | 1949 | 1198 | 27493450
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 926 | 22361455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 627840 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 44 | 263040
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 297728
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 7326144 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 480375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1183680
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 48 | 376128 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1554 | 32916390
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1505470
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 522732
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 174 | 4188315 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 2272175
| Barisal Area Total |  |  |  | 462 | 412 | 8488692
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under shut down.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 213976
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 46 | 108703
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 306820
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 673501
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 48 | 94132
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4699245 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4661527 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 395 | 9691363 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 82542
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 507840
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 9 | 294660
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240282
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 593760
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 68 | 239020 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 102 | 755520 | Engine problem
| Rajshahi Area Total |  |  |  | 2070 | 1316 | 23162891
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 67 | 642327
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 283 | 6835900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 83000
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 102000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1894080
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23258
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 5760
| Rangpur Area Total |  |  |  | 718 | 490 | 9586325
| Total |  |  |  | 19018 | 11707 | 234571419
| Eastern Grid Total |  |  |  | 13454 | 7935 | 160417121
| Western Grid Total |  |  |  | 5564 | 3772 | 74154298
| National Grid Total |  |  |  | 19018 | 11707 | 234571419
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-21
(a) ENTIRE EASTERN GRID : |  | 7615 | MW | (b) ENTIRE WESTERN GRID : |  | 3390 | MW
i) Dhaka area |  | 4232 | MW | i) Khulna area |  | 1362 | MW
ii) Chittagong area |  | 999 | MW | ii) Rajshahi area |  | 1075 | MW
iii) Comilla area |  | 1098 | MW | iii) Barisal area |  | 315 | MW
iv) Mymensingh area |  | 811 | MW | iv) Rangpur area |  | 638 | MW
v) Sylhet area |  | 475 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11005 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 2300 | Srimongal | 38 | 1830 | Bottail | 116 | 1800
Munsiganj | 118 | 2000 | Shahjibazar | 113 | 1800 | G.K Project | 57 | 1830
Sonargaon | 80 | 1900 | Fenchuganj | 42 | 1800 | Faridpur | 170 | 1930
Shyampur | 192 | 1000 | Kulawara | 46 | 1800 | Madaripur | 83 | 1930
Bhulta | 182 | 1200 | Sylhet | 137 | 1900 | Sariatpur | 56 | 2000
Madanganj | 59 | 1900 | Chatak | 30 | 1930 | Gopalganj | 86 | 1900
Shitalakhya | 120 | 1200 | Sunamganj | 36 | 1930 | Bagerhat | 82 | 1830
Rahim steel | 18 | 1500 | Biani Bazar | 51 | 2000 | Mongla | 34 | 900
Matuail | 90 | 1000 | Comilla (S) | 184 | 1930 | Satkhira | 96 | 1930
Ghorasal | 85 | 1800 | Comilla(N) | 121 | 1830 | Gallamari | 48 | 1300
Narsingdi | 137 | 1930 | Chandpur | 101 | 2000 | Magura | 46 | 1900
Haripur (SBU) | 105 | 1800 | Feni | 140 | 1800 | Norail | 23 | 1830
Ullon | 89 | 1700 | Chowmuhani | 172 | 1830 | Chuadanga | 79 | 1830
Hasnabad | 199 | 2000 | Ashuganj | 57 | 2200 | Barisal(N) | 45 | 2100
Magbazar | 125 | 1200 | Daudkandi | 124 | 1930 | Barisal (S) | 100 | 2000
Maniknagar | 112 | 1200 | B.Baria | 132 | 1900 | Patuakhali | 106 | 2100
Bangabhaban | 23 | 1200 | Ramganj | 90 | 1930 | Bhandaria | 50 | 1800
Narinda | 104 | 1830 | Madunaghat | 59 | 1900 | Borhan Uddin | 36 | 2100
Dhanmondi | 179 | 1300 | Hathazari | 98 | 2000 | Ishurdi | 52 | 1830
Lalbag | 87 | 1300 | Khulshi | 191 | 1600 | Ruppur Paromanobik | 2 | 1800
Madartek | 60 | 2000 | Halishahar | 149 | 1400 | Natore | 114 | 1830
Mirpur | 108 | 1800 | Baraulia | 146 | 200 | Bogra | 167 | 1830
Kalyanpur | 102 | 1800 | Sikalbaha | 37 | 1800 | Noagaon | 97 | 1930
Gulshan | 142 | 1300 | Dohazari | 86 | 1800 | Rajshahi | 127 | 2000
Uttara | 63 | 1800 | Cox'sbazar | 97 | 1900 | Rajshahi New | 12 | 2000
Uttara New | 44 | 1300 | Chandraghona | 30 | 1800 | C.Nawabganj | 67 | 1900
Kamrangirchar | 73 | 1830 | Kaptai | 5 | 1830 | Amnura | 29 | 1830
Savar | 141 | 1500 | A. Khaer Stl. | 6 | 400 | Pabna | 107 | 1930
Bhasantec | 160 | 1800 | Bakulia | 107 | 1830 | Shahjadpur | 99 | 1830
Agargaon | 62 | 1300 | Julda | 20 | 1500 | Serajganj | 89 | 1930
Satmosjid | 116 | 1800 | TK chemical | 4 | 1000 | Niyamatpur | 51 | 1830
Tongi | 153 | 1100 | Modern Steel | 14 | 600 | Joypurhat | 50 | 1830
Kabirpur | 237 | 1830 | Shahmirpur | 32 | 1800 | Sherpur(Bogura) | 39 | 1800
Basundhara | 142 | 1800 | Khagrachhari | 20 | 1800 | Mohastangor | 12 | 1800
Manikganj | 86 | 2000 | Matarbari | 29 | 1930 | Rangpur | 121 | 1900
Joydevpur | 228 | 1800 | Baroiar Hat | 24 | 1800 | Lalmonirhat | 56 | 1830
New Tongi | 106 | 1800 | Rangamati | 12 | 1800 | Saidpur | 95 | 1830
Korda | 189 | 1930 | Abul Khair 230 | 6 | 2000 | Purbasadipur | 90 | 1830
Dhamrai | 66 | 1830 | BSRM | 108 | 1500 | Thakurgaon | 62 | 1830
Valuka | 110 | 1800 | GPH Ispat | 0.2 | 200 | Palashbari | 98 | 1800
Tangail | 163 | 1830 | Goalpara | 25 | 1930 | Barapukuria | 45 | 1800
Mymensing | 191 | 1900 | Central s/s | 93 | 1930 | Panchagar | 38 | 1800
Kishorganj | 121 | 1930 | Noapara | 68 | 1930 | Joldhaka | 21 | 1830
Netrokona | 92 | 1830 | Jessore | 112 | 1900 | Kurigram | 31 | 1830
Jamalpur | 104 | 2100 | Benapol | 40 | 1830
Sherpur | 88 | 2000 | Jhenida | 97 | 1830
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-21 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 385 | 21:00 | 375 | 16:00 | Kaliakoir | 364 | 21:00 | 350 | 16:00
Bheramara | 400 | 8:00 | 387 | 19:00 | Bhulta | 373 | 20:00 | 359 | 11:00
Ashuganj(N) | 379 | 22:00 | 365 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
Ghorasal | 222 | 1:00 | 220 | 15:00 | Hathazari | 219 | 19:30 | 212 | 11:00
Ishurdi | 235 | 9:00 | 229 | 1:00 | Megnaghat | 218 | 1:00 | 212 | 11:00
Ashuganj | 230 | 19:30 | 222 | 11:00 | Fenchuganj | 233 | 19:30 | 228 | 16:00
Serajganj | 230 | 9:00 | 226 | 3:00 | Siddhirganj | 218 | 19:30 | 209 | 16:00
Baghabari | 234 | 23:00 | 231 | 1:00 | Maniknagar | 216 | 21:00 | 208 | 11:00
Barapukuria | 229 | 17:00 | 223 | 18:00 | Old Airport | 215 | 19:30 | 206 | 11:00
Bogra | 228 | 23:00 | 222 | 12:00 | Barisal | 234 | 9:00 | 224 | 12:00
Khulna South | 226 | 10:00 | 213 | 3:00 | AKSML | 216 | 21:00 | 210 | 11:00
Rampura | 219 | 21:00 | 210 | 10:00 | BSRM | 218 | 20:00 | 213 | 5:00
Haripur | 216 | 19:30 | 210 | 11:00 | Bibiyana | 230 | 6:00 | 223 | 10:00
Hasnabad | 215 | 1:00 | 208 | 13:00 | Bhulta | 219 | 19:30 | 210 | 11:00
Aminbazar | 217 | 19:30 | 208 | 16:00 | Ashuganj (S) | 230 | 21:00 | 222 | 16:00
Tongi | 216 | 19:30 | 207 | 15:00 | Kaliakoir | 220 | 19:00 | 211 | 16:00
Comilla (N) | 226 | 19:30 | 220 | 10:00 | GPH | 216 | 20:00 | 211 | 6:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 1930 | 124 | 1100 | Halishahar | 133 | 2000 | 127 | 600
Munsiganj | 133 | 1930 | 124 | 1000 | Baraulia | 126 | 1830 | 125 | 1100
Megnaghat | 129 | 1900 | 125 | 700 | Sikalbaha | 133 | 1930 | 127 | 800
Shyampur | 132 | 200 | 126 | 1500 | Dohazari | 130 | 1830 | 124 | 600
Bhulta | 125 | 2000 | 119 | 1100 | Cox'sbazar | 122 | 900 | 117 | 400
Madanganj | 131 | 2000 | 121 | 1100 | Chandraghona | 131 | 2000 | 127 | 1500
Shitalakhya | 136 | 1930 | 126 | 1100 | Kaptai | 131 | 1930 | 128 | 400
Rahim steal | 131 | 1930 | 125 | 1100 | A. Khaer Stl. | 130 | 2000 | 126 | 100
Matuail | 130 | 1930 | 123 | 1100 | Bakulia | 131 | 1930 | 126 | 800
Ghorasal | 135 | 100 | 132 | 1500 | Julda | 132 | 2000 | 126 | 1000
Narsinghdi | 132 | 700 | 126 | 1930 | TK Chemical | 131 | 1830 | 127 | 400
Haripur (SBU) | 131 | 1900 | 125 | 1100 | Modern Steel | 132 | 1930 | 127 | 1000
Ullon | 134 | 600 | 127 | 1200 | Shahmirpur | 132 | 1930 | 127 | 600
Hasnabad | 134 | 2000 | 128 | 1200 | Khagrachhari | 129 | 100 | 126 | 1100
Magbazar | 135 | 600 | 126 | 1200 | Matarbari | 125 | 1600 | 120 | 200
Maniknagar | 134 | 600 | 128 | 1100 | Baroiar Hat | 126 | 2100 | 122 | 1500
Bangabhaban | 134 | 600 | 128 | 1100 | Rangamati | 130 | 1930 | 127 | 600
Narinda | 134 | 600 | 128 | 1100 | Goalpara | 136 | 1400 | 129 | 100
Dhanmondi | 134 | 600 | 127 | 1200 | Central s/s | 137 | 1700 | 127 | 200
Lalbag | 132 | 1930 | 122 | 1100 | Noapara | 133 | 1700 | 126 | 1830
Madartek | 134 | 700 | 127 | 1200 | Jessore | 129 | 800 | 120 | 1830
Mirpur | 131 | 100 | 127 | 1000 | Benapol | 130 | 400 | 122 | 1800
Kalyanpur | 133 | 100 | 128 | 1600 | Jhenida | 129 | 600 | 119 | 1830
Gulshan | 133 | 200 | 126 | 1100 | Bottail | 135 | 600 | 129 | 2000
Uttara | 131 | 300 | 124 | 1100 | G.K Project | 141 | 900 | 138 | 1830
Uttara New | 130 | 100 | 123 | 1600 | Faridpur | 132 | 600 | 125 | 100
Kamrangirchar | 130 | 1930 | 122 | 1100 | Madaripur | 137 | 900 | 125 | 1200
Savar | 130 | 300 | 124 | 1600 | Sariatpur | 133 | 900 | 124 | 1300
Bhasantec | 133 | 600 | 125 | 1100 | Gopalganj | 138 | 1700 | 126 | 1200
Agargaon | 134 | 600 | 127 | 1100 | Bagerhat | 135 | 2300 | 128 | 100
Satmosjid | 133 | 200 | 126 | 1100 | Mongla | 132 | 1700 | 124 | 1600
Tongi | 132 | 1830 | 126 | 1500 | Satkhira | 136 | 1000 | 127 | 100
Kabirpur | 131 | 700 | 125 | 1300 | Gallamari | 137 | 1000 | 128 | 300
Basundhara | 130 | 500 | 122 | 1100 | Magura | 128 | 900 | 118 | 1830
Manikganj | 136 | 1900 | 130 | 300 | Norail | 137 | 6900 | 115 | 1830
Joydevpur | 134 | 1930 | 126 | 1600 | Chuadanga | 127 | 900 | 111 | 1830
New Tongi | 131 | 2100 | 124 | 1600 | Barisal(N) | 140 | 900 | 132 | 500
Kodda | 134 | 1930 | 122 | 600 | Barisal (S) | 138 | 900 | 131 | 1200
Dhamrai | 131 | 400 | 125 | 1800 | Patuakhali | 135 | 800 | 130 | 1100
Valuka | 125 | 500 | 112 | 1800 | Bhandaria | 134 | 800 | 127 | 300
Tangail | 132 | 400 | 122 | 1800 | Ishurdi | 139 | 900 | 135 | 1500
Mymensing | 129 | 800 | 117 | 1100 | Ruppur Paromanobik | 138 | 1700 | 135 | 1200
Kishorganj | 127 | 400 | 116 | 1800 | Natore | 136 | 1700 | 131 | 400
Netrokona | 127 | 600 | 115 | 1100 | Bogra | 136 | 1700 | 133 | 1300
Jamalpur | 138 | 2300 | 128 | 1100 | Noagaon | 132 | 1700 | 128 | 100
Sherpur | 137 | 1830 | 128 | 1100 | Rajshahi | 136 | 1830 | 126 | 200
Srimongal | 137 | 900 | 133 | 1800 | Rajshahi New | 137 | 1800 | 124 | 300
Shahjibazar | 136 | 800 | 132 | 1800 | C.Nawabganj | 133 | 1900 | 121 | 1200
Fenchuganj | 135 | 800 | 132 | 100 | Amnura | 137 | 1800 | 122 | 1100
Khulawara | 134 | 500 | 131 | 1800 | Pabna | 137 | 900 | 133 | 1200
Sylhet | 135 | 600 | 131 | 1800 | Shahjadpur | 140 | 1700 | 135 | 1200
Chatak | 134 | 600 | 130 | 1800 | Serajganj | 135 | 600 | 132 | 1100
Sunamganj | 133 | 600 | 129 | 1830 | Niyamatpur | 132 | 1700 | 125 | 1930
Biani Bazar | 133 | 700 | 128 | 1800 | Joypurhat | 133 | 1700 | 126 | 100
Comilla(s) | 125 | 500 | 121 | 900 | Sherpur(Bogura) | 135 | 1700 | 132 | 900
Comilla(n) | 133 | 1830 | 129 | 1600 | Mohastangor | 134 | 1700 | 130 | 1100
Chandpur | 132 | 2100 | 126 | 1100 | Rangpur | 128 | 1700 | 120 | 1900
Feni | 125 | 700 | 123 | 2200 | Lalmonirhat | 122 | 1700 | 112 | 1830
Chowmuhani | 124 | 1400 | 120 | 100 | Saidpur | 136 | 1700 | 117 | 1830
Ashuganj | 136 | 800 | 133 | 1800 | Purbasadipur | 126 | 1600 | 116 | 1830
Daudkandi | 127 | 1930 | 122 | 1100 | Thakurgaon | 122 | 1700 | 110 | 1830
B.Baria | 132 | 700 | 128 | 2000 | Palashbari | 131 | 1830 | 125 | 800
Ramganj | 122 | 1700 | 120 | 1900 | Barapukuria | 129 | 1700 | 123 | 1800
Madanhat | 132 | 100 | 127 | 1000 | Panchagar | 120 | 900 | 106 | 1830
Hathazari | 131 | 2100 | 127 | 600 | Joldhaka | 125 | 1700 | 117 | 1830
Khulshi | 28 | 1830 | 124 | 1500 | Kurigram | 125 | 1700 | 114 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 290 | 7016 | 3264 | 10280 |  |  |  | QF-LDC-12
0:30 | 226 | 6929.5 | 3186 | 10115.5 | Date: | 2019-10-21
1:00 | 162 | 6843 | 3108 | 9951
1:30 | 153 | 6739 | 3035 | 9774
2:00 | 144 | 6635 | 2962 | 9597
2:30 | 157 | 6518 | 2891 | 9409 | [5 empty] | Gen. at Eve. Peak | 11707 | 11707 MW (19:00 )
3:00 | 170 | 6401 | 2820 | 9221 | [6 empty] | 19:00
3:30 | 210 | 6323.5 | 2812.5 | 9136 | [5 empty] | Gen. at Day Peak | 9272 | 9272 MW (12:00 )
4:00 | 250 | 6246 | 2805 | 9051 | [6 empty] | 12:00
4:30 | 245 | 6142.5 | 2772 | 8914.5 | [5 empty] | Highest Generation | 11707
5:00 | 240 | 6039 | 2739 | 8778 | [6 empty] | 19:00
5:30 | 300 | 5848.511 | 2735.5 | 8584.011
6:00 | 360 | 5658.022 | 2732 | 8390.022
6:30 | 345 | 5571.141 | 2741.1 | 8312.241
7:00 | 330 | 5484.26 | 2750.2 | 8234.46
7:30 | 325 | 5432.25 | 2736.15 | 8168.4
8:00 | 320 | 5380.24 | 2722.1 | 8102.34
8:30 | 355 | 5629.47 | 2728.6 | 8358.07
9:00 | 390 | 5878.7 | 2735.1 | 8613.8
9:30 | 465 | 5834.95 | 2773.15 | 8608.1
10:00 | 540 | 5791.2 | 2811.2 | 8602.4
10:30 | 545 | 5934.4 | 2833.1 | 8767.5
11:00 | 550 | 6077.6 | 2855 | 8932.6
11:30 | 490 | 6222 | 2880.3 | 9102.3
12:00 | 430 | 6366.4 | 2905.6 | 9272
12:30 | 385 | 6447.2 | 2925.9 | 9373.1
13:00 | 340 | 6528 | 2946.2 | 9474.2
13:30 | 405 | 6456.35 | 2933.75 | 9390.1
14:00 | 470 | 6384.7 | 2921.3 | 9306
14:30 | 513 | 6445.9 | 2956.95 | 9402.85
15:00 | 556 | 6507.1 | 2992.6 | 9499.7
15:30 | 579 | 6478.5 | 2982.35 | 9460.85
16:00 | 602 | 6449.9 | 2972.1 | 9422
16:30 | 601 | 6290.4 | 2963.6 | 9254
17:00 | 600 | 6130.9 | 2955.1 | 9086
17:30 | 373 | 6705.95 | 3269.55 | 9975.5
18:00 | 146 | 7281 | 3584 | 10865
18:30 | 128 | 7608 | 3678 | 11286
19:00 | 110 | 7935 | 3772 | 11707
19:30 | 80 | 7968 | 3719 | 11687
20:00 | 40 | 7861 | 3617 | 11478 |  |  |  | Executive Engineer
20:30 | 55 | 7836.5 | 3601.5 | 11438 |  |  |  | Network Operation Division
21:00 | 70 | 7812 | 3586 | 11398
21:30 | 98 | 7675.5 | 3511 | 11186.5
22:00 | 126 | 7539 | 3436 | 10975 |  |  |  |  | Page 6 of 7
22:30 | 193 | 7365.5 | 3415 | 10780.5
23:00 | 260 | 7192 | 3394 | 10586
23:30 | 275 | 7104 | 3329 | 10433
24:00 | 290 | 7016 | 3264 | 10280
11707 MW (19:00 )
9272 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-21 |  | Energy | 234571419
[10 empty] | 2019-10-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4136 | 926 | 2185 | 2379 | 346 | 88 | 54 | 0 | 166
0:30 | 4228.5 | 932 | 2196.5 | 2142 | 312.5 | 62.5 | 82.5 | 0 | 159 | Date: | 2019-10-21
1:00 | 4321 | 938 | 2208 | 1905 | 279 | 37 | 111 | 0 | 152
1:30 | 4285.5 | 937.5 | 2192.5 | 1820 | 279.5 | 37 | 72 | 0 | 150 | [7 empty] | Total Energy | 234.5714 | Total Energy Gen 234.571 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 234.571 MKWHr
2:00 | 4250 | 937 | 2177 | 1735 | 280 | 37 | 33 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 4259 | 937.5 | 2194.5 | 1538.5 | 280 | 37 | 16.5 | 0 | 146 | [7 empty] | Energy Requirement | 234.5714
3:00 | 4268 | 938 | 2212 | 1342 | 280 | 37 | 0 | 0 | 144
3:30 | 4268.5 | 938 | 2212.5 | 1234 | 280 | 61 | 0 | 0 | 142 | [6 empty] | Shortage
4:00 | 4269 | 938 | 2213 | 1126 | 280 | 85 | 0 | 0 | 140
4:30 | 4293.5 | 938 | 2216 | 964 | 280 | 85 | 0 | 0 | 138
5:00 | 4318 | 938 | 2219 | 802 | 280 | 85 | 0 | 0 | 136
5:30 | 4228.5 | 938 | 2216 | 703.5 | 280 | 85 | 0 | 0 | 133
6:00 | 4139 | 938 | 2213 | 605 | 280 | 85 | 0 | 0 | 130
6:30 | 4086.5 | 937.5 | 2152.5 | 647.5 | 280 | 83.5 | 0 | 0 | 122 |  |  |  |  | Coal
7:00 | 4034 | 937 | 2092 | 690 | 280 | 82 | 0 | 0 | 114
7:30 | 4010 | 937.5 | 1992.5 | 743.5 | 280 | 82 | 0 | 0 | 113 |  |  |  | Oil |  |  |  | ,
8:00 | 3986 | 938 | 1893 | 797 | 280 | 82 | 0 | 0 | 112
8:30 | 4018.5 | 938 | 1954.5 | 948.5 | 280 | 82.5 | 0 | 0 | 118
9:00 | 4051 | 938 | 2016 | 1100 | 280 | 83 | 0 | 0 | 124
9:30 | 3966 | 938.5 | 1984 | 1207 | 280 | 83.5 | 0 | 0 | 125
10:00 | 3881 | 939 | 1952 | 1314 | 280 | 84 | 0 | 0 | 126
10:30 | 3966 | 938.5 | 2016.5 | 1333.5 | 280 | 83 | 0 | 0 | 130
11:00 | 4051 | 938 | 2081 | 1353 | 280 | 82 | 0 | 0 | 134
11:30 | 4058.5 | 932.5 | 2108.5 | 1478 | 282 | 82.5 | 0 | 0 | 138
12:00 | 4066 | 927 | 2136 | 1603 | 284 | 83 | 0 | 0 | 142
12:30 | 4095 | 926.5 | 2136.5 | 1662 | 284.5 | 83 | 8 | 0 | 147
13:00 | 4124 | 926 | 2137 | 1721 | 285 | 83 | 16 | 0 | 152
13:30 | 4124 | 926 | 2137 | 1721 | 285 | 83 | 16 | 0 | 152
14:00 | 4124 | 926 | 2137 | 1721 | 285 | 83 | 16 | 0 | 152
14:30 | 4091.5 | 926 | 2094 | 1781 | 315 | 84 | 17.5 | 0 | 154
15:00 | 4059 | 926 | 2051 | 1841 | 345 | 85 | 19 | 0 | 156
15:30 | 4035.5 | 926.5 | 2067 | 1805.5 | 348.5 | 80 | 30.5 | 0 | 154
16:00 | 4012 | 927 | 2083 | 1770 | 352 | 75 | 42 | 0 | 152
16:30 | 3955.5 | 926.5 | 1967.5 | 1744.5 | 346.5 | 75 | 84.5 | 0 | 149
17:00 | 3899 | 926 | 1852 | 1719 | 341 | 75 | 127 | 0 | 146
17:30 | 4013 | 926.5 | 2026 | 2099.5 | 341.5 | 81.5 | 323 | 0 | 164
18:00 | 4127 | 927 | 2200 | 2480 | 342 | 88 | 519 | 0 | 182
18:30 | 4137 | 926.5 | 2210 | 2860 | 346 | 88.5 | 537 | 0 | 181
19:00 | 4147 | 926 | 2220 | 3240 | 350 | 89 | 555 | 0 | 180
19:30 | 4103 | 927 | 2193 | 3318 | 350 | 89 | 523 | 0 | 184
20:00 | 4130 | 926 | 2214 | 3187 | 351 | 88 | 402 | 0 | 180
20:30 | 4128.5 | 926.5 | 2206.5 | 3162 | 351 | 88 | 394.5 | 0 | 181
21:00 | 4127 | 927 | 2199 | 3137 | 351 | 88 | 387 | 0 | 182
21:30 | 4117.5 | 927 | 2188.5 | 3039 | 351.5 | 88 | 296 | 0 | 179
22:00 | 4108 | 927 | 2178 | 2941 | 352 | 88 | 205 | 0 | 176
22:30 | 4103 | 927 | 2165.5 | 2774.5 | 350.5 | 88 | 196 | 0 | 176
23:00 | 4098 | 927 | 2153 | 2608 | 349 | 88 | 187 | 0 | 176
23:30 | 4117 | 926.5 | 2169 | 2493.5 | 347.5 | 88 | 120.5 | 0 | 171 | Max Temp. in Dhaka |  | 33.7° C
24:00 | 4136 | 926 | 2185 | 2379 | 346 | 88 | 54 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 234.571 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 234.571 MKWHr
Note on W13: Author:

## Generation
2019-10-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 37 | 37 | 37 | 85 | 85 | 85 | 82 | 82 | 83 | 84 | 82 | 83 | 83 | 83 | 85 | 75 | 75 | 88 |  | 89 | 89 | 88 | 88 | 88 | 88 | 88 | 1941769
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 5 |  | 25 | 25 | 25 | 25 | 8 |  |  | 100854
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 10.64 | 15.6 | 18 | 4 | 19.5 | 18.6 | 16.3 | 11 | 6.5 | 0.7 | [9 empty] | 138510
6 | Sikalbaha 225MW CCPP (Gas) | 208 | 204 | 205 | 204 | 205 | 204 | 204 | 205 | 204 | 205 | 208 | 205 | 205 | 205 | 218 | 204 | 205 | 206 |  | 205 | 205 | 205 | 205 | 204 | 204 | 204 | 4921516
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 134 | 134 | 134 | 134 | 134 | 104 | 104 | 104 | 134 | 94 | 134 | 134 | 134 | 104 | 135 | 143 | 110 | 143 |  | 145 | 144 | 144 | 145 | 146 | 144 | 145 | 3171788
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 79 | 17 | 0 | [11 empty] | 3 | 6 | 4 | 78 |  | 71 | 73 | 80 | 65 | 34 | 51 | 17 | 530644
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 30 |  | 145 | 145 | 145 | 145 | 45 | 14 | 0 | 627273
19 | Ashuganj 195MW PP (APSCL-United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 40 | 63 | 63 | 63 | 63 | 63 | 63 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1053818
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 767000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 201 | 202 | 200 | 200 | 200 | 200 | 200 | 201 | 200 | 200 | 200 | 197 | 200 | 200 | 200 | 200 | 200 |  | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 4795000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 365 |  | 370 | 370 | 370 | 370 | 350 | 350 | 330 | 8620218
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | [11 empty] | 1196206
29 | Ashuganj TPP Unit- 4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2216480
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 23 | 23 | 23 | 23 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 596016
33 | Ashuganj 225 MW CCPP | 193 | 179 | 179 | 183 | 194 | 161 | 165 | 172 | 179 | 179 | 194 | 180 | 179 | 179 | 173 | 186 | 179 | 213 |  | 214 | 213 | 213 | 213 | 214 | 214 | 213 | 4645000
34 | Ashuganj 450 MW CCPP(South) | 325 | 315 | 315 | 315 | 330 | 275 | 265 | 275 | 315 | 290 | 305 | 315 | 315 | 315 | 290 | 260 | 280 | 285 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7290500
| Ashuganj 450 MW CCPP(North) | 320 | 310 | 310 | 310 | 325 | 300 | 260 | 270 | 340 | 280 | 300 | 315 | 340 | 340 | 360 | 340 | 290 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8007500
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 54 | 55 | 55 | 54 | 56 | 55 | 55 | 54 | 53 | 51 | 52 | 51 | 47 | 48 | 49 | 51 |  | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 1259040
36 | Chandpur 150 MW CCPP | 126 | 127 | 126 | 127 | 126 | 126 | 126 | 126 | 120 | 126 | 127 | 127 | 126 | 126 | 126 | 127 | 120 | 126 |  | 128 | 126 | 127 | 120 | 126 | 126 | 127 | 3013810
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 357 | 353 | 350 | 349 | 354 | 370 | 348 | 346 | 361 | 346 | 362 | 351 | 348 | 348 | 373 | 362 | 350 | 364 |  | 353 | 345 | 346 | 346 | 345 | 346 | 347 | 8597420
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 330 | 360 | 360 | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 420 |  | 420 | 420 | 420 | 420 | 420 | 400 | 400 | 9218375
41 | Haripur 360MW CCPP(HPL) | 353 | 355 | 355 | 356 | 355 | 356 | 320 | 278 | 355 | 325 | 346 | 348 | 347 | 324 | 324 | 346 | 311 | 349 |  | 351 | 355 | 352 | 353 | 353 | 353 | 353 | 8177000
42 | RPCL 210MW CCPP | 123 | 123 | 144 | 145 | 144 | 145 | 144 | 143 | 71 | 71 | 70 | 69 | 69 | 90 | 79 | 76 | 74 | 79 |  | 89 | 74 | 99 | 103 | 115 | 108 | 126 | 2359440
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 |  | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 1426000
45 | Fenchugonj CCPP Phase-2 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 53 | 72 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1752000
46 | Shajibazar 330 MW CCPP | 101 | 102 | 103 | 101 | 101 | 101 | 102 | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 102 | 100 | 102 | 101 |  | 101 | 101 | 102 | 100 | 100 | 100 | 102 | 2220000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 65 | 64 | 63 | 61 | 62 | 61 | 62 | 63 | 65 | 65 |  | 65 | 66 | 65 | 66 | 66 | 66 | 66 | 1555488
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 78 | 80 | 80 | 80 | 80 | 80 | 50 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 1865280
49 | Shahjibazar 50MW PP (EPL) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 920160
50 | Sylhet 150 MW CCPP | 122 | 113 | 113 | 113 | 115 | 76 | 70 | 84 | 70 | 72 | 79 | 77 | 107 | 71 | 122 | 114 | 71 | 120 |  | 119 | 109 | 109 | 109 | 112 | 109 | 109 | 2513480
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 440000
52 | Sylhet 50MW PP (EPL) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 40 | 40 | 35 | 35 | 35 | 37 | 36 | 19 | 37 |  | 37 | 37 | 37 | 36 | 37 | 37 | 36 | 911500
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248580
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 |  | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  | 11 | 235920
55 | Fenchugonj 51 MW PP (Barakatullah) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 39 | 36 | 36 | 42 | 42 | 39 | 42 | 11 | 41 |  | 39 | 39 | 39 | 39 | 39 | 39 | 37 | 908400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 566160
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 300 | 300 | 300 | 310 | 310 | 300 | 300 | 280 | 270 | 300 | 300 | 295 | 270 | 300 | 300 | 295 | 305 |  | 310 | 290 | 285 | 300 | 275 | 290 | 300 | 7366000
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 26 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 803955
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 454608
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 |  |  | 19 | 403128
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515160
63 | Impoprt (Tripura) | 152 | 148 | 144 | 140 | 136 | 130 | 114 | 112 | 124 | 126 | 134 | 142 | 152 | 156 | 156 | 152 | 146 | 182 |  | 180 | 184 | 180 | 182 | 176 | 176 | 166 | 3645120
64 | Malancha, Ctg. EPZ (United) | 25 | 20 | 39 | 39 | 40 | 40 | 34 | 7 | 2 | 2 | 2 | 2 | 2 | 5 | 2 | 8 | 9 | 9 |  | 12 | 24 | 26 | 31 | 33 | 37 | 34 | 462720
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 16 | 19 | 19 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498528
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186480
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 |  | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 781000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 464710
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 25 | 27 | 27 | 27 | 20 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 650880
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793400
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 0 | 30 |  | 90 | 100 | 100 | 100 | 100 | 24 |  | 493440
78 | Gazipur 52 MW PP | [17 empty] | 5 |  | 48 | 51 | 16 |  |  |  |  | 100440
79 | Kodda 150MW PP | 32 | 16 | 0 | [9 empty] | 16 | 16 | 16 | 16 | 16 | 85 |  | 100 | 100 | 100 | 100 | 100 | 65 | 32 | 698880
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 91 | 91 | 91 | 91 | 83 | 91 | 91 | 91 | 91 | 91 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2258880
81 | Jangalia 52 MW PP (Lakdanavi) | 0 | [16 empty] | 12 |  | 50 | 52 | 52 | 52 | 43 | 8 | 0 | 248323
| Gazipur 100 MW PP | 34 | [7 empty] | 68 | 68 | 68 | 68 | 68 | 70 | 70 | 70 | 70 | 87 |  | 87 | 87 | 87 | 88 | 88 | 88 | 56 | 1284420
| Kaptai 7 MW Solar PP | [5 empty] | 0.022 | 0.96 | 2.2 | 3.6 | 4.4 | 4.8 | 4.7 | 4.3 | 3.5 | 2.4 | 1 | 0.1 | 0 | [8 empty] | 31920
| Jodiac Power | [25 empty] | 0 | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | 97 | 97 | 48 | 18 | 15 | 15 | 15 | 20 | 30 | 30 | 30 | 53 | 64 | 64 | 64 | 64 | 64 | 66 |  | 81 | 81 | 84 | 97 | 97 | 97 | 97 | 1481060
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 25 |  | 50 | 50 | 10 |  |  |  | 0 | 126853
86 | Meghnaghat CCPP(Summit) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5881309
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 22 |  | 100 | 100 | 100 | 100 | 60 |  | 0 | 425280
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 90 | 40 | 0 | [7 empty] | 10 | 10 | 10 | 20 | 30 | 30 | 85 |  | 88 | 88 | 88 | 90 | 90 | 90 | 90 | 933120
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 45 | 45 | 45 | 45 | 45 | 48 | 10 | 33 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1125648
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840580
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 7 | 24 | 50 | 50 | 50 | 50 | 24 | 24 | 65 |  | 64 | 64 | 7 | 0 |  |  |  | 463968
95 | Patenga 50MW PP (Baraka) | 12 | [7 empty] | 3 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 19 |  | 46 | 50 | 50 | 50 | 46 | 46 | 45 | 421440
96 | Chattogram 108 MW PP (ECPV) | 90 | 90 | 90 | 90 | 60 | 12 | 17 | 14 | 54 | 90 | 90 | 89 | 89 | 89 | 89 | 95 | 95 | 95 |  | 95 | 95 | 95 | 96 | 90 | 97 | 97 | 1959360
97 | Katpotti 52 MW PP (Sinha) | [19 empty] | 14 | 47 | 48 | 12 | 12 |  | 0 | 117888
98 | Bosila 108MW PP(CLC) | 71 | 71 | 30 | 30 | 30 | 30 | 30 | 30 | 65 | 71 | 70 | 70 | 69 | 68 | 68 | 69 | 69 | 69 |  | 68 | 72 | 69 | 69 | 70 | 70 | 70 | 1386240
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [7 empty] | 38 | 32 | 32 | 44 | 43 | 43 | 43 | 43 | 43 |  | 46 | 55 | 55 | 55 | 55 | 55 | 55 | 755927
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 36 | 765916
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 130 | 100 | 100 | 130 | 130 | 100 | 130 | 130 | 130 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3438834
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.3 | 0.4 | 1.5 | 1.8 | 1.8 | 2.2 | 2.1 | 1.9 | 0.7 | 0.4 | 0.1 | 0 | [8 empty] | 10850
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 483840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 24 | 24 | 24 | [7 empty] | 5 | 16 | 16 | 16 | 16 | 16 | 16 | 86 |  | 150 | 150 | 150 | 150 | 130 | 70 | 70 | 1104000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 93 | 42 | 35 | 35 | 55 | 120 | 149 | 149 | 149 | 149 | 150 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3088800
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 70 | 10 | 10 | 10 | 10 | 10 | 15 | 50 | 50 | 50 | 70 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1661760
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 160 | 105 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 61 | 120 | 122 | 120 | 120 | 120 | 155 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2917920
117 | Ashuganj 150MW PP (Midland) | [15 empty] | 4 | 4 | 22 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 317818
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 50 | 50 | 50 | 50 | 80 | 80 | 99 | 109 | 115 | 115 | 115 | 115 | 78 | 86 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2412000
| Anwara 300 MW PP (United) | 197 | 197 | 197 | 197 | 143 | 71 | 71 | 71 | 120 | 120 | 120 | 120 | 124 | 140 | 161 | 161 | 161 | 161 |  | 161 | 161 | 162 | 162 | 161 | 162 | 162 | 3552873
120 | Eastern Zone Total | 6843 | 6635 | 6401 | 6246 | 6039 | 5658.022 | 5484.26 | 5380.24 | 5878.7 | 5791.2 | 6077.6 | 6366.4 | 6528 | 6384.7 | 6507.1 | 6449.9 | 6130.9 | 7281 |  | 7935 | 7968 | 7861 | 7812 | 7539 | 7192 | 7016 | 160417121
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [8 empty] | 0 | 32 | 32 | 35 | 38 | 49 | 49 | 16 | 16 | 49 |  | 66 | 66 | 66 | 66 | 66 | 32 | 0 | 627840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 0 | 15 | 44 |  | 44 | 44 | 43 | 43 | 37 | 37 | 5 | 263040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 0 | [5 empty] | 0 | 35 | 35 | 35 | 35 | 35 | 53 | 53 | 35 | 90 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1183680
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 80 | 80 | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 64 | 64 | 64 | 96 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1505470
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 96 | 97 | 95 | 95 | 97 | 95 | 94 | 94 | 92 | 93 | 93 | 91 | 92 | 92 | 91 | 92 | 96 |  | 98 | 98 | 98 | 97 | 97 | 97 | 97 | 2272175
| Bhola 225 MW CCPP | 173 | 173 | 173 | 173 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 173 | 174 | 173 | 173 | 173 |  | 174 | 173 | 173 | 173 | 173 | 174 | 173 | 4188315
140 | Bhola 33 MW PP (Venture) | 26 | 25 | 24 | 25 | 23 | 20 | 16 | 14 | 15 | 13 | 8 | 8 | 22 | 25 | 22 | 22 | 21 | 30 |  | 30 | 30 | 29 | 30 | 29 | 28 | 26 | 522732
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 0 | 24 | 24 | 40 | 40 | 40 | 40 | 8 | 8 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 480375
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 20 | 53 | 59 |  | 60 | 53 | 53 | 53 | 0 |  |  | 297728
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 33 | 11 | 0 | [14 empty] | 16 |  | 48 | 50 | 49 | 51 | 51 | 51 | 54 | 376128
146 | Bheramara HVDC | 938 | 937 | 938 | 938 | 938 | 938 | 937 | 938 | 938 | 939 | 938 | 927 | 926 | 927 | 926 | 927 | 926 | 927 |  | 926 | 927 | 926 | 927 | 927 | 927 | 926 | 22361455
147 | Bheramara 360 MW CCPP | 345 | 330 | 330 | 330 | 330 | 330 | 335 | 330 | 315 | 315 | 315 | 305 | 295 | 285 | 280 | 270 | 275 | 265 |  | 265 | 265 | 265 | 265 | 265 | 275 | 275 | 7326144
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | [13 empty] | 49 | 60 | 67 | 58 | 59 |  | 67 | 67 | 68 | 68 | 69 | 66 | 66 | 642327
152 | Barapukuria 275 MW TPP Unit-3 | 279 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 284 | 285 | 280 | 285 | 285 | 283 | 283 |  | 283 | 283 | 283 | 283 | 283 | 283 | 280 | 6835900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 5 | 50 |  | 50 | 50 | 50 | 50 | 0 | 0 |  | 213976
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 190 | 186 | 187 | 188 | 187 | 185 | 181 | 177 | 180 | 167 | 181 | 186 | 197 | 161 | 181 | 202 | 188 | 191 |  | 190 | 181 | 181 | 183 | 180 | 181 | 184 | 4699245
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 201 | 196 | 193 | 194 | 199 | 200 | 163 | 160 | 168 | 155 | 169 | 190 | 195 | 161 | 177 | 199 | 188 | 181 |  | 188 | 188 | 188 | 187 | 188 | 188 | 192 | 4661527
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 426 | 415 | 431 | 431 | 429 | 424 | 425 | 370 | 383 | 396 | 423 | 424 | 412 | 400 | 399 | 398 | 346 | 402 |  | 395 | 372 | 400 | 365 | 368 | 377 | 406 | 9691363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 46 |  | 46 | 20 | 0 | 0 | 0 |  |  | 108703
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507840
163 | Bogura 20 MW PP (Energyprima) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 294660
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240282
165 | Amnura 50 MW PP(Sinha) | 24 | 0 | [13 empty] | 6 | 6 | 50 |  | 50 | 50 | 50 | 50 | 50 | 25 | 0 | 306820
166 | Katakhali 50 MW PP (Northern) | 50 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 32 | 25 | 8 | 8 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 673501
167 | Katakhali 50 MW Peaking PP | [16 empty] | 0 | 45 |  | 48 | 48 | 0 | 0 | 0 |  |  | 94132
168 | Santahar 50 MW Peaking PP | [16 empty] | 9 | 34 |  | 35 | 34 | 0 | 0 | 0 |  |  | 82542
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 39 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 593760
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 15 | 60 |  | 68 | 68 | 43 | 42 | 0 | 0 |  | 239020
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence) | 35 | 0 | [15 empty] | 42 |  | 102 | 113 | 113 | 113 | 113 | 113 | 74 | 755520
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 4 | 0 |  | 0 | [6 empty] | 5760
173 | Rangpur 20 MW GTPP | [19 empty] | 16 | 16 | 16 | 17 | 17 | 17 | 0 | 83000
175 | Saidpur 20 MW GTPP | [17 empty] | 18 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 102000
176 | Rangpur 113 MW PP (Confidence) | 42 | 32 | 0 |  |  |  | 60 | 100 | 100 | 100 | 100 | 100 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1894080
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1.1 | 1.1 | 2.2 | 3 | 4.6 | 5.2 | 5.3 | 3.6 | 1.1 | 0.1 | 0 | [8 empty] | 23258
178
178