## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-20 | Sunday
|  | Date (day): | 2019-10-20 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12990 | MW |  |  | (b) At Evening Peak Hour : |  | 14830 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-19 | 2019-10-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 370 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 379 | 360 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 350 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 330 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 230 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 65 | 64 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 30 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under shut down
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 101 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 46 | 47 | 47
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 54 | 68 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 53 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 34 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 230 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 41 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 87 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2247 | 3398 | 3944 | 4347 | 501 | 965
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 105 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 90 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3.9 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 90 | 82 | 166 | 166 | 64 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 215 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 95 | 104 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 19 | 15 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 49 | 96 | 50 | 97 |  | 11 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.8 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 49 | 160 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 113 | 113
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 818.7 | 1250 | 1494.4 | 1652 | 319 | 109
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 125 | 120 | 120
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 197 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 295 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 295 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 17 | 23 | 23 | 23 |  | 22 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 50 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 55 | 55 | 140 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 35 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 25 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 126 | 127 | 140 | 141
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 180 | 128 | 180
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1482 | 1742 | 1989 | 2292 | 403 | 43
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 131 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 91 | 91 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 150 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 267.2 | 509 | 583.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 60 | 60 | 60
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 157 | 154 | 155 |  | 175 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 40 | 50 | 50
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 27 | 48 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 68 | 68 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 75 | 75 | 75 |  | 11 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 83 | 81 | 110 | 130
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 39 | 42 | 42 | 42 |  | 8 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 318 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1042 | 1178 | 1278 | 1299 | 0 | 604
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 928 | 927 | 395 | 938
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 0 | 75
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 390 | 375 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 102 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1318 | 1721 | 1445 | 2158 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 34 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 173 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 88 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 283 | 413 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 45 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 24 | 50 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 199 | 171 | 225 | 225 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 175 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 410 | 335 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 93 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 872 | 1161 | 1477 | 1627 | 220 | 171
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 279 | 280 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 15
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 105 | 107 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.1 | 0 | 8 | 0
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 798 | 718 | 391.1 | 419 | 401 | 425 | 0 | 170
| Total |  |  |  |  | 19541 | 19018 | 8721 | 11791 | 12990 | 14830 | 1495 | 2062
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8335.6518 | 11270 | 12416.0207 | 14174.718
A. |  | 2019-10-19 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11791 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 7642.3 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11791 | MW
3 | Day peak Generation : |  |  | 8721 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11270 | MW
4 | Evening peak Generation : |  |  | 11791 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 227.9187 | MKWHr | By Solar | 0.21833 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 154.3764 | MKWHr |  | By Oil: | 38.7424 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.7606 | MKWHr |  | By Hydro: | 1.9936 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1495 | MW | Dhaka | 4093 | 4093 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2062 | MW | Chittagong | 1160 | 1160 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3557 | MW | Khulna | 1411 | 1411 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1267.23 | MMCFD |  |  | Rajshahi | 1146 | 1146 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 144424675.984 | ii) Oil : | Taka | 329571134.64 | Comilla | 1099 | 1099 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 27650854 | Total | Taka | 501646664.624 | Mymensingh | 932 | 932 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.529 | MKWHr. | Sylhet | 467 | 467 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -34 | MW (E to W) at | 19:30 | hrs | Barisal | 333 | 333 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -34 | MW at | 19:30 | hrs | Rangpur | 629 | 629 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35° C |  |  | Total | 11270 | 11270 |  | 0
B. |  | 2019-10-20 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14830 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 2830 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 231.9586 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8198.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2407 | MKWHr. | ii) HVDC Flow at Peak Time |  | 927 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5866 | MKWHr. | iii) Maximum HVDC Flow : |  | 928 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.02 |  | (b) Today: | 102.95 |  | (c) Rule Curve: |  | 2.3
.

## YesterdayGen
2019-10-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 346 | 322 |  | 0 | 400 | 260 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 204 | 0 | 133 | 0 |  | 0 | 0 | 0 | 80 | 97 | 5 | 19 | 32 | 125 | 0 | 0 | 340 | 310 | 179 | 55 | 140 | 27 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 148 | 158 | 95 | 22 | 0 | 60 | 60 | 42 | 49 | 130 | 155 | 66 | 75 | 40 | 110 | 17 | 43 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 100 | 200 | 0 | 0 | 96 | 0 | 0 | 0 | 33 | 0 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 4 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 0 | 11 | 0 | 194 | 0 | 97 | 0 | 192 | 0 | 407 | 35 | 0 | 0 | 34 | 110 | 0 | 0 | 0 |  | 6427 | 3060 | 9487 | 4447 | 925 | 2154 | 1443 | 280 | 90 | 0 | 148 | 0 | 0 | 103.03
2:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 346 | 323 |  | 0 | 360 | 260 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 19 | 41 | 125 | 0 | 0 | 340 | 310 | 185 | 55 | 140 | 27 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 144 | 157 | 95 | 22 | 0 | 60 | 60 | 42 | 49 | 130 | 155 | 66 | 75 | 40 | 111 | 17 | 43 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 120 | 0 | 0 | 38 | 0 | 0 | 0 | 33 | 0 | 0 |  | 927 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 0 | 19 | 0 | 172 | 0 | 97 | 0 | 197 | 0 | 431 | 35 | 0 | 0 | 17 | 61 | 0 | 0 | 0 |  | 6115 | 2936 | 9051 | 4451 | 927 | 2140 | 1019 | 280 | 90 | 0 | 144 | 0 | 0 | 103.03
3:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 346 | 322 |  | 0 | 360 | 260 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 19 | 37 | 125 | 0 | 0 | 340 | 310 | 181 | 55 | 140 | 27 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 140 | 164 | 95 | 22 | 0 | 60 | 60 | 42 | 49 | 130 | 154 | 66 | 75 | 40 | 81 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 8 | 0 | 0 | 0 | 33 | 0 | 0 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 0 | 18 | 0 | 150 | 0 | 97 | 0 | 197 | 0 | 432 | 35 | 0 | 0 | 0 | 46 | 0 | 0 | 0 |  | 5949 | 2842 | 8791 | 4395 | 926 | 2145 | 815 | 280 | 90 | 0 | 140 | 0 | 0 | 103.03
4:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 351 | 322 |  | 0 | 360 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 19 | 42 | 100 | 0 | 0 | 340 | 315 | 188 | 55 | 140 | 27 | 52 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 136 | 205 | 48 | 22 | 0 | 60 | 60 | 11 | 49 | 100 | 155 | 66 | 75 | 40 | 70 | 17 | 43 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 0 | 0 | 8 | 0 | 0 | 0 | 32 | 0 | 0 |  | 926 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 0 | 21 | 0 | 138 | 0 | 97 | 0 | 200 | 0 | 431 | 35 | 0 | 0 | 0 | 32 | 0 | 0 | 0 |  | 5767 | 2814 | 8581 | 4397 | 926 | 2063 | 689 | 280 | 90 | 0 | 136 | 0 | 0 | 103.02
5:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 345 | 321 |  | 0 | 360 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 50 | 0 | 19 | 42 | 100 | 0 | 0 | 340 | 315 | 184 | 55 | 140 | 27 | 52 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 120 | 207 | 40 | 22 | 0 | 60 | 60 | 11 | 49 | 100 | 154 | 67 | 50 | 40 | 72 | 17 | 41 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 |  | 926 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 280 | 0 | 0 | 25 | 0 | 128 | 0 | 96 | 0 | 200 | 0 | 432 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5650 | 2723 | 8373 | 4367 | 926 | 2029 | 561 | 280 | 90 | 0 | 120 | 0 | 0 | 103.02
6:00 | 35 | 0 | 200 | 0 | 330 | 0 | 0 | 346 | 322 |  | 0 | 330 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 203 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 50 | 0 | 19 | 42 | 100 | 0 | 0 | 340 | 310 | 179 | 55 | 140 | 27 | 52 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 116 | 207 | 40 | 22 | 0 | 60 | 60 | 11 | 10 | 100 | 155 | 67 | 10 | 10 | 71 | 17 | 12 | 10 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 0.057 | 16 | 0 | 0 |  | 927 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 281 | 0 | 0 | 92 | 0 | 0 | 0 | 63 | 0 | 199 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5375.057 | 2550 | 7925.057 | 4271 | 927 | 1790 | 450 | 281 | 90 | 0 | 116 | 0.057 | 0 | 103.02
7:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 348 | 282 |  | 0 | 330 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 203 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 24 | 0 | 19 | 30 | 100 | 0 | 0 | 280 | 275 | 190 | 8 | 140 | 24 | 51 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 110 | 207 | 8 | 22 | 0 | 60 | 60 | 11 | 10 | 100 | 154 | 68 | 10 | 10 | 78 | 17 | 15 | 0 | 295 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 16 | 0 | 0 |  | 926 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 280 | 0 | 0 | 183 | 0 | 0 | 0 | 63 | 0 | 183 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 5040.2 | 2602.1 | 7642.3 | 4182 | 926 | 1672 | 375 | 280 | 90 | 0 | 110 | 7.3 | 0 | 103.01
8:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 348 | 282 |  | 0 | 330 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 205 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 12 | 100 | 0 | 0 | 270 | 265 | 183 | 8 | 140 | 24 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 114 | 191 | 10 | 22 | 1 | 60 | 60 | 11 | 10 | 100 | 154 | 64 | 10 | 10 | 82 | 17 | 20 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 16 | 0 | 0 |  | 926 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 279 | 0 | 0 | 205 | 0 | 0 | 0 | 63 | 0 | 180 | 0 | 428 | 0 | 0 | 0 | 0 | 10 | 0 | 2.6 | 0 |  | 5018.4 | 2673.6 | 7692 | 4170 | 926 | 1708 | 388 | 279 | 90 | 0 | 114 | 17 | 0 | 103.01
9:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 363 | 280 |  | 0 | 330 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 212 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 25 | 1 | 19 | 2 | 100 | 0 | 0 | 290 | 285 | 195 | 8 | 140 | 24 | 52 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 124 | 187 | 40 | 20 | 1.6 | 60 | 60 | 11 | 10 | 100 | 156 | 63 | 10 | 10 | 81 | 17 | 20 | 0 | 315 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 15.48 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 16 | 0 | 0 |  | 926 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 0 | 201 | 0 | 0 | 0 | 62 | 0 | 170 | 0 | 423 | 0 | 0 | 0 | 0 | 39 | 0 | 3.6 | 0 |  | 5155.58 | 2721.6 | 7877.18 | 4243 | 926 | 1696 | 494 | 280 | 90 | 0 | 124 | 24.18 | 0 | 103.01
10:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 360 | 280 |  | 0 | 330 | 260 | 0 | 32 | 7 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 29 | 0 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 211 | 0 | 95 | 0 |  | 0 | 0 | 0 | 0 | 25 | 15 | 19 | 2 | 100 | 0 | 0 | 295 | 330 | 200 | 55 | 140 | 17 | 53 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 8 | 18 | 132 | 171 | 91 | 20 | 2.2 | 60 | 60 | 11 | 10 | 100 | 158 | 63 | 10 | 10 | 83 | 17 | 20 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 18.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 16 | 0 | 0 |  | 926 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 0 | 198 | 0 | 0 | 0 | 60 | 0 | 170 | 0 | 420 | 0 | 0 | 0 | 0 | 70 | 0 | 3.6 | 0 |  | 5278.1 | 2761.6 | 8039.7 | 4237 | 926 | 1734 | 612 | 280 | 90 | 0 | 132 | 28.7 | 0 | 103
11:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 369 | 349 |  | 0 | 380 | 260 | 0 | 47 | 30 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 0 | 212 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 25 | 18 | 19 | 2 | 100 | 0 | 0 | 355 | 330 | 213 | 55 | 125 | 17 | 52 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 8 | 18 | 134 | 171 | 95 | 20 | 2.2 | 58 | 60 | 11 | 10 | 130 | 156 | 63 | 10 | 10 | 83 | 17 | 15 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 16 | 0 | 0 |  | 928 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 61 | 0 | 173 | 0 | 418 | 0 | 0 | 0 | 0 | 96 | 0 | 3.4 | 0 |  | 5548 | 2816.4 | 8364.4 | 4331 | 928 | 1884 | 705 | 280 | 90 | 0 | 134 | 12.4 | 0 | 103
12:00 | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 379 | 348 |  | 0 | 380 | 260 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 30 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 120 | 0 | 218 | 0 | 95 | 0 |  | 0 | 0 | 0 | 0 | 49 | 18 | 19 | 2 | 100 | 0 | 0 | 360 | 350 | 200 | 55 | 126 | 17 | 51 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 140 | 154 | 91 | 20 | 2.2 | 58 | 60 | 11 | 27 | 130 | 158 | 63 | 10 | 40 | 83 | 17 | 39 | 7 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 3.9 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 49 | 0 | 0 |  | 928 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 279 | 0 | 0 | 199 | 0 | 0 | 0 | 88 | 0 | 180 | 0 | 410 | 0 | 0 | 0 | 0 | 105 | 0 | 7.1 | 6 |  | 5856.9 | 2870.1 | 8727 | 4425 | 928 | 1975 | 872 | 279 | 90 | 0 | 140 | 18 | 0 | 103
13:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 364 | 348 |  | 0 | 450 | 260 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 120 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 94 | 18 | 19 | 2 | 125 | 0 | 0 | 340 | 320 | 183 | 55 | 125 | 23 | 51 | 0 | 9 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 144 | 154 | 90 | 20 | 2.1 | 60 | 60 | 47 | 48 | 130 | 153 | 63 | 75 | 40 | 70 | 17 | 42 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18.05 | 50 | 0 | 0 | 0 | 6 | 0 | 0 | 4.5 | 48 | 0 | 0 |  | 928 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 21 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 201 | 0 | 0 | 0 | 95 | 0 | 184 | 0 | 416 | 17 | 0 | 0 | 0 | 104 | 0 | 2.6 | 10 |  | 6173.65 | 2863.6 | 9037.25 | 4406 | 928 | 2183 | 985 | 280 | 84 | 0 | 144 | 27.25 | 0 | 102.99
14:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 372 | 300 |  | 0 | 400 | 250 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 120 | 0 | 218 | 0 | 116 | 0 |  | 0 | 0 | 0 | 10 | 96 | 18 | 19 | 2 | 125 | 0 | 0 | 305 | 320 | 201 | 55 | 127 | 23 | 51 | 0 | 28 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 144 | 139 | 95 | 22 | 1.5 | 59 | 60 | 47 | 48 | 100 | 161 | 63 | 75 | 40 | 85 | 17 | 41 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17 | 50 | 0 | 0 | 0 | 16 | 0 | 0 | 3.69 | 52 | 0 | 0 |  | 928 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 21 | 13 | 11 | 0 | 0 | 282 | 0 | 0 | 176 | 0 | 0 | 0 | 93 | 0 | 210 | 0 | 408 | 17 | 0 | 0 | 0 | 100 | 0 | 4.2 | 11 |  | 6072.19 | 2901.2 | 8973.39 | 4462 | 928 | 2054 | 993 | 282 | 84 | 0 | 144 | 26.39 | 0 | 102.99
15:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 383 | 352 |  | 0 | 390 | 240 | 0 | 80 | 35 | 0 | 0 | 0 | 0 | 45 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 84 | 0 | 100 | 120 | 0 | 212 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 96 | 18 | 19 | 4 | 125 | 0 | 0 | 355 | 335 | 189 | 55 | 126 | 23 | 49 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 152 | 137 | 95 | 22 | 1 | 60 | 60 | 41 | 48 | 163 | 154 | 62 | 75 | 40 | 119 | 17 | 41 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 80 | 11 | 0 | 0 | 40 | 0 | 0 | 3 | 85 | 0 | 0 |  | 928 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 21 | 10 | 11 | 0 | 0 | 280 | 0 | 0 | 194 | 0 | 0 | 0 | 92 | 0 | 210 | 0 | 410 | 17 | 0 | 0 | 0 | 102 | 0 | 3 | 14 |  | 6445 | 2902 | 9347 | 4583 | 928 | 2176 | 1124 | 280 | 84 | 0 | 152 | 20 | 0 | 102.99
16:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 352 | 352 |  | 0 | 330 | 230 | 0 | 80 | 55 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 82 | 0 | 100 | 120 | 0 | 205 | 0 | 133 | 0 |  | 0 | 0 | 0 | 10 | 96 | 18 | 19 | 6 | 125 | 0 | 0 | 340 | 315 | 185 | 55 | 127 | 23 | 49 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 146 | 139 | 91 | 22 | 0 | 60 | 60 | 42 | 48 | 163 | 155 | 63 | 75 | 40 | 110 | 17 | 44 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 80 | 36 | 0 | 0 | 40 | 0 | 0 | 2.79 | 88 | 0 | 0 |  | 928 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 174 | 20 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 0 | 205 | 0 | 414 | 17 | 0 | 0 | 0 | 107 | 0 | 1.7 | 15 |  | 6366.79 | 2939.7 | 9306.49 | 4462 | 928 | 2105 | 1283 | 280 | 82 | 10 | 146 | 10.49 | 0 | 102.98
17:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 347 | 352 |  | 0 | 330 | 230 | 1 | 80 | 55 | 0 | 0 | 0 | 0 | 60 | 16 | 16 | 5 | 19 | 0 | 0 | 53 | 35 | 17 | 7 | 25 | 29 | 33 | 33 | 0 | 0 | 80 | 0 | 100 | 120 | 2 | 169 | 0 | 104 | 0 |  | 0 | 0 | 3 | 10 | 96 | 18 | 19 | 7 | 125 | 0 | 0 | 300 | 270 | 158 | 55 | 127 | 23 | 49 | 0 | 35 | 0 | 9 | 3 | 22 | 8 | 33 | 20 | 144 | 143 | 91 | 22 | 0 | 59 | 60 | 42 | 48 | 163 | 152 | 64 | 75 | 40 | 76 | 17 | 42 | 10 | 285 | 24 | 11 | 0 | 9 | 0 | 0 | 0 | 0 | 106 | 1 | 80 | 34 | 0 | 0 | 67 | 20 | 0 | 0.126 | 88 | 0 | 0 |  | 927 | 0 | 345 | 0 | 9 | 0 | 0 | 0 | 6 | 18 | 0 | 163 | 21 | 64 | 0 | 0 | 0 | 0 | 10 | 20 | 20 | 24 | 0 | 0 | 10 | 22 | 5 | 8 | 0 | 0 | 280 | 0 | 17 | 182 | 0 | 0 | 0 | 76 | 0 | 197 | 0 | 328 | 17 | 0 | 3 | 0 | 50 | 0 | 0.2 | 18 |  | 6286.126 | 2840.2 | 9126.326 | 4200 | 927 | 1985 | 1400 | 280 | 80 | 109 | 144 | 1.326 | 0 | 102.98
18:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 322 | 348 |  | 0 | 330 | 230 | 28 | 64 | 55 | 0 | 0 | 0 | 0 | 88 | 80 | 100 | 12 | 48 | 0 | 17 | 53 | 55 | 55 | 22 | 25 | 21 | 33 | 33 | 26 | 0 | 80 | 0 | 100 | 120 | 23 | 207 | 0 | 134 | 0 |  | 0 | 0 | 68 | 70 | 96 | 39 | 19 | 2 | 125 | 0 | 0 | 300 | 305 | 190 | 55 | 126 | 23 | 49 | 0 | 35 | 0 | 8 | 25 | 22 | 8 | 33 | 20 | 182 | 138 | 90 | 22 | 0 | 60 | 60 | 43 | 48 | 130 | 155 | 63 | 75 | 40 | 118 | 17 | 42 | 10 | 265 | 24 | 11 | 0 | 111 | 0 | 0 | 57 | 0 | 144 | 0 | 100 | 104 | 0 | 0 | 115 | 87 | 0 | 0 | 160 | 0 | 0 |  | 927 | 0 | 365 | 0 | 93 | 0 | 0 | 0 | 39 | 40 | 40 | 174 | 30 | 110 | 0 | 0 | 0 | 50 | 39 | 86 | 50 | 50 | 28 | 52 | 29 | 22 | 5 | 8 | 0 | 0 | 280 | 17 | 0 | 163 | 0 | 0 | 0 | 97 | 0 | 165 | 0 | 404 | 105 | 0 | 70 | 70 | 107 | 0 | 0 | 0 |  | 7403 | 3715 | 11118 | 4336 | 927 | 2030 | 2779 | 280 | 80 | 504 | 182 | 0 | 0 | 102.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 348 | 350 |  | 0 | 330 | 230 | 100 | 64 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 149 | 62 | 54 | 0 | 42 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 33 | 0 | 82 | 0 | 105 | 120 | 25 | 203 | 0 | 104 | 0 |  | 0 | 0 | 85 | 100 | 96 | 50 | 19 | 11 | 125 | 0 | 0 | 295 | 275 | 187 | 55 | 126 | 23 | 50 | 0 | 35 | 0 | 25 | 52 | 22 | 8 | 33 | 12 | 182 | 132 | 95 | 22 | 0 | 60 | 60 | 40 | 48 | 130 | 155 | 65 | 75 | 40 | 75 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 87 | 0 | 0 | 160 | 0 | 0 |  | 927 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 42 | 20 | 40 | 173 | 34 | 110 | 0 | 0 | 0 | 50 | 46 | 93 | 50 | 50 | 0 | 52 | 0 | 22 | 13 | 11 | 0 | 0 | 280 | 17 | 15 | 183 | 0 | 0 | 0 | 97 | 0 | 181 | 0 | 335 | 105 | 0 | 93 | 102 | 107 | 0 | 0 | 0 |  | 7994 | 3713 | 11707 | 4270 | 927 | 2017 | 3407 | 280 | 82 | 542 | 182 | 0 | 0 | 102.97
19:30 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 360 | 350 |  | 0 | 330 | 230 | 100 | 64 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 149 | 50 | 54 | 0 | 46 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 82 | 0 | 105 | 90 | 25 | 215 | 0 | 104 | 0 |  | 0 | 0 | 85 | 100 | 96 | 50 | 19 | 19 | 125 | 0 | 0 | 295 | 295 | 197 | 55 | 127 | 23 | 50 | 0 | 35 | 0 | 25 | 52 | 22 | 8 | 33 | 20 | 180 | 131 | 91 | 22 | 0 | 60 | 60 | 40 | 48 | 130 | 157 | 65 | 75 | 40 | 81 | 17 | 42 | 10 | 318 | 24 | 11 | 0 | 230 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 87 | 0 | 0 | 160 | 0 | 0 |  | 927 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 37 | 20 | 40 | 173 | 34 | 110 | 0 | 0 | 0 | 50 | 45 | 93 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 17 | 15 | 171 | 0 | 0 | 0 | 96 | 0 | 175 | 0 | 335 | 105 | 0 | 93 | 102 | 107 | 0 | 0 | 0 |  | 8077 | 3714 | 11791 | 4317 | 927 | 2043 | 3426 | 280 | 82 | 536 | 180 | 0 | 0 | 0
20:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 363 | 351 |  | 0 | 330 | 230 | 100 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 149 | 50 | 54 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 40 | 0 | 82 | 0 | 105 | 35 | 25 | 206 | 0 | 104 | 0 |  | 0 | 0 | 85 | 100 | 96 | 50 | 19 | 19 | 125 | 0 | 0 | 285 | 290 | 192 | 55 | 126 | 23 | 48 | 0 | 35 | 0 | 25 | 52 | 22 | 8 | 33 | 20 | 180 | 129 | 91 | 22 | 0 | 60 | 60 | 40 | 48 | 130 | 155 | 65 | 75 | 40 | 78 | 17 | 42 | 10 | 310 | 24 | 11 | 0 | 230 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 87 | 0 | 0 | 160 | 0 | 0 |  | 927 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 37 | 20 | 40 | 173 | 34 | 110 | 0 | 0 | 0 | 50 | 45 | 93 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 17 | 15 | 171 | 0 | 0 | 0 | 96 | 0 | 171 | 0 | 332 | 103 | 0 | 93 | 102 | 107 | 0 | 0 | 0 |  | 8002 | 3695 | 11697 | 4214 | 927 | 2031 | 3447 | 280 | 82 | 536 | 180 | 0 | 0 | 102.97
21:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 361 | 351 |  | 0 | 330 | 230 | 100 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 7 | 149 | 0 | 54 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 0 | 105 | 0 | 25 | 204 | 0 | 134 | 0 |  | 0 | 0 | 85 | 100 | 96 | 50 | 19 | 32 | 125 | 0 | 0 | 335 | 305 | 189 | 55 | 126 | 23 | 49 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 176 | 130 | 95 | 22 | 0 | 60 | 60 | 41 | 49 | 130 | 154 | 65 | 75 | 40 | 117 | 17 | 42 | 10 | 310 | 24 | 11 | 0 | 230 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 87 | 0 | 0 | 162 | 0 | 0 |  | 928 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 37 | 20 | 40 | 173 | 35 | 110 | 0 | 0 | 0 | 50 | 30 | 40 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 17 | 15 | 174 | 0 | 0 | 0 | 96 | 0 | 175 | 0 | 418 | 105 | 0 | 93 | 101 | 107 | 0 | 0 | 0 |  | 7906 | 3718 | 11624 | 4308 | 928 | 2134 | 3270 | 280 | 85 | 443 | 176 | 0 | 0 | 102.97
22:00 | 35 | 0 | 201 | 0 | 370 | 0 | 0 | 351 | 353 |  | 0 | 330 | 220 | 65 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 149 | 0 | 62 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 84 | 0 | 105 | 0 | 25 | 204 | 0 | 134 | 0 |  | 0 | 0 | 85 | 90 | 96 | 50 | 19 | 35 | 125 | 0 | 0 | 340 | 315 | 179 | 55 | 126 | 23 | 49 | 0 | 35 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 174 | 132 | 95 | 22 | 0 | 59 | 60 | 41 | 49 | 130 | 154 | 65 | 75 | 40 | 109 | 17 | 42 | 10 | 315 | 24 | 11 | 0 | 95 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 50 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 37 | 20 | 40 | 174 | 35 | 110 | 0 | 0 | 0 | 50 | 0 | 40 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 17 | 15 | 189 | 0 | 0 | 0 | 97 | 0 | 195 | 0 | 405 | 105 | 0 | 93 | 101 | 107 | 0 | 0 | 0 |  | 7635 | 3691 | 11326 | 4313 | 927 | 2132 | 3003 | 280 | 84 | 413 | 174 | 0 | 0 | 102.96
23:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 351 | 353 |  | 0 | 330 | 220 | 10 | 80 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 84 | 0 | 62 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 87 | 0 | 105 | 0 | 25 | 209 | 0 | 134 | 0 |  | 0 | 0 | 85 | 90 | 0 | 31 | 19 | 37 | 125 | 0 | 0 | 355 | 325 | 194 | 55 | 126 | 23 | 49 | 0 | 35 | 0 | 0 | 47 | 22 | 8 | 33 | 20 | 170 | 130 | 95 | 22 | 0 | 60 | 60 | 41 | 49 | 130 | 157 | 65 | 75 | 40 | 121 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 50 | 0 | 0 | 162 | 0 | 0 |  | 928 | 0 | 370 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 188 | 0 | 0 | 0 | 97 | 0 | 195 | 0 | 423 | 105 | 0 | 93 | 102 | 107 | 0 | 0 | 0 |  | 7338 | 3520 | 10858 | 4400 | 928 | 2136 | 2688 | 280 | 87 | 169 | 170 | 0 | 0 | 102.96
24:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 359 | 352 |  | 0 | 330 | 220 | 0 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 63 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 87 | 0 | 105 | 0 | 25 | 204 | 0 | 134 | 0 |  | 0 | 0 | 85 | 90 | 0 | 24 | 19 | 31 | 125 | 0 | 0 | 340 | 315 | 180 | 55 | 126 | 23 | 49 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 166 | 137 | 95 | 22 | 0 | 60 | 60 | 35 | 49 | 163 | 154 | 67 | 75 | 40 | 110 | 17 | 42 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 50 | 0 | 0 | 162 | 0 | 0 |  | 927 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 195 | 0 | 0 | 0 | 97 | 0 | 202 | 0 | 430 | 105 | 0 | 93 | 67 | 107 | 0 | 0 | 0 |  | 7194 | 3419 | 10613 | 4345 | 927 | 2171 | 2502 | 280 | 87 | 135 | 166 | 0 | 0 | 102.96
KWH | 756000 | 0 | 4631000 | 0 | 8566782 | 0 | 0 | 8646660 | 7842000 |  | 0 | 8645000 | 6048582 | 428160 | 1484856 | 665761 | 0 | 0 | 0 | 0 | 990720 | 398880 | 854400 | 157312 | 379200 | 0 | 174672 | 859680 | 390045 | 379159 | 461052 | 600000 | 624600 | 781200 | 818600 | 114120 | 0 | 1401627 | 592000 | 2500000 | 2400000 | 176020 | 4872048 | 0 | 2858958 | 0 |  | 0 | 0 | 548092 | 749880 | 1665600 | 454080 | 451248 | 447840 | 2787852 | 0 | 0 | 8130000 | 7539500 | 4580000 | 1154181 | 3148680 | 535896 | 1222560 | 0 | 578112 | 0 | 54288 | 302160 | 496980 | 186840 | 600500 | 470090 | 3586560 | 3771400 | 1913280 | 483012 | 13550 | 1428000 | 1440800 | 705000 | 980496 | 3145647 | 3536000 | 1553472 | 1351680 | 790920 | 2262610 | 439000 | 857700 | 195300 | 7458750 | 424296 | 252960 | 0 | 943418 | 0 | 0 | 964800 | 0 | 1609920 | 138240 | 1404480 | 2019840 | 0 | 0 | 1240800 | 494604 | 0 | 32520 | 1758873 | 0 | 0 |  | 22240727 | 0 | 8736192 | 0 | 685440 | 0 | 0 | 0 | 185280 | 133888 | 270375 | 4213315 | 601736 | 1111680 | 0 | 0 | 0 | 260168 | 149651 | 357580 | 401230 | 819865 | 36468 | 386880 | 42245 | 505440 | 312120 | 249102 | 0 | 0 | 6760600 | 72000 | 71000 | 3863627 | 0 | 841300 | 0 | 2075864 | 0 | 4782700 | 0 | 9783781 | 1002720 | 0 | 644160 | 664416 | 1745280 | 0 | 34021 | 76400 |  | 153801401 | 74117251 | 227918652 | 105722272 | 22240727 | 48654127 | 35977348 | 6760600 | 1993627 | 2765060 | 3586560 | 218331 | 0
Fuel Cost | 846720 | 0 | 4955170 | 0 | 6339418.68 | 0 | 0 | 6225595.2 | 5959920 |  | 0 | 6916000 | 5443723.8 | 4367232 | 16080990.48 | 6830707.86 | 0 | 0 | 0 | 0 | 10996992 | 4052620.8 | 8467104 | 1648629.76 | 3450720 | 0 | 1634929.92 | 8244331.2 | 3721029.3 | 3776423.64 | 345789 | 450000 | 0 | 0 | 0 | 1093269.6 | 0 | 364423.02 | 153920 | 3825000 | 3672000 | 1691552.2 | 5115650.4 | 0 | 3630876.66 | 0 |  | 0 | 0 | 5749485.08 | 7716265.2 | 15839856 | 4250188.8 | 415148.16 | 1244995.2 | 2927244.6 | 0 | 0 | 6016200 | 6333180 | 4213600 | 1131097.38 | 4187744.4 | 439434.72 | 1259236.8 | 0 | 826700.16 | 0 | 636255.36 | 2840304 | 506919.6 | 140130 | 1134945 | 352567.5 | 24747264 | 3092548 | 18195292.8 | 492672.24 | 222220 | 1942080 | 1959488 | 958800 | 1225620 | 3900602.28 | 3253120 | 2314673.28 | 2378956.8 | 877921.2 | 3439167.2 | 698010 | 1003509 | 458955 | 5295712.5 | 318222 | 192249.6 | 0 | 9877586.46 | 0 | 0 | 9281376 | 0 | 16244092.8 | 1595289.6 | 13089753.6 | 18946099.2 | 0 | 0 | 10881816 | 4406921.64 | 0 | 0 | 16216809.06 | 0 | 0 |  | 60049962.9 | 0 | 6814229.76 | 0 | 6607641.6 | 0 | 0 | 0 | 2149248 | 1753932.8 | 2674008.75 | 3370652 | 932690.8 | 11939443.2 | 0 | 0 | 0 | 2898271.52 | 1833224.75 | 3540042 | 4160755.1 | 9600619.15 | 439439.4 | 3853324.8 | 416113.25 | 555984 | 514998 | 188570.214 | 0 | 0 | 27650854 | 2408400 | 2004330 | 3399991.76 | 0 | 782409 | 0 | 3300623.76 | 0 | 4208776 | 0 | 7142160.13 | 9485731.2 | 0 | 5913388.8 | 5919946.56 | 16300915.2 | 0 | 0 | 0 |  | 375969065.74 | 212810678.404 | 588779744.144 | 98540192.974 | 60049962.9 | 45884483.01 | 297275288.48 | 27650854 | 518343.02 | 32295846.16 | 24747264 | 1817509.6 | 0
Yesterday Day Peak | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 379 | 348 |  | 0 | 380 | 260 | 0 | 65 | 30 | 0 | 0 | 0 | 0 | 30 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 27 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 120 | 0 | 218 | 0 | 95 | 0 |  | 0 | 0 | 0 | 0 | 49 | 18 | 19 | 2 | 100 | 0 | 0 | 360 | 350 | 200 | 55 | 126 | 17 | 51 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 140 | 154 | 91 | 20 | 2.2 | 58 | 60 | 11 | 27 | 130 | 158 | 63 | 10 | 40 | 83 | 17 | 39 | 7 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 3.9 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 49 | 0 | 0 |  | 928 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 279 | 0 | 0 | 199 | 0 | 0 | 0 | 88 | 0 | 180 | 0 | 410 | 0 | 0 | 0 | 0 | 105 | 0 | 7.1 |  |  | 8721 | DayPeak
Yesterday Evening Peak | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 360 | 350 | 0 | 0 | 330 | 230 | 100 | 64 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 149 | 50 | 54 | 0 | 46 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 34 | 0 | 82 | 0 | 105 | 90 | 25 | 215 | 0 | 104 | 0 | 0 | 0 | 0 | 85 | 100 | 96 | 50 | 19 | 19 | 125 | 0 | 0 | 295 | 295 | 197 | 55 | 127 | 23 | 50 | 0 | 35 | 0 | 25 | 52 | 22 | 8 | 33 | 20 | 180 | 131 | 91 | 22 | 0 | 60 | 60 | 40 | 48 | 130 | 157 | 65 | 75 | 40 | 81 | 17 | 42 | 10 | 318 | 24 | 11 | 0 | 230 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 87 | 0 | 0 | 160 | 0 | 0 |  | 927 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 37 | 20 | 40 | 173 | 34 | 110 | 0 | 0 | 0 | 50 | 45 | 93 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 17 | 15 | 171 | 0 | 0 | 0 | 96 | 0 | 175 | 0 | 335 | 105 | 0 | 93 | 102 | 107 | 0 | 0 |  |  | 11791 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 84 | 82 | 105 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 97 | 50 | 22 | 20 | 120 | 0 | 0 | 360 | 360 | 225 | 55 | 141 | 23 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 180 | 150 | 95 | 22 | 0 | 60 | 60 | 50 | 50 | 163 | 155 | 68 | 75 | 40 | 130 | 20 | 42 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 | 54 | 113 |  | 938 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 75 | 40 | 180 | 33 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 50 | 40 | 52 | 35 | 22 | 14 | 11 | 0 | 0 | 280 | 17 | 15 | 225 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 68 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 84 | 82 | 105 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 50 | 50 | 22 | 15 | 120 | 0 | 0 | 360 | 360 | 225 | 55 | 140 | 23 | 55 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 128 | 150 | 95 | 22 | 1.6 | 60 | 60 | 50 | 50 | 163 | 154 | 68 | 75 | 40 | 110 | 20 | 42 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 0 | 4.4 | 230 | 54 | 113 |  | 395 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 50 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 358 | 340 | 0 | 0 | 330 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 82 | 105 | 0 | 0 | 205 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 19 | 8 | 100 | 0 | 0 | 290 | 280 | 190 | 55 | 127 | 23 | 49 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 120 | 140 | 48 | 22 | 0.7 | 59 | 60 | 37 | 46 | 100 | 154 | 64 | 75 | 40 | 79 | 17 | 42 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10.8 | 100 | 17 | 0 | 0 | 0 | 0 | 0 | 2.2 | 162 | 0 | 0 | 0 | 938 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 279 | 0 | 0 | 173 | 0 | 0 | 0 | 95 | 0 | 176 | 0 | 422 | 0 | 0 | 0 | 0 | 107 | 0 | 1.4 | 0 | 0
199
| Minimum Generation |  | 7642.3 | 7:00
| Highest Generation |  | 11791 | 19:30
| Day Peak Generation |  | 8721 | 12:00
| Evening Peak Generation |  | 11791 | 19:30
| HVDC Max Flow |  | 928 | 11:00
| HVDC EvPeak Flow |  | 927 | 19:30
| Load factor L.F |  | 80.54%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-20
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8721 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8198.4 | MW
Evening Peak Generation : |  | 11791 | MW Hour : | 19:30 | Available Max Generation : |  | 14830 | MW
E.P. Demand (at gen end) : |  | 11791 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11791 | MW Hour : | 19:30 | Reserve(Generation end) |  | 2830 | MW
Total Gen. (MKWH) : |  | 227.9187 | System Load Factor : | 80.54% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -34 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-20
Actual : | 102.95 | Ft.(MSL) , | Rule curve : | 2.3 | Ft.( MSL )
Gas Consumed : | Total = | 1267.23 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144424675.984
|  | Coal : | 27650854 | Oil : | 329571134.64 | Total : | 501646664.624
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4266.2002 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1453.0516 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1302.2972 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1176.8813 |  |  | 0 | 0%
) | 0 | 0:00 | 1063.4501 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 858.1724 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 476.8786 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 220.8777 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 661.8794 |  |  | 0 | 0%
Total | 0 |  | 11479.6886 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 & 2. | 7) Sirajganj 225 MW Unit-2
|  |  |  | 2) Khulna ST 110 MW | 8) Raozan #2
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Siddirganj-335 MW
4) Ashuganj #3,4
5) Baghabari 100 MW,
6) Ghorasal Unit-1,3 & 5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Chandraghona-Rangamati 132 kV Ckt-1 was under shut down from 08:44 to 13:01 for A/M.
b) Aminbazar-Kaliakoir 132 kV Ckt-2 was under shut down from 09:10 to 15:45 for A/M.
c) Siddhirganj-Maniknagar 230 kV Ckt-1 was under shut down from 08:49 to 17:17 for A/M.
d) Tongi 132 kV Bus-1 was under shut down from 09:10 to 15:15 for D/W.
e) Palashbari 132/33 kV T-4 transformer was under shut down from 08:10 to 15:08 for A/M.
f) Purbasadipur 132/33 kV T-2 transformer was under shut down from 08:55 to 15:03 for A/M.
g) Naogaon 132/33 kV T-2 transformer was under shut down from 08:15 to 15:15 for A/M.
h) Barapukuria 230/132 kV TR-2 transformer was under shut down from 11:13 to 15:43 for D/W.
i) Bakulia 132/33 kV T-2 transformer was under shut down from 06:57 to 16:18 for D/W.
j) Joshore-Benapole 132 kV Ckt-1 was under shut down from 11:33 to 15:07 for D/W.
k) Joshore-Benapole 132 kV Ckt-2 was under shut down from 15:11 to 16:16 for D/W.
l) Raozan #2 was shut down at 20:03 due to condenser tube leakage.
m) Chandraghona-Modunaghat 132 kV Ckt-1 is under shut down since 07:25(20/10/19) for A/M.
n) Naogaon 132/33 kV T-3 transformer is under shut down since 07:20(20/10/19) for A/M.
o) Barapukuria 230/132 kV TR-2 transformer is under shut down since 07:25(20/10/19) for D/W.
p) Julda-Sikalbaha 132 kV Ckt tripped at 22:17 showing dist. O/C relay and was switched on at 22:44.
q) Sikalbaha-ECPV 132 kV Ckt tripped at 22:15 due to Y-phase PT burst at Sikalbaha end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 756000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4631000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 370 | 8566782
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8646660 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 7842000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 8645000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 428160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 6048582 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 1484856 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 665761
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 157312 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 461052
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 990720
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 101 | 398880
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 46 | 174672 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 859680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 854400
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 390045
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 379159
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 54 | 379200 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1224600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 781200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 818600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 34 | 114120 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 230 | 943418 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1609920
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 87 | 494604 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 3398 | 58746383
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 90 | 2400000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 176020
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 138240
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 454080
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1993627 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 215 | 4872048
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2858958 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer & Line overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 548092
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 749880
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1404480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 451248
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 19 | 447840
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 1665600 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32520
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 160 | 1758873 | Transformer & Line overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1250 | 22451506
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 2787852 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 197 | 4580000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 8130000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7539500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 535896 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1222560
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 1154181 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 578112 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 54288 | Low demand
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 127 | 3148680
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2019840
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 496980
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 186840 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 180 | 3586560
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 600500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 302160
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 470090 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1742 | 37394039
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 131 | 3771400 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 483012
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 1913280
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13550
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 964800 | High Voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1240800
| Mymensingh Area Total |  |  |  | 637 | 509 | 8386842
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1428000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1440800
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3145647 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 3536000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 40 | 705000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 48 | 980496
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 252960
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1553472 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1351680
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 790920 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 81 | 2262610
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 439000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 42 | 857700 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 424296
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 318 | 7458750 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 195300
| Sylhet Area Total |  |  |  | 1949 | 1178 | 26822631
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 927 | 22240727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 685440
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 185280
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 133888 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 375 | 8736192 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 270375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1002720
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 102 | 664416
| Khulna Area Total |  |  |  | 2314 | 1721 | 33919038
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1111680
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 601736
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 4213315 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2075864
| Barisal Area Total |  |  |  | 462 | 413 | 8002595
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under shut down.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 260168
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 45 | 149651
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 401230
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 819865
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 36468 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 171 | 3863627 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 841300 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 175 | 4782700 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 335 | 9783781 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 42245 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 505440
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 312120 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249102
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 386880
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 357580 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 93 | 644160 | Engine problem
| Rajshahi Area Total |  |  |  | 2070 | 1161 | 23436317
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6760600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 72000
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 71000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1745280
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34021
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 76400
| Rangpur Area Total |  |  |  | 718 | 419 | 8759301
| Total |  |  |  | 19018 | 11791 | 227918652
| Eastern Grid Total |  |  |  | 13454 | 8077 | 153801401
| Western Grid Total |  |  |  | 5564 | 3714 | 74117251
| National Grid Total |  |  |  | 19018 | 11791 | 227918652
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-19
(a) ENTIRE EASTERN GRID : |  | 7751 | MW | (b) ENTIRE WESTERN GRID : |  | 3519 | MW
i) Dhaka area |  | 4093 | MW | i) Khulna area |  | 1411 | MW
ii) Chittagong area |  | 1160 | MW | ii) Rajshahi area |  | 1146 | MW
iii) Comilla area |  | 1099 | MW | iii) Barisal area |  | 333 | MW
iv) Mymensingh area |  | 932 | MW | iv) Rangpur area |  | 629 | MW
v) Sylhet area |  | 467 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11270 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 1830 | Sherpur | 94 | 1930 | Jhenida | 104 | 1830
Munsiganj | 112 | 1930 | Srimongal | 39 | 1830 | Bottail | 122 | 1830
Sonargaon | 79 | 1900 | Shahjibazar | 118 | 1930 | G.K Project | 58 | 1830
Shyampur | 200 | 0 | Fenchuganj | 41 | 1830 | Faridpur | 170 | 1900
Bhulta | 189 | 1930 | Kulawara | 45 | 1800 | Madaripur | 84 | 2200
Madanganj | 63 | 100 | Sylhet | 143 | 1900 | Sariatpur | 60 | 2000
Shitalakhya | 111 | 1200 | Chatak | 34 | 1800 | Gopalganj | 89 | 2200
Rahim steel | 22 | 1100 | Sunamganj | 35 | 2000 | Bagerhat | 89 | 1830
Matuail | 88 | 900 | Biani Bazar | 56 | 1800 | Mongla | 36 | 100
Ghorasal | 80 | 1800 | Comilla (S) | 182 | 1800 | Satkhira | 100 | 2100
Narsingdi | 146 | 2000 | Comilla(N) | 117 | 1930 | Gallamari | 47 | 1800
Haripur (SBU) | 80 | 100 | Chandpur | 140 | 1830 | Magura | 48 | 1830
Ullon | 86 | 1930 | Feni | 170 | 1900 | Norail | 22 | 1900
Hasnabad | 205 | 1900 | Chowmuhani | 56 | 2100 | Chuadanga | 81 | 1930
Magbazar | 115 | 1600 | Ashuganj | 124 | 2200 | Barisal(N) | 45 | 1930
Maniknagar | 106 | 1300 | Daudkandi | 136 | 1930 | Barisal (S) | 100 | 2100
Bangabhaban | 14 | 1300 | B.Baria | 94 | 1900 | Patuakhali | 107 | 2100
Narinda | 98 | 1300 | Ramganj | 61 | 1900 | Bhandaria | 52 | 1930
Dhanmondi | 169 | 1300 | Madunaghat | 102 | 1930 | Borhan Uddin | 37 | 2200
Lalbag | 84 | 1300 | Hathazari | 102 | 1930 | Ishurdi | 59 | 1800
Madartek | 61 | 2100 | Khulshi | 194 | 2000 | Ruppur Paromanobik | 1 | 100
Mirpur | 111 | 1800 | Halishahar | 140 | 1400 | Natore | 119 | 1930
Kalyanpur | 105 | 1800 | Baraulia | 166 | 1600 | Bogra | 183 | 1830
Gulshan | 130 | 1300 | Sikalbaha | 38 | 1830 | Noagaon | 102 | 1800
Uttara | 60 | 1800 | Dohazari | 82 | 1800 | Rajshahi | 129 | 900
Uttara New | 45 | 1800 | Cox'sbazar | 97 | 1830 | Rajshahi New | 12 | 2000
Kamrangirchar | 75 | 1830 | Chandraghona | 32 | 1830 | C.Nawabganj | 69 | 2000
Savar | 135 | 1830 | Kaptai | 5 | 1800 | Amnura | 32 | 1830
Bhasantec | 158 | 1800 | A. Khaer Stl. | 5 | 200 | Pabna | 109 | 1900
Agargaon | 55 | 1830 | Bakulia | 104 | 1900 | Shahjadpur | 100 | 1900
Satmosjid | 117 | 1800 | Julda | 19 | 700 | Serajganj | 86 | 2000
Tongi | 158 | 1500 | TK chemical | 4 | 100 | Niyamatpur | 54 | 1900
Kabirpur | 126 | 1100 | Modern Steel | 11 | 800 | Joypurhat | 54 | 1830
Basundhara | 88 | 1830 | Shahmirpur | 32 | 1830 | Sherpur(Bogura) | 42 | 1800
Manikganj | 239 | 1930 | Khagrachhari | 21 | 2100 | Mohastangor | 16 | 1930
Joydevpur | 106 | 1830 | Matarbari | 30 | 1830 | Rangpur | 129 | 1900
New Tongi | 144 | 1930 | Baroiar Hat | 24 | 1800 | Lalmonirhat | 60 | 1800
Korda | 68 | 1830 | Rangamati | 12 | 1800 | Saidpur | 86 | 1800
Dhamrai | 126 | 1800 | Abul Khair 230 | 15 | 1200 | Purbasadipur | 82 | 1800
Valuka | 126 | 1800 | BSRM | 108 | 400 | Thakurgaon | 61 | 1930
Tangail | 184 | 1800 | Goalpara | 37 | 1830 | Palashbari | 102 | 1800
Mymensing | 200 | 1800 | Central s/s | 84 | 1830 | Barapukuria | 45 | 1900
Kishorganj | 128 | 1930 | Noapara | 67 | 2100 | Panchagar | 41 | 1830
Netrokona | 99 | 1900 | Jessore | 114 | 1830 | Joldhaka | 22 | 1830
Jamalpur | 118 | 1830 | Benapol | 40 | 1830 | Kurigram | 35 | 1830
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-19 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 385 | 6:00 | 375 | 16:00 | Kaliakoir | 364 | 6:00 | 351 | 16:00
Bheramara | 394 | 7:00 | 389 | 19:30 | Bhulta | 372 | 6:00 | 358 | 15:00
Ashuganj(N) | 378 | 5:00 | 365 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal |  | 7:00 | 220 | 10:00 | Hathazari | 219 | 18:30 | 213 | 11:00
Ishurdi | 234 | 17:00 | 226 | 1:00 | Megnaghat | 220 | 19:00 | 210 | 13:00
Ashuganj | 228 | 6:00 | 221 | 13:00 | Fenchuganj | 232 | 5:00 | 229 | 11:00
Serajganj | 230 | 22:00 | 225 | 11:00 | Siddhirganj | 218 | 4:00 | 209 | 12:00
Baghabari | 234 | 16:00 | 230 | 12:00 | Maniknagar | 217 | 6:00 | 206 | 13:00
Barapukuria | 227 | 18:00 | 220 | 18:30 | Old Airport | 216 | 6:00 | 205 | 11:00
Bogra | 224 | 24:00 | 219 | 20:00 | Barisal | 232 | 24:00 | 222 | 3:00
Khulna South | 226 | 22:00 | 209 | 1:00 | AKSML | 215 | 1:00 | 210 | 11:00
Rampura | 218 | 5:00 | 206 | 11:00 | BSRM | 216 | 18:00 | 211 | 11:00
Haripur | 217 | 4:00 | 210 | 11:00 | Bibiyana | 230 | 6:00 | 225 | 10:00
Hasnabad | 215 | 2:00 | 207 | 15:00 | Bhulta | 219 | 6:00 | 210 | 11:00
Aminbazar | 217 | 6:00 | 206 | 14:00 | Ashuganj (S) | 228 | 18:30 | 222 | 10:00
Tongi | 219 | 18:30 | 206 | 11:00 | Kaliakoir | 221 | 20:00 | 212 | 17:00
Comilla (N) | 225 | 5:00 | 220 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 130 | 700 | 125 | 1100 | Halishahar | 132 | 1930 | 126 | 1100
Munsiganj | 133 | 2000 | 126 | 900 | Baraulia | 128 | 100 | 124 | 1100
Megnaghat | 130 | 1930 | 123 | 1200 | Sikalbaha | 132 | 1900 | 126 | 1100
Shyampur | 131 | 1900 | 125 | 1200 | Dohazari | 130 | 1930 | 124 | 1100
Bhulta | 125 | 600 | 120 | 1000 | Cox'sbazar | 120 | 800 | 110 | 1000
Madanganj | 136 | 2000 | 126 | 1400 | Chandraghona | 131 | 2100 | 127 | 1100
Shitalakhya | 137 | 1900 | 128 | 100 | Kaptai | 130 | 100 | 127 | 1200
Rahim steal | 131 | 2000 | 126 | 1100 | A. Khaer Stl. | 128 | 1930 | 125 | 1100
Matuail | 129 | 1900 | 124 | 1100 | Bakulia | 130 | 1930 | 124 | 1100
Ghorasal | 135 | 1830 | 130 | 1500 | Julda | 132 | 2000 | 125 | 1100
Narsinghdi | 131 | 1700 | 125 | 1900 | TK Chemical | 131 | 2100 | 126 | 1100
Haripur (SBU) | 131 | 500 | 126 | 1300 | Modern Steel | 131 | 1830 | 127 | 1100
Ullon | 133 | 600 | 124 | 1200 | Shahmirpur | 131 | 1900 | 125 | 1100
Hasnabad | 133 | 600 | 125 | 1200 | Khagrachhari | 129 | 800 | 126 | 1400
Magbazar | 133 | 600 | 124 | 1200 | Matarbari | 124 | 1600 | 119 | 100
Maniknagar | 134 | 2100 | 121 | 1100 | Baroiar Hat | 125 | 700 | 123 | 1000
Bangabhaban | 134 | 2100 | 121 | 1100 | Rangamati | 129 | 700 | 126 | 1100
Narinda | 134 | 2100 | 121 | 1100 | Goalpara | 136 | 2300 | 124 | 1100
Dhanmondi | 133 | 600 | 124 | 1200 | Central s/s | 138 | 2200 | 122 | 1200
Lalbag | 132 | 2000 | 121 | 1200 | Noapara | 131 | 2200 | 122 | 1500
Madartek | 133 | 600 | 123 | 1000 | Jessore | 136 | 1700 | 120 | 1200
Mirpur | 133 | 100 | 124 | 1200 | Benapol | 129 | 1700 | 120 | 1200
Kalyanpur | 135 | 500 | 127 | 1100 | Jhenida | 126 | 1900 | 117 | 1930
Gulshan | 132 | 500 | 123 | 1000 | Bottail | 134 | 1700 | 127 | 2000
Uttara | 131 | 1900 | 122 | 1100 | G.K Project | 142 | 1700 | 137 | 1500
Uttara New | 131 | 400 | 123 | 1000 | Faridpur | 132 | 900 | 124 | 1500
Kamrangirchar | 131 | 400 | 121 | 1200 | Madaripur | 134 | 900 | 122 | 1500
Savar | 131 | 400 | 122 | 1200 | Sariatpur | 132 | 1700 | 122 | 1400
Bhasantec | 134 | 600 | 125 | 1200 | Gopalganj | 140 | 1800 | 126 | 1400
Agargaon | 135 | 500 | 126 | 1200 | Bagerhat | 133 | 2300 | 121 | 1200
Satmosjid | 135 | 600 | 125 | 1200 | Mongla | 132 | 2300 | 118 | 1200
Tongi | 135 | 1930 | 125 | 1000 | Satkhira | 136 | 2200 | 122 | 1200
Kabirpur | 130 | 100 | 124 | 1600 | Gallamari | 138 | 2200 | 125 | 1200
Basundhara | 132 | 1000 | 123 | 1100 | Magura | 130 | 1700 | 115 | 1830
Manikganj | 139 | 1900 | 128 | 1100 | Norail | 126 | 300 | 113 | 1930
Joydevpur | 137 | 2000 | 126 | 1400 | Chuadanga | 123 | 1700 | 109 | 1930
New Tongi | 133 | 1900 | 124 | 1300 | Barisal(N) | 137 | 1800 | 130 | 300
Kodda | 137 | 1900 | 122 | 1400 | Barisal (S) | 137 | 1800 | 126 | 1500
Dhamrai | 129 | 400 | 124 | 1800 | Patuakhali | 135 | 100 | 126 | 1400
Valuka | 124 | 500 | 117 | 800 | Bhandaria | 135 | 2200 | 125 | 300
Tangail | 130 | 400 | 121 | 1800 | Ishurdi | 138 | 1700 | 134 | 100
Mymensing | 126 | 1000 | 120 | 1800 | Ruppur Paromanobik | 138 | 1700 | 135 | 1300
Kishorganj | 128 | 700 | 121 | 2000 | Natore | 134 | 1700 | 129 | 1500
Netrokona | 125 | 600 | 117 | 1800 | Bogra | 136 | 1700 | 131 | 1900
Jamalpur | 138 | 2300 | 118 | 700 | Noagaon | 130 | 500 | 125 | 1900
Sherpur | 136 | 1830 | 119 | 800 | Rajshahi | 134 | 1700 | 125 | 700
Srimongal | 135 | 400 | 133 | 1930 | Rajshahi New | 132 | 1700 | 124 | 800
Shahjibazar | 134 | 1300 | 131 | 1800 | C.Nawabganj | 129 | 1830 | 120 | 1200
Fenchuganj | 133 | 100 | 132 | 400 | Amnura | 133 | 1800 | 121 | 500
Khulawara | 133 | 400 | 130 | 1830 | Pabna | 134 | 500 | 131 | 1400
Sylhet | 135 | 1600 | 131 | 1100 | Shahjadpur | 140 | 1700 | 135 | 1100
Chatak | 133 | 500 | 129 | 1800 | Serajganj | 135 | 300 | 130 | 1200
Sunamganj | 132 | 800 | 128 | 1800 | Niyamatpur | 129 | 600 | 118 | 1930
Biani Bazar | 131 | 300 | 127 | 1800 | Joypurhat | 133 | 1700 | 122 | 2000
Comilla(s) | 126 | 500 | 119 | 1800 | Sherpur(Bogura) | 136 | 1700 | 130 | 1400
Comilla(n) | 132 | 700 | 129 | 1500 | Mohastangor | 131 | 1700 | 126 | 2000
Chandpur | 128 | 700 | 125 | 1400 | Rangpur | 125 | 300 | 110 | 1830
Feni | 125 | 900 | 121 | 1500 | Lalmonirhat | 120 | 400 | 110 | 1800
Chowmuhani | 124 | 800 | 115 | 1600 | Saidpur | 123 | 600 | 111 | 1800
Ashuganj | 135 | 600 | 132 | 2100 | Purbasadipur | 120 | 1700 | 104 | 1800
Daudkandi | 127 | 700 | 122 | 1100 | Thakurgaon | 118 | 500 | 105 | 1800
B.Baria | 131 | 700 | 127 | 2000 | Palashbari | 128 | 1800 | 121 | 700
Ramganj | 122 | 700 | 118 | 1800 | Barapukuria | 126 | 400 | 117 | 1800
Madanhat | 132 | 2000 | 128 | 1100 | Panchagar | 116 | 400 | 96 | 1800
Hathazari | 130 | 300 | 126 | 1100 | Joldhaka | 121 | 500 | 109 | 1800
Khulshi | 128 | 1830 | 123 | 700 | Kurigram | 123 | 300 | 110 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 200 | 7194 | 3419 | 10613 |  |  |  | QF-LDC-12
0:30 | 200 | 6810.5 | 3239.5 | 10050 | Date: | 2019-10-19
1:00 | 200 | 6427 | 3060 | 9487
1:30 | 206 | 6271 | 2998 | 9269
2:00 | 212 | 6115 | 2936 | 9051
2:30 | 216 | 6032 | 2889 | 8921 | [5 empty] | Gen. at Eve. Peak | 11791 | 11791 MW (19:30 )
3:00 | 220 | 5949 | 2842 | 8791 | [6 empty] | 19:30
3:30 | 225 | 5858 | 2828 | 8686 | [5 empty] | Gen. at Day Peak | 8721 | 8721 MW (12:00 )
4:00 | 230 | 5767 | 2814 | 8581 | [6 empty] | 12:00
4:30 | 253 | 5708.5 | 2768.5 | 8477 | [5 empty] | Highest Generation | 11791
5:00 | 276 | 5650 | 2723 | 8373 | [6 empty] | 19:30
5:30 | 300 | 5512.5285 | 2636.5 | 8149.0285
6:00 | 324 | 5375.057 | 2550 | 7925.057
6:30 | 332 | 5207.6285 | 2576.05 | 7783.6785
7:00 | 340 | 5040.2 | 2602.1 | 7642.3
7:30 | 365 | 5029.3 | 2637.85 | 7667.15
8:00 | 390 | 5018.4 | 2673.6 | 7692
8:30 | 460 | 5086.99 | 2697.6 | 7784.59
9:00 | 530 | 5155.58 | 2721.6 | 7877.18
9:30 | 555 | 5216.84 | 2741.6 | 7958.44
10:00 | 580 | 5278.1 | 2761.6 | 8039.7
10:30 | 570 | 5413.05 | 2789 | 8202.05
11:00 | 560 | 5548 | 2816.4 | 8364.4
11:30 | 520 | 5702.45 | 2843.25 | 8545.7
12:00 | 480 | 5856.9 | 2870.1 | 8727
12:30 | 425 | 6015.275 | 2866.85 | 8882.125
13:00 | 370 | 6173.65 | 2863.6 | 9037.25
13:30 | 385 | 6122.92 | 2882.4 | 9005.32
14:00 | 400 | 6072.19 | 2901.2 | 8973.39
14:30 | 370 | 6258.595 | 2901.6 | 9160.195
15:00 | 340 | 6445 | 2902 | 9347
15:30 | 405 | 6405.895 | 2920.85 | 9326.745
16:00 | 470 | 6366.79 | 2939.7 | 9306.49
16:30 | 427 | 6326.458 | 2889.95 | 9216.408
17:00 | 384 | 6286.126 | 2840.2 | 9126.326
17:30 | 269 | 6844.563 | 3277.6 | 10122.163
18:00 | 154 | 7403 | 3715 | 11118
18:30 | 84 | 7698.5 | 3714 | 11412.5
19:00 | 14 | 7994 | 3713 | 11707
19:30 | 34 | 8077 | 3714 | 11791
20:00 | 34 | 8002 | 3695 | 11697 |  |  |  | Executive Engineer
20:30 | 57 | 7954 | 3706.5 | 11660.5 |  |  |  | Network Operation Division
21:00 | 80 | 7906 | 3718 | 11624
21:30 | 125 | 7770.5 | 3704.5 | 11475
22:00 | 170 | 7635 | 3691 | 11326 |  |  |  |  | Page 6 of 7
22:30 | 192 | 7486.5 | 3605.5 | 11092
23:00 | 214 | 7338 | 3520 | 10858
23:30 | 207 | 7266 | 3469.5 | 10735.5
24:00 | 200 | 7194 | 3419 | 10613
11791 MW (19:30 )
8721 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-19 |  | Energy | 227918652
[10 empty] | 2019-10-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4345 | 927 | 2171 | 2502 | 280 | 87 | 135 | 0 | 166
0:30 | 4396 | 926 | 2162.5 | 1972.5 | 280 | 88.5 | 67.5 | 0 | 157 | Date: | 2019-10-19
1:00 | 4447 | 925 | 2154 | 1443 | 280 | 90 | 0 | 0 | 148
1:30 | 4449 | 926 | 2147 | 1231 | 280 | 90 | 0 | 0 | 146 | [7 empty] | Total Energy | 227.9187 | Total Energy Gen 227.919 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 227.919 MKWHr
2:00 | 4451 | 927 | 2140 | 1019 | 280 | 90 | 0 | 0 | 144 | [7 empty] | Energy not Served | 0
2:30 | 4423 | 926.5 | 2142.5 | 917 | 280 | 90 | 0 | 0 | 142 | [7 empty] | Energy Requirement | 227.9187
3:00 | 4395 | 926 | 2145 | 815 | 280 | 90 | 0 | 0 | 140
3:30 | 4396 | 926 | 2104 | 752 | 280 | 90 | 0 | 0 | 138 | [6 empty] | Shortage
4:00 | 4397 | 926 | 2063 | 689 | 280 | 90 | 0 | 0 | 136
4:30 | 4382 | 926 | 2046 | 625 | 280 | 90 | 0 | 0 | 128
5:00 | 4367 | 926 | 2029 | 561 | 280 | 90 | 0 | 0 | 120
5:30 | 4319 | 926.5 | 1909.5 | 505.5 | 280.5 | 90 | 0 | 0 | 118
6:00 | 4271 | 927 | 1790 | 450 | 281 | 90 | 0 | 0 | 116
6:30 | 4226.5 | 926.5 | 1731 | 412.5 | 280.5 | 90 | 0 | 0 | 113 |  |  |  |  | Coal
7:00 | 4182 | 926 | 1672 | 375 | 280 | 90 | 0 | 0 | 110
7:30 | 4176 | 926 | 1690 | 381.5 | 279.5 | 90 | 0 | 0 | 112 |  |  |  | Oil |  |  |  | ,
8:00 | 4170 | 926 | 1708 | 388 | 279 | 90 | 0 | 0 | 114
8:30 | 4206.5 | 926 | 1702 | 441 | 279.5 | 90 | 0 | 0 | 119
9:00 | 4243 | 926 | 1696 | 494 | 280 | 90 | 0 | 0 | 124
9:30 | 4240 | 926 | 1715 | 553 | 280 | 90 | 0 | 0 | 128
10:00 | 4237 | 926 | 1734 | 612 | 280 | 90 | 0 | 0 | 132
10:30 | 4284 | 927 | 1809 | 658.5 | 280 | 90 | 0 | 0 | 133
11:00 | 4331 | 928 | 1884 | 705 | 280 | 90 | 0 | 0 | 134
11:30 | 4378 | 928 | 1929.5 | 788.5 | 279.5 | 90 | 0 | 0 | 137
12:00 | 4425 | 928 | 1975 | 872 | 279 | 90 | 0 | 0 | 140
12:30 | 4415.5 | 928 | 2079 | 928.5 | 279.5 | 87 | 0 | 0 | 142
13:00 | 4406 | 928 | 2183 | 985 | 280 | 84 | 0 | 0 | 144
13:30 | 4406 | 928 | 2183 | 985 | 280 | 84 | 0 | 0 | 144
14:00 | 4406 | 928 | 2183 | 985 | 280 | 84 | 0 | 0 | 144
14:30 | 4494.5 | 928 | 2179.5 | 1054.5 | 280 | 84 | 0 | 0 | 148
15:00 | 4583 | 928 | 2176 | 1124 | 280 | 84 | 0 | 0 | 152
15:30 | 4522.5 | 928 | 2140.5 | 1203.5 | 280 | 83 | 5 | 0 | 149
16:00 | 4462 | 928 | 2105 | 1283 | 280 | 82 | 10 | 0 | 146
16:30 | 4331 | 927.5 | 2045 | 1341.5 | 280 | 81 | 59.5 | 0 | 145
17:00 | 4200 | 927 | 1985 | 1400 | 280 | 80 | 109 | 0 | 144
17:30 | 4268 | 927 | 2007.5 | 2089.5 | 280 | 80 | 306.5 | 0 | 163
18:00 | 4336 | 927 | 2030 | 2779 | 280 | 80 | 504 | 0 | 182
18:30 | 4303 | 927 | 2023.5 | 3093 | 280 | 81 | 523 | 0 | 182
19:00 | 4270 | 927 | 2017 | 3407 | 280 | 82 | 542 | 0 | 182
19:30 | 4317 | 927 | 2043 | 3426 | 280 | 82 | 536 | 0 | 180
20:00 | 4214 | 927 | 2031 | 3447 | 280 | 82 | 536 | 0 | 180
20:30 | 4261 | 927.5 | 2082.5 | 3358.5 | 280 | 83.5 | 489.5 | 0 | 178
21:00 | 4308 | 928 | 2134 | 3270 | 280 | 85 | 443 | 0 | 176
21:30 | 4310.5 | 927.5 | 2133 | 3136.5 | 280 | 84.5 | 428 | 0 | 175
22:00 | 4313 | 927 | 2132 | 3003 | 280 | 84 | 413 | 0 | 174
22:30 | 4356.5 | 927.5 | 2134 | 2845.5 | 280 | 85.5 | 291 | 0 | 172
23:00 | 4400 | 928 | 2136 | 2688 | 280 | 87 | 169 | 0 | 170
23:30 | 4372.5 | 927.5 | 2153.5 | 2595 | 280 | 87 | 152 | 0 | 168 | Max Temp. in Dhaka |  | 35° C
24:00 | 4345 | 927 | 2171 | 2502 | 280 | 87 | 135 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 227.919 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 227.919 MKWHr
Note on W13: Author:

## Generation
2019-10-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 84 | 84 | 84 | 82 | 80 | 80 |  | 82 | 82 | 82 | 85 | 84 | 87 | 87 | 1401627
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | [12 empty] | 592000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 90 | 35 | 0 |  |  |  | 2400000
5 | Raozan 25 MW PP | [16 empty] | 2 | 23 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 176020
| Teknaf 20MW PP (Solartech) | [6 empty] | 5.1 | 11.1 | 15.48 | 18.6 | 2 | 3.9 | 18.05 | 17 | 13 | 6 | 1 | [9 empty] | 138240
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 203 | 203 | 205 | 212 | 211 | 212 | 218 | 205 | 218 | 212 | 205 | 169 | 207 |  | 203 | 215 | 206 | 204 | 204 | 209 | 204 | 4872048
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 133 | 134 | 135 | 134 | 134 | 134 | 94 | 94 | 94 | 95 | 94 | 95 | 134 | 116 | 134 | 133 | 104 | 134 |  | 104 | 104 | 104 | 134 | 134 | 134 | 134 | 2858958
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 0 | [15 empty] | 3 | 68 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 548092
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [16 empty] | 9 | 8 |  | 25 | 25 | 25 | 0 | 0 |  |  | 54288
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 9 | 111 |  | 200 | 230 | 230 | 230 | 95 | 0 | 0 | 943418
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 8 | 8 | 8 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1154181
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 756000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 201 | 200 | 200 | 4631000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 350 | 370 | 370 | 370 | 370 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 8566782
26
28 | Ashuganj TPP Unit- 3 | 125 | 125 | 125 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2787852
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 0 | 0 | 0 | 0 | 0 | 0
32 | Ashuganj 50 MW PP | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 17 | 17 | 17 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 535896
33 | Ashuganj 225 MW CCPP | 179 | 185 | 181 | 188 | 184 | 179 | 190 | 183 | 195 | 200 | 213 | 200 | 183 | 201 | 189 | 185 | 158 | 190 |  | 187 | 197 | 192 | 189 | 179 | 194 | 180 | 4580000
34 | Ashuganj 450 MW CCPP(South) | 310 | 310 | 310 | 315 | 315 | 310 | 275 | 265 | 285 | 330 | 330 | 350 | 320 | 320 | 335 | 315 | 270 | 305 |  | 275 | 295 | 290 | 305 | 315 | 325 | 315 | 7539500
| Ashuganj 450 MW CCPP(North) | 340 | 340 | 340 | 340 | 340 | 340 | 280 | 270 | 290 | 295 | 355 | 360 | 340 | 305 | 355 | 340 | 300 | 300 |  | 295 | 295 | 285 | 335 | 340 | 355 | 340 | 8130000
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 53 | 52 | 53 | 52 | 51 | 51 | 51 | 49 | 49 | 49 | 49 |  | 50 | 50 | 48 | 49 | 49 | 49 | 49 | 1222560
36 | Chandpur 150 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 125 | 126 | 125 | 127 | 126 | 127 | 127 | 126 |  | 126 | 127 | 126 | 126 | 126 | 126 | 126 | 3148680
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 346 | 346 | 346 | 351 | 345 | 346 | 348 | 348 | 363 | 360 | 369 | 379 | 364 | 372 | 383 | 352 | 347 | 322 |  | 348 | 360 | 363 | 361 | 351 | 351 | 359 | 8646660
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 360 | 360 | 360 | 360 | 330 | 330 | 330 | 330 | 330 | 380 | 380 | 450 | 400 | 390 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 8645000
41 | Haripur 360MW CCPP(HPL) | 322 | 323 | 322 | 322 | 321 | 322 | 282 | 282 | 280 | 280 | 349 | 348 | 348 | 300 | 352 | 352 | 352 | 348 |  | 350 | 350 | 351 | 351 | 353 | 353 | 352 | 7842000
42 | RPCL 210MW CCPP | 158 | 157 | 164 | 205 | 207 | 207 | 207 | 191 | 187 | 171 | 171 | 154 | 154 | 139 | 137 | 139 | 143 | 138 |  | 132 | 131 | 129 | 130 | 132 | 130 | 137 | 3771400
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 60 | 59 | 60 | 60 | 59 | 60 |  | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 1428000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440800
46 | Shajibazar 330 MW CCPP | 155 | 155 | 154 | 155 | 154 | 155 | 154 | 154 | 156 | 158 | 156 | 158 | 153 | 161 | 154 | 155 | 152 | 155 |  | 155 | 157 | 155 | 154 | 154 | 157 | 154 | 3536000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 66 | 66 | 67 | 67 | 68 | 64 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 63 | 64 | 63 |  | 65 | 65 | 65 | 65 | 65 | 65 | 67 | 1553472
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1351680
49 | Shahjibazar 50MW PP (EPL) | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 790920
50 | Sylhet 150 MW CCPP | 110 | 111 | 81 | 70 | 72 | 71 | 78 | 82 | 81 | 83 | 83 | 83 | 70 | 85 | 119 | 110 | 76 | 118 |  | 75 | 81 | 78 | 117 | 109 | 121 | 110 | 2262610
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 439000
52 | Sylhet 50MW PP (EPL) | 43 | 43 | 43 | 43 | 41 | 12 | 15 | 20 | 20 | 20 | 15 | 39 | 42 | 41 | 41 | 44 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 857700
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 |  |  |  | 7 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 195300
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252960
55 | Fenchugonj 51 MW PP (Barakatullah) | 42 | 42 | 42 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 47 | 47 | 41 | 42 | 42 | 43 |  | 40 | 40 | 40 | 41 | 41 | 41 | 35 | 705000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 0 | [5 empty] | 16 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 424296
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 290 | 300 | 305 | 300 | 300 | 295 | 310 | 315 | 310 | 320 | 315 | 310 | 300 | 320 | 305 | 285 | 265 |  | 300 | 318 | 310 | 310 | 315 | 300 | 310 | 7458750
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 379159
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 451248
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 7 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 461052
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 483012
63 | Impoprt (Tripura) | 148 | 144 | 140 | 136 | 120 | 116 | 110 | 114 | 124 | 132 | 134 | 140 | 144 | 144 | 152 | 146 | 144 | 182 |  | 182 | 180 | 180 | 176 | 174 | 170 | 166 | 3586560
64 | Malancha, Ctg. EPZ (United) | 32 | 41 | 37 | 42 | 42 | 42 | 30 | 12 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 6 | 7 | 2 |  | 11 | 19 | 19 | 32 | 35 | 37 | 31 | 447840
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496980
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 600500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 |  | 12 | 20 | 20 | 20 | 20 | 20 | 21 | 470090
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | 27 | 29 | 29 | 27 | 27 | 29 | 21 |  | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 624600
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 781200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818600
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 0 | 30 | 40 | 40 | 45 | 60 | 60 | 88 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 990720
78 | Gazipur 52 MW PP | [17 empty] | 26 |  | 33 | 34 | 40 | 0 |  |  |  | 114120
79 | Kodda 150MW PP | [16 empty] | 16 | 100 |  | 149 | 149 | 149 | 149 | 149 | 84 | 50 | 854400
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 48 | 40 | 40 | 8 | 10 | 40 | 91 | 95 | 91 | 90 | 95 | 95 | 91 | 91 | 90 |  | 95 | 91 | 91 | 95 | 95 | 95 | 95 | 1913280
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 3 | 25 |  | 52 | 52 | 52 | 52 | 52 | 47 | 0 | 302160
| Gazipur 100 MW PP | [16 empty] | 20 | 87 |  | 87 | 87 | 87 | 87 | 50 | 50 | 50 | 494604
| Kaptai 7 MW Solar PP | [5 empty] | 0.057 | 1.1 | 2.3 | 3.5 | 4.3 | 4.8 | 4.8 | 4.5 | 3.69 | 3 | 2.79 | 0.126 | 0 | [8 empty] | 32520
| Jodiac Power | [26 empty] | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | 64 | 48 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 47 | 65 | 80 | 80 | 80 | 80 | 80 | 64 |  | 64 | 64 | 80 | 80 | 80 | 80 | 81 | 1484856
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 5 | 12 |  | 62 | 50 | 50 | 0 |  |  |  | 157312
86 | Meghnaghat CCPP(Summit) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 240 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 220 | 220 | 220 | 6048582
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 28 |  | 100 | 100 | 100 | 100 | 65 | 10 |  | 428160
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 0 | [9 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 70 |  | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 749880
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 10 | 10 | 10 | 10 | 27 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 980496
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 28 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 578112
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 3 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 80 |  | 101 | 101 | 101 | 7 | 0 |  |  | 398880
95 | Patenga 50MW PP (Baraka) | 5 | 0 | [6 empty] | 1 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 39 |  | 50 | 50 | 50 | 50 | 50 | 31 | 24 | 454080
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 97 | 50 | 50 | 24 | 25 | 25 | 25 | 25 | 49 | 94 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 0 |  | 1665600
97 | Katpotti 52 MW PP (Sinha) | [16 empty] | 0 | 17 |  | 42 | 46 | 47 | 47 | 6 |  |  | 174672
98 | Bosila 108MW PP(CLC) | [16 empty] | 19 | 48 |  | 54 | 54 | 54 | 54 | 62 | 62 | 63 | 379200
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 7 | 30 | 30 | 30 | 30 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 665761
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 390045
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 100 | 163 | 163 | 163 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 3145647
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 1 | 1.6 | 2.2 | 2.2 | 2.2 | 2.1 | 1.5 | 1 | 0 | [10 empty] | 13550
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 859680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 0 | 57 |  | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 964800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 41 | 0 | [5 empty] | 0 | 30 | 30 | 30 | 41 | 50 | 50 | 60 | 100 | 106 | 144 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 1609920
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 60 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1404480
116 | Chandpur 200MW (Desh energy) | 200 | 120 | 50 | 50 | 50 | 17 | 0 | 0 | [6 empty] | 11 | 36 | 34 | 104 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 2019840
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 96 | 38 | 8 | 8 | 0 | [7 empty] | 6 | 16 | 40 | 40 | 67 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1240800
| Anwara 300 MW PP (United) | 33 | 33 | 33 | 32 | 33 | 16 | 16 | 16 | 16 | 16 | 16 | 49 | 48 | 52 | 85 | 88 | 88 | 160 |  | 160 | 160 | 160 | 162 | 162 | 162 | 162 | 1758873
120 | Eastern Zone Total | 6427 | 6115 | 5949 | 5767 | 5650 | 5375.057 | 5040.2 | 5018.4 | 5155.58 | 5278.1 | 5548 | 5856.9 | 6173.65 | 6072.19 | 6445 | 6366.79 | 6286.126 | 7403 |  | 7994 | 8077 | 8002 | 7906 | 7635 | 7338 | 7194 | 153801401
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 9 | 93 |  | 115 | 115 | 115 | 115 | 115 | 100 | 66 | 685440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 6 | 39 |  | 42 | 37 | 37 | 37 | 37 | 0 |  | 185280
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 17 | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | 105 | 103 | 105 | 105 | 105 | 105 | 1002720
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 48 | 16 | 16 | 0 | [10 empty] | 64 | 64 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1111680
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 97 | 97 | 97 | 96 | 63 | 63 | 63 | 62 | 60 | 61 | 88 | 95 | 93 | 92 | 95 | 76 | 97 |  | 97 | 96 | 96 | 96 | 97 | 97 | 97 | 2075864
| Bhola 225 MW CCPP | 173 | 174 | 173 | 174 | 174 | 174 | 173 | 173 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 163 | 174 |  | 173 | 173 | 173 | 173 | 174 | 174 | 174 | 4213315
140 | Bhola 33 MW PP (Venture) | 31 | 28 | 27 | 27 | 26 | 18 | 17 | 17 | 19 | 19 | 20 | 21 | 20 | 22 | 20 | 20 | 21 | 30 |  | 34 | 34 | 34 | 35 | 35 | 34 | 32 | 601736
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 270375
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 10 | 18 | 40 |  | 20 | 20 | 20 | 20 | 20 | 0 |  | 133888
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 34 | 17 | 0 | [14 empty] | 70 |  | 102 | 102 | 102 | 101 | 101 | 102 | 67 | 664416
146 | Bheramara HVDC | 925 | 927 | 926 | 926 | 926 | 927 | 926 | 926 | 926 | 926 | 928 | 928 | 928 | 928 | 928 | 928 | 927 | 927 |  | 927 | 927 | 927 | 928 | 927 | 928 | 927 | 22240727
147 | Bheramara 360 MW CCPP | 345 | 350 | 345 | 355 | 340 | 340 | 325 | 335 | 350 | 355 | 380 | 390 | 350 | 395 | 380 | 350 | 345 | 365 |  | 350 | 375 | 365 | 360 | 340 | 370 | 345 | 8736192
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 281 | 280 | 279 | 280 | 280 | 280 | 279 | 280 | 282 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6760600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 260168
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 11 | 19 | 18 | 21 | 25 | 92 | 183 | 205 | 201 | 198 | 200 | 199 | 201 | 176 | 194 | 190 | 182 | 163 |  | 183 | 171 | 171 | 174 | 189 | 188 | 195 | 3863627
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 194 | 172 | 150 | 138 | 128 | 0 | [20 empty] | 841300
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 197 | 197 | 200 | 200 | 199 | 183 | 180 | 170 | 170 | 173 | 180 | 184 | 210 | 210 | 205 | 197 | 165 |  | 181 | 175 | 171 | 175 | 195 | 195 | 202 | 4782700
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 407 | 431 | 432 | 431 | 432 | 401 | 396 | 428 | 423 | 420 | 418 | 410 | 416 | 408 | 410 | 414 | 328 | 404 |  | 335 | 335 | 332 | 418 | 405 | 423 | 430 | 9783781
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 39 |  | 46 | 45 | 45 | 30 | 0 | 0 | 0 | 149651
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505440
163 | Bogura 20 MW PP (Energyprima) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 13 | 10 | 0 | 5 | 5 |  | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 312120
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249102
165 | Amnura 50 MW PP(Sinha) | 12 | 0 | [7 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 20 | 50 |  | 50 | 50 | 50 | 50 | 50 | 25 | 0 | 401230
166 | Katakhali 50 MW PP (Northern) | 50 | 50 | 50 | 32 | 32 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 819865
167 | Katakhali 50 MW Peaking PP | [17 empty] | 28 |  | 0 | [6 empty] | 36468
168 | Santahar 50 MW Peaking PP | [16 empty] | 10 | 29 |  | 0 | [6 empty] | 42245
169 | Natore 52 MW PP (Rajlanka) | 4 | 0 | [15 empty] | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 386880
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 20 | 86 |  | 93 | 93 | 93 | 40 | 40 | 0 | 0 | 357580
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence) | [16 empty] | 3 | 70 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 644160
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 0 | 6 | 10 | 11 | 14 | 15 | 18 | 0 | [8 empty] | 76400
173 | Rangpur 20 MW GTPP | [16 empty] | 0 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 72000
175 | Saidpur 20 MW GTPP | [16 empty] | 17 | 0 |  | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 71000
176 | Rangpur 113 MW PP (Confidence) | 110 | 61 | 46 | 32 | 0 |  |  | 10 | 39 | 70 | 96 | 105 | 104 | 100 | 102 | 107 | 50 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1745280
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1.1 | 2.6 | 3.6 | 3.6 | 3.4 | 7.1 | 2.6 | 4.2 | 3 | 1.7 | 0.2 | 0 | [8 empty] | 34021
178
178