## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-19 | Saturday
|  | Date (day): | 2019-10-19 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13244 | MW |  |  | (b) At Evening Peak Hour : |  | 15075 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-18 | 2019-10-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 370 | 380 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  | 78 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 |  | 108 | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 386 | 379 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 350 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 5 | 230 | 305 | 305 | 0
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 98 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 50 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  |  | Under shut down
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 47 | 47
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 36 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 36 | 70 | 72 | 72 |  |  | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 53 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 50 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 34 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1991 | 2767 | 3948 | 4348 | 315 | 779
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 105 | 105 | 105 | 75 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 16 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 92 | 90 | 168 | 168 | 62 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 219 | 0 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 111 | 134 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 15 | 85 | 85 | 85
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 72 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 28 | 30 | 15 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 97 | 50 | 97 |  | 11 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 0 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 113 | 113
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 930 | 918 | 1616.4 | 1774 | 197 | 109
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 125 | 120 | 120 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 196 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 360 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 330 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 27 | 27 | 27 | 27 |  | 18 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 50 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 55 | 55 | 140 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 140 | 141
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 64 | 200 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 168 | 128 | 171
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21 |  | 4 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1548 | 1770 | 1985 | 2279 | 404 | 47
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 138 | 155 | 190 | 190 | 12 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 56 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 224 | 485 | 623.6 | 622 | 12 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 60 | 62 | 62
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 155 | 230 | 240 |  | 90 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 42 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 49 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 68 | 68 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 75 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 122 | 81 | 110 | 130
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 39 | 42 | 44 | 44 |  | 6 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 320 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1191 | 1214 | 1364 | 1394 | 0 | 506
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 0 | 922 | 395 | 938
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 0 | 75
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 375 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 34 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 532 | 1664 | 1445 | 2158 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 29 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 173 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 304 | 409 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 18 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 50 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 225 | 225 | 210 |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 209 | 206 | 0 | 0 |  |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 209 | 207 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 412 | 422 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 17 | 20 | 20
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 44 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 34 | 25 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 989 | 1097 | 1483 | 1628 | 210 | 171
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 290 | 270 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 16
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 15
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 78 | 65 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 374 | 367 | 401 | 424 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 8083 | 10691 | 13244 | 15075 | 1138 | 1782
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7682.2901 | 10161 | 12587.4365 | 14327.6658
A. |  | 2019-10-18 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10691 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7265.4 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10691 | MW
3 | Day peak Generation : |  |  | 8083 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10161 | MW
4 | Evening peak Generation : |  |  | 10691 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 208.4813 | MKWHr | By Solar | 0.22438 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 151.4425 | MKWHr |  | By Oil: | 30.6016 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.7928 | MKWHr |  | By Hydro: | 2.5794 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1138 | MW | Dhaka | 3603 | 3603 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1782 | MW | Chittagong | 1031 | 1031 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2920 | MW | Khulna | 1306 | 1306 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1269.63 | MMCFD |  |  | Rajshahi | 1050 | 1050 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 143786869.176 | ii) Oil : | Taka | 294295320.27 | Comilla | 1041 | 1041 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 27782552 | Total | Taka | 465864741.446 | Mymensingh | 804 | 804 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.053 | MKWHr. | Sylhet | 467 | 467 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -46 | MW (E to W) at | 21:00 | hrs | Barisal | 318 | 318 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -46 | MW at | 21:00 | hrs | Rangpur | 541 | 541 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.7° C |  |  | Total | 10161 | 10161 |  | 0
B. |  | 2019-10-19 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15075 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 3575 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 224.2573 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7642.3 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.5833 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2573 | MKWHr. | iii) Maximum HVDC Flow : |  | 928 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.1 |  | (b) Today: | 103.02 |  | (c) Rule Curve: |  | 2.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-10-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 344 | 356 |  | 0 | 450 | 0 | 0 | 97 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 86 | 50 | 100 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 14 | 90 | 97 | 0 | 19 | 22 | 100 | 0 | 0 | 340 | 285 | 220 | 55 | 140 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 150 | 124 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 154 | 64 | 75 | 40 | 110 | 17 | 43 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 146 | 0 | 100 | 180 | 0 | 0 | 115 | 0 | 0 | 0 | 162 | 0 | 0 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 52 | 0 | 22 | 16 | 11 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 187 | 0 | 97 | 0 | 186 | 0 | 389 | 70 | 0 | 0 | 20 | 112 | 0 | 0 |  | 6947 | 3072 | 10019 | 4592 | 926 | 2235 | 1685 | 281 | 136 | 14 | 150 | 0 | 0 | 103.15
2:00 | 35 | 0 | 201 | 0 | 350 | 0 | 0 | 348 | 353 |  | 0 | 450 | 0 | 0 | 48 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 87 | 50 | 100 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 14 | 20 | 97 | 0 | 19 | 30 | 100 | 0 | 0 | 350 | 295 | 188 | 55 | 140 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 148 | 123 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 154 | 64 | 75 | 40 | 110 | 17 | 42 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 100 | 160 | 0 | 0 | 115 | 0 | 0 | 0 | 162 | 0 | 0 |  | 926 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 27 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 16 | 11 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 186 | 0 | 96 | 0 | 190 | 0 | 428 | 17 | 0 | 0 | 0 | 43 | 0 | 0 |  | 6597 | 2885 | 9482 | 4601 | 926 | 2278 | 1100 | 278 | 137 | 14 | 148 | 0 | 0 | 103.14
3:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 354 |  | 0 | 450 | 0 | 0 | 48 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 87 | 50 | 100 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 14 | 10 | 97 | 0 | 19 | 31 | 100 | 0 | 0 | 340 | 285 | 178 | 55 | 138 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 144 | 123 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 153 | 64 | 75 | 40 | 109 | 17 | 42 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 60 | 125 | 0 | 0 | 80 | 0 | 0 | 0 | 162 | 0 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 193 | 0 | 95 | 0 | 189 | 0 | 418 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 6381 | 2812 | 9193 | 4552 | 925 | 2278 | 873 | 270 | 137 | 14 | 144 | 0 | 0 | 103.13
4:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 355 |  | 0 | 450 | 0 | 0 | 48 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 50 | 100 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 14 | 10 | 97 | 0 | 19 | 32 | 100 | 0 | 0 | 340 | 280 | 178 | 55 | 138 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 140 | 124 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 154 | 64 | 75 | 40 | 110 | 17 | 42 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 60 | 125 | 0 | 0 | 45 | 0 | 0 | 0 | 108 | 0 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 187 | 0 | 96 | 0 | 186 | 0 | 396 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 6267 | 2772 | 9039 | 4533 | 925 | 2244 | 789 | 260 | 134 | 14 | 140 | 0 | 0 | 103.12
5:00 | 35 | 0 | 200 | 0 | 350 | 0 | 0 | 345 | 354 |  | 0 | 450 | 0 | 0 | 48 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 84 | 50 | 100 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 14 | 10 | 50 | 0 | 19 | 33 | 100 | 0 | 0 | 340 | 285 | 186 | 55 | 140 | 27 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 136 | 123 | 74 | 20 | 0 | 60 | 60 | 11 | 49 | 163 | 153 | 67 | 75 | 40 | 70 | 17 | 42 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 10 | 17 | 0 | 0 | 8 | 0 | 0 | 0 | 52 | 0 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 187 | 0 | 96 | 0 | 188 | 0 | 430 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 5901 | 2768 | 8669 | 4519 | 925 | 2250 | 421 | 270 | 134 | 14 | 136 | 0 | 0 | 103.11
6:00 | 35 | 0 | 165 | 0 | 350 | 0 | 0 | 345 | 302 |  | 0 | 420 | 0 | 0 | 48 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 83 | 50 | 100 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 14 | 10 | 50 | 0 | 19 | 35 | 100 | 0 | 0 | 320 | 285 | 178 | 55 | 138 | 27 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 130 | 146 | 72 | 20 | 0 | 30 | 60 | 11 | 10 | 100 | 156 | 69 | 75 | 40 | 70 | 17 | 42 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0.3 | 10 | 17 | 0 | 0 | 8 | 0 | 0 | 0.07 | 52 | 0 | 0 |  | 924 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 24 | 4 | 16 | 0 | 22 | 16 | 8 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 186 | 0 | 50 | 0 | 184 | 0 | 315 | 0 | 0 | 0 | 0 | 35 | 0 | 0 |  | 5548.37 | 2644 | 8192.37 | 4387 | 924 | 1872 | 440 | 270 | 133 | 36 | 130 | 0.37 | 0 | 103.1
7:00 | 35 | 0 | 170 | 0 | 300 | 0 | 0 | 315 | 272 |  | 0 | 340 | 0 | 0 | 30 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 80 | 50 | 100 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 14 | 10 | 48 | 0 | 19 | 41 | 100 | 0 | 0 | 270 | 285 | 178 | 55 | 138 | 27 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 100 | 145 | 40 | 20 | 0.3 | 30 | 60 | 11 | 10 | 100 | 154 | 50 | 40 | 10 | 71 | 17 | 18 | 10 | 260 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4.6 | 10 | 17 | 0 | 0 | 8 | 0 | 0 | 0.8 | 52 | 0 | 0 |  | 924 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 30 | 18 | 16 | 3 | 16 | 0 | 22 | 16 | 8 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 155 | 0 | 43 | 0 | 155 | 0 | 315 | 0 | 0 | 0 | 0 | 35 | 0 | 0.5 |  | 5090.7 | 2545.5 | 7636.2 | 4136 | 924 | 1647 | 366 | 280 | 130 | 47 | 100 | 6.2 | 0 | 0
8:00 | 35 | 0 | 171 | 0 | 300 | 0 | 0 | 305 | 271 |  | 0 | 340 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 80 | 50 | 100 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 14 | 10 | 0 | 0 | 19 | 37 | 100 | 0 | 0 | 270 | 285 | 178 | 55 | 137 | 27 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 86 | 125 | 40 | 20 | 1 | 30 | 60 | 11 | 10 | 100 | 154 | 52 | 40 | 10 | 69 | 17 | 18 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11 | 10 | 17 | 0 | 0 | 8 | 0 | 0 | 1.87 | 52 | 0 | 0 |  | 924 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 30 | 18 | 16 | 0 | 16 | 0 | 22 | 16 | 8 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 153 | 0 | 81 | 0 | 155 | 0 | 304 | 46 | 0 | 0 | 0 | 48 | 0 | 0.4 |  | 4813.87 | 2615.4 | 7429.27 | 3872 | 924 | 1686 | 393 | 280 | 130 | 44 | 86 | 14.27 | 0 | 103.09
9:00 | 35 | 0 | 172 | 0 | 300 | 0 | 0 | 305 | 273 |  | 0 | 340 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 28 | 16 | 0 | 0 | 80 | 50 | 100 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 15 | 10 | 0 | 0 | 19 | 34 | 100 | 0 | 0 | 270 | 285 | 190 | 55 | 140 | 27 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 96 | 124 | 40 | 20 | 1.5 | 30 | 60 | 11 | 10 | 100 | 155 | 65 | 40 | 10 | 75 | 17 | 17 | 9 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 15 | 10 | 17 | 0 | 0 | 8 | 0 | 0 | 3.4 | 52 | 0 | 0 |  | 579 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 174 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 16 | 0 | 16 | 0 | 22 | 16 | 8 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 151 | 0 | 81 | 0 | 156 | 0 | 395 | 53 | 0 | 0 | 0 | 70 | 0 | 3.5 |  | 4817.9 | 2447.5 | 7265.4 | 3889 | 579 | 1764 | 452 | 284 | 130 | 48 | 96 | 23.4 | 0 | 103.09
10:00 | 35 | 0 | 172 | 0 | 375 | 0 | 0 | 345 | 351 |  | 0 | 340 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 28 | 33 | 0 | 0 | 82 | 50 | 100 | 120 | 0 | 226 | 0 | 104 | 0 |  | 0 | 0 | 14 | 10 | 0 | 0 | 19 | 36 | 100 | 0 | 0 | 336 | 315 | 187 | 55 | 140 | 27 | 51 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 98 | 123 | 40 | 20 | 2 | 30 | 60 | 44 | 36 | 100 | 154 | 63 | 75 | 40 | 112 | 17 | 39 | 9 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 30 | 19 | 0 | 0 | 8 | 0 | 0 | 4.46 | 52 | 0 | 0 |  | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 16 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 194 | 0 | 81 | 0 | 206 | 0 | 421 | 90 | 0 | 0 | 0 | 76 | 0 | 4.1 |  | 5386.46 | 2079.1 | 7465.56 | 4296 | 0 | 2053 | 520 | 290 | 132 | 48 | 98 | 28.56 | 0 | 103.08
11:00 | 35 | 0 | 171 | 0 | 375 | 0 | 0 | 352 | 335 |  | 0 | 380 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 15 | 0 | 33 | 0 | 0 | 84 | 50 | 100 | 120 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 15 | 10 | 0 | 0 | 19 | 36 | 100 | 0 | 0 | 350 | 330 | 195 | 55 | 141 | 27 | 48 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 110 | 124 | 40 | 20 | 2.3 | 30 | 60 | 44 | 48 | 100 | 155 | 63 | 73 | 40 | 121 | 17 | 39 | 9 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 100 | 52 | 0 | 0 | 8 | 0 | 0 | 4.89 | 52 | 0 | 0 |  | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 16 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 200 | 0 | 81 | 0 | 205 | 0 | 419 | 90 | 0 | 0 | 0 | 76 | 0 | 6 |  | 5588.19 | 2107 | 7695.19 | 4333 | 0 | 2105 | 642 | 290 | 134 | 49 | 110 | 32.19 | 0 | 103.08
12:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 386 | 347 |  | 0 | 450 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 0 | 33 | 0 | 0 | 42 | 50 | 100 | 120 | 0 | 219 | 0 | 111 | 0 |  | 0 | 0 | 15 | 50 | 0 | 0 | 19 | 28 | 100 | 0 | 0 | 360 | 345 | 202 | 55 | 140 | 27 | 47 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 120 | 138 | 56 | 20 | 2 | 30 | 60 | 47 | 48 | 130 | 160 | 63 | 73 | 40 | 122 | 17 | 39 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 100 | 64 | 0 | 0 | 8 | 0 | 0 | 4 | 52 | 0 | 0 |  | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 44 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 209 | 0 | 95 | 0 | 209 | 0 | 412 | 105 | 0 | 0 | 0 | 78 | 0 | 6 |  | 5884 | 2199 | 8083 | 4502 | 0 | 2231 | 767 | 290 | 92 | 49 | 120 | 32 | 0 | 103.08
13:00 | 35 | 0 | 198 | 0 | 380 | 0 | 0 | 396 | 348 |  | 0 | 450 | 5 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 0 | 33 | 0 | 0 | 42 | 50 | 100 | 120 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 70 | 0 | 2 | 19 | 29 | 125 | 0 | 0 | 335 | 310 | 181 | 55 | 140 | 27 | 46 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 20 | 124 | 138 | 90 | 0 | 2.2 | 60 | 60 | 47 | 48 | 163 | 153 | 63 | 74 | 40 | 103 | 17 | 42 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 19 | 100 | 168 | 0 | 0 | 26 | 0 | 0 | 4.56 | 52 | 0 | 0 |  | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 52 | 0 | 21 | 15 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 203 | 0 | 94 | 0 | 214 | 0 | 429 | 105 | 0 | 0 | 0 | 110 | 0 | 5.9 |  | 6152.76 | 2209.9 | 8362.66 | 4434 | 0 | 2276 | 1081 | 290 | 92 | 34 | 124 | 31.66 | 0 | 103.07
14:00 | 35 | 0 | 200 | 0 | 375 | 0 | 0 | 367 | 344 |  | 0 | 450 | 5 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 33 | 0 | 0 | 40 | 50 | 100 | 120 | 0 | 214 | 0 | 104 | 0 |  | 0 | 0 | 0 | 70 | 2 | 12 | 19 | 29 | 125 | 0 | 0 | 290 | 330 | 195 | 55 | 140 | 27 | 43 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 130 | 137 | 95 | 20 | 1.8 | 59 | 60 | 44 | 45 | 163 | 154 | 63 | 74 | 40 | 83 | 17 | 41 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 17.64 | 100 | 198 | 0 | 0 | 40 | 0 | 0 | 3.8 | 52 | 0 | 0 |  | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 52 | 0 | 21 | 16 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 184 | 0 | 92 | 0 | 181 | 0 | 410 | 105 | 0 | 0 | 0 | 113 | 0 | 4.6 |  | 6170.24 | 2167.6 | 8337.84 | 4339 | 0 | 2232 | 1195 | 290 | 90 | 34 | 130 | 27.84 | 0 | 103.07
15:00 | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 359 | 345 |  | 0 | 450 | 6 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 0 | 33 | 0 | 0 | 40 | 50 | 100 | 120 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 70 | 46 | 19 | 19 | 27 | 125 | 0 | 0 | 350 | 320 | 192 | 55 | 140 | 27 | 43 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 132 | 151 | 95 | 20 | 1.3 | 60 | 60 | 44 | 45 | 163 | 155 | 63 | 74 | 40 | 74 | 17 | 41 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 13.2 | 100 | 200 | 0 | 0 | 71 | 0 | 0 | 2.8 | 75 | 0 | 0 |  | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 52 | 0 | 21 | 16 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 207 | 0 | 94 | 0 | 201 | 0 | 410 | 105 | 0 | 0 | 0 | 113 | 0 | 4.1 |  | 6351.3 | 2204.1 | 8555.4 | 4434 | 0 | 2250 | 1304 | 290 | 90 | 34 | 132 | 21.4 | 0 | 103.07
16:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 347 | 348 |  | 0 | 450 | 6 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 0 | 33 | 25 | 0 | 0 | 40 | 50 | 100 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 70 | 52 | 6 | 19 | 30 | 125 | 0 | 0 | 340 | 305 | 179 | 55 | 140 | 27 | 47 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 130 | 154 | 95 | 20 | 0.6 | 60 | 60 | 44 | 45 | 163 | 156 | 65 | 74 | 40 | 69 | 17 | 40 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 6.63 | 100 | 200 | 0 | 0 | 115 | 0 | 0 | 1.8 | 105 | 0 | 0 |  | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 150 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 52 | 0 | 21 | 16 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 200 | 0 | 94 | 0 | 188 | 0 | 380 | 53 | 0 | 0 | 0 | 100 | 0 | 1.8 |  | 6356.03 | 2016.8 | 8372.83 | 4369 | 0 | 2181 | 1264 | 290 | 90 | 38 | 130 | 10.83 | 0 | 103.06
17:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 347 | 348 |  | 0 | 450 | 20 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 0 | 33 | 25 | 0 | 0 | 40 | 50 | 100 | 120 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 40 | 52 | 6 | 19 | 29 | 125 | 0 | 0 | 340 | 305 | 180 | 55 | 135 | 27 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 118 | 153 | 95 | 20 | 0.1 | 60 | 60 | 17 | 20 | 163 | 154 | 63 | 40 | 20 | 69 | 17 | 22 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 1 | 100 | 150 | 0 | 0 | 45 | 0 | 0 | 0 | 107 | 0 | 0 |  | 0 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 7 | 23 | 8 | 169 | 22 | 16 | 0 | 0 | 0 | 0 | 10 | 34 | 18 | 8 | 0 | 17 | 0 | 21 | 16 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 188 | 0 | 51 | 0 | 188 | 0 | 398 | 17 | 0 | 0 | 14 | 35 | 0 | 0.4 |  | 5950.1 | 1927.4 | 7877.5 | 4365 | 0 | 2012 | 927 | 290 | 90 | 74 | 118 | 1.5 | 0 | 103.06
18:00 | 35 | 0 | 196 | 0 | 380 | 0 | 0 | 362 | 349 |  | 0 | 450 | 40 | 1 | 83 | 3 | 0 | 0 | 0 | 0 | 10 | 0 | 32 | 0 | 24 | 0 | 0 | 30 | 55 | 35 | 19 | 25 | 22 | 33 | 33 | 4 | 0 | 40 | 50 | 100 | 120 | 1 | 205 | 0 | 134 | 0 |  | 0 | 0 | 85 | 80 | 72 | 12 | 19 | 30 | 125 | 0 | 0 | 340 | 305 | 182 | 55 | 140 | 27 | 20 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 160 | 153 | 95 | 20 | 0 | 60 | 60 | 29 | 35 | 130 | 150 | 65 | 74 | 40 | 109 | 17 | 43 | 10 | 285 | 24 | 11 | 0 | 0 | 51 | 0 | 45 | 0 | 95 | 0 | 100 | 126 | 0 | 0 | 77 | 5 | 0 | 0 | 107 | 0 | 0 |  | 177 | 0 | 350 | 0 | 63 | 0 | 0 | 0 | 38 | 50 | 32 | 173 | 28 | 110 | 0 | 0 | 0 | 50 | 35 | 83 | 50 | 50 | 44 | 44 | 27 | 22 | 17 | 11 | 0 | 0 | 290 | 16 | 16 | 0 | 0 | 196 | 0 | 96 | 5 | 199 | 0 | 404 | 90 | 0 | 14 | 60 | 44 | 0 | 0 |  | 6657 | 2884 | 9541 | 4483 | 177 | 2152 | 1713 | 290 | 90 | 476 | 160 | 0 | 0 | 103.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 200 | 0 | 360 | 0 | 0 | 346 | 355 |  | 0 | 450 | 80 | 20 | 96 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 16 | 0 | 46 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 120 | 16 | 204 | 0 | 134 | 0 |  | 0 | 0 | 85 | 72 | 96 | 47 | 19 | 30 | 125 | 0 | 0 | 340 | 305 | 179 | 55 | 140 | 27 | 48 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 164 | 158 | 95 | 20 | 0 | 60 | 60 | 42 | 48 | 100 | 155 | 65 | 74 | 40 | 106 | 17 | 43 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 134 | 0 | 100 | 200 | 0 | 0 | 115 | 34 | 0 | 0 | 107 | 0 | 0 |  | 686 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 40 | 30 | 32 | 149 | 32 | 110 | 0 | 0 | 0 | 50 | 0 | 43 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 175 | 0 | 96 | 0 | 186 | 0 | 375 | 105 | 0 | 35 | 32 | 0 | 0 | 0 |  | 7040 | 3115 | 10155 | 4378 | 686 | 2132 | 2164 | 277 | 90 | 264 | 164 | 0 | 0 | 103.05
19:30 | 35 | 0 | 200 | 0 | 360 | 0 | 0 | 362 | 350 |  | 0 | 450 | 100 | 7 | 98 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 16 | 0 | 65 | 0 | 0 | 36 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 50 | 105 | 120 | 16 | 214 | 0 | 108 | 0 |  | 0 | 0 | 85 | 72 | 97 | 50 | 19 | 30 | 125 | 0 | 0 | 320 | 305 | 197 | 55 | 140 | 27 | 48 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 168 | 155 | 95 | 22 | 0 | 60 | 60 | 42 | 48 | 100 | 160 | 65 | 75 | 40 | 83 | 17 | 43 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 134 | 0 | 100 | 200 | 0 | 0 | 115 | 34 | 0 | 0 | 107 | 0 | 0 |  | 928 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 43 | 30 | 40 | 173 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 270 | 0 | 15 | 0 | 0 | 163 | 0 | 97 | 0 | 174 | 0 | 370 | 105 | 0 | 35 | 34 | 0 | 0 | 0 |  | 7139 | 3331 | 10470 | 4409 | 928 | 2184 | 2207 | 270 | 90 | 214 | 168 | 0 | 0 | 0
20:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 367 | 350 |  | 0 | 450 | 105 | 9 | 98 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 16 | 0 | 65 | 0 | 0 | 36 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 40 | 50 | 105 | 120 | 16 | 0 | 0 | 142 | 0 |  | 0 | 0 | 85 | 72 | 97 | 50 | 0 | 30 | 125 | 0 | 0 | 355 | 345 | 200 | 55 | 140 | 27 | 48 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 166 | 155 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 100 | 165 | 65 | 75 | 40 | 83 | 17 | 43 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 135 | 0 | 100 | 200 | 0 | 0 | 115 | 34 | 0 | 0 | 0 | 0 | 0 |  | 928 | 0 | 395 | 0 | 115 | 0 | 0 | 0 | 43 | 30 | 40 | 174 | 29 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 270 | 0 | 15 | 0 | 0 | 173 | 0 | 93 | 0 | 181 | 0 | 410 | 105 | 0 | 35 | 34 | 4 | 0 | 0 |  | 6888 | 3411 | 10299 | 4351 | 928 | 2168 | 2112 | 270 | 90 | 214 | 166 | 0 | 0 | 103.05
21:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 379 | 350 |  | 0 | 450 | 230 | 7 | 98 | 40 | 0 | 0 | 0 | 0 | 50 | 0 | 16 | 0 | 70 | 0 | 0 | 36 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 40 | 50 | 105 | 120 | 16 | 0 | 0 | 134 | 0 |  | 0 | 0 | 85 | 72 | 97 | 50 | 19 | 30 | 125 | 0 | 0 | 360 | 330 | 196 | 55 | 140 | 27 | 50 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 168 | 155 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 155 | 65 | 75 | 40 | 81 | 17 | 42 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 34 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 43 | 30 | 40 | 173 | 29 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 270 | 16 | 16 | 0 | 0 | 206 | 0 | 97 | 0 | 207 | 0 | 422 | 105 | 0 | 35 | 34 | 65 | 0 | 0 |  | 7154 | 3537 | 10691 | 4387 | 922 | 2298 | 2325 | 270 | 90 | 231 | 168 | 0 | 0 | 103.05
22:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 360 | 352 |  | 0 | 450 | 230 | 7 | 98 | 55 | 0 | 0 | 0 | 0 | 50 | 0 | 16 | 0 | 70 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 40 | 50 | 105 | 120 | 16 | 81 | 0 | 134 | 0 |  | 0 | 0 | 85 | 72 | 97 | 50 | 19 | 38 | 125 | 0 | 0 | 340 | 310 | 180 | 55 | 140 | 27 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 166 | 156 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 155 | 63 | 75 | 40 | 69 | 17 | 42 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 43 | 30 | 40 | 173 | 29 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 270 | 16 | 17 | 0 | 0 | 205 | 0 | 97 | 0 | 200 | 0 | 405 | 105 | 0 | 35 | 34 | 113 | 0 | 0 |  | 7130 | 3531 | 10661 | 4343 | 922 | 2267 | 2371 | 270 | 90 | 232 | 166 | 0 | 0 | 103.04
23:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 345 | 352 |  | 0 | 420 | 230 | 0 | 98 | 15 | 0 | 0 | 0 | 0 | 30 | 0 | 16 | 0 | 70 | 0 | 0 | 53 | 17 | 17 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 43 | 50 | 105 | 120 | 16 | 80 | 0 | 134 | 0 |  | 0 | 0 | 85 | 80 | 97 | 50 | 19 | 32 | 125 | 0 | 0 | 340 | 310 | 216 | 55 | 140 | 27 | 49 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 160 | 156 | 95 | 22 | 0 | 60 | 60 | 42 | 49 | 163 | 155 | 66 | 75 | 40 | 87 | 17 | 43 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 110 | 0 | 100 | 200 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 0 | 0 |  | 923 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 43 | 8 | 40 | 174 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 270 | 17 | 17 | 0 | 0 | 197 | 0 | 98 | 0 | 186 | 0 | 409 | 105 | 0 | 35 | 34 | 113 | 0 | 0 |  | 6912 | 3467 | 10379 | 4360 | 923 | 2207 | 2180 | 270 | 93 | 186 | 160 | 0 | 0 | 103.04
24:00 | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 346 | 352 |  | 0 | 420 | 260 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 43 | 50 | 105 | 120 | 0 | 190 | 0 | 134 | 0 |  | 0 | 0 | 4 | 82 | 97 | 48 | 19 | 32 | 125 | 0 | 0 | 340 | 310 | 187 | 55 | 140 | 27 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 156 | 157 | 95 | 22 | 0 | 60 | 60 | 42 | 49 | 130 | 155 | 66 | 75 | 40 | 109 | 17 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 59 | 0 | 100 | 200 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 0 | 0 |  | 922 | 0 | 340 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 16 | 174 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 17 | 0 | 0 | 195 | 0 | 96 | 0 | 189 | 0 | 428 | 105 | 0 | 0 | 34 | 113 | 0 | 0 |  | 6709 | 3239 | 9948 | 4475 | 922 | 2230 | 1771 | 280 | 93 | 21 | 156 | 0 | 0 | 103.04
KWH | 755000 | 0 | 0 | 0 | 7222936 | 0 | 0 | 8526850 | 8062000 |  | 0 | 9900875 | 1127418 | 58560 | 1608792 | 207126 | 1501692 | 0 | 0 | 0 | 360960 | 0 | 129120 | 0 | 770880 | 0 | 0 | 344880 | 324055 | 284777 | 307476 | 600000 | 519660 | 663800 | 746400 | 0 | 0 | 1387440 | 1192000 | 2400000 | 3000000 | 100035 | 4316620 | 0 | 2947530 | 0 |  | 0 | 0 | 708531 | 1084680 | 1390080 | 356160 | 436080 | 724800 | 2708764 | 0 | 0 | 8264900 | 7439000 | 4605000 | 1338181 | 3280050 | 614016 | 1197600 | 0 | 752608 | 0 | 0 | 0 | 360180 | 132300 | 818300 | 518150 | 3257280 | 3232360 | 1963200 | 457308 | 15100 | 1227000 | 1440720 | 843600 | 1015344 | 3522575 | 3484000 | 1513152 | 1652160 | 832680 | 2287040 | 438000 | 904800 | 241200 | 7252000 | 566496 | 223152 | 0 | 0 | 26797 | 0 | 691200 | 0 | 2157120 | 137700 | 1826880 | 3155520 | 8363 | 0 | 1612800 | 0 | 0 | 33120 | 1846690 | 0 | 0 |  | 13583272 | 0 | 8661888 | 0 | 657600 | 0 | 0 | 0 | 243840 | 196992 | 532875 | 4119515 | 565501 | 1307520 | 0 | 0 | 0 | 93504 | 34102 | 801250 | 576570 | 657252 | 42280 | 783840 | 33183 | 506880 | 374976 | 245628 | 0 | 0 | 6792800 | 76000 | 105000 | 0 | 0 | 4725873 | 0 | 2099274 | 21120 | 4778982 | 0 | 9569672 | 1549440 | 0 | 269760 | 305568 | 169248 | 0 | 38457 |  | 143961619 | 64519662 | 208481281 | 100085818 | 13583272 | 51356726 | 28137766 | 6792800 | 2579440 | 2463802 | 3257280 | 224377 | 0
Fuel Cost | 845600 | 0 | 0 | 0 | 5344972.64 | 0 | 0 | 6139332 | 6127120 |  | 0 | 7920700 | 1014676.2 | 597312 | 17423217.36 | 2125112.76 | 1862098.08 | 0 | 0 | 0 | 4006656 | 0 | 1279579.2 | 0 | 7015008 | 0 | 0 | 3307399.2 | 3091484.7 | 2836378.92 | 230607 | 450000 | 0 | 0 | 0 | 0 | 0 | 360734.4 | 309920 | 3672000 | 4590000 | 961336.35 | 4532451 | 0 | 3743363.1 | 0 |  | 0 | 0 | 7432490.19 | 11161357.2 | 13219660.8 | 3333657.6 | 401193.6 | 2014944 | 2844202.2 | 0 | 0 | 6116026 | 6248760 | 4236600 | 1311417.38 | 4362466.5 | 503493.12 | 1233528 | 0 | 1076229.44 | 0 | 0 | 0 | 367383.6 | 99225 | 1546587 | 388612.5 | 22475232 | 2650535.2 | 18670032 | 466454.16 | 247640 | 1668720 | 1959379.2 | 1147296 | 1269180 | 4367993 | 3205280 | 2254596.48 | 2907801.6 | 924274.8 | 3476300.8 | 696420 | 1058616 | 566820 | 5148920 | 424872 | 169595.52 | 0 | 0 | 458228.7 | 0 | 6649344 | 0 | 21765340.8 | 1589058 | 17026521.6 | 29598777.6 | 78361.31 | 0 | 14144256 | 0 | 0 | 0 | 17026481.8 | 0 | 0 |  | 36674834.4 | 0 | 6756272.64 | 0 | 6339264 | 0 | 0 | 0 | 2828544 | 2580595.2 | 5270133.75 | 3295612 | 876526.55 | 14042764.8 | 0 | 0 | 0 | 1041634.56 | 417749.5 | 7932375 | 5979030.9 | 7696420.92 | 509474 | 7807046.4 | 326852.55 | 557568 | 618710.4 | 185940.396 | 0 | 0 | 27782552 | 2542200 | 2964150 | 0 | 0 | 4395061.89 | 0 | 3337845.66 | 356928 | 4205504.16 | 0 | 6985860.56 | 14657702.4 | 0 | 2476396.8 | 2722610.88 | 1580776.32 | 0 | 0 |  | 341777221.61 | 185744938.636 | 527522160.246 | 94335517.786 | 36674834.4 | 49451351.39 | 264439676.07 | 27782552 | 670654.4 | 29855644.2 | 22475232 | 1836698 | 0
Yesterday Day Peak | 35 | 0 | 200 | 0 | 370 | 0 | 0 | 386 | 347 |  | 0 | 450 | 5 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 0 | 33 | 0 | 0 | 42 | 50 | 100 | 120 | 0 | 219 | 0 | 111 | 0 |  | 0 | 0 | 15 | 50 | 0 | 0 | 19 | 28 | 100 | 0 | 0 | 360 | 345 | 202 | 55 | 140 | 27 | 47 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 120 | 138 | 56 | 20 | 2 | 30 | 60 | 47 | 48 | 130 | 160 | 63 | 73 | 40 | 122 | 17 | 39 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 100 | 64 | 0 | 0 | 8 | 0 | 0 | 4 | 52 | 0 | 0 |  | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 174 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 16 | 0 | 44 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 209 | 0 | 95 | 0 | 209 | 0 | 412 | 105 | 0 | 0 | 0 | 78 | 0 | 6 |  | 8083 | DayPeak
Yesterday Evening Peak | 35 | 0 | 200 | 0 | 380 | 0 | 0 | 379 | 350 | 0 | 0 | 450 | 230 | 7 | 98 | 40 | 0 | 0 | 0 | 0 | 50 | 0 | 16 | 0 | 70 | 0 | 0 | 36 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 40 | 50 | 105 | 120 | 16 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 85 | 72 | 97 | 50 | 19 | 30 | 125 | 0 | 0 | 360 | 330 | 196 | 55 | 140 | 27 | 50 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 168 | 155 | 95 | 20 | 0 | 60 | 60 | 42 | 49 | 163 | 155 | 65 | 75 | 40 | 81 | 17 | 42 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 200 | 0 | 0 | 115 | 34 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 43 | 30 | 40 | 173 | 29 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 270 | 16 | 16 | 0 | 0 | 206 | 0 | 97 | 0 | 207 | 0 | 422 | 105 | 0 | 35 | 34 | 65 | 0 | 0 |  | 10691 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 84 | 84 | 105 | 120 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 97 | 50 | 22 | 20 | 120 | 0 | 0 | 360 | 360 | 225 | 55 | 141 | 27 | 55 | 0 | 35 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 171 | 190 | 95 | 22 | 0 | 60 | 62 | 51 | 50 | 163 | 240 | 68 | 80 | 40 | 130 | 20 | 44 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 | 54 | 113 |  | 938 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 75 | 40 | 180 | 33 | 110 | 30 | 0 | 0 | 50 | 40 | 100 | 50 | 50 | 40 | 52 | 35 | 22 | 20 | 11 | 0 | 0 | 280 | 16 | 15 | 225 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 200 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 |  | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 84 | 84 | 105 | 120 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 50 | 50 | 22 | 15 | 120 | 0 | 0 | 360 | 360 | 225 | 55 | 140 | 27 | 55 | 0 | 35 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 128 | 190 | 95 | 22 | 1.6 | 60 | 62 | 51 | 50 | 163 | 230 | 68 | 80 | 40 | 110 | 20 | 44 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 0 | 4.4 | 230 | 54 | 113 |  | 395 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 50 | 40 | 52 | 0 | 22 | 20 | 11 | 0 | 0 | 280 | 0 | 0 | 225 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 200 | 0 | 300 | 0 | 0 | 348 | 282 | 0 | 0 | 330 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 40 | 40 | 105 | 120 | 0 | 205 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19 | 12 | 100 | 0 | 0 | 270 | 265 | 183 | 8 | 140 | 24 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 114 | 191 | 10 | 22 | 1 | 60 | 60 | 11 | 10 | 100 | 154 | 64 | 10 | 10 | 82 | 17 | 20 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 16 | 0 | 0 | 0 | 926 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 279 | 0 | 0 | 205 | 0 | 0 | 0 | 63 | 0 | 180 | 0 | 428 | 0 | 0 | 0 | 0 | 10 | 0 | 2.6 | 0
199
| Minimum Generation |  | 7265.4 | 9:00
| Highest Generation |  | 10691 | 21:00
| Day Peak Generation |  | 8083 | 12:00
| Evening Peak Generation |  | 10691 | 21:00
| HVDC Max Flow |  | 928 | 19:30
| HVDC EvPeak Flow |  | 922 | 21:00
| Load factor L.F |  | 81.25%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8083 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7642.3 | MW
Evening Peak Generation : |  | 10691 | MW Hour : | 21:00 | Available Max Generation : |  | 15075 | MW
E.P. Demand (at gen end) : |  | 10691 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 10691 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3575 | MW
Total Gen. (MKWH) : |  | 208.4813 | System Load Factor : | 81.25% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -46 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-19
Actual : | 103.02 | Ft.(MSL) , | Rule curve : | 2.7 | Ft.( MSL )
Gas Consumed : | Total = | 1269.63 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 143786869.176
|  | Coal : | 27782552 | Oil : | 294295320.27 | Total : | 465864741.446
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4068.3466 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1384.3359 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1240.4747 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1120.9287 |  |  | 0 | 0%
) | 0 | 0:00 | 1012.9366 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 817.4062 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 455.93 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 210.4304 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 630.4296 |  |  | 0 | 0%
Total | 0 |  | 10941.2187 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 & 2. | 7) Sirajganj 225 MW Unit-2
2) Khulna ST 110 MW
3) Sikalbaha ST 60 MW
4) Ashuganj #3,4
5) Baghabari 100 MW,
6) Ghorasal Unit-1,3 & 5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Maniknagar-Siddhirganj 230 kV Ckt-1 was under shut down from 08:51 to 18:27 for D/W.
b) T.K Chemical 132/33 kV T2 transformer was under shut down from 08:15 to 16:55 for C/M.
c) Bheramara-Baharampur 400 kV Ckt-1 was under shut down from 10:09 to 17:35 for D/W.
d) Bheramara-Baharampur 400 kV Ckt-2 was under shut down from 10:11 to 17:41 for D/W.
e) Bagura-Mohastangarh 132 kV Ckt-1 was shut down at 10:55 for D/W.
f) Khulna©-KPCL-2 132 kV Ckt was under shut down from 07:29 to 14:02 for C/M.
g) Khulna©-Khulna(S) 132 kV Ckt-1 was under shut down from 08:23 to 14:01 for C/M.
h) Summit Meghnaghat CCPP GT-2 was synchronized at 09:51.
i) Barisal(N)-Bhola 230 kV Ckt-2 tripped at 13:15 from both end showing E/F, Dist.34.67 kV at Barisal
end & carrier trip at Bhola end and was switched on at 14:00.
j) Naogaon-Santahar 132 kV Ckt tripped at 18:40 showing O/C, E/F relays at Naogaon end and was
switched on at 18:58.
k) Bagura-Mohastangarh 132 kV Ckt-2 tripped at 18:40 showing Dist. ABC, Z1 relays at Mohastangarh end
and was switched on at 19:01.
l) Barapukuria 230/132 kV T6 transformer tripped at 18:40 showing O/C relay at 132 kV end & due to |  |  |  |  | About 478 MW power interruption occurred under Rangpur Zone area
above tripping full Zone and was switched on at 18:52. At the same time Rangpur Confidence, |  |  |  |  | from 11:50 to 13:39.
Rangpur GT, Saidpur GT also tripped.
m) Sikalbaha 230/132 kV T1 & T2 transformers tripped at 19:43 showing O/C relay at T1 & Diff. Dir O/C
RYB-phase at T2 end and were switched on at 20:48, 23:44 respectively. At the same time
Sikalbaha 225 MW, Anwara 300 MW also tripped.
n) Sikalbaha 225 MW GT synchronized at 21:32.
o) Summit Meghnaghat ST was synchronized at 16:07.
p) Summit Meghnaghat GT-1 was synchronized at 20:30.
q) Bakulia 132 kV Bus & 132/33 kV T2 transformer was shut down at 07:35(19/10/2019) for D/W.
r) Chandraghona-Madnaghat 132 kV Ckt-1 was shut down at 07:36(19/10/2019) for A/M.
s) Ullon-Haripur 132 kV Ckt-2 was shut down at 06:44 (19/10/19) for D/W.
t) Sylhet 132/33 kV T4 transformer along with Bus-section-4 were shut down at 06:41 (19/10/19) for C/M.
u) Sirajganj 225 MW Unit-1 was synchronized at 00:11(19/10/2019).
v) Sirajganj 225 MW Unit-2 was shut down at 05:17(19/10/2019) for gas shortage.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 755000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7222936
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 379 | 8526850 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 8062000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9900875
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 58560 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 1127418 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 98 | 1608792
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 207126 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 307476
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 360960 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1501692 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 36 | 344880 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 129120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 324055
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 284777
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 70 | 770880 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1119660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 663800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 746400 | Machine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 26797 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2157120
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 0 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2767 | 46207174
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 100035 | Engine problem
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137700
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 356160
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 90 | 2579440 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 4316620 | Transformer Tripped
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 134 | 2947530 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer & Line overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 708531
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 72 | 1084680 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1826880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436080
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 724800
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1390080 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33120
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 1846690 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 918 | 23888346
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 2708764 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4605000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8264900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7439000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 27 | 614016 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1197600
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 1338181 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 752608 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 8363 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3280050
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3155520
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 360180
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 132300 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 168 | 3257280
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 518150 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1770 | 38450212
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 155 | 3232360 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 457308
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1963200
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 691200 | High Voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1612800
| Mymensingh Area Total |  |  |  | 637 | 485 | 7971968
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1227000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1440720
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3522575
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 155 | 3484000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 42 | 843600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1015344
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 223152
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1513152 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1652160
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 832680 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 81 | 2287040
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 438000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 42 | 904800 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 566496
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7252000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 241200
| Sylhet Area Total |  |  |  | 1949 | 1214 | 27443919
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 13583272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 657600
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 243840
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 196992 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 375 | 8661888 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 532875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 21120 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1549440
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 34 | 305568 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1664 | 25752595
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1307520
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 565501 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 4119515 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 2099274
| Barisal Area Total |  |  |  | 462 | 409 | 8091810
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under shut down.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 93504 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 34102 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 576570
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 657252
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 42280 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 206 | 4725873 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 207 | 4778982 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 422 | 9569672 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 33183 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 506880
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 17 | 374976
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245628
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 783840
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 25 | 801250
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 269760
| Rajshahi Area Total |  |  |  | 2070 | 1097 | 23493752
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 270 | 6792800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 76000
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 105000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 65 | 169248
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38457
| Rangpur Area Total |  |  |  | 605 | 367 | 7181505
| Total |  |  |  | 18905 | 10691 | 208481281
| Eastern Grid Total |  |  |  | 13454 | 7154 | 143961619
| Western Grid Total |  |  |  | 5451 | 3537 | 64519662
| National Grid Total |  |  |  | 18905 | 10691 | 208481281
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-18
(a) ENTIRE EASTERN GRID : |  | 6946 | MW | (b) ENTIRE WESTERN GRID : |  | 3215 | MW
i) Dhaka area |  | 3603 | MW | i) Khulna area |  | 1306 | MW
ii) Chittagong area |  | 1031 | MW | ii) Rajshahi area |  | 1050 | MW
iii) Comilla area |  | 1041 | MW | iii) Barisal area |  | 318 | MW
iv) Mymensingh area |  | 804 | MW | iv) Rangpur area |  | 541 | MW
v) Sylhet area |  | 467 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10161 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 2100 | Sherpur | 94 | 1900 | Jhenida | 99 | 1830
Munsiganj | 114 | 1930 | Srimongal | 37 | 1830 | Bottail | 108 | 1830
Sonargaon | 86 | 100 | Shahjibazar | 110 | 2000 | G.K Project | 52 | 1830
Shyampur | 184 | 2400 | Fenchuganj | 39 | 1930 | Faridpur | 158 | 2000
Bhulta | 173 | 100 | Kulawara | 48 | 1830 | Madaripur | 86 | 2100
Madanganj | 64 | 2300 | Sylhet | 134 | 1930 | Sariatpur | 58 | 2100
Shitalakhya | 87 | 100 | Chatak | 26 | 1930 | Gopalganj | 84 | 1900
Rahim steel | 14 | 500 | Sunamganj | 41 | 1900 | Bagerhat | 80 | 1900
Matuail | 83 | 100 | Biani Bazar | 50 | 1930 | Mongla | 36 | 100
Ghorasal | 74 | 1930 | Comilla (S) | 168 | 2100 | Satkhira | 93 | 2100
Narsingdi | 135 | 2000 | Comilla(N) | 117 | 2200 | Gallamari | 44 | 1300
Haripur (SBU) | 85 | 200 | Chandpur | 95 | 2100 | Magura | 47 | 1830
Ullon | 83 | 2000 | Feni | 134 | 2100 | Norail | 22 | 1800
Hasnabad | 175 | 2000 | Chowmuhani | 166 | 2200 | Chuadanga | 82 | 1930
Magbazar | 95 | 2000 | Ashuganj | 58 | 2300 | Barisal(N) | 45 | 2000
Maniknagar | 86 | 1800 | Daudkandi | 124 | 1930 | Barisal (S) | 90 | 2200
Bangabhaban | 16 | 1300 | B.Baria | 132 | 2000 | Patuakhali | 101 | 2100
Narinda | 80 | 1200 | Ramganj | 88 | 1800 | Bhandaria | 50 | 2000
Dhanmondi | 130 | 1900 | Madunaghat | 61 | 1830 | Borhan Uddin | 35 | 2100
Lalbag | 58 | 2200 | Hathazari | 94 | 2000 | Ishurdi | 55 | 1830
Madartek | 61 | 2300 | Khulshi | 76 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 101 | 1930 | Halishahar | 132 | 1930 | Natore | 109 | 1900
Kalyanpur | 96 | 1930 | Baraulia | 140 | 100 | Bogra | 175 | 1900
Gulshan | 124 | 1800 | Sikalbaha | 35 | 1830 | Noagaon | 96 | 2100
Uttara | 50 | 1100 | Dohazari | 88 | 1900 | Rajshahi | 124 | 2100
Uttara New | 42 | 1830 | Cox'sbazar | 90 | 2100 | Rajshahi New | 11 | 1830
Kamrangirchar | 61 | 100 | Chandraghona | 30 | 1830 | C.Nawabganj | 70 | 2100
Savar | 107 | 1830 | Kaptai | 5 | 1830 | Amnura | 32 | 1900
Bhasantec | 144 | 1900 | A. Khaer Stl. | 8 | 1830 | Pabna | 95 | 1900
Agargaon | 52 | 1800 | Bakulia | 96 | 1930 | Shahjadpur | 93 | 1830
Satmosjid | 111 | 1930 | Julda | 18 | 100 | Serajganj | 74 | 1900
Tongi | 129 | 1900 | TK chemical | 5 | 1600 | Niyamatpur | 57 | 1900
Kabirpur | 110 | 2100 | Modern Steel | 29 | 100 | Joypurhat | 52 | 1830
Basundhara | 80 | 1800 | Shahmirpur | 18 | 1830 | Sherpur(Bogura) | 42 | 1800
Manikganj | 195 | 1930 | Khagrachhari | 29 | 1830 | Mohastangor | 7 | 1930
Joydevpur | 80 | 2100 | Matarbari | 24 | 1800 | Rangpur | 107 | 2100
New Tongi | 192 | 2100 | Baroiar Hat | 12 | 1800 | Lalmonirhat | 51 | 1800
Korda | 60 | 2100 | Rangamati | 16 | 1600 | Saidpur | 90 | 2000
Dhamrai | 92 | 1900 | Abul Khair 230 | 109 | 200 | Purbasadipur | 82 | 100
Valuka | 92 | 1900 | BSRM | 109 | 200 | Thakurgaon | 61 | 2000
Tangail | 181 | 1830 | Goalpara | 33 | 2300 | Palashbari | 100 | 1800
Mymensing | 193 | 2200 | Central s/s | 78 | 2000 | Barapukuria | 44 | 2000
Kishorganj | 120 | 1930 | Noapara | 59 | 2200 | Panchagar | 40 | 1830
Netrokona | 95 | 1900 | Jessore | 102 | 1830 | Joldhaka | 18 | 1800
Jamalpur | 108 | 1830 | Benapol | 40 | 1830 | Kurigram | 35 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-18 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 383 | 6:00 | 376 | 9:00 | Kaliakoir | 363 | 6:00 | 352 | 9:00
Bheramara | 394 | 1:00 | 390 | 11:00 | Bhulta | 375 | 21:00 | 358 | 10:00
Ashuganj(N) | 377 | 22:00 | 365 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 10:00
Ghorasal | 222 | 1:00 | 220 | 13:00 | Hathazari | 216 | 1:00 | 210 | 11:00
Ishurdi | 236 | 17:00 | 225 | 14:00 | Megnaghat | 220 | 8:00 | 210 | 10:00
Ashuganj | 228 | 7:00 | 223 | 9:00 | Fenchuganj | 233 | 6:00 | 229 | 15:00
Serajganj | 228 | 1:00 | 225 | 10:00 | Siddhirganj | 219 | 6:00 | 210 | 10:00
Baghabari | 232 | 1:00 | 230 | 7:00 | Maniknagar | 216 | 4:00 | 208 | 10:00
Barapukuria | 230 | 5:00 | 219 | 18:00 | Old Airport | 215 | 6:00 | 205 | 10:00
Bogra | 224 | 16:00 | 218 | 1:00 | Barisal | 233 | 18:30 | 225 | 10:00
Khulna South | 227 | 6:00 | 209 | 13:00 | AKSML | 216 | 21:00 | 206 | 10:00
Rampura | 219 | 7:00 | 209 | 12:00 | BSRM | 215 | 2:00 | 208 | 10:00
Haripur | 216 | 1:00 | 210 | 10:00 | Bibiyana | 230 | 19:00 | 225 | 1:00
Hasnabad | 215 | 1:00 | 208 | 10:00 | Bhulta | 219 | 6:00 | 210 | 10:00
Aminbazar | 216 | 6:00 | 207 | 10:00 | Ashuganj (S) | 228 | 22:00 | 222 | 9:00
Tongi | 217 | 18:30 | 209 | 15:00 | Kaliakoir | 220 | 19:00 | 212 | 9:00
Comilla (N) | 225 | 20:00 | 219 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 1830 | 127 | 100 | Halishahar | 131 | 1600 | 128 | 1200
Munsiganj | 132 | 1800 | 126 | 1100 | Baraulia | 130 | 1800 | 125 | 2100
Megnaghat | 129 | 1800 | 124 | 100 | Sikalbaha | 132 | 1800 | 127 | 2000
Shyampur | 131 | 1800 | 127 | 1200 | Dohazari | 127 | 300 | 125 | 2000
Bhulta | 126 | 1800 | 122 | 100 | Cox'sbazar | 123 | 800 | 114 | 2000
Madanganj | 133 | 2100 | 126 | 900 | Chandraghona | 131 | 1700 | 127 | 2000
Shitalakhya | 133 | 1800 | 127 | 100 | Kaptai | 130 | 100 | 128 | 1200
Rahim steal | 131 | 1800 | 128 | 100 | A. Khaer Stl. | 129 | 1700 | 126 | 100
Matuail | 129 | 1700 | 126 | 1100 | Bakulia | 130 | 1830 | 125 | 2000
Ghorasal | 135 | 700 | 132 | 100 | Julda | 131 | 1800 | 127 | 2000
Narsinghdi | 132 | 700 | 125 | 1930 | TK Chemical | 131 | 1600 | 127 | 2000
Haripur (SBU) | 131 | 400 | 128 | 1300 | Modern Steel | 131 | 1700 | 126 | 100
Ullon | 131 | 600 | 128 | 1200 | Shahmirpur | 131 | 1800 | 126 | 2000
Hasnabad | 132 | 1800 | 128 | 1200 | Khagrachhari | 129 | 200 | 126 | 2000
Magbazar | 133 | 500 | 128 | 1200 | Matarbari | 127 | 1000 | 118 | 2000
Maniknagar | 131 | 600 | 125 | 1200 | Baroiar Hat | 130 | 600 | 122 | 2200
Bangabhaban | 131 | 600 | 125 | 1200 | Rangamati | 130 | 600 | 126 | 2000
Narinda | 131 | 600 | 125 | 1200 | Goalpara | 140 | 900 | 130 | 1600
Dhanmondi | 131 | 600 | 128 | 1200 | Central s/s | 139 | 800 | 129 | 100
Lalbag | 132 | 2100 | 126 | 1200 | Noapara | 138 | 900 | 125 | 100
Madartek | 133 | 600 | 128 | 1200 | Jessore | 130 | 600 | 120 | 1930
Mirpur | 134 | 200 | 127 | 1100 | Benapol | 134 | 800 | 121 | 1900
Kalyanpur | 134 | 600 | 130 | 1100 | Jhenida | 131 | 800 | 117 | 1830
Gulshan | 131 | 300 | 127 | 1200 | Bottail | 137 | 800 | 127 | 1830
Uttara | 132 | 900 | 124 | 1100 | G.K Project | 142 | 600 | 137 | 1100
Uttara New | 131 | 2100 | 126 | 1200 | Faridpur | 135 | 800 | 124 | 1930
Kamrangirchar | 131 | 1830 | 126 | 1100 | Madaripur | 137 | 1700 | 124 | 1930
Savar | 131 | 1700 | 124 | 1200 | Sariatpur | 136 | 800 | 124 | 1930
Bhasantec | 133 | 600 | 128 | 1200 | Gopalganj | 140 | 1800 | 127 | 1300
Agargaon | 134 | 600 | 129 | 1200 | Bagerhat | 140 | 800 | 126 | 1930
Satmosjid | 134 | 600 | 129 | 1200 | Mongla | 131 | 2300 | 123 | 100
Tongi | 132 | 2200 | 126 | 1100 | Satkhira | 135 | 600 | 126 | 1900
Kabirpur | 132 | 400 | 125 | 1200 | Gallamari | 141 | 800 | 129 | 1930
Basundhara | 132 | 800 | 127 | 1300 | Magura | 130 | 600 | 115 | 1830
Manikganj | 136 | 2200 | 128 | 1200 | Norail | 129 | 600 | 112 | 1930
Joydevpur | 134 | 600 | 129 | 1300 | Chuadanga | 128 | 600 | 109 | 2100
New Tongi | 131 | 2200 | 125 | 1000 | Barisal(N) | 140 | 800 | 130 | 1100
Kodda | 133 | 1800 | 120 | 1000 | Barisal (S) | 138 | 800 | 130 | 1400
Dhamrai | 131 | 600 | 126 | 1200 | Patuakhali | 138 | 700 | 125 | 900
Valuka | 126 | 500 | 116 | 1200 | Bhandaria | 135 | 700 | 129 | 1900
Tangail | 131 | 600 | 125 | 1100 | Ishurdi | 139 | 700 | 134 | 1000
Mymensing | 129 | 1600 | 118 | 1100 | Ruppur Paromanobik | 138 | 500 | 135 | 1830
Kishorganj | 129 | 500 | 123 | 1200 | Natore | 137 | 600 | 127 | 200
Netrokona | 128 | 700 | 120 | 1000 | Bogra | 137 | 1900 | 131 | 2000
Jamalpur | 137 | 1600 | 120 | 1000 | Noagaon | 132 | 600 | 126 | 2000
Sherpur | 136 | 1900 | 120 | 1000 | Rajshahi | 134 | 1800 | 124 | 200
Srimongal | 137 | 600 | 133 | 1900 | Rajshahi New | 136 | 1800 | 123 | 200
Shahjibazar | 136 | 600 | 131 | 1930 | C.Nawabganj | 134 | 1800 | 120 | 200
Fenchuganj | 135 | 600 | 132 | 1900 | Amnura | 139 | 1800 | 122 | 100
Khulawara | 134 | 500 | 131 | 2000 | Pabna | 140 | 600 | 131 | 1930
Sylhet | 135 | 800 | 131 | 1930 | Shahjadpur | 140 | 1800 | 136 | 1100
Chatak | 134 | 600 | 130 | 1830 | Serajganj | 136 | 400 | 131 | 2000
Sunamganj | 133 | 700 | 128 | 1800 | Niyamatpur | 130 | 600 | 122 | 2100
Biani Bazar | 134 | 1000 | 128 | 1900 | Joypurhat | 134 | 600 | 124 | 2000
Comilla(s) | 127 | 700 | 120 | 1800 | Sherpur(Bogura) | 135 | 600 | 131 | 2000
Comilla(n) | 133 | 700 | 130 | 1800 | Mohastangor | 135 | 600 | 127 | 2000
Chandpur | 134 | 1500 | 128 | 600 | Rangpur | 128 | 400 | 118 | 1930
Feni | 128 | 1100 | 123 | 2300 | Lalmonirhat | 128 | 1900 | 115 | 1930
Chowmuhani | 125 | 800 | 118 | 2100 | Saidpur | 130 | 1900 | 119 | 2000
Ashuganj | 136 | 900 | 132 | 1900 | Purbasadipur | 130 | 1900 | 116 | 2000
Daudkandi | 128 | 700 | 124 | 1930 | Thakurgaon | 122 | 600 | 115 | 100
B.Baria | 133 | 700 | 128 | 2100 | Palashbari | 131 | 600 | 122 | 2000
Ramganj | 123 | 1800 | 120 | 2100 | Barapukuria | 133 | 1900 | 122 | 2000
Madanhat | 131 | 2200 | 128 | 100 | Panchagar | 129 | 1900 | 111 | 1800
Hathazari | 130 | 200 | 127 | 2000 | Joldhaka | 134 | 1900 | 117 | 2000
Khulshi | 128 | 700 | 125 | 500 | Kurigram | 135 | 1900 | 117 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 170 | 6709 | 3239 | 9948 |  |  |  | QF-LDC-12
0:30 | 140 | 6828 | 3155.5 | 9983.5 | Date: | 2019-10-18
1:00 | 110 | 6947 | 3072 | 10019
1:30 | 118 | 6772 | 2978.5 | 9750.5
2:00 | 126 | 6597 | 2885 | 9482
2:30 | 153 | 6489 | 2848.5 | 9337.5 | [5 empty] | Gen. at Eve. Peak | 10691 | 10691 MW (21:00 )
3:00 | 180 | 6381 | 2812 | 9193 | [6 empty] | 21:00
3:30 | 210 | 6324 | 2792 | 9116 | [5 empty] | Gen. at Day Peak | 8083 | 8083 MW (12:00 )
4:00 | 240 | 6267 | 2772 | 9039 | [6 empty] | 12:00
4:30 | 265 | 6084 | 2770 | 8854 | [5 empty] | Highest Generation | 10691
5:00 | 290 | 5901 | 2768 | 8669 | [6 empty] | 21:00
5:30 | 300 | 5724.685 | 2706 | 8430.685
6:00 | 310 | 5548.37 | 2644 | 8192.37
6:30 | 260 | 5319.535 | 2594.75 | 7914.285
7:00 | 210 | 5090.7 | 2545.5 | 7636.2
7:30 | 280 | 4952.285 | 2580.45 | 7532.735
8:00 | 350 | 4813.87 | 2615.4 | 7429.27
8:30 | 385 | 4815.885 | 2531.45 | 7347.335
9:00 | 420 | 4817.9 | 2447.5 | 7265.4
9:30 | 437 | 5102.18 | 2263.3 | 7365.48
10:00 | 454 | 5386.46 | 2079.1 | 7465.56
10:30 | 447 | 5487.325 | 2093.05 | 7580.375
11:00 | 440 | 5588.19 | 2107 | 7695.19
11:30 | 380 | 5736.095 | 2153 | 7889.095
12:00 | 320 | 5884 | 2199 | 8083
12:30 | 315 | 6018.38 | 2204.45 | 8222.83
13:00 | 310 | 6152.76 | 2209.9 | 8362.66
13:30 | 315 | 6161.5 | 2188.75 | 8350.25
14:00 | 320 | 6170.24 | 2167.6 | 8337.84
14:30 | 365 | 6260.77 | 2185.85 | 8446.62
15:00 | 410 | 6351.3 | 2204.1 | 8555.4
15:30 | 417 | 6353.665 | 2110.45 | 8464.115
16:00 | 424 | 6356.03 | 2016.8 | 8372.83
16:30 | 437 | 6153.065 | 1972.1 | 8125.165
17:00 | 450 | 5950.1 | 1927.4 | 7877.5
17:30 | 270 | 6303.55 | 2405.7 | 8709.25
18:00 | 90 | 6657 | 2884 | 9541
18:30 | 48 | 6848.5 | 2999.5 | 9848
19:00 | 6 | 7040 | 3115 | 10155
19:30 | 30 | 7139 | 3331 | 10470
20:00 | 16 | 6888 | 3411 | 10299 |  |  |  | Executive Engineer
20:30 | 31 | 7021 | 3474 | 10495 |  |  |  | Network Operation Division
21:00 | 46 | 7154 | 3537 | 10691
21:30 | 25 | 7142 | 3534 | 10676
22:00 | 4 | 7130 | 3531 | 10661 |  |  |  |  | Page 6 of 7
22:30 | 62 | 7021 | 3499 | 10520
23:00 | 120 | 6912 | 3467 | 10379
23:30 | 145 | 6810.5 | 3353 | 10163.5
24:00 | 170 | 6709 | 3239 | 9948
10691 MW (21:00 )
8083 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-18 |  | Energy | 208481281
[10 empty] | 2019-10-18 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4475 | 922 | 2230 | 1771 | 280 | 93 | 21 | 0 | 156
0:30 | 4533.5 | 924 | 2232.5 | 1728 | 280.5 | 114.5 | 17.5 | 0 | 153 | Date: | 2019-10-18
1:00 | 4592 | 926 | 2235 | 1685 | 281 | 136 | 14 | 0 | 150
1:30 | 4596.5 | 926 | 2256.5 | 1392.5 | 279.5 | 136.5 | 14 | 0 | 149 | [7 empty] | Total Energy | 208.4813 | Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
2:00 | 4601 | 926 | 2278 | 1100 | 278 | 137 | 14 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 4576.5 | 925.5 | 2278 | 986.5 | 274 | 137 | 14 | 0 | 146 | [7 empty] | Energy Requirement | 208.4813
3:00 | 4552 | 925 | 2278 | 873 | 270 | 137 | 14 | 0 | 144
3:30 | 4542.5 | 925 | 2261 | 831 | 265 | 135.5 | 14 | 0 | 142 | [6 empty] | Shortage
4:00 | 4533 | 925 | 2244 | 789 | 260 | 134 | 14 | 0 | 140
4:30 | 4526 | 925 | 2247 | 605 | 265 | 134 | 14 | 0 | 138
5:00 | 4519 | 925 | 2250 | 421 | 270 | 134 | 14 | 0 | 136
5:30 | 4453 | 924.5 | 2061 | 430.5 | 270 | 133.5 | 25 | 0 | 133
6:00 | 4387 | 924 | 1872 | 440 | 270 | 133 | 36 | 0 | 130
6:30 | 4261.5 | 924 | 1759.5 | 403 | 275 | 131.5 | 41.5 | 0 | 115 |  |  |  |  | Coal
7:00 | 4136 | 924 | 1647 | 366 | 280 | 130 | 47 | 0 | 100
7:30 | 4004 | 924 | 1666.5 | 379.5 | 280 | 130 | 45.5 | 0 | 93 |  |  |  | Oil |  |  |  | ,
8:00 | 3872 | 924 | 1686 | 393 | 280 | 130 | 44 | 0 | 86
8:30 | 3880.5 | 751.5 | 1725 | 422.5 | 282 | 130 | 46 | 0 | 91
9:00 | 3889 | 579 | 1764 | 452 | 284 | 130 | 48 | 0 | 96
9:30 | 4092.5 | 289.5 | 1908.5 | 486 | 287 | 131 | 48 | 0 | 97
10:00 | 4296 | 0 | 2053 | 520 | 290 | 132 | 48 | 0 | 98
10:30 | 4314.5 | 0 | 2079 | 581 | 290 | 133 | 48.5 | 0 | 104
11:00 | 4333 | 0 | 2105 | 642 | 290 | 134 | 49 | 0 | 110
11:30 | 4417.5 | 0 | 2168 | 704.5 | 290 | 113 | 49 | 0 | 115
12:00 | 4502 | 0 | 2231 | 767 | 290 | 92 | 49 | 0 | 120
12:30 | 4468 | 0 | 2253.5 | 924 | 290 | 92 | 41.5 | 0 | 122
13:00 | 4434 | 0 | 2276 | 1081 | 290 | 92 | 34 | 0 | 124
13:30 | 4434 | 0 | 2276 | 1081 | 290 | 92 | 34 | 0 | 124
14:00 | 4434 | 0 | 2276 | 1081 | 290 | 92 | 34 | 0 | 124
14:30 | 4434 | 0 | 2263 | 1192.5 | 290 | 91 | 34 | 0 | 128
15:00 | 4434 | 0 | 2250 | 1304 | 290 | 90 | 34 | 0 | 132
15:30 | 4401.5 | 0 | 2215.5 | 1284 | 290 | 90 | 36 | 0 | 131
16:00 | 4369 | 0 | 2181 | 1264 | 290 | 90 | 38 | 0 | 130
16:30 | 4367 | 0 | 2096.5 | 1095.5 | 290 | 90 | 56 | 0 | 124
17:00 | 4365 | 0 | 2012 | 927 | 290 | 90 | 74 | 0 | 118
17:30 | 4424 | 88.5 | 2082 | 1320 | 290 | 90 | 275 | 0 | 139
18:00 | 4483 | 177 | 2152 | 1713 | 290 | 90 | 476 | 0 | 160
18:30 | 4430.5 | 431.5 | 2142 | 1938.5 | 283.5 | 90 | 370 | 0 | 162
19:00 | 4378 | 686 | 2132 | 2164 | 277 | 90 | 264 | 0 | 164
19:30 | 4409 | 928 | 2184 | 2207 | 270 | 90 | 214 | 0 | 168
20:00 | 4351 | 928 | 2168 | 2112 | 270 | 90 | 214 | 0 | 166
20:30 | 4369 | 925 | 2233 | 2218.5 | 270 | 90 | 222.5 | 0 | 167
21:00 | 4387 | 922 | 2298 | 2325 | 270 | 90 | 231 | 0 | 168
21:30 | 4365 | 922 | 2282.5 | 2348 | 270 | 90 | 231.5 | 0 | 167
22:00 | 4343 | 922 | 2267 | 2371 | 270 | 90 | 232 | 0 | 166
22:30 | 4351.5 | 922.5 | 2237 | 2275.5 | 270 | 91.5 | 209 | 0 | 163
23:00 | 4360 | 923 | 2207 | 2180 | 270 | 93 | 186 | 0 | 160
23:30 | 4417.5 | 922.5 | 2218.5 | 1975.5 | 275 | 93 | 103.5 | 0 | 158 | Max Temp. in Dhaka |  | 34.7° C
24:00 | 4475 | 922 | 2230 | 1771 | 280 | 93 | 21 | 0 | 156
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
Note on W13: Author:

## Generation
2019-10-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 86 | 87 | 87 | 84 | 84 | 83 | 80 | 80 | 80 | 82 | 84 | 42 | 42 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 43 | 43 | 1387440
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1192000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 2400000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 100035
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.3 | 4.6 | 11 | 15 | 18 | 19 | 20 | 19 | 17.64 | 13.2 | 6.63 | 1 | [9 empty] | 137700
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 226 | 206 | 219 | 205 | 214 | 205 | 204 | 205 | 205 |  | 204 | 214 |  |  | 81 | 80 | 190 | 4316620
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 134 | 134 | 134 | 134 | 134 | 104 | 104 | 104 | 104 | 104 | 104 | 111 | 134 | 104 | 134 | 134 | 134 | 134 |  | 134 | 108 | 142 | 134 | 134 | 134 | 134 | 2947530
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 15 | 15 | 0 | 0 |  |  | 0 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 4 | 708531
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 206 | 205 | 205 | 205 | 205 | 205 | 205 | 0 | [18 empty] | 1501692
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1338181
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 755000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 201 | 200 | 200 | 200 | 165 | 170 | 171 | 172 | 172 | 171 | 200 | 198 | 200 | 200 | 200 | 200 | 196 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 375 | 375 | 370 | 380 | 375 | 370 | 380 | 380 | 380 |  | 360 | 360 | 380 | 380 | 380 | 380 | 380 | 7222936
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2708764
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 614016
33 | Ashuganj 225 MW CCPP | 220 | 188 | 178 | 178 | 186 | 178 | 178 | 178 | 190 | 187 | 195 | 202 | 181 | 195 | 192 | 179 | 180 | 182 |  | 179 | 197 | 200 | 196 | 180 | 216 | 187 | 4605000
34 | Ashuganj 450 MW CCPP(South) | 285 | 295 | 285 | 280 | 285 | 285 | 285 | 285 | 285 | 315 | 330 | 345 | 310 | 330 | 320 | 305 | 305 | 305 |  | 305 | 305 | 345 | 330 | 310 | 310 | 310 | 7439000
| Ashuganj 450 MW CCPP(North) | 340 | 350 | 340 | 340 | 340 | 320 | 270 | 270 | 270 | 336 | 350 | 360 | 335 | 290 | 350 | 340 | 340 | 340 |  | 340 | 320 | 355 | 360 | 340 | 340 | 340 | 8264900
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 51 | 48 | 47 | 46 | 43 | 43 | 47 | 20 | 20 |  | 48 | 48 | 48 | 50 | 51 | 49 | 52 | 1197600
36 | Chandpur 150 MW CCPP | 140 | 140 | 138 | 138 | 140 | 138 | 138 | 137 | 140 | 140 | 141 | 140 | 140 | 140 | 140 | 140 | 135 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3280050
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 344 | 348 | 345 | 345 | 345 | 345 | 315 | 305 | 305 | 345 | 352 | 386 | 396 | 367 | 359 | 347 | 347 | 362 |  | 346 | 362 | 367 | 379 | 360 | 345 | 346 | 8526850
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 420 | 340 | 340 | 340 | 340 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 420 | 420 | 9900875
41 | Haripur 360MW CCPP(HPL) | 356 | 353 | 354 | 355 | 354 | 302 | 272 | 271 | 273 | 351 | 335 | 347 | 348 | 344 | 345 | 348 | 348 | 349 |  | 355 | 350 | 350 | 350 | 352 | 352 | 352 | 8062000
42 | RPCL 210MW CCPP | 124 | 123 | 123 | 124 | 123 | 146 | 145 | 125 | 124 | 123 | 124 | 138 | 138 | 137 | 151 | 154 | 153 | 153 |  | 158 | 155 | 155 | 155 | 156 | 156 | 157 | 3232360
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 59 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1227000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440720
46 | Shajibazar 330 MW CCPP | 154 | 154 | 153 | 154 | 153 | 156 | 154 | 154 | 155 | 154 | 155 | 160 | 153 | 154 | 155 | 156 | 154 | 150 |  | 155 | 160 | 165 | 155 | 155 | 155 | 155 | 3484000
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 64 | 64 | 64 | 67 | 69 | 50 | 52 | 65 | 63 | 63 | 63 | 63 | 63 | 63 | 65 | 63 | 65 |  | 65 | 65 | 65 | 65 | 63 | 66 | 66 | 1513152
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 40 | 75 | 73 | 73 | 74 | 74 | 74 | 74 | 40 | 74 |  | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 1652160
49 | Shahjibazar 50MW PP (EPL) | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 832680
50 | Sylhet 150 MW CCPP | 110 | 110 | 109 | 110 | 70 | 70 | 71 | 69 | 75 | 112 | 121 | 122 | 103 | 83 | 74 | 69 | 69 | 109 |  | 106 | 83 | 83 | 81 | 69 | 87 | 109 | 2287040
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438000
52 | Sylhet 50MW PP (EPL) | 43 | 42 | 42 | 42 | 42 | 42 | 18 | 18 | 17 | 39 | 39 | 39 | 42 | 41 | 41 | 40 | 22 | 43 |  | 43 | 43 | 43 | 42 | 42 | 43 | 43 | 904800
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241200
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223152
55 | Fenchugonj 51 MW PP (Barakatullah) | 42 | 42 | 42 | 42 | 11 | 11 | 11 | 11 | 11 | 44 | 44 | 47 | 47 | 44 | 44 | 44 | 17 | 29 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 843600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 566496
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 300 | 285 | 290 | 285 | 260 | 280 | 270 | 300 | 310 | 320 | 310 | 300 | 315 | 270 | 275 | 285 |  | 260 | 320 | 270 | 320 | 295 | 265 | 300 | 7252000
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 35 |  | 55 | 55 | 55 | 55 | 55 | 17 | 0 | 284777
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 436080
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 0 | [6 empty] | 19 | 19 | 19 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 307476
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 |  | 20 | 22 | 20 | 20 | 20 | 22 | 22 | 457308
63 | Impoprt (Tripura) | 150 | 148 | 144 | 140 | 136 | 130 | 100 | 86 | 96 | 98 | 110 | 120 | 124 | 130 | 132 | 130 | 118 | 160 |  | 164 | 168 | 166 | 168 | 166 | 160 | 156 | 3257280
64 | Malancha, Ctg. EPZ (United) | 22 | 30 | 31 | 32 | 33 | 35 | 41 | 37 | 34 | 36 | 36 | 28 | 29 | 29 | 27 | 30 | 29 | 30 |  | 30 | 30 | 30 | 30 | 38 | 32 | 32 | 724800
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | [7 empty] | 22 | 22 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 360180
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | [7 empty] | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 132300
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 518150
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 15 | 15 | 17 | 13 | 12 | 13 | 0 |  | 22 |  | 28 | 28 | 28 | 28 | 29 | 29 | 30 | 519660
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 0 |  |  |  |  | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 663800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 |  | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 746400
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 |  | 50 | 50 | 50 | 50 | 50 | 30 | 0 | 360960
78 | Gazipur 52 MW PP | [17 empty] | 4
79 | Kodda 150MW PP | [17 empty] | 32 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 129120
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 74 | 72 | 40 | 40 | 40 | 40 | 40 | 56 | 90 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1963200
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 0
| Gazipur 100 MW PP | [17 empty] | 5 |  | 34 | 34 | 34 | 34 | 0
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.07 | 0.8 | 1.87 | 3.4 | 4.46 | 4.89 | 4 | 4.56 | 3.8 | 2.8 | 1.8 | 0 | 0 | [8 empty] | 33120
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 48 | 48 | 48 | 48 | 48 | 30 | 30 | 30 | 30 | 30 | 30 | 48 | 80 | 80 | 80 | 80 | 83 |  | 96 | 98 | 98 | 98 | 98 | 98 | 98 | 1608792
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | [9 empty] | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 20 | 40 |  | 80 | 100 | 105 | 230 | 230 | 230 | 260 | 1127418
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 1 |  | 20 | 7 | 9 | 7 | 7 |  | 0 | 58560
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 70 | 70 | 70 | 70 | 40 | 80 |  | 72 | 72 | 72 | 72 | 72 | 80 | 82 | 1084680
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 10 | 10 | 36 | 48 | 48 | 48 | 45 | 45 | 45 | 20 | 35 |  | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 1015344
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 10 | 10 | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 752608
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [12 empty] | 2 | 12 | 19 | 6 | 6 | 12 |  | 47 | 50 | 50 | 50 | 50 | 50 | 48 | 356160
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 97 | 50 | 50 | 48 | 0 | [5 empty] | 2 | 46 | 52 | 52 | 72 |  | 96 | 97 | 97 | 97 | 97 | 97 | 97 | 1390080
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | 72 | 24 | [7 empty] | 5 | 24 | 36 | 60 | 60 | 60 | 60 | 24 | 24 |  | 46 | 65 | 65 | 70 | 70 | 70 | 8 | 770880
99 | Madanganj-55 MW PP(Summit) | 0 | [16 empty] | 3 |  | 30 | 30 | 30 | 40 | 55 | 15 | 0 | 207126
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 55 |  | 55 | 55 | 55 | 55 | 55 | 17 | 0 | 324055
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 163 | 163 | 130 |  | 100 | 100 | 100 | 163 | 163 | 163 | 130 | 3522575
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.3 | 1 | 1.5 | 2 | 2.3 | 2 | 2.2 | 1.8 | 1.3 | 0.6 | 0.1 | 0 | [8 empty] | 15100
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 17 | [15 empty] | 30 |  | 35 | 36 | 36 | 36 | 53 | 53 | 53 | 344880
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 51 | [7 empty] | 0 | 26797
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 70 | [16 empty] | 45 |  | 100 | 100 | 100 | 100 | 100 | 50 | 7 | 691200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 146 | 90 | 65 | 70 | 69 | 64 | 50 | 50 | 50 | 50 | 50 | 50 | 104 | 114 | 115 | 105 | 52 | 95 |  | 134 | 134 | 135 | 149 | 149 | 110 | 59 | 2157120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 60 | 60 | 10 | 10 | 10 | 10 | 10 | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1826880
116 | Chandpur 200MW (Desh energy) | 180 | 160 | 125 | 125 | 17 | 17 | 17 | 17 | 17 | 19 | 52 | 64 | 168 | 198 | 200 | 200 | 150 | 126 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3155520
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 8363
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 80 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 40 | 71 | 115 | 45 | 77 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1612800
| Anwara 300 MW PP (United) | 162 | 162 | 162 | 108 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 75 | 105 | 107 | 107 |  | 107 | 107 |  |  | 0 | 33 | 33 | 1846690
120 | Eastern Zone Total | 6947 | 6597 | 6381 | 6267 | 5901 | 5548.37 | 5090.7 | 4813.87 | 4817.9 | 5386.46 | 5588.19 | 5884 | 6152.76 | 6170.24 | 6351.3 | 6356.03 | 5950.1 | 6657 |  | 7040 | 7139 | 6888 | 7154 | 7130 | 6912 | 6709 | 143961619
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 63 |  | 115 | 115 | 115 | 115 | 115 | 115 | 24 | 657600
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 7 | 38 |  | 40 | 43 | 43 | 43 | 43 | 43 | 0 | 243840
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 17 | 0 |  |  |  |  | 46 | 53 | 90 | 90 | 105 | 105 | 105 | 105 | 53 | 17 | 90 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1549440
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 80 | 64 | 64 | 16 | 16 | 16 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1307520
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 96 | 95 | 96 | 96 | 50 | 43 | 81 | 81 | 81 | 81 | 95 | 94 | 92 | 94 | 94 | 51 | 96 |  | 96 | 97 | 93 | 97 | 97 | 98 | 96 | 2099274
| Bhola 225 MW CCPP | 173 | 173 | 174 | 174 | 174 | 174 | 174 | 150 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 150 | 169 | 173 |  | 149 | 173 | 174 | 173 | 173 | 174 | 174 | 4119515
140 | Bhola 33 MW PP (Venture) | 31 | 27 | 26 | 26 | 24 | 19 | 19 | 16 | 16 | 19 | 17 | 19 | 20 | 20 | 22 | 19 | 22 | 28 |  | 32 | 32 | 29 | 29 | 29 | 31 | 32 | 565501
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 5 |  | 0 | [6 empty] | 21120
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 0 | [6 empty] | 24 | 32 | 32 | 32 | 32 | 40 | 40 | 8 | 8 | 32 |  | 32 | 40 | 40 | 40 | 40 | 40 | 16 | 532875
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 4 | 23 | 50 |  | 30 | 30 | 30 | 30 | 30 | 8 | 0 | 196992
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 20 | 0 | [14 empty] | 14 | 60 |  | 32 | 34 | 34 | 34 | 34 | 34 | 34 | 305568
146 | Bheramara HVDC | 926 | 926 | 925 | 925 | 925 | 924 | 924 | 924 | 579 | 0 | [7 empty] | 177 |  | 686 | 928 | 928 | 922 | 922 | 923 | 922 | 13583272
147 | Bheramara 360 MW CCPP | 345 | 360 | 345 | 345 | 345 | 345 | 300 | 300 | 300 | 345 | 370 | 395 | 350 | 370 | 360 | 345 | 350 | 350 |  | 345 | 370 | 395 | 375 | 345 | 340 | 340 | 8661888
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 281 | 278 | 270 | 260 | 270 | 270 | 280 | 280 | 284 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 277 | 270 | 270 | 270 | 270 | 270 | 280 | 6792800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 50 |  | 50 | 0 | [5 empty] | 93504
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 187 | 186 | 193 | 187 | 187 | 186 | 155 | 153 | 151 | 194 | 200 | 209 | 203 | 184 | 207 | 200 | 188 | 196 |  | 175 | 163 | 173 | 206 | 205 | 197 | 195 | 4725873
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 190 | 189 | 186 | 188 | 184 | 155 | 155 | 156 | 206 | 205 | 209 | 214 | 181 | 201 | 188 | 188 | 199 |  | 186 | 174 | 181 | 207 | 200 | 186 | 189 | 4778982
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 389 | 428 | 418 | 396 | 430 | 315 | 315 | 304 | 395 | 421 | 419 | 412 | 429 | 410 | 410 | 380 | 398 | 404 |  | 375 | 370 | 410 | 422 | 405 | 409 | 428 | 9569672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 35 |  | 0 | 0 | 0 |  |  |  |  | 34102
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 506880
163 | Bogura 20 MW PP (Energyprima) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 15 | 16 | 16 | 16 | 16 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 374976
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245628
165 | Amnura 50 MW PP(Sinha) | 12 | 0 |  |  | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 576570
166 | Katakhali 50 MW PP (Northern) | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 657252
167 | Katakhali 50 MW Peaking PP |  |  |  |  | 0 | 4 | 3 | 0 | [8 empty] | 0 | 44 |  | 0 | [6 empty] | 42280
168 | Santahar 50 MW Peaking PP | [16 empty] | 0 | 27 |  | 0 | [6 empty] | 33183
169 | Natore 52 MW PP (Rajlanka) | 52 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 44 | 52 | 52 | 52 | 52 | 17 | 44 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 783840
170 | Chapainawabganj 100 MW Peaking PP |  |  |  |  | 0 | 18 | 30 | 30 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 83 |  | 43 | 25 | 25 | 25 | 25 | 0 |  | 801250
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | [17 empty] | 14 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 269760
173 | Rangpur 20 MW GTPP | [16 empty] | 0 | 16 |  | 0 |  |  | 16 | 16 | 17 | 0 | 76000
175 | Saidpur 20 MW GTPP | [16 empty] | 0 | 16 |  | 0 | 15 | 15 | 16 | 17 | 17 | 17 | 105000
176 | Rangpur 113 MW PP (Confidence) | 112 | 43 | 35 | 35 | 35 | 35 | 35 | 48 | 70 | 76 | 76 | 78 | 110 | 113 | 113 | 100 | 35 | 44 |  | 0 |  | 4 | 65 | 113 | 113 | 113 | 169248
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.5 | 0.4 | 3.5 | 4.1 | 6 | 6 | 5.9 | 4.6 | 4.1 | 1.8 | 0.4 | 0 | [8 empty] | 38457
178
178