## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-10 | Thursday
|  | Date (day): | 2019-10-10 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13735 | MW |  |  | (b) At Evening Peak Hour : |  | 15063 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-09 | 2019-10-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 36 | 36 | 38 | 38 |  |  | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 158 | 159 | 210 | 210
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under S/D
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 290 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  | 78 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 |  | 108 | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 344 | 375 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 349 | 357 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 100 | 0 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 32 | 97 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 70 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 350 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 46 | 46 |  | 5 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 54 | 69 | 70 | 70 |  |  | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 47 | 52 | 43 | 43 |  | 9 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 142 | 135 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 52 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2638 | 2802 | 4104 | 4541 | 470 | 748
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 75 | 75 | 75 | 75 | 105 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13.76 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 48 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 130 | 140 | 140 | 90 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 179 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 105 | 134 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 0 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 85 | 85
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 20 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 21 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 78 | 97 | 97 | 97 |  | 11 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.2 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 116 | 160 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 113 | 113
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 792.96 | 1066 | 1580.4 | 1696 | 275 | 109
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 170 | 180 | 200 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 330 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 275 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 33 | 33 |  | 12 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 56 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 83 | 83 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 87 | 86 | 90 | 90 |  | 73 | Engine problem
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 82 | 181 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 132 | 129 | 168
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1440 | 1489 | 1941 | 2255 | 451 | 98
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 156 | 155 | 155 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 0 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 95 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 16 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 281.1 | 366 | 588.6 | 587 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 22 | 22 | 30 | 30
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 230 | 243 | 230 | 240 |  | 90 | ST under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 42 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 3 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 68 | 68 | 68 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 78 | 82 | 82
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 42 | 43 | 47 | 47
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 69 | 110 | 110 | 130
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under S/D
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 45 | 43 | 43 |  | 7 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 16 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 335 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  |  | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1109 | 1209 | 1314 | 1350 | 0 | 97
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 916 | 916 | 918 | 918
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 69 | 0 | 75
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 340 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 54 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1261 | 1558 | 1968 | 2138 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 25 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 179 | 182 | 182
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 42 | 51 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 234 | 319 | 380 | 450 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 30 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 46 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 173 | 160 | 214 | 214 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 157 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 383 | 429 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 17 | 20 | 20
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 92 |  | 12 | Engine problem
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 811 | 1061 | 1458 | 1620 | 0 | 112
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 16
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 10 | 17 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 100 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 297.6 | 414 | 401 | 426 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 8864.66 | 10284 | 13735 | 15063 | 1238 | 1249
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8384.534 | 9727 | 12991.0876 | 14247.1607
A. |  | 2019-10-09 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10284 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 7421 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10284 | MW
3 | Day peak Generation : |  |  | 8864.66 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9727 | MW
4 | Evening peak Generation : |  |  | 10284 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 211.6314 | MKWHr | By Solar | 0.18096 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 149.7004 | MKWHr |  | By Oil: | 27.6154 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.7949 | MKWHr |  | By Hydro: | 2.921 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1238 | MW | Dhaka | 3805 | 3805 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1249 | MW | Chittagong | 1036 | 1036 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2487 | MW | Khulna | 1148 | 1148 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1202.93 | MMCFD |  |  | Rajshahi | 918 | 918 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 139463072.392 | ii) Oil : | Taka | 257483125.88 | Comilla | 904 | 904 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 27791141 | Total | Taka | 424737339.272 | Mymensingh | 680 | 680 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 365 | 365 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 230 | MW (E to W) at | 20:00 | hrs | Barisal | 283 | 283 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 124 | MW at | 22:00 | hrs | Rangpur | 588 | 588 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.7° C |  |  | Total | 9727 | 9727 |  | 0
B. |  | 2019-10-10 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 30.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15063 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 4563 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 216.0764 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6980.386 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9622 | MKWHr. | ii) HVDC Flow at Peak Time |  | 916 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4566 | MKWHr. | iii) Maximum HVDC Flow : |  | 916 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.46 |  | (b) Today: | 103.46 |  | (c) Rule Curve: |  | 106.81
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-10-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 36 | 169 | 0 | 0 | 380 | 0 | 0 | 348 | 356 |  | 0 | 0 | 150 | 0 | 30 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 87 | 40 | 75 | 0 | 0 | 206 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 90 | 0 | 19 | 39 | 0 | 0 | 100 | 360 | 305 | 145 | 82 | 87 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 104 | 155 | 95 | 22 | 0 | 58 | 22 | 41 | 49 | 100 | 226 | 67 | 75 | 44 | 108 | 0 | 44 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 100 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 |  | 914 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 179 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 186 | 0 | 0 | 0 | 97 | 0 | 199 | 0 | 427 | 17 | 0 | 0 | 67 | 0 | 0 | 0 |  | 6003 | 2822 | 8825 | 4568 | 914 | 1791 | 1031 | 280 | 127 | 10 | 104 | 0 | 0 | 103.47
2:00 | 36 | 169 | 0 | 0 | 380 | 0 | 0 | 345 | 360 |  | 0 | 0 | 150 | 0 | 30 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 40 | 75 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 90 | 0 | 19 | 42 | 0 | 0 | 100 | 360 | 305 | 145 | 82 | 87 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 8 | 15 | 102 | 157 | 70 | 22 | 0 | 60 | 22 | 41 | 49 | 100 | 228 | 67 | 75 | 44 | 119 | 0 | 44 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 10 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 |  | 914 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 185 | 0 | 0 | 0 | 96 | 0 | 197 | 0 | 362 | 17 | 0 | 0 | 66 | 0 | 0 | 0 |  | 5793 | 2729 | 8522 | 4552 | 914 | 1702 | 846 | 280 | 126 | 0 | 102 | 0 | 0 | 103.47
3:00 | 36 | 169 | 0 | 0 | 340 | 0 | 0 | 346 | 357 |  | 0 | 20 | 120 | 0 | 30 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 40 | 75 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 90 | 0 | 19 | 42 | 0 | 0 | 100 | 360 | 305 | 145 | 82 | 87 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 8 | 15 | 100 | 157 | 50 | 22 | 0 | 60 | 22 | 41 | 49 | 130 | 222 | 67 | 40 | 44 | 110 | 0 | 44 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 10 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 |  | 913 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 187 | 0 | 0 | 0 | 96 | 0 | 192 | 0 | 429 | 0 | 0 | 0 | 51 | 0 | 0 | 0 |  | 5544 | 2743 | 8287 | 4493 | 913 | 1780 | 593 | 280 | 128 | 0 | 100 | 0 | 0 | 103.47
4:00 | 36 | 169 | 0 | 0 | 340 | 0 | 0 | 350 | 355 |  | 0 | 25 | 120 | 0 | 30 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 40 | 75 | 0 | 0 | 216 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 19 | 42 | 0 | 0 | 100 | 360 | 305 | 145 | 82 | 86 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 8 | 15 | 94 | 156 | 24 | 22 | 0 | 60 | 22 | 11 | 49 | 130 | 224 | 67 | 10 | 44 | 120 | 0 | 44 | 0 | 290 | 24 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 10 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 914 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 192 | 0 | 0 | 0 | 62 | 0 | 201 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5363 | 2656 | 8019 | 4516 | 914 | 1693 | 394 | 280 | 128 | 0 | 94 | 0 | 0 | 103.47
5:00 | 36 | 169 | 0 | 0 | 340 | 0 | 0 | 348 | 324 |  | 0 | 75 | 120 | 0 | 30 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 40 | 75 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 19 | 42 | 0 | 0 | 100 | 360 | 310 | 145 | 82 | 87 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 8 | 15 | 90 | 155 | 24 | 22 | 0 | 58 | 22 | 11 | 49 | 130 | 226 | 67 | 10 | 44 | 115 | 0 | 44 | 0 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 914 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 183 | 0 | 0 | 0 | 62 | 0 | 188 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5320 | 2649 | 7969 | 4490 | 914 | 1722 | 351 | 280 | 122 | 0 | 90 | 0 | 0 | 103.46
6:00 | 36 | 157 | 0 | 0 | 340 | 0 | 0 | 345 | 324 |  | 0 | 165 | 120 | 0 | 30 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 0 | 33 | 0 | 0 | 82 | 40 | 75 | 0 | 0 | 205 | 0 | 134 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 19 | 42 | 0 | 0 | 100 | 360 | 305 | 145 | 82 | 86 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 8 | 15 | 80 | 157 | 8 | 22 | 0 | 60 | 22 | 11 | 10 | 100 | 224 | 68 | 10 | 10 | 113 | 0 | 18 | 0 | 270 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 11 | 0 | 163 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5133 | 2374 | 7507 | 4342 | 916 | 1432 | 335 | 280 | 122 | 0 | 80 | 0 | 0 | 103.46
7:00 | 36 | 123 | 0 | 0 | 300 | 0 | 0 | 346 | 283 |  | 0 | 220 | 120 | 0 | 30 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 40 | 75 | 0 | 0 | 217 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 63 | 0 | 0 | 32 | 0 | 0 | 100 | 300 | 340 | 145 | 45 | 87 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 8 | 15 | 74 | 155 | 8 | 22 | 0 | 60 | 22 | 11 | 10 | 100 | 230 | 66 | 10 | 10 | 84 | 0 | 12 | 0 | 275 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 4 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 916 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 5 | 0 | 0 | 280 | 0 | 0 | 162 | 0 | 0 | 0 | 12 | 0 | 154 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4984 | 2437 | 7421 | 4242 | 916 | 1449 | 334 | 280 | 122 | 0 | 74 | 4 | 0 | 0
8:00 | 36 | 130 | 0 | 0 | 300 | 0 | 0 | 378 | 325 |  | 0 | 230 | 120 | 0 | 30 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 40 | 75 | 0 | 0 | 218 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 63 | 0 | 19 | 5 | 0 | 0 | 100 | 300 | 360 | 150 | 45 | 86 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 22 | 5 | 8 | 6 | 80 | 153 | 8 | 22 | 0 | 60 | 22 | 11 | 10 | 100 | 235 | 65 | 10 | 10 | 84 | 0 | 12 | 0 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 10 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 |  | 916 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 5 | 0 | 0 | 280 | 0 | 0 | 178 | 0 | 0 | 0 | 12 | 0 | 184 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5129 | 2576 | 7705 | 4379 | 916 | 1582 | 334 | 280 | 122 | 0 | 80 | 12 | 0 | 103.51
9:00 | 36 | 220 | 0 | 0 | 300 | 0 | 0 | 363 | 323 |  | 0 | 270 | 120 | 0 | 30 | 2 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 21 | 0 | 82 | 40 | 75 | 0 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 60 | 0 | 19 | 2 | 0 | 0 | 100 | 300 | 305 | 181 | 45 | 87 | 23 | 56 | 0 | 24 | 0 | 0 | 0 | 22 | 5 | 30 | 6 | 80 | 154 | 16 | 20 | 0 | 60 | 22 | 44 | 38 | 130 | 230 | 65 | 59 | 43 | 70 | 0 | 43 | 10 | 300 | 24 | 11 | 0 | 20 | 0 | 0 | 0 | 0 | 115 | 13 | 10 | 26 | 0 | 0 | 8 | 105 | 0 | 4 | 16 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 5 | 0 | 0 | 280 | 0 | 0 | 198 | 0 | 0 | 0 | 50 | 0 | 212 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5659 | 2627 | 8286 | 4417 | 916 | 1877 | 576 | 280 | 122 | 0 | 80 | 18 | 0 | 103.51
10:00 | 36 | 189 | 0 | 0 | 300 | 0 | 0 | 361 | 323 |  | 0 | 370 | 120 | 0 | 30 | 40 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 28 | 33 | 33 | 52 | 0 | 82 | 40 | 75 | 0 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 60 | 8 | 19 | 2 | 0 | 0 | 100 | 360 | 325 | 165 | 45 | 87 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 19 | 5 | 33 | 18 | 90 | 152 | 83 | 20 | 0 | 60 | 22 | 44 | 49 | 100 | 232 | 30 | 75 | 42 | 72 | 0 | 44 | 10 | 300 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 149 | 16 | 10 | 52 | 0 | 0 | 8 | 104 | 0 | 4 | 16 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 13 | 5 | 0 | 0 | 280 | 0 | 0 | 174 | 0 | 0 | 0 | 42 | 0 | 182 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 6072 | 2553 | 8625 | 4353 | 916 | 1963 | 878 | 280 | 122 | 0 | 90 | 23 | 0 | 103.51
11:00 | 33 | 189 | 0 | 0 | 300 | 0 | 0 | 354 | 343 |  | 0 | 370 | 120 | 0 | 30 | 55 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 28 | 33 | 33 | 52 | 0 | 77 | 40 | 75 | 0 | 0 | 186 | 0 | 110 | 0 |  | 0 | 0 | 0 | 10 | 65 | 18 | 19 | 2 | 0 | 0 | 100 | 360 | 340 | 181 | 45 | 87 | 23 | 53 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 20 | 92 | 150 | 95 | 20 | 1 | 60 | 22 | 44 | 49 | 100 | 234 | 30 | 74 | 42 | 72 | 0 | 42 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 152 | 17 | 30 | 52 | 0 | 0 | 8 | 104 | 0 | 5 | 65 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 280 | 0 | 0 | 169 | 0 | 0 | 0 | 42 | 0 | 176 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 6211 | 2548 | 8759 | 4346 | 916 | 1990 | 992 | 280 | 117 | 0 | 92 | 26 | 0 | 103.5
12:00 | 36 | 158 | 0 | 0 | 300 | 0 | 0 | 360 | 349 |  | 0 | 370 | 100 | 0 | 32 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 8 | 33 | 33 | 47 | 0 | 82 | 40 | 75 | 0 | 0 | 179 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 78 | 18 | 19 | 2 | 0 | 0 | 100 | 360 | 310 | 170 | 45 | 87 | 23 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 20 | 94 | 149 | 95 | 20 | 1.1 | 60 | 22 | 44 | 49 | 100 | 230 | 30 | 71 | 42 | 69 | 0 | 42 | 10 | 305 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 142 | 13.8 | 50 | 82 | 0 | 0 | 16 | 105 | 0 | 5.2 | 116 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 14 | 0 | 0 | 0 | 280 | 0 | 10 | 173 | 0 | 0 | 0 | 42 | 0 | 176 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6 |  | 6261.1 | 2603.6 | 8864.7 | 4269 | 916 | 1991 | 1155 | 280 | 122 | 10 | 94 | 27.7 | 0 | 103.5
13:00 | 36 | 159 | 0 | 0 | 330 | 0 | 0 | 348 | 324 |  | 0 | 320 | 0 | 0 | 48 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 30 | 33 | 17 | 52 | 0 | 82 | 40 | 75 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 79 | 18 | 19 | 5 | 0 | 0 | 100 | 360 | 305 | 160 | 45 | 87 | 23 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 20 | 82 | 149 | 95 | 20 | 1 | 60 | 22 | 49 | 49 | 100 | 233 | 65 | 74 | 5 | 68 | 0 | 42 | 10 | 280 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 135 | 16 | 50 | 105 | 0 | 0 | 40 | 105 | 0 | 0 | 122 | 0 | 0 |  | 915 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 52 | 0 | 22 | 16 | 5 | 0 | 0 | 280 | 0 | 7 | 164 | 0 | 0 | 0 | 42 | 0 | 180 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 6 |  | 6175 | 2580 | 8755 | 4341 | 915 | 1822 | 1163 | 280 | 122 | 7 | 82 | 23 | 0 | 103.5
14:00 | 36 | 159 | 0 | 0 | 300 | 0 | 0 | 300 | 283 |  | 0 | 300 | 0 | 0 | 48 | 55 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 43 | 0 | 86 | 40 | 75 | 0 | 0 | 183 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 95 | 18 | 19 | 3 | 0 | 0 | 100 | 320 | 305 | 165 | 8 | 87 | 23 | 53 | 0 | 5 | 0 | 0 | 0 | 19 | 5 | 33 | 20 | 92 | 156 | 95 | 22 | 1 | 60 | 22 | 11 | 10 | 100 | 232 | 63 | 40 | 5 | 77 | 0 | 18 | 10 | 280 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 135 | 12 | 50 | 105 | 0 | 0 | 40 | 105 | 0 | 0 | 122 | 0 | 0 |  | 916 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 52 | 0 | 22 | 16 | 0 | 0 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 43 | 0 | 178 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5740 | 2600 | 8340 | 4139 | 916 | 1602 | 1170 | 280 | 126 | 0 | 92 | 15 | 0 | 103.5
15:00 | 36 | 159 | 0 | 0 | 300 | 0 | 0 | 300 | 283 |  | 0 | 300 | 0 | 0 | 48 | 55 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 25 | 17 | 5 | 0 | 25 | 30 | 33 | 33 | 47 | 0 | 86 | 40 | 75 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 97 | 18 | 19 | 2 | 0 | 0 | 100 | 320 | 320 | 168 | 8 | 87 | 23 | 49 | 0 | 5 | 0 | 0 | 0 | 19 | 5 | 33 | 20 | 94 | 156 | 95 | 0 | 0 | 60 | 22 | 11 | 10 | 100 | 242 | 64 | 40 | 43 | 73 | 0 | 18 | 10 | 310 | 24 | 11 | 0 | 85 | 0 | 0 | 0 | 0 | 135 | 7 | 50 | 105 | 0 | 0 | 40 | 105 | 0 | 2 | 122 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 52 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 174 | 0 | 0 | 0 | 42 | 0 | 172 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 4 |  | 5829 | 2619 | 8448 | 4158 | 916 | 1665 | 1196 | 280 | 126 | 0 | 94 | 13 | 0 | 103.5
16:00 | 36 | 159 | 0 | 0 | 300 | 0 | 0 | 300 | 283 |  | 0 | 300 | 0 | 0 | 80 | 55 | 220 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 46 | 0 | 0 | 53 | 35 | 55 | 0 | 25 | 30 | 33 | 33 | 52 | 0 | 86 | 40 | 75 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 97 | 18 | 19 | 3 | 0 | 0 | 100 | 320 | 285 | 159 | 8 | 86 | 0 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 5 | 33 | 20 | 102 | 157 | 50 | 0 | 0 | 60 | 32 | 11 | 10 | 100 | 242 | 65 | 40 | 10 | 68 | 0 | 18 | 10 | 290 | 24 | 11 | 0 | 65 | 0 | 0 | 0 | 0 | 135 | 8 | 50 | 70 | 0 | 0 | 8 | 105 | 0 | 0 | 126 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 179 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 162 | 0 | 0 | 0 | 42 | 0 | 165 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5745 | 2548 | 8293 | 4082 | 916 | 1606 | 1166 | 280 | 126 | 6 | 102 | 9 | 0 | 103.49
17:00 | 36 | 159 | 0 | 0 | 300 | 0 | 0 | 295 | 282 |  | 0 | 300 | 0 | 0 | 97 | 55 | 220 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 69 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 30 | 33 | 33 | 52 | 0 | 89 | 40 | 75 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 97 | 18 | 19 | 9 | 0 | 0 | 100 | 280 | 265 | 164 | 8 | 86 | 23 | 53 | 0 | 5 | 0 | 9 | 0 | 22 | 5 | 33 | 20 | 114 | 155 | 50 | 0 | 0 | 60 | 42 | 11 | 10 | 100 | 242 | 67 | 10 | 10 | 76 | 0 | 18 | 10 | 290 | 24 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 136 | 1 | 50 | 70 | 0 | 0 | 8 | 105 | 0 | 0 | 122 | 0 | 0 |  | 916 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 5 | 27 | 0 | 180 | 14 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 15 | 163 | 0 | 0 | 0 | 42 | 0 | 166 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5742 | 2589 | 8331 | 4051 | 916 | 1542 | 1232 | 280 | 129 | 66 | 114 | 1 | 0 | 103.49
18:00 | 36 | 158 | 0 | 0 | 300 | 0 | 0 | 280 | 324 |  | 0 | 300 | 0 | 11 | 97 | 55 | 220 | 0 | 0 | 0 | 32 | 7 | 100 | 0 | 69 | 0 | 3 | 53 | 47 | 55 | 19 | 25 | 20 | 33 | 33 | 52 | 0 | 89 | 40 | 75 | 0 | 16 | 204 | 0 | 104 | 0 |  | 0 | 0 | 85 | 10 | 97 | 18 | 19 | 5 | 0 | 0 | 100 | 250 | 270 | 173 | 8 | 86 | 23 | 55 | 0 | 5 | 0 | 0 | 7 | 22 | 5 | 33 | 20 | 134 | 154 | 75 | 0 | 0 | 60 | 22 | 40 | 20 | 100 | 244 | 68 | 70 | 10 | 113 | 0 | 44 | 0 | 275 | 8 | 0 | 0 | 62 | 0 | 0 | 7 | 0 | 135 | 0 | 100 | 94 | 3 | 0 | 38 | 105 | 0 | 0 | 160 | 0 | 0 |  | 916 | 0 | 346 | 0 | 59 | 0 | 0 | 0 | 31 | 51 | 40 | 179 | 21 | 48 | 0 | 0 | 0 | 50 | 32 | 51 | 50 | 42 | 34 | 37 | 10 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 18 | 162 | 0 | 0 | 0 | 67 | 0 | 160 | 0 | 330 | 53 | 0 | 20 | 43 | 60 | 0 | 0 |  | 6289 | 3234 | 9523 | 4029 | 916 | 1713 | 1860 | 280 | 129 | 462 | 134 | 0 | 0 | 103.49
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 36 | 159 | 0 | 0 | 270 | 0 | 0 | 345 | 284 |  | 0 | 300 | 0 | 48 | 97 | 55 | 220 | 0 | 0 | 0 | 65 | 7 | 90 | 0 | 69 | 0 | 47 | 53 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 40 | 75 | 0 | 25 | 204 | 0 | 134 | 0 |  | 0 | 0 | 85 | 20 | 97 | 40 | 19 | 7 | 0 | 0 | 100 | 300 | 260 | 180 | 8 | 88 | 23 | 56 | 0 | 22 | 0 | 0 | 23 | 22 | 8 | 33 | 20 | 130 | 157 | 95 | 0 | 0 | 60 | 22 | 42 | 49 | 100 | 245 | 66 | 78 | 43 | 70 | 0 | 43 | 10 | 270 | 16 | 5 | 0 | 110 | 0 | 0 | 7 | 0 | 135 | 0 | 100 | 180 | 33 | 0 | 115 | 52 | 0 | 0 | 162 | 0 | 0 |  | 916 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 37 | 76 | 40 | 179 | 23 | 64 | 0 | 0 | 0 | 50 | 0 | 51 | 50 | 50 | 0 | 52 | 30 | 22 | 17 | 11 | 0 | 0 | 280 | 0 | 17 | 159 | 0 | 0 | 0 | 52 | 0 | 157 | 0 | 307 | 70 | 0 | 70 | 59 | 95 | 0 | 0 |  | 6822 | 3389 | 10211 | 4124 | 916 | 1733 | 2462 | 280 | 130 | 436 | 130 | 0 | 0 | 103.49
19:30 | 36 | 158 | 0 | 0 | 270 | 0 | 0 | 345 | 314 |  | 0 | 370 | 0 | 7 | 97 | 55 | 290 | 0 | 0 | 0 | 70 | 0 | 32 | 0 | 69 | 0 | 47 | 53 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 40 | 75 | 0 | 25 | 204 | 0 | 134 | 0 |  | 0 | 0 | 36 | 20 | 97 | 50 | 19 | 11 | 0 | 0 | 100 | 330 | 275 | 180 | 8 | 86 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 136 | 157 | 95 | 0 | 0 | 60 | 22 | 42 | 49 | 100 | 242 | 68 | 78 | 43 | 72 | 0 | 45 | 10 | 280 | 16 | 3 | 0 | 15 | 0 | 0 | 0 | 0 | 135 | 0 | 100 | 180 | 50 | 0 | 115 | 52 | 0 | 0 | 160 | 0 | 0 |  | 916 | 0 | 345 | 0 | 80 | 0 | 0 | 0 | 37 | 70 | 40 | 179 | 24 | 64 | 0 | 0 | 0 | 50 | 0 | 51 | 0 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 16 | 17 | 160 | 0 | 0 | 0 | 51 | 0 | 155 | 0 | 390 | 70 | 0 | 113 | 54 | 97 | 0 | 0 |  | 6818 | 3411 | 10229 | 4239 | 916 | 1945 | 2274 | 280 | 130 | 309 | 136 | 0 | 0 | 103.49
20:00 | 36 | 159 | 0 | 0 | 290 | 0 | 0 | 344 | 357 |  | 0 | 400 | 0 | 0 | 97 | 55 | 350 | 0 | 0 | 0 | 70 | 0 | 32 | 0 | 69 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 40 | 75 | 0 | 25 | 203 | 0 | 134 | 0 |  | 0 | 0 | 34 | 20 | 97 | 48 | 19 | 21 | 0 | 0 | 100 | 330 | 275 | 180 | 8 | 86 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 132 | 156 | 95 | 0 | 0 | 60 | 22 | 42 | 49 | 130 | 243 | 68 | 78 | 43 | 110 | 0 | 45 | 10 | 290 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 100 | 181 | 0 | 0 | 115 | 52 | 0 | 0 | 160 | 0 | 0 |  | 916 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 37 | 69 | 40 | 179 | 25 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 17 | 17 | 160 | 0 | 0 | 0 | 51 | 0 | 157 | 0 | 429 | 70 | 0 | 113 | 54 | 100 | 0 | 0 |  | 6932 | 3352 | 10284 | 4353 | 916 | 2108 | 2109 | 280 | 130 | 256 | 132 | 0 | 0 | 103.48
21:00 | 36 | 159 | 0 | 0 | 300 | 0 | 0 | 345 | 357 |  | 0 | 400 | 0 | 0 | 97 | 55 | 346 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 40 | 75 | 40 | 8 | 204 | 0 | 134 | 0 |  | 0 | 0 | 34 | 20 | 97 | 16 | 19 | 27 | 0 | 0 | 100 | 330 | 280 | 188 | 8 | 87 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 132 | 157 | 95 | 0 | 0 | 60 | 32 | 42 | 49 | 130 | 242 | 68 | 78 | 40 | 115 | 0 | 45 | 0 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 100 | 180 | 0 | 0 | 40 | 18 | 0 | 0 | 162 | 0 | 0 |  | 916 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 37 | 48 | 0 | 179 | 26 | 48 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 0 | 280 | 0 | 17 | 163 | 0 | 0 | 0 | 51 | 0 | 166 | 0 | 430 | 70 | 0 | 0 | 50 | 104 | 0 | 0 |  | 6728 | 3124 | 9852 | 4455 | 916 | 2113 | 1608 | 280 | 130 | 218 | 132 | 0 | 0 | 103.48
22:00 | 36 | 158 | 0 | 0 | 300 | 0 | 0 | 344 | 357 |  | 0 | 400 | 0 | 0 | 97 | 30 | 350 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 40 | 75 | 60 | 8 | 203 | 0 | 134 | 0 |  | 0 | 0 | 17 | 20 | 97 | 0 | 19 | 34 | 0 | 0 | 100 | 330 | 290 | 180 | 8 | 87 | 23 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 124 | 157 | 95 | 0 | 0 | 60 | 42 | 42 | 49 | 130 | 245 | 68 | 78 | 40 | 115 | 0 | 44 | 0 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 100 | 180 | 0 | 0 | 72 | 0 | 0 | 0 | 162 | 0 | 0 |  | 916 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 37 | 4 | 0 | 179 | 26 | 48 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 280 | 0 | 17 | 159 | 0 | 0 | 0 | 51 | 0 | 164 | 0 | 422 | 17 | 0 | 0 | 50 | 76 | 0 | 0 |  | 6592 | 2891 | 9483 | 4485 | 916 | 2090 | 1359 | 280 | 130 | 99 | 124 | 0 | 0 | 103.51
23:00 | 36 | 158 | 0 | 0 | 300 | 0 | 0 | 345 | 358 |  | 0 | 400 | 0 | 0 | 97 | 30 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 82 | 40 | 75 | 80 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 19 | 34 | 0 | 0 | 100 | 330 | 290 | 182 | 8 | 87 | 23 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 134 | 155 | 95 | 0 | 0 | 60 | 42 | 42 | 49 | 130 | 232 | 67 | 78 | 40 | 110 | 0 | 44 | 0 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 100 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 180 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 162 | 0 | 0 | 0 | 51 | 0 | 164 | 0 | 425 | 0 | 0 | 0 | 50 | 0 | 0 | 0 |  | 6338 | 2755 | 9093 | 4494 | 916 | 2108 | 1024 | 280 | 122 | 15 | 134 | 0 | 0 | 103.51
24:00 | 36 | 159 | 0 | 0 | 300 | 0 | 0 | 360 | 358 |  | 0 | 400 | 0 | 0 | 80 | 30 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 80 | 40 | 75 | 100 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 97 | 0 | 19 | 32 | 0 | 0 | 100 | 330 | 300 | 190 | 8 | 87 | 23 | 53 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 128 | 154 | 48 | 0 | 0 | 60 | 53 | 42 | 49 | 130 | 232 | 68 | 78 | 40 | 120 | 0 | 44 | 0 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 280 | 0 | 0 | 172 | 0 | 0 | 0 | 72 | 0 | 164 | 0 | 430 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 6178 | 2669 | 8847 | 4577 | 916 | 2143 | 683 | 280 | 120 | 0 | 128 | 0 | 0 | 103.51
KWH | 754000 | 4180300 | 0 | 0 | 7847918 | 0 | 0 | 8293170 | 7745000 |  | 0 | 6080000 | 1645963 | 83520 | 1432272 | 775981 | 7189800 | 0 | 0 | 0 | 256752 | 17568 | 251520 | 0 | 706560 | 0 | 97392 | 435240 | 402708 | 327560 | 332172 | 600000 | 682380 | 789300 | 796100 | 702156 | 0 | 1944976 | 976000 | 1800000 | 200000 | 93915 | 4827317 | 0 | 3008002 | 0 |  | 0 | 0 | 245676 | 313200 | 2008320 | 262560 | 440784 | 506880 | 0 | 0 | 2404320 | 8252700 | 7414000 | 4002000 | 936727 | 2059120 | 514080 | 1318080 | 0 | 575316 | 0 | 7968 | 33446 | 480276 | 178380 | 629600 | 478980 | 2456640 | 3649040 | 1654080 | 291456 | 7900 | 1427000 | 619080 | 720600 | 914616 | 2926227 | 5286000 | 1503936 | 1261440 | 789480 | 2317080 | 0 | 850520 | 151740 | 7281500 | 540096 | 208176 | 0 | 963491 | 0 | 0 | 19200 | 0 | 2783520 | 120015 | 1240320 | 2318400 | 75272 | 0 | 666000 | 1180920 | 0 | 23760 | 2391164 | 0 | 0 |  | 21962181 | 0 | 8492832 | 0 | 231360 | 0 | 0 | 0 | 207840 | 276992 | 126000 | 4367405 | 479280 | 382080 | 0 | 0 | 0 | 218947 | 54030 | 105520 | 65540 | 385483 | 32139 | 409440 | 27232 | 481440 | 356904 | 137556 | 0 | 0 | 6794900 | 16000 | 101000 | 4388373 | 0 | 0 | 0 | 1247361 | 0 | 4450227 | 0 | 9244330 | 330240 | 0 | 268800 | 531936 | 452160 | 0 | 29286 |  | 144976624 | 66654814 | 211631438 | 105832956 | 21962181 | 43867441 | 26070519 | 6794900 | 2920976 | 1544864 | 2456640 | 180961 | 0
Fuel Cost | 844480 | 4514724 | 0 | 0 | 5807459.32 | 0 | 0 | 5971082.4 | 5886200 |  | 0 | 4864000 | 1481366.7 | 851904 | 15511505.76 | 7961565.06 | 8915352 | 0 | 0 | 0 | 2849947.2 | 178490.88 | 2492563.2 | 0 | 6429696 | 0 | 911589.12 | 4173951.6 | 3841834.32 | 3262497.6 | 249129 | 450000 | 0 | 0 | 0 | 6726654.48 | 0 | 505693.76 | 253760 | 2754000 | 306000 | 902523.15 | 5068682.85 | 0 | 3820162.54 | 0 |  | 0 | 0 | 2577141.24 | 3222828 | 19099123.2 | 2457561.6 | 405521.28 | 1409126.4 | 0 | 0 | 2524536 | 6106998 | 6227760 | 3681840 | 917992.46 | 2738629.6 | 421545.6 | 1357622.4 | 0 | 822701.88 | 0 | 93384.96 | 314392.4 | 489881.52 | 133785 | 1189944 | 359235 | 16950816 | 2992212.8 | 15730300.8 | 297285.12 | 129560 | 1940720 | 841948.8 | 980016 | 1143270 | 3628521.48 | 4863120 | 2240864.64 | 2220134.4 | 876322.8 | 3521961.6 | 0 | 995108.4 | 356589 | 5169865 | 405072 | 158213.76 | 0 | 10087750.77 | 0 | 0 | 184704 | 0 | 28085716.8 | 1384973.1 | 11559782.4 | 21746592 | 705298.64 | 0 | 5840820 | 10521997.2 | 0 | 0 | 22046532.08 | 0 | 0 |  | 59297888.7 | 0 | 6624408.96 | 0 | 2230310.4 | 0 | 0 | 0 | 2410944 | 3628595.2 | 1246140 | 3493924 | 742884 | 4103539.2 | 0 | 0 | 0 | 2439069.58 | 661867.5 | 1044648 | 679649.8 | 4514005.93 | 387274.95 | 4078022.4 | 268235.2 | 529584 | 588891.6 | 104129.892 | 0 | 0 | 27791141 | 535200 | 2851230 | 3861768.24 | 0 | 0 | 0 | 1983303.99 | 0 | 3916199.76 | 0 | 6748360.9 | 3124070.4 | 0 | 2467584 | 4739549.76 | 4223174.4 | 0 | 0 |  | 341944435.07 | 161315595.762 | 503260030.832 | 98242577.682 | 59297888.7 | 41220494.71 | 238092972.05 | 27791141 | 759453.76 | 19390153.83 | 16950816 | 1514533.1 | 0
Yesterday Day Peak | 36 | 158 | 0 | 0 | 300 | 0 | 0 | 360 | 349 |  | 0 | 370 | 100 | 0 | 32 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 8 | 33 | 33 | 47 | 0 | 82 | 40 | 75 | 0 | 0 | 179 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 78 | 18 | 19 | 2 | 0 | 0 | 100 | 360 | 310 | 170 | 45 | 87 | 23 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 20 | 94 | 149 | 95 | 20 | 1.1 | 60 | 22 | 44 | 49 | 100 | 230 | 30 | 71 | 42 | 69 | 0 | 42 | 10 | 305 | 24 | 11 | 0 | 95 | 0 | 0 | 0 | 0 | 142 | 13.76 | 50 | 82 | 0 | 0 | 16 | 105 | 0 | 5.2 | 116 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 14 | 0 | 0 | 0 | 280 | 0 | 10 | 173 | 0 | 0 | 0 | 42 | 0 | 176 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6 |  | 8864.66 | DayPeak
Yesterday Evening Peak | 36 | 159 | 0 | 0 | 290 | 0 | 0 | 344 | 357 | 0 | 0 | 400 | 0 | 0 | 97 | 55 | 350 | 0 | 0 | 0 | 70 | 0 | 32 | 0 | 69 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 90 | 40 | 75 | 0 | 25 | 203 | 0 | 134 | 0 | 0 | 0 | 0 | 34 | 20 | 97 | 48 | 19 | 21 | 0 | 0 | 100 | 330 | 275 | 180 | 8 | 86 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 132 | 156 | 95 | 0 | 0 | 60 | 22 | 42 | 49 | 130 | 243 | 68 | 78 | 43 | 110 | 0 | 45 | 10 | 290 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 100 | 181 | 0 | 0 | 115 | 52 | 0 | 0 | 160 | 0 | 0 |  | 916 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 37 | 69 | 40 | 179 | 25 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 280 | 17 | 17 | 160 | 0 | 0 | 0 | 51 | 0 | 157 | 0 | 429 | 70 | 0 | 113 | 54 | 100 | 0 | 0 |  | 10284 | EvPeak
Forecast for Evening | 38 | 210 | 0 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 90 | 50 | 75 | 100 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 97 | 50 | 22 | 20 | 0 | 0 | 100 | 360 | 360 | 225 | 83 | 90 | 33 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 168 | 155 | 95 | 22 | 0 | 60 | 30 | 51 | 50 | 163 | 240 | 68 | 82 | 47 | 130 | 0 | 43 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 | 54 | 113 |  | 918 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 75 | 40 | 182 | 33 | 110 | 30 | 0 | 0 | 50 | 45 | 92 | 50 | 50 | 46 | 52 | 35 | 22 | 20 | 11 | 0 | 0 | 280 | 16 | 17 | 214 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 38 | 210 | 0 | 0 | 365 | 0 | 0 | 375 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 90 | 50 | 75 | 100 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 100 | 97 | 50 | 22 | 10 | 0 | 0 | 100 | 360 | 360 | 200 | 83 | 90 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 129 | 155 | 95 | 22 | 1.6 | 60 | 30 | 51 | 50 | 163 | 230 | 68 | 82 | 47 | 110 | 0 | 43 | 10 | 335 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 0 | 4.4 | 230 | 54 | 113 |  | 918 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 182 | 33 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 30 | 50 | 46 | 52 | 0 | 22 | 20 | 11 | 0 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 36 | 159 | 0 | 0 | 280 | 0 | 0 | 375 | 352 | 0 | 0 | 320 | 0 | 0 | 30 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 86 | 40 | 75 | 100 | 0 | 217 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 19 | 2 | 0 | 0 | 80 | 305 | 300 | 180 | 8 | 86 | 23 | 10 | 0 | 10 | 0 | 8 | 0 | 0 | 3 | 0 | 12 | 100 | 154 | 22 | 0 | 0.3 | 16 | 22 | 11 | 10 | 100 | 222 | 67 | 10 | 10 | 84 | 0 | 12 | 0 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 16 | 0 | 0 | 0 | 614 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 280 | 0 | 0 | 176 | 0 | 0 | 0 | 11 | 0 | 179 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0
199
| Minimum Generation |  | 7421 | 7:00
| Highest Generation |  | 10284 | 20:00
| Day Peak Generation |  | 8864.66 | 12:00
| Evening Peak Generation |  | 10284 | 20:00
| HVDC Max Flow |  | 916 | 6:00
| HVDC EvPeak Flow |  | 916 | 20:00
| Load factor L.F |  | 85.74%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8864.66 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6980.386 | MW
Evening Peak Generation : |  | 10284 | MW Hour : | 20:00 | Available Max Generation : |  | 15063 | MW
E.P. Demand (at gen end) : |  | 10284 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 10284 | MW Hour : | 20:00 | Reserve(Generation end) |  | 4563 | MW
Total Gen. (MKWH) : |  | 211.6314 | System Load Factor : | 85.74% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 124 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-10
Actual : | 103.46 | Ft.(MSL) , | Rule curve : | 106.81 | Ft.( MSL )
Gas Consumed : | Total = | 1202.93 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 139463072.392
|  | Coal : | 27791141 | Oil : | 257483125.88 | Total : | 424737339.272
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3701.8848 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1257.0618 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1125.9678 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1017.294 |  |  | 0 | 0%
) | 0 | 0:00 | 919.3761 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 741.8995 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 417.1293 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 191.0799 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 572.1787 |  |  | 0 | 0%
Total | 0 |  | 9943.872 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorasal Unit-1,4 & 5
|  |  |  | 2) Khulna ST 110 MW | 8) Chattogram TPP-2
3) Sikalbaha ST 60 MW
4) Siddhirganj ST
5) Ashuganj #3,4
6) Baghabari 100 MW,
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Rangamati-Khagrachori 132 kV Ckt-1 was under shut down from 08:17 to 17:03 for A/M.
b) Aminbazar-Agargaon 132 kV Ckt- 2 was under shut down at 09:55 to 13:53 for C/M.
c) Barapukuria-Saidpur 132 kV Ckt-2 was under shut down from 10:40 to 00:43(10/10/2019) for C/M.
d) Saidpur 132/33 kV T4 transformer was under shut down from 08:40 to 11:45 for A/M.
e) Summit Meghnaghat CCPP GT-1 was shut down at 12:18 due to gas shortage.
f) Ashuganj-Kishorganj 132 kV Ckt-1 tripped at 15:50 from both end showing Dist. Z1 R-phase at
Kishorganj end & Dist. A-phase at Ashuganj end and was switched on at 16:20.
g) Jamalpur 132/33 kV T4 transformer was under shut down from 22:10 to 23:43 due to red hot |  |  |  |  | About 5 MW power interruption occurred under Jamalpur S/S area
maintenance at 33 kV DS. |  |  |  |  | from 22:10 to 23:43.
h) Feni 132/33 kV T1 & T2 transformers tripped at 00:12(10/10/2019) sowing O/C relays due to 33 kV |  |  |  |  | About 25 MW power interruption occurred under Feni S/S area
feeder CT burst and were switched on at 00:54,01:54(10/10/2019) respectively. |  |  |  |  | from00:12(10/10/2019) to 00:54(10/10/2019).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 36 | 754000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 159 | 4180300 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 290 | 7847918 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Engine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8293170 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 357 | 7745000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 6080000 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 83520 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 1645963 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1432272
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 775981
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 332172 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 70 | 256752 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 350 | 7189800
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 17568 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 97392 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 435240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 251520 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 402708
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 327560
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 69 | 706560 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1282380 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 789300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 796100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 702156
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 963491 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 135 | 2783520 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 1180920 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2802 | 57353263
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 75 | 1800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 200000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 93915
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120015
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 262560
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 130 | 2920976
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4827317 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 134 | 3008002 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 245676 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 313200 | Line overload
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1240320
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440784 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 506880
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 2008320 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23760
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 160 | 2391164 | Transformer overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer overload
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer overload
| Chattogram area Total |  |  |  | 2166 | 1066 | 20402889
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2404320 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4002000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 8252700 | Gas shortage
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7414000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 514080 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1318080
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 936727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 575316 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 75272 | Transformer overload
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 7968 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2059120 | Engine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 181 | 2318400 | Load increasing
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 480276
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 178380 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 2456640
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 629600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 33446 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 478980 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1489 | 34135305
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3649040 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 291456 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1654080
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7900
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 19200 | High voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 666000
| Mymensingh Area Total |  |  |  | 637 | 366 | 6287676
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1427000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 619080
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2926227 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 243 | 5286000 | ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 42 | 720600 | Engine problem
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 914616
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 208176 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1503936 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1261440
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 43 | 789480 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 110 | 2317080 | FGMO
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 45 | 850520 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 540096 | Engine problem
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7281500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under S/D
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 151740
| Sylhet Area Total |  |  |  | 1949 | 1209 | 26797491
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 916 | 21962181
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 231360 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 207840
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 69 | 276992
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8492832 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 126000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 330240 | Line overload
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 54 | 531936 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1558 | 32159381
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 382080 | Line overload
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 479280 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 179 | 4367405 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 51 | 1247361 | Line overload
| Barisal Area Total |  |  |  | 462 | 319 | 6476126
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under shut down.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 218947
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 54030 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 65540 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 385483
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 32139 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4388373 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 157 | 4450227 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 429 | 9244330 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 27232 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 481440
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 17 | 356904
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 137556
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 409440
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 105520 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 268800
| Rajshahi Area Total |  |  |  | 2070 | 1061 | 20625961
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6794900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 16000
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 101000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 100 | 452160
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29286
| Rangpur Area Total |  |  |  | 605 | 414 | 7393346
| Total |  |  |  | 18905 | 10284 | 211631438
| Eastern Grid Total |  |  |  | 13454 | 6932 | 144976624
| Western Grid Total |  |  |  | 5451 | 3352 | 66654814
| National Grid Total |  |  |  | 18905 | 10284 | 211631438
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-09
(a) ENTIRE EASTERN GRID : |  | 6790 | MW | (b) ENTIRE WESTERN GRID : |  | 2937 | MW
i) Dhaka area |  | 3805 | MW | i) Khulna area |  | 1148 | MW
ii) Chittagong area |  | 1036 | MW | ii) Rajshahi area |  | 918 | MW
iii) Comilla area |  | 904 | MW | iii) Barisal area |  | 283 | MW
iv) Mymensingh area |  | 680 | MW | iv) Rangpur area |  | 588 | MW
v) Sylhet area |  | 365 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9727 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1800 | Sherpur | 72 | 1830 | Jhenida | 92 | 1830
Munsiganj | 104 | 1930 | Srimongal | 33 | 2000 | Bottail | 110 | 1830
Sonargaon | 71 | 200 | Shahjibazar | 93 | 1930 | G.K Project | 48 | 1900
Shyampur | 192 | 100 | Fenchuganj | 28 | 2100 | Faridpur | 154 | 1930
Bhulta | 181 | 1900 | Kulawara | 29 | 1500 | Madaripur | 74 | 2000
Madanganj | 50 | 1800 | Sylhet | 125 | 1930 | Sariatpur | 46 | 1930
Shitalakhya | 109 | 1200 | Chatak | 27 | 1900 | Gopalganj | 75 | 1830
Rahim steel | 23 | 1700 | Sunamganj | 31 | 2000 | Bagerhat | 71 | 1830
Matuail | 92 | 1000 | Biani Bazar | 48 | 1800 | Mongla | 83 | 1400
Ghorasal | 75 | 1930 | Comilla (S) | 136 | 1930 | Satkhira | 73 | 1930
Narsingdi | 147 | 2000 | Comilla(N) | 125 | 1830 | Gallamari | 40 | 1200
Haripur (SBU) | 84 | 2000 | Chandpur | 101 | 1830 | Magura | 40 | 1800
Ullon | 77 | 1800 | Feni | 144 | 2000 | Norail | 26 | 1800
Hasnabad | 184 | 2000 | Chowmuhani | 49 | 1300 | Chuadanga | 76 | 1830
Magbazar | 120 | 1300 | Ashuganj | 118 | 1830 | Barisal(N) | 35 | 1930
Maniknagar | 112 | 1200 | Daudkandi | 120 | 1900 | Barisal (S) | 90 | 1800
Bangabhaban | 36 | 1200 | B.Baria | 80 | 1800 | Patuakhali | 96 | 1930
Narinda | 94 | 1300 | Ramganj | 51 | 2000 | Bhandaria | 42 | 1900
Dhanmondi | 165 | 1200 | Madunaghat | 92 | 1830 | Borhan Uddin | 29 | 100
Lalbag | 84 | 1800 | Hathazari | 92 | 1830 | Ishurdi | 53 | 1830
Madartek | 55 | 2000 | Khulshi | 185 | 1600 | Ruppur Paromanobik | 1 | 100
Mirpur | 101 | 1800 | Halishahar | 140 | 1100 | Natore | 101 | 1900
Kalyanpur | 111 | 1830 | Baraulia | 147 | 1000 | Bogra | 148 | 1930
Gulshan | 160 | 1000 | Sikalbaha | 20 | 1200 | Noagaon | 86 | 2000
Uttara | 55 | 1200 | Dohazari | 76 | 1900 | Rajshahi | 111 | 1830
Uttara New | 41 | 1100 | Cox'sbazar | 82 | 2100 | Rajshahi New | 8 | 1830
Kamrangirchar | 70 | 1830 | Chandraghona | 36 | 1930 | C.Nawabganj | 52 | 1900
Savar | 126 | 1200 | Kaptai | 4 | 1800 | Amnura | 22 | 1900
Bhasantec | 159 | 1300 | A. Khaer Stl. | 0 | 0 | Pabna | 92 | 1830
Agargaon | 60 | 1300 | Bakulia | 104 | 1830 | Shahjadpur | 79 | 1900
Satmosjid | 92 | 1800 | Julda | 19 | 900 | Serajganj | 84 | 1930
Tongi | 148 | 1200 | TK chemical | 14 | 1830 | Niyamatpur | 45 | 1930
Kabirpur | 97 | 1800 | Modern Steel | 16 | 1300 | Joypurhat | 39 | 2000
Basundhara | 80 | 1900 | Shahmirpur | 29 | 1800 | Sherpur(Bogura) | 31 | 1800
Manikganj | 199 | 1800 | Khagrachhari | 16 | 1830 | Mohastangor | 13 | 1830
Joydevpur | 103 | 1200 | Matarbari | 25 | 1930 | Rangpur | 118 | 1830
New Tongi | 233 | 1000 | Baroiar Hat | 30 | 1900 | Lalmonirhat | 51 | 1930
Korda | 58 | 1830 | Rangamati | 12 | 1800 | Saidpur | 98 | 1830
Dhamrai | 80 | 1000 | Abul Khair 230 | 147 | 700 | Purbasadipur | 82 | 1830
Valuka | 80 | 1000 | BSRM | 102 | 1800 | Thakurgaon | 58 | 1930
Tangail | 140 | 1830 | Goalpara | 32 | 1930 | Palashbari | 85 | 1830
Mymensing | 165 | 1300 | Central s/s | 69 | 1830 | Barapukuria | 41 | 1900
Kishorganj | 96 | 100 | Noapara | 48 | 1900 | Panchagar | 40 | 1830
Netrokona | 68 | 100 | Jessore | 90 | 1900 | Joldhaka | 20 | 1900
Jamalpur | 88 | 1900 | Benapol | 28 | 1900 | Kurigram | 32 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-09 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 382 | 13:00 | 375 | 10:00 | Kaliakoir | 360 | 18:00 | 351 | 8:00
Bheramara | 397 | 3:00 | 394 | 18:30 | Bhulta | 370 | 20:00 | 360 | 11:00
Ashuganj(N) | 377 | 6:00 | 368 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
Ghorasal | 222 | 1:00 | 222 | 1:00 | Hathazari | 218 | 1:00 | 209 | 9:00
Ishurdi | 235 | 18:00 | 229 | 4:00 | Megnaghat | 218 | 19:00 | 212 | 10:00
Ashuganj | 228 | 18:30 | 223 | 15:00 | Fenchuganj | 232 | 18:30 | 227 | 11:00
Serajganj | 230 | 5:00 | 226 | 13:00 | Siddhirganj | 216 | 3:00 | 210 | 11:00
Baghabari | 234 | 18:30 | 230 | 10:00 | Maniknagar | 215 | 6:00 | 208 | 11:00
Barapukuria | 230 | 6:00 | 223 | 23:00 | Old Airport | 214 | 6:00 | 205 | 11:00
Bogra | 227 | 18:00 | 220 | 22:00 | Barisal | 231 | 18:00 | 222 | 24:00
Khulna South | 229 | 18:00 | 212 | 1:00 | AKSML | 215 | 2:00 | 204 | 9:00
Rampura | 215 | 4:00 | 210 | 10:00 | BSRM | 216 | 6:00 | 208 | 9:00
Haripur | 215 | 5:00 | 210 | 10:00 | Bibiyana | 229 | 14:00 | 224 | 6:00
Hasnabad | 214 | 18:30 | 209 | 10:00 | Bhulta | 217 | 6:00 | 210 | 11:00
Aminbazar | 215 | 19:00 | 209 | 11:00 | Ashuganj (S) | 228 | 18:30 | 223 | 11:00
Tongi | 215 | 13:00 | 210 | 1:00 | Kaliakoir | 220 | 18:00 | 211 | 23:00
Comilla (N) | 224 | 18:30 | 217 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 130 | 1800 | 124 | 1100 | Halishahar | 132 | 1830 | 124 | 1000
Munsiganj | 134 | 1830 | 123 | 1100 | Baraulia | 129 | 1300 | 121 | 1000
Megnaghat | 129 | 1830 | 123 | 100 | Sikalbaha | 132 | 1800 | 126 | 1000
Shyampur | 131 | 1830 | 124 | 1100 | Dohazari | 132 | 1830 | 124 | 900
Bhulta | 125 | 1800 | 118 | 1100 | Cox'sbazar | 125 | 1300 | 118 | 500
Madanganj | 130 | 1800 | 123 | 1100 | Chandraghona | 131 | 1830 | 126 | 1000
Shitalakhya | 132 | 1830 | 125 | 1100 | Kaptai | 130 | 100 | 125 | 1100
Rahim steal | 131 | 1800 | 125 | 1000 | A. Khaer Stl. | 129 | 400 | 124 | 1000
Matuail | 129 | 1900 | 123 | 1100 | Bakulia | 131 | 1830 | 124 | 1000
Ghorasal | 135 | 1800 | 132 | 100 | Julda | 131 | 1830 | 125 | 900
Narsinghdi | 131 | 1400 | 127 | 100 | TK Chemical | 131 | 1830 | 125 | 1000
Haripur (SBU) | 130 | 700 | 125 | 1100 | Modern Steel | 131 | 1800 | 124 | 900
Ullon | 131 | 600 | 124 | 1200 | Shahmirpur | 131 | 1830 | 125 | 900
Hasnabad | 130 | 1800 | 126 | 1200 | Khagrachhari | 130 | 1830 | 124 | 1000
Magbazar | 133 | 500 | 124 | 1100 | Matarbari | 128 | 1300 | 119 | 800
Maniknagar | 130 | 600 | 124 | 1100 | Baroiar Hat | 125 | 1500 | 121 | 1000
Bangabhaban | 130 | 600 | 124 | 1100 | Rangamati | 131 | 1830 | 125 | 1000
Narinda | 130 | 600 | 124 | 1100 | Goalpara | 138 | 1830 | 127 | 100
Dhanmondi | 130 | 600 | 124 | 1100 | Central s/s | 137 | 1800 | 125 | 200
Lalbag | 129 | 600 | 121 | 1100 | Noapara | 135 | 1800 | 123 | 2200
Madartek | 131 | 600 | 124 | 1000 | Jessore | 129 | 1800 | 120 | 2100
Mirpur | 132 | 600 | 124 | 1100 | Benapol | 129 | 1800 | 120 | 100
Kalyanpur | 134 | 600 | 127 | 1100 | Jhenida | 129 | 600 | 121 | 100
Gulshan | 131 | 600 | 121 | 1100 | Bottail | 134 | 1700 | 129 | 2100
Uttara | 130 | 1830 | 125 | 800 | G.K Project | 141 | 1800 | 137 | 100
Uttara New | 130 | 400 | 123 | 1100 | Faridpur | 132 | 1800 | 126 | 100
Kamrangirchar | 129 | 600 | 122 | 1000 | Madaripur | 135 | 1800 | 124 | 2200
Savar | 131 | 1900 | 123 | 1100 | Sariatpur | 132 | 1800 | 114 | 2100
Bhasantec | 133 | 600 | 124 | 1100 | Gopalganj | 141 | 1800 | 125 | 400
Agargaon | 135 | 700 | 126 | 1200 | Bagerhat | 135 | 1800 | 126 | 1300
Satmosjid | 134 | 600 | 126 | 1100 | Mongla | 132 | 1800 | 123 | 2200
Tongi | 134 | 1300 | 128 | 800 | Satkhira | 138 | 1800 | 125 | 100
Kabirpur | 130 | 1400 | 123 | 1100 | Gallamari | 138 | 1800 | 128 | 100
Basundhara | 131 | 300 | 121 | 1300 | Magura | 127 | 900 | 120 | 100
Manikganj | 138 | 1300 | 127 | 800 | Norail | 126 | 600 | 119 | 100
Joydevpur | 137 | 1900 | 128 | 1200 | Chuadanga | 125 | 600 | 116 | 100
New Tongi | 132 | 1300 | 126 | 100 | Barisal(N) | 137 | 1800 | 131 | 400
Kodda | 136 | 1300 | 118 | 800 | Barisal (S) | 136 | 1800 | 130 | 1300
Dhamrai | 131 | 1400 | 124 | 1100 | Patuakhali | 132 | 900 | 126 | 1400
Valuka | 130 | 1500 | 115 | 800 | Bhandaria | 134 | 1800 | 125 | 2200
Tangail | 135 | 1400 | 121 | 1100 | Ishurdi | 139 | 1800 | 135 | 100
Mymensing | 133 | 1500 | 120 | 800 | Ruppur Paromanobik | 138 | 1700 | 136 | 100
Kishorganj | 133 | 1500 | 124 | 1100 | Natore | 138 | 1700 | 130 | 100
Netrokona | 131 | 1500 | 118 | 1100 | Bogra | 138 | 1900 | 133 | 1300
Jamalpur | 138 | 1500 | 121 | 500 | Noagaon | 134 | 1800 | 130 | 1500
Sherpur | 137 | 1830 | 116 | 800 | Rajshahi | 136 | 1800 | 125 | 100
Srimongal | 135 | 900 | 134 | 100 | Rajshahi New | 139 | 1830 | 125 | 1100
Shahjibazar | 137 | 1900 | 131 | 400 | C.Nawabganj | 133 | 1830 | 121 | 1100
Fenchuganj | 134 | 1930 | 130 | 500 | Amnura | 139 | 1800 | 124 | 100
Khulawara | 133 | 1900 | 130 | 1500 | Pabna | 137 | 500 | 134 | 1930
Sylhet | 133 | 200 | 131 | 1300 | Shahjadpur | 141 | 1800 | 137 | 1200
Chatak | 132 | 300 | 129 | 1500 | Serajganj | 135 | 400 | 132 | 1100
Sunamganj | 131 | 300 | 128 | 1400 | Niyamatpur | 134 | 600 | 128 | 100
Biani Bazar | 133 | 1900 | 128 | 1300 | Joypurhat | 135 | 500 | 130 | 100
Comilla(s) | 128 | 600 | 122 | 1800 | Sherpur(Bogura) | 137 | 600 | 132 | 1100
Comilla(n) | 134 | 1830 | 127 | 1000 | Mohastangor | 135 | 600 | 131 | 1100
Chandpur | 130 | 1500 | 126 | 900 | Rangpur | 128 | 500 | 121 | 1830
Feni | 124 | 1830 | 122 | 700 | Lalmonirhat | 124 | 600 | 116 | 1930
Chowmuhani | 122 | 1900 | 118 | 1000 | Saidpur | 128 | 600 | 115 | 1830
Ashuganj | 136 | 1600 | 132 | 100 | Purbasadipur | 128 | 400 | 116 | 1830
Daudkandi | 127 | 1600 | 121 | 1100 | Thakurgaon | 125 | 600 | 110 | 1830
B.Baria | 133 | 1500 | 130 | 1300 | Palashbari | 130 | 600 | 124 | 1200
Ramganj | 123 | 2000 | 118 | 1200 | Barapukuria | 130 | 600 | 124 | 1830
Madanhat | 132 | 1900 | 126 | 900 | Panchagar | 124 | 600 | 103 | 1830
Hathazari | 131 | 300 | 125 | 900 | Joldhaka | 126 | 600 | 114 | 1830
Khulshi | 128 | 1900 | 121 | 1000 | Kurigram | 126 | 200 | 115 | 1830
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 216 | 6178 | 2669 | 8847 |  |  |  | QF-LDC-12
0:30 | 273 | 6090.5 | 2745.5 | 8836 | Date: | 2019-10-09
1:00 | 330 | 6003 | 2822 | 8825
1:30 | 335 | 5898 | 2775.5 | 8673.5
2:00 | 340 | 5793 | 2729 | 8522
2:30 | 350 | 5668.5 | 2736 | 8404.5 | [5 empty] | Gen. at Eve. Peak | 10284 | 10284 MW (20:00 )
3:00 | 360 | 5544 | 2743 | 8287 | [6 empty] | 20:00
3:30 | 400 | 5453.5 | 2699.5 | 8153 | [5 empty] | Gen. at Day Peak | 8864.66 | 8864.66 MW (12:00 )
4:00 | 440 | 5363 | 2656 | 8019 | [6 empty] | 12:00
4:30 | 410 | 5341.5 | 2652.5 | 7994 | [5 empty] | Highest Generation | 10284
5:00 | 380 | 5320 | 2649 | 7969 | [6 empty] | 20:00
5:30 | 385 | 5226.5 | 2511.5 | 7738
6:00 | 390 | 5133 | 2374 | 7507
6:30 | 385 | 5058.5 | 2405.5 | 7464
7:00 | 380 | 4984 | 2437 | 7421
7:30 | 464 | 5056.5 | 2506.5 | 7563
8:00 | 548 | 5129 | 2576 | 7705
8:30 | 564 | 5394 | 2601.5 | 7995.5
9:00 | 580 | 5659 | 2627 | 8286
9:30 | 553 | 5865.5 | 2590 | 8455.5
10:00 | 526 | 6072 | 2553 | 8625
10:30 | 525 | 6141.5 | 2550.5 | 8692
11:00 | 524 | 6211 | 2548 | 8759
11:30 | 488 | 6236.05 | 2575.8 | 8811.85
12:00 | 452 | 6261.1 | 2603.6 | 8864.7
12:30 | 421 | 6218.05 | 2591.8 | 8809.85
13:00 | 390 | 6175 | 2580 | 8755
13:30 | 415 | 5957.5 | 2590 | 8547.5
14:00 | 440 | 5740 | 2600 | 8340
14:30 | 465 | 5784.5 | 2609.5 | 8394
15:00 | 490 | 5829 | 2619 | 8448
15:30 | 500 | 5787 | 2583.5 | 8370.5
16:00 | 510 | 5745 | 2548 | 8293
16:30 | 513 | 5743.5 | 2568.5 | 8312
17:00 | 516 | 5742 | 2589 | 8331
17:30 | 453 | 6015.5 | 2911.5 | 8927
18:00 | 390 | 6289 | 3234 | 9523
18:30 | 319 | 6555.5 | 3311.5 | 9867
19:00 | 248 | 6822 | 3389 | 10211
19:30 | 222 | 6818 | 3411 | 10229
20:00 | 230 | 6932 | 3352 | 10284 |  |  |  | Executive Engineer
20:30 | 212 | 6830 | 3238 | 10068 |  |  |  | Network Operation Division
21:00 | 194 | 6728 | 3124 | 9852
21:30 | 159 | 6660 | 3007.5 | 9667.5
22:00 | 124 | 6592 | 2891 | 9483 |  |  |  |  | Page 6 of 7
22:30 | 137 | 6465 | 2823 | 9288
23:00 | 150 | 6338 | 2755 | 9093
23:30 | 183 | 6258 | 2712 | 8970
24:00 | 216 | 6178 | 2669 | 8847
10284 MW (20:00 )
8864.66 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-09 |  | Energy | 211631438
[10 empty] | 2019-10-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4577 | 916 | 2143 | 683 | 280 | 120 | 0 | 0 | 128
0:30 | 4572.5 | 915 | 1967 | 857 | 280 | 123.5 | 5 | 0 | 116 | Date: | 2019-10-09
1:00 | 4568 | 914 | 1791 | 1031 | 280 | 127 | 10 | 0 | 104
1:30 | 4560 | 914 | 1746.5 | 938.5 | 280 | 126.5 | 5 | 0 | 103 | [7 empty] | Total Energy | 211.6314 | Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
2:00 | 4552 | 914 | 1702 | 846 | 280 | 126 | 0 | 0 | 102 | [7 empty] | Energy not Served | 0
2:30 | 4522.5 | 913.5 | 1741 | 719.5 | 280 | 127 | 0 | 0 | 101 | [7 empty] | Energy Requirement | 211.6314
3:00 | 4493 | 913 | 1780 | 593 | 280 | 128 | 0 | 0 | 100
3:30 | 4504.5 | 913.5 | 1736.5 | 493.5 | 280 | 128 | 0 | 0 | 97 | [6 empty] | Shortage
4:00 | 4516 | 914 | 1693 | 394 | 280 | 128 | 0 | 0 | 94
4:30 | 4503 | 914 | 1707.5 | 372.5 | 280 | 125 | 0 | 0 | 92
5:00 | 4490 | 914 | 1722 | 351 | 280 | 122 | 0 | 0 | 90
5:30 | 4416 | 915 | 1577 | 343 | 280 | 122 | 0 | 0 | 85
6:00 | 4342 | 916 | 1432 | 335 | 280 | 122 | 0 | 0 | 80
6:30 | 4292 | 916 | 1440.5 | 334.5 | 280 | 122 | 0 | 0 | 77 |  |  |  |  | Coal
7:00 | 4242 | 916 | 1449 | 334 | 280 | 122 | 0 | 0 | 74
7:30 | 4310.5 | 916 | 1515.5 | 334 | 280 | 122 | 0 | 0 | 77 |  |  |  | Oil |  |  |  | ,
8:00 | 4379 | 916 | 1582 | 334 | 280 | 122 | 0 | 0 | 80
8:30 | 4398 | 916 | 1729.5 | 455 | 280 | 122 | 0 | 0 | 80
9:00 | 4417 | 916 | 1877 | 576 | 280 | 122 | 0 | 0 | 80
9:30 | 4385 | 916 | 1920 | 727 | 280 | 122 | 0 | 0 | 85
10:00 | 4353 | 916 | 1963 | 878 | 280 | 122 | 0 | 0 | 90
10:30 | 4349.5 | 916 | 1976.5 | 935 | 280 | 119.5 | 0 | 0 | 91
11:00 | 4346 | 916 | 1990 | 992 | 280 | 117 | 0 | 0 | 92
11:30 | 4307.5 | 916 | 1990.5 | 1073.5 | 280 | 119.5 | 5 | 0 | 93
12:00 | 4269 | 916 | 1991 | 1155 | 280 | 122 | 10 | 0 | 94
12:30 | 4305 | 915.5 | 1906.5 | 1159 | 280 | 122 | 8.5 | 0 | 88
13:00 | 4341 | 915 | 1822 | 1163 | 280 | 122 | 7 | 0 | 82
13:30 | 4341 | 915 | 1822 | 1163 | 280 | 122 | 7 | 0 | 82
14:00 | 4341 | 915 | 1822 | 1163 | 280 | 122 | 7 | 0 | 82
14:30 | 4249.5 | 915.5 | 1743.5 | 1179.5 | 280 | 124 | 3.5 | 0 | 88
15:00 | 4158 | 916 | 1665 | 1196 | 280 | 126 | 0 | 0 | 94
15:30 | 4120 | 916 | 1635.5 | 1181 | 280 | 126 | 3 | 0 | 98
16:00 | 4082 | 916 | 1606 | 1166 | 280 | 126 | 6 | 0 | 102
16:30 | 4066.5 | 916 | 1574 | 1199 | 280 | 127.5 | 36 | 0 | 108
17:00 | 4051 | 916 | 1542 | 1232 | 280 | 129 | 66 | 0 | 114
17:30 | 4040 | 916 | 1627.5 | 1546 | 280 | 129 | 264 | 0 | 124
18:00 | 4029 | 916 | 1713 | 1860 | 280 | 129 | 462 | 0 | 134
18:30 | 4076.5 | 916 | 1723 | 2161 | 280 | 129.5 | 449 | 0 | 132
19:00 | 4124 | 916 | 1733 | 2462 | 280 | 130 | 436 | 0 | 130
19:30 | 4239 | 916 | 1945 | 2274 | 280 | 130 | 309 | 0 | 136
20:00 | 4353 | 916 | 2108 | 2109 | 280 | 130 | 256 | 0 | 132
20:30 | 4404 | 916 | 2110.5 | 1858.5 | 280 | 130 | 237 | 0 | 132
21:00 | 4455 | 916 | 2113 | 1608 | 280 | 130 | 218 | 0 | 132
21:30 | 4470 | 916 | 2101.5 | 1483.5 | 280 | 130 | 158.5 | 0 | 128
22:00 | 4485 | 916 | 2090 | 1359 | 280 | 130 | 99 | 0 | 124
22:30 | 4489.5 | 916 | 2099 | 1191.5 | 280 | 126 | 57 | 0 | 129
23:00 | 4494 | 916 | 2108 | 1024 | 280 | 122 | 15 | 0 | 134
23:30 | 4535.5 | 916 | 2125.5 | 853.5 | 280 | 121 | 7.5 | 0 | 131 | Max Temp. in Dhaka |  | 32.7° C
24:00 | 4577 | 916 | 2143 | 683 | 280 | 120 | 0 | 0 | 128
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
Note on W13: Author:

## Generation
2019-10-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 87 | 86 | 88 | 88 | 82 | 82 | 82 | 82 | 82 | 82 | 77 | 82 | 82 | 86 | 86 | 86 | 89 | 89 |  | 90 | 90 | 90 | 90 | 90 | 82 | 80 | 1944976
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976000
3 | Chattogram TPP-1 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1800000
4 | Chattogram TPP-2 | [21 empty] | 0 | 40 | 60 | 80 | 100 | 200000
5 | Raozan 25 MW PP | [17 empty] | 16 |  | 25 | 25 | 25 | 8 | 8 | 0 |  | 93915
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 10 | 13 | 16 | 17 | 13.8 | 16 | 12 | 7 | 8 | 1 | [9 empty] | 120015
6 | Sikalbaha 225MW CCPP (Gas) | 206 | 204 | 205 | 216 | 205 | 205 | 217 | 218 | 204 | 205 | 186 | 179 | 204 | 183 | 202 | 203 | 204 | 204 |  | 204 | 204 | 203 | 204 | 203 | 204 | 204 | 4827317
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 134 | 134 | 134 | 134 | 134 | 134 | 140 | 140 | 135 | 135 | 110 | 105 | 105 | 105 | 104 | 104 | 104 | 104 |  | 134 | 134 | 134 | 134 | 134 | 134 | 135 | 3008002
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 85 |  | 85 | 36 | 34 | 34 | 17 | 0 |  | 245676
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [15 empty] | 0 | 9 | 0 |  | 0 | [6 empty] | 7968
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 350 | 349 | 346 | 349 | 346 | 300 | 280 | 270 | 270 | 270 | 270 | 300 | 300 | 220 | 220 | 220 | 220 | 220 |  | 220 | 290 | 350 | 346 | 350 | 350 | 348 | 7189800
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 0 | 20 | 95 | 95 | 95 | 95 | 95 | 85 | 65 | 61 | 62 |  | 110 | 15 | 0 | 0 |  |  |  | 963491
19 | Ashuganj 195MW PP (APSCL-United) | 82 | 82 | 82 | 82 | 82 | 82 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 936727
20 | Ghorasal TPP (Unit-1&2) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 754000
21 | Ghorasal Repowered CCPP Unit-3 | 169 | 169 | 169 | 169 | 169 | 157 | 123 | 130 | 220 | 189 | 189 | 158 | 159 | 159 | 159 | 159 | 159 | 158 |  | 159 | 158 | 159 | 159 | 158 | 158 | 159 | 4180300
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 380 | 380 | 340 | 340 | 340 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 300 | 300 | 300 | 300 | 300 |  | 270 | 270 | 290 | 300 | 300 | 300 | 300 | 7847918
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2404320
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 514080
33 | Ashuganj 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 150 | 181 | 165 | 181 | 170 | 160 | 165 | 168 | 159 | 164 | 173 |  | 180 | 180 | 180 | 188 | 180 | 182 | 190 | 4002000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 305 | 305 | 310 | 305 | 340 | 360 | 305 | 325 | 340 | 310 | 305 | 305 | 320 | 285 | 265 | 270 |  | 260 | 275 | 275 | 280 | 290 | 290 | 300 | 7414000
| Ashuganj 450 MW CCPP(North) | 360 | 360 | 360 | 360 | 360 | 360 | 300 | 300 | 300 | 360 | 360 | 360 | 360 | 320 | 320 | 320 | 280 | 250 |  | 300 | 330 | 330 | 330 | 330 | 330 | 330 | 8252700
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 53 | 54 | 54 | 53 | 49 | 53 | 53 | 55 |  | 56 | 56 | 56 | 56 | 55 | 55 | 53 | 1318080
36 | Chandpur 150 MW CCPP | 87 | 87 | 87 | 86 | 87 | 86 | 87 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 |  | 88 | 86 | 86 | 87 | 87 | 87 | 87 | 2059120
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 348 | 345 | 346 | 350 | 348 | 345 | 346 | 378 | 363 | 361 | 354 | 360 | 348 | 300 | 300 | 300 | 295 | 280 |  | 345 | 345 | 344 | 345 | 344 | 345 | 360 | 8293170
40 | Meghnaghat 450 MW CCPP(MPL) |  | 0 | 20 | 25 | 75 | 165 | 220 | 230 | 270 | 370 | 370 | 370 | 320 | 300 | 300 | 300 | 300 | 300 |  | 300 | 370 | 400 | 400 | 400 | 400 | 400 | 6080000
41 | Haripur 360MW CCPP(HPL) | 356 | 360 | 357 | 355 | 324 | 324 | 283 | 325 | 323 | 323 | 343 | 349 | 324 | 283 | 283 | 283 | 282 | 324 |  | 284 | 314 | 357 | 357 | 357 | 358 | 358 | 7745000
42 | RPCL 210MW CCPP | 155 | 157 | 157 | 156 | 155 | 157 | 155 | 153 | 154 | 152 | 150 | 149 | 149 | 156 | 156 | 157 | 155 | 154 |  | 157 | 157 | 156 | 157 | 157 | 155 | 154 | 3649040
43
44 | Fenchugonj CCPP Phase-1 | 58 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1427000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 32 | 42 | 22 |  | 22 | 22 | 22 | 32 | 42 | 42 | 53 | 619080
46 | Shajibazar 330 MW CCPP | 226 | 228 | 222 | 224 | 226 | 224 | 230 | 235 | 230 | 232 | 234 | 230 | 233 | 232 | 242 | 242 | 242 | 244 |  | 245 | 242 | 243 | 242 | 245 | 232 | 232 | 5286000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 67 | 68 | 66 | 65 | 65 | 30 | 30 | 30 | 65 | 63 | 64 | 65 | 67 | 68 |  | 66 | 68 | 68 | 68 | 68 | 67 | 68 | 1503936
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 40 | 10 | 10 | 10 | 10 | 10 | 59 | 75 | 74 | 71 | 74 | 40 | 40 | 40 | 10 | 70 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1261440
49 | Shahjibazar 50MW PP (EPL) | 44 | 44 | 44 | 44 | 44 | 10 | 10 | 10 | 43 | 42 | 42 | 42 | 5 | 5 | 43 | 10 | 10 | 10 |  | 43 | 43 | 43 | 40 | 40 | 40 | 40 | 789480
50 | Sylhet 150 MW CCPP | 108 | 119 | 110 | 120 | 115 | 113 | 84 | 84 | 70 | 72 | 72 | 69 | 68 | 77 | 73 | 68 | 76 | 113 |  | 70 | 72 | 110 | 115 | 115 | 110 | 120 | 2317080
51 | Sylhet 20 MW GTPP | [13 empty] | 0
52 | Sylhet 50MW PP (EPL) | 44 | 44 | 44 | 44 | 44 | 18 | 12 | 12 | 43 | 44 | 42 | 42 | 42 | 18 | 18 | 18 | 18 | 44 |  | 43 | 45 | 45 | 45 | 44 | 44 | 44 | 850520
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 0 |  |  |  | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 |  | 10 | 10 | 10 | 0 |  |  |  | 151740
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 1 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 |  | 5 | 3 | 3 | 11 | 11 | 11 | 11 | 208176
55 | Fenchugonj 51 MW PP (Barakatullah) | 41 | 41 | 41 | 11 | 11 | 11 | 11 | 11 | 44 | 44 | 44 | 44 | 49 | 11 | 11 | 11 | 11 | 40 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 720600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 |  | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 540096
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 265 | 265 | 290 | 290 | 270 | 275 | 315 | 300 | 300 | 310 | 305 | 280 | 280 | 310 | 290 | 290 | 275 |  | 270 | 280 | 290 | 300 | 280 | 295 | 310 | 7281500
58 | Nababganj 55 MW PP (Southern power ) | [14 empty] | 5 | 55 | 55 | 55 |  | 55 | 55 | 55 | 17 | 0 |  |  | 327560
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440784
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 0 | 0 |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 332172
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 22 | 0 | [11 empty] | 291456
63 | Impoprt (Tripura) | 104 | 102 | 100 | 94 | 90 | 80 | 74 | 80 | 80 | 90 | 92 | 94 | 82 | 92 | 94 | 102 | 114 | 134 |  | 130 | 136 | 132 | 132 | 124 | 134 | 128 | 2456640
64 | Malancha, Ctg. EPZ (United) | 39 | 42 | 42 | 42 | 42 | 42 | 32 | 5 | 2 | 2 | 2 | 2 | 5 | 3 | 2 | 3 | 9 | 5 |  | 7 | 11 | 21 | 27 | 34 | 34 | 32 | 506880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 480276
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178380
67 | Jangalia 33MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 629600
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 6 | 6 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 478980
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 8 | 30 | 30 | 30 | 30 | 30 | 20 |  | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 682380
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 789300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 796100
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [14 empty] | 0 | 32 | 32 | 32 |  | 65 | 70 | 70 | 0 |  |  |  | 256752
78 | Gazipur 52 MW PP | [8 empty] | 21 | 52 | 52 | 47 | 52 | 43 | 47 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 0 |  | 702156
79 | Kodda 150MW PP | 10 | [15 empty] | 0 | 100 |  | 90 | 32 | 32 | 32 | 16 | 0 |  | 251520
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 70 | 50 | 24 | 24 | 8 | 8 | 8 | 16 | 83 | 95 | 95 | 95 | 95 | 95 | 50 | 50 | 75 |  | 95 | 95 | 95 | 95 | 95 | 95 | 48 | 1654080
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 0 | 7 |  | 23 | 0 | 0 | 0 |  |  |  | 33446
| Gazipur 100 MW PP | [8 empty] | 105 | 104 | 104 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 52 | 52 | 52 | 18 | 0 |  |  | 1180920
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 4 | 4 | 5 | 5.2 | 0 | 0 | 2 | 0 | [10 empty] | 23760
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 48 | 48 | 48 | 80 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 80 | 1432272
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 0 | [13 empty] | 1645963
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 0 | 11 |  | 48 | 7 | 0 |  |  |  |  | 83520
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 20 | 20 | 20 | 20 | 0 |  | 313200
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 10 | 38 | 49 | 49 | 49 | 49 | 10 | 10 | 10 | 10 | 20 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 914616
93 | Ashuganj 51 MW PP (Midland) | 35 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 24 | 35 | 35 | 35 | 35 | 5 | 5 | 5 | 5 | 5 |  | 22 | 35 | 35 | 35 | 35 | 35 | 35 | 575316
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 0 | 7 |  | 7 | 0 | 0 | 0 |  |  |  | 17568
95 | Patenga 50MW PP (Baraka) | [9 empty] | 8 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 40 | 50 | 48 | 16 | 0 |  |  | 262560
96 | Chattogram 108 MW PP (ECPV) | 90 | 90 | 90 | 64 | 64 | 64 | 63 | 63 | 60 | 60 | 65 | 78 | 79 | 95 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2008320
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 3 |  | 47 | 47 | 0 |  |  |  |  | 97392
98 | Bosila 108MW PP(CLC) | [9 empty] | 24 | 24 | 54 | 69 | 69 | 69 | 46 | 69 | 69 |  | 69 | 69 | 69 | 72 | 0 |  |  | 706560
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 0 | 2 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 775981
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 47 |  | 55 | 55 | 55 | 17 | 17 | 0 |  | 402708
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 2926227
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1.1 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 7900
103 | Kamalaghat 54 MW PP(Banco Energy) | [14 empty] | 25 | 53 | 54 | 53 |  | 53 | 53 | 53 | 53 | 53 | 35 | 0 | 435240
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 0 | 7 |  | 7 | 0 | [5 empty] | 19200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 110 | 85 | 60 | 60 | 60 | 60 | 60 | 60 | 115 | 149 | 152 | 142 | 135 | 135 | 135 | 135 | 136 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 136 | 2783520
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 1240320
116 | Chandpur 200MW (Desh energy) | 160 | 160 | 120 | 60 | 17 | 17 | 17 | 17 | 26 | 52 | 52 | 82 | 105 | 105 | 105 | 70 | 70 | 94 |  | 180 | 180 | 181 | 180 | 180 | 125 | 17 | 2318400
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 0 | 3 |  | 33 | 50 | 0 |  |  |  |  | 75272
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [8 empty] | 8 | 8 | 8 | 16 | 40 | 40 | 40 | 8 | 8 | 38 |  | 115 | 115 | 115 | 40 | 72 | 0 |  | 666000
| Anwara 300 MW PP (United) | 162 | 142 | 52 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 65 | 116 | 122 | 122 | 122 | 126 | 122 | 160 |  | 162 | 160 | 160 | 162 | 162 | 162 | 162 | 2391164
120 | Eastern Zone Total | 6003 | 5793 | 5544 | 5363 | 5320 | 5133 | 4984 | 5129 | 5659 | 6072 | 6211 | 6261.1 | 6175 | 5740 | 5829 | 5745 | 5742 | 6289 |  | 6822 | 6818 | 6932 | 6728 | 6592 | 6338 | 6178 | 144976624
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [15 empty] | 0 | 16 | 59 |  | 115 | 80 | 32 | 0 |  |  |  | 231360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 0 | 5 | 31 |  | 37 | 37 | 37 | 37 | 37 | 15 | 0 | 207840
| Khulna 225 MW CCPP | [26 empty] | 0
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 0 | [13 empty] | 0 | 53 |  | 70 | 70 | 70 | 70 | 17 | 0 |  | 330240
130
131
132
133
| Barisal 110 MW PP (Summit ) | 16 | 16 | 0 | [12 empty] | 0 | 16 | 48 |  | 64 | 64 | 64 | 48 | 48 | 48 | 0 | 382080
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 96 | 96 | 62 | 62 | 11 | 12 | 12 | 50 | 42 | 42 | 42 | 42 | 43 | 42 | 42 | 42 | 67 |  | 52 | 51 | 51 | 51 | 51 | 51 | 72 | 1247361
| Bhola 225 MW CCPP | 179 | 180 | 180 | 179 | 179 | 181 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 179 | 179 | 180 | 179 |  | 179 | 179 | 179 | 179 | 179 | 180 | 180 | 4367405
140 | Bhola 33 MW PP (Venture) | 27 | 27 | 26 | 26 | 26 | 22 | 20 | 15 | 17 | 8 | 10 | 12 | 15 | 16 | 13 | 14 | 14 | 21 |  | 23 | 24 | 25 | 26 | 26 | 25 | 23 | 479280
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 0 | [14 empty] | 0 | 40 |  | 40 | 40 | 40 | 0 |  |  |  | 126000
143 | Gopalganj 100 MW Peaking PP | [14 empty] | 0 | 6 | 27 | 51 |  | 76 | 70 | 69 | 48 | 4 | 0 |  | 276992
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 67 | 66 | 51 | 0 | [12 empty] | 0 | 43 |  | 59 | 54 | 54 | 50 | 50 | 50 | 35 | 531936
146 | Bheramara HVDC | 914 | 914 | 913 | 914 | 914 | 916 | 916 | 916 | 916 | 916 | 916 | 916 | 915 | 916 | 916 | 916 | 916 | 916 |  | 916 | 916 | 916 | 916 | 916 | 916 | 916 | 21962181
147 | Bheramara 360 MW CCPP | 345 | 345 | 345 | 340 | 345 | 345 | 365 | 390 | 345 | 345 | 345 | 345 | 345 | 340 | 345 | 345 | 340 | 346 |  | 340 | 345 | 340 | 340 | 340 | 345 | 345 | 8492832
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6794900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 50 | 8 | 0 |  | 218947
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 186 | 185 | 187 | 192 | 183 | 160 | 162 | 178 | 198 | 174 | 169 | 173 | 164 | 160 | 174 | 162 | 163 | 162 |  | 159 | 160 | 160 | 163 | 159 | 162 | 172 | 4388373
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 199 | 197 | 192 | 201 | 188 | 163 | 154 | 184 | 212 | 182 | 176 | 176 | 180 | 178 | 172 | 165 | 166 | 160 |  | 157 | 155 | 157 | 166 | 164 | 164 | 164 | 4450227
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 427 | 362 | 429 | 418 | 428 | 267 | 330 | 403 | 389 | 383 | 383 | 383 | 335 | 379 | 382 | 370 | 331 | 330 |  | 307 | 390 | 429 | 430 | 422 | 425 | 430 | 9244330
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 0 | 10 | 32 |  | 0 | [6 empty] | 54030
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 7 | 7 | 7 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 481440
163 | Bogura 20 MW PP (Energyprima) | 17 | 17 | 17 | 17 | 17 | 17 | 6 | 6 | 12 | 13 | 14 | 14 | 16 | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 356904
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 0 | 5 | 0 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 137556
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 50 | 0 | [5 empty] | 65540
166 | Katakhali 50 MW PP (Northern) | [11 empty] | 0 | 16 | 16 | 16 | 16 | 16 | 42 |  | 50 | 50 | 50 | 50 | 50 | 50 | 8 | 385483
167 | Katakhali 50 MW Peaking PP | [16 empty] | 0 | 34 |  | 0 | [6 empty] | 32139
168 | Santahar 50 MW Peaking PP | [17 empty] | 10 |  | 30 | 0 | [5 empty] | 27232
169 | Natore 52 MW PP (Rajlanka) | 8 | 0 | [8 empty] | 0 | 43 | 52 | 52 | 52 | 8 | 8 | 37 |  | 52 | 52 | 52 | 52 | 0 |  |  | 409440
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 51 |  | 51 | 51 | 0 |  |  |  |  | 105520
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | [17 empty] | 20 |  | 70 | 113 | 113 | 0 |  |  |  | 268800
173 | Rangpur 20 MW GTPP | [20 empty] | 16 | 17 | 0 |  |  |  | 16000
175 | Saidpur 20 MW GTPP | [10 empty] | 0 | 10 | 7 | 0 |  |  | 15 | 18 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 101000
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 60 |  | 95 | 97 | 100 | 104 | 76 | 0 |  | 452160
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 3 | 3 | 7.6 | 6 | 2 | 4 | 1 | 0 | 0 | [8 empty] | 29286
178
178