## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-10-31 | Thursday
|  | Date (day): | 2019-10-31 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13274 | MW |  |  | (b) At Evening Peak Hour : |  | 14491 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-10-30 | 2019-10-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 128 | 100 | 150
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 350 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 345 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 305 | 304 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 350 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 36 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 150 | 150 | 150 | 155 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 10 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 48 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 16 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 16 | 11 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 20 | 47 | 45 | 46
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 70 | 69 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 8 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 152 | 300 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 10 | 145 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 70 | 70 | 70 |  | 35 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2269 | 2856 | 4001 | 4452 | 656 | 654
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.7 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 90 | 94 | 94 | 94 | 136 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 226 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 146 | 100 | 135 | 135
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 51 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 70 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 5 | 6 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 96 | 96 | 96 |  | 12 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.6 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 48 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 780.3 | 1115 | 1512.4 | 1581 | 396 | 110
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 180 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 270 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 265 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 33 | 33 |  | 12 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 53 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 36 | 36 | 36 | 159 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 25 | 30 | 30 |  | 21 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 10 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 125 | 125 | 140 | 140
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 8 | 188 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 154 | 120 | 164
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 30 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 22 | 22 | 22
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1349 | 1536 | 1957 | 2243 | 457 | 33
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 152 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 72 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 200 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 7 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 212.2 | 453 | 593.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 44 | 44 | 44 | 44
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 104 | 100 | 100 | 100 |  | 230 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 22 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 30 | 46 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 40 | 75 | 77 |  | 9 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 28 | 31 | 30 | 30 |  | 20 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 260 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 8 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 893 | 933 | 1085 | 1087 | 0 | 811
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 930 | 911 | 689 | 689 |  |  | Problem in India Side
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 4 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 310 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 103 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1255 | 1454 | 1739 | 1904 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 29 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 150 | 150 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 40 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 211 | 291 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 50 | 50 | 60 | 60 | 40 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 16 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 181 | 160 | 225 | 225 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 144 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 185 | 176 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 382 | 362 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 25 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 111 | 113 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 28 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 870 | 1141 | 1529 | 1679 | 260 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 68 | 68 | 68
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 290 | 290 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 107 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 359.2 | 465 | 479 | 505 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 8198.7 | 10244 | 13274 | 14491 | 1811 | 1772
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7820.1384 | 9771 | 12661.0947 | 13821.9017
A. |  | 2019-10-30 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10244 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6567 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10244 | MW
3 | Day peak Generation : |  |  | 8198.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9771 | MW
4 | Evening peak Generation : |  |  | 10244 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 195.8866 | MKWHr | By Solar | 0.20402 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 137.9323 | MKWHr |  | By Oil: | 23.5053 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.5685 | MKWHr |  | By Hydro: | 2.1943 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1811 | MW | Dhaka | 3741 | 3741 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1772 | MW | Chittagong | 1107 | 1107 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3583 | MW | Khulna | 1086 | 1086 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1165.6 | MMCFD |  |  | Rajshahi | 925 | 925 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 126385924.6 | ii) Oil : | Taka | 182266580.69 | Comilla | 923 | 923 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 38592162.32 | Total | Taka | 347244667.61 | Mymensingh | 730 | 730 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 427 | 427 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 296 | MW (E to W) at | 19:00 | hrs | Barisal | 270 | 270 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 296 | MW at | 19:00 | hrs | Rangpur | 562 | 562 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.6° C |  |  | Total | 9771 | 9771 |  | 0
B. |  | 2019-10-31 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 30.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14491 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8300 | MW
4 | Reserve(Generation end) |  |  |  | 4091 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 198.8696 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6541 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.4015 | MKWHr. | ii) HVDC Flow at Peak Time |  | 911 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0806 | MKWHr. | iii) Maximum HVDC Flow : |  | 931 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 102.1 | 102.17 |  | (b) Today: | 102.1 |  | (c) Rule Curve: |  | 108.9
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-10-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 345 | 310 |  | 0 | 370 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 46 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 44 | 0 | 19 | 39 | 80 | 0 | 0 | 260 | 265 | 180 | 8 | 124 | 32 | 51 | 0 | 25 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 122 | 155 | 0 | 22 | 0 | 60 | 44 | 50 | 49 | 100 | 100 | 67 | 10 | 40 | 0 | 17 | 28 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 68 | 0 | 0 | 0 | 0 |  | 930 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 25 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 174 | 0 | 0 | 0 | 96 | 0 | 172 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4860 | 2654 | 7514 | 3676 | 930 | 1875 | 453 | 354 | 96 | 8 | 122 | 0 | 0 | 102.17
2:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 346 | 310 |  | 0 | 370 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 46 | 50 | 100 | 0 | 0 | 204 | 0 | 5 | 0 |  | 0 | 0 | 0 | 30 | 44 | 0 | 19 | 39 | 80 | 0 | 0 | 260 | 265 | 181 | 8 | 126 | 32 | 52 | 0 | 25 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 120 | 154 | 0 | 22 | 0 | 60 | 44 | 50 | 49 | 100 | 101 | 67 | 10 | 40 | 0 | 17 | 28 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 68 | 0 | 0 | 0 | 0 |  | 684 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 64 | 289 | 0 | 0 | 159 | 0 | 0 | 0 | 95 | 0 | 173 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4864 | 2403 | 7267 | 3671 | 684 | 1896 | 439 | 353 | 96 | 8 | 120 | 0 | 0 | 102.17
3:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 346 | 310 |  | 0 | 370 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 46 | 50 | 100 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 30 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 265 | 185 | 8 | 126 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 120 | 154 | 0 | 22 | 0 | 60 | 44 | 5 | 5 | 100 | 102 | 66 | 10 | 5 | 0 | 0 | 8 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 684 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 65 | 290 | 0 | 0 | 158 | 0 | 0 | 0 | 51 | 0 | 170 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4577 | 2364 | 6941 | 3707 | 684 | 1659 | 312 | 355 | 96 | 8 | 120 | 0 | 0 | 102.17
4:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 351 | 280 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 46 | 50 | 100 | 0 | 0 | 212 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 285 | 290 | 178 | 8 | 126 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 116 | 154 | 0 | 0 | 0 | 60 | 44 | 5 | 5 | 100 | 103 | 67 | 10 | 5 | 0 | 0 | 8 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 684 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 164 | 0 | 0 | 0 | 32 | 0 | 167 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4383 | 2367 | 6750 | 3642 | 684 | 1570 | 280 | 354 | 96 | 8 | 116 | 0 | 0 | 102.17
5:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 362 | 280 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 46 | 50 | 100 | 0 | 0 | 212 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 285 | 290 | 179 | 8 | 126 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 114 | 154 | 0 | 0 | 0 | 60 | 44 | 5 | 5 | 100 | 103 | 66 | 10 | 5 | 0 | 0 | 8 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 684 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 64 | 290 | 0 | 0 | 170 | 0 | 0 | 0 | 12 | 0 | 172 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4359 | 2326 | 6685 | 3622 | 684 | 1527 | 280 | 354 | 96 | 8 | 114 | 0 | 0 | 102.17
6:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 367 | 280 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 275 | 280 | 175 | 8 | 126 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 102 | 156 | 0 | 0 | 0 | 60 | 44 | 5 | 5 | 100 | 102 | 66 | 10 | 5 | 0 | 0 | 8 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 684 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 171 | 0 | 0 | 0 | 12 | 0 | 172 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4256 | 2311 | 6567 | 3529 | 684 | 1519 | 280 | 355 | 90 | 8 | 102 | 0 | 0 | 102.17
7:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 373 | 280 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 218 | 0 | 117 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 16 | 36 | 80 | 0 | 0 | 300 | 305 | 181 | 8 | 126 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 92 | 154 | 0 | 0 | 0.1 | 60 | 44 | 5 | 5 | 100 | 104 | 66 | 10 | 5 | 0 | 0 | 8 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.23 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0.327 | 0 | 0 | 0 |  | 684 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 171 | 0 | 0 | 0 | 12 | 0 | 171 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 4367.657 | 2366.7 | 6734.357 | 3673 | 684 | 1536 | 289 | 355 | 92 | 8 | 92 | 5.357 | 0 | 102.17
8:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 373 | 280 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 44 | 50 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 4 | 16 | 8 | 80 | 0 | 0 | 270 | 275 | 192 | 8 | 125 | 30 | 42 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 100 | 156 | 0 | 0 | 0.3 | 60 | 44 | 5 | 5 | 100 | 104 | 65 | 10 | 5 | 0 | 0 | 8 | 0 | 315 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 52 | 34 | 1.9 | 0 | 0 | 0 |  | 684 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 174 | 0 | 0 | 0 | 12 | 0 | 176 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 |  | 4424.8 | 2363.9 | 6788.7 | 3624 | 684 | 1532 | 376 | 355 | 94 | 8 | 100 | 15.7 | 0 | 0
9:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 355 | 289 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 17 | 0 | 0 | 25 | 31 | 33 | 33 | 4 | 0 | 44 | 50 | 100 | 0 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 17 | 19 | 2 | 80 | 0 | 0 | 275 | 280 | 203 | 8 | 125 | 30 | 52 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 110 | 153 | 0 | 0 | 1.6 | 59 | 44 | 5 | 5 | 100 | 102 | 65 | 10 | 5 | 0 | 0 | 8 | 0 | 310 | 0 | 0 | 0 | 91 | 0 | 0 | 14 | 0 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 52 | 34 | 3.1 | 0 | 0 | 0 |  | 931 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 64 | 290 | 0 | 0 | 175 | 0 | 0 | 0 | 12 | 0 | 168 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4575 | 2568.2 | 7143.2 | 3593 | 931 | 1540 | 489 | 354 | 94 | 8 | 110 | 24.2 | 0 | 0
10:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 371 | 305 |  | 0 | 330 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 45 | 50 | 100 | 0 | 0 | 230 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 19 | 2 | 80 | 0 | 0 | 325 | 290 | 197 | 8 | 125 | 30 | 51 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 0 | 16 | 114 | 150 | 0 | 22 | 2.1 | 60 | 44 | 5 | 5 | 100 | 101 | 63 | 10 | 5 | 0 | 0 | 8 | 10 | 315 | 0 | 11 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 70 | 46 | 3.9 | 0 | 0 | 0 |  | 930 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 188 | 0 | 0 | 0 | 12 | 0 | 175 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 19 |  | 4902 | 2625.6 | 7527.6 | 3811 | 930 | 1586 | 599 | 354 | 95 | 8 | 114 | 30.6 | 0 | 0
11:00 | 35 | 0 | 99 | 0 | 300 | 0 | 0 | 375 | 305 |  | 0 | 400 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 0 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 40 | 50 | 100 | 0 | 0 | 226 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 0 | 18 | 19 | 2 | 80 | 0 | 0 | 325 | 305 | 201 | 36 | 125 | 33 | 49 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 118 | 150 | 0 | 22 | 2.4 | 60 | 44 | 5 | 5 | 100 | 103 | 63 | 10 | 5 | 0 | 0 | 8 | 10 | 320 | 24 | 11 | 0 | 145 | 0 | 0 | 31 | 0 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 70 | 81 | 2.6 | 0 | 0 | 0 |  | 930 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 8 | 0 | 63 | 290 | 0 | 0 | 195 | 0 | 0 | 0 | 11 | 0 | 194 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 23 |  | 5215.6 | 2668.8 | 7884.4 | 3984 | 930 | 1686 | 693 | 353 | 90 | 8 | 118 | 22.4 | 0 | 0
12:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 375 | 305 |  | 0 | 400 | 230 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 20 | 0 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 40 | 50 | 100 | 0 | 0 | 226 | 0 | 146 | 0 |  | 0 | 0 | 0 | 50 | 0 | 18 | 19 | 2 | 80 | 0 | 0 | 320 | 290 | 198 | 36 | 125 | 33 | 50 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 128 | 148 | 0 | 22 | 2.2 | 60 | 44 | 5 | 30 | 130 | 104 | 60 | 10 | 40 | 0 | 17 | 28 | 10 | 320 | 24 | 11 | 0 | 152 | 0 | 0 | 40 | 0 | 10 | 19.7 | 0 | 8 | 0 | 0 | 0 | 70 | 105 | 4.6 | 0 | 0 | 0 |  | 930 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 63 | 290 | 0 | 0 | 181 | 0 | 0 | 0 | 40 | 0 | 185 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 28 |  | 5503.5 | 2695.2 | 8198.7 | 3989 | 930 | 1850 | 826 | 353 | 90 | 0 | 128 | 32.7 | 0 | 0
13:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 384 | 334 |  | 0 | 400 | 230 | 0 | 0 | 9 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 20 | 0 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 8 | 0 | 40 | 50 | 100 | 0 | 0 | 226 | 0 | 146 | 0 |  | 0 | 0 | 0 | 50 | 0 | 18 | 19 | 5 | 80 | 0 | 0 | 310 | 290 | 196 | 36 | 125 | 33 | 49 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 22 | 128 | 149 | 0 | 22 | 1.1 | 58 | 44 | 5 | 49 | 130 | 102 | 63 | 10 | 40 | 0 | 17 | 27 | 8 | 325 | 24 | 11 | 0 | 165 | 0 | 0 | 40 | 0 | 45 | 18.1 | 0 | 17 | 0 | 0 | 0 | 70 | 105 | 4.3 | 0 | 0 | 0 |  | 912 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 21 | 0 | 0 | 50 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 196 | 0 | 5 | 0 | 43 | 0 | 185 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 15 |  | 5613.5 | 2708 | 8321.5 | 4015 | 912 | 1907 | 878 | 354 | 90 | 8 | 128 | 29.5 | 0 | 0
14:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 355 | 303 |  | 0 | 360 | 230 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 20 | 17 | 17 | 0 | 19 | 25 | 24 | 33 | 33 | 8 | 0 | 41 | 50 | 100 | 0 | 0 | 227 | 0 | 146 | 0 |  | 0 | 0 | 0 | 50 | 0 | 18 | 18 | 5 | 80 | 0 | 0 | 290 | 270 | 180 | 36 | 125 | 33 | 50 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 134 | 149 | 0 | 22 | 2 | 60 | 44 | 42 | 49 | 100 | 101 | 63 | 30 | 40 | 0 | 17 | 27 | 8 | 300 | 24 | 11 | 0 | 165 | 0 | 0 | 58 | 0 | 45 | 15.5 | 0 | 17 | 0 | 0 | 0 | 70 | 105 | 3.7 | 0 | 0 | 0 |  | 913 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 22 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 194 | 0 | 10 | 0 | 60 | 0 | 169 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 14 |  | 5536.2 | 2690.4 | 8226.6 | 3937 | 913 | 1854 | 918 | 354 | 91 | 0 | 134 | 25.6 | 0 | 0
15:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 370 | 302 |  | 0 | 360 | 150 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 20 | 17 | 17 | 0 | 19 | 25 | 20 | 0 | 33 | 8 | 0 | 38 | 50 | 100 | 0 | 0 | 226 | 0 | 143 | 0 |  | 0 | 0 | 0 | 50 | 0 | 18 | 18 | 2 | 80 | 0 | 0 | 315 | 295 | 199 | 36 | 126 | 33 | 50 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 134 | 148 | 0 | 22 | 1.3 | 60 | 44 | 47 | 49 | 130 | 102 | 63 | 46 | 40 | 0 | 17 | 28 | 8 | 305 | 24 | 11 | 0 | 165 | 0 | 0 | 70 | 0 | 45 | 11.15 | 0 | 17 | 0 | 0 | 0 | 70 | 105 | 2.1 | 0 | 0 | 0 |  | 911 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 177 | 0 | 10 | 0 | 60 | 0 | 177 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 4 |  | 5578.55 | 2687.6 | 8266.15 | 3994 | 911 | 1928 | 840 | 354 | 88 | 0 | 134 | 17.15 | 0 | 0
16:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 370 | 304 |  | 0 | 360 | 150 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 20 | 17 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 35 | 50 | 100 | 0 | 0 | 227 | 0 | 143 | 0 |  | 0 | 0 | 0 | 50 | 0 | 18 | 18 | 2 | 80 | 0 | 0 | 290 | 270 | 188 | 36 | 126 | 33 | 50 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 130 | 149 | 0 | 22 | 0.6 | 60 | 44 | 47 | 49 | 130 | 100 | 61 | 68 | 40 | 0 | 17 | 26 | 8 | 310 | 24 | 11 | 0 | 165 | 0 | 0 | 70 | 0 | 45 | 5.66 | 0 | 17 | 0 | 0 | 0 | 70 | 105 | 0.8 | 0 | 0 | 0 |  | 912 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 8 | 0 | 64 | 290 | 0 | 0 | 178 | 0 | 15 | 0 | 63 | 0 | 182 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 23 |  | 5573.06 | 2699.2 | 8272.26 | 3972 | 912 | 1952 | 859 | 354 | 85 | 0 | 130 | 8.26 | 0 | 0
17:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 348 | 305 |  | 0 | 360 | 150 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 69 | 0 | 19 | 17 | 17 | 0 | 0 | 25 | 31 | 33 | 33 | 8 | 0 | 35 | 50 | 100 | 0 | 0 | 230 | 0 | 146 | 0 |  | 0 | 0 | 0 | 50 | 4 | 18 | 18 | 5 | 80 | 0 | 0 | 290 | 265 | 180 | 36 | 125 | 33 | 52 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 128 | 151 | 0 | 22 | 0 | 60 | 44 | 47 | 20 | 130 | 100 | 65 | 40 | 40 | 0 | 17 | 29 | 8 | 300 | 24 | 11 | 0 | 165 | 0 | 0 | 70 | 0 | 45 | 0.5 | 10 | 17 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 910 | 0 | 325 | 0 | 1 | 0 | 0 | 0 | 2 | 10 | 0 | 148 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 65 | 290 | 0 | 0 | 167 | 0 | 53 | 0 | 61 | 0 | 177 | 0 | 343 | 4 | 0 | 6 | 3 | 76 | 0 | 0.1 | 12 |  | 5468.5 | 2768.1 | 8236.6 | 3942 | 910 | 1843 | 951 | 355 | 85 | 22 | 128 | 0.6 | 0 | 0
18:00 | 35 | 0 | 130 | 0 | 380 | 0 | 0 | 356 | 304 |  | 0 | 350 | 150 | 7 | 0 | 17 | 12 | 0 | 0 | 0 | 19 | 32 | 149 | 11 | 69 | 0 | 22 | 53 | 55 | 55 | 0 | 25 | 22 | 33 | 33 | 17 | 0 | 36 | 50 | 100 | 0 | 18 | 204 | 0 | 100 | 0 |  | 0 | 0 | 102 | 90 | 38 | 26 | 18 | 3 | 80 | 0 | 0 | 280 | 275 | 190 | 36 | 120 | 33 | 53 | 0 | 25 | 0 | 0 | 1 | 22 | 8 | 33 | 22 | 160 | 150 | 17 | 22 | 0 | 60 | 44 | 22 | 23 | 100 | 99 | 65 | 40 | 40 | 0 | 17 | 27 | 8 | 275 | 24 | 11 | 0 | 224 | 0 | 0 | 127 | 0 | 61 | 0 | 100 | 72 | 3 | 0 | 31 | 70 | 105 | 0 | 0 | 22 | 0 |  | 911 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 39 | 20 | 40 | 150 | 28 | 16 | 0 | 50 | 0 | 34 | 0 | 48 | 40 | 42 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 170 | 0 | 117 | 0 | 70 | 0 | 179 | 0 | 379 | 70 | 0 | 83 | 64 | 100 | 0 | 0 | 0 |  | 6318 | 3404 | 9722 | 4005 | 911 | 1819 | 1991 | 358 | 86 | 392 | 160 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 128 | 0 | 350 | 0 | 0 | 345 | 304 |  | 0 | 350 | 150 | 36 | 10 | 48 | 11 | 0 | 0 | 0 | 0 | 0 | 149 | 16 | 69 | 0 | 47 | 53 | 55 | 55 | 0 | 25 | 31 | 33 | 33 | 8 | 0 | 44 | 50 | 100 | 0 | 25 | 204 | 0 | 100 | 0 |  | 0 | 0 | 70 | 100 | 96 | 50 | 18 | 5 | 80 | 0 | 0 | 270 | 265 | 180 | 36 | 125 | 33 | 53 | 0 | 25 | 0 | 0 | 30 | 22 | 10 | 33 | 22 | 154 | 152 | 72 | 22 | 0 | 60 | 44 | 22 | 46 | 163 | 100 | 67 | 40 | 40 | 0 | 17 | 31 | 8 | 260 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 145 | 0 | 100 | 188 | 10 | 0 | 7 | 70 | 105 | 0 | 0 | 48 | 0 |  | 911 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 40 | 150 | 29 | 16 | 0 | 50 | 0 | 0 | 0 | 25 | 50 | 16 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 160 | 0 | 144 | 0 | 96 | 0 | 176 | 0 | 362 | 70 | 0 | 111 | 103 | 107 | 0 | 0 | 0 |  | 6893 | 3351 | 10244 | 3951 | 911 | 1906 | 2622 | 358 | 94 | 248 | 154 | 0 | 0 | 102.32
19:30 | 35 | 0 | 130 | 0 | 350 | 0 | 0 | 345 | 305 |  | 0 | 350 | 150 | 0 | 0 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 69 | 0 | 47 | 17 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 44 | 50 | 100 | 0 | 25 | 204 | 0 | 100 | 0 |  | 0 | 0 | 68 | 100 | 97 | 50 | 19 | 16 | 80 | 0 | 0 | 270 | 265 | 181 | 36 | 120 | 33 | 53 | 0 | 25 | 0 | 0 | 8 | 22 | 11 | 33 | 22 | 156 | 154 | 95 | 22 | 0 | 60 | 44 | 36 | 46 | 100 | 100 | 67 | 40 | 40 | 0 | 17 | 31 | 8 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 100 | 0 | 100 | 200 | 10 | 0 | 7 | 70 | 105 | 0 | 0 | 54 | 0 |  | 913 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 150 | 29 | 16 | 0 | 60 | 0 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 161 | 0 | 151 | 0 | 96 | 0 | 173 | 0 | 361 | 70 | 0 | 113 | 103 | 107 | 0 | 0 | 0 |  | 6737 | 3333 | 10070 | 4015 | 913 | 1898 | 2443 | 358 | 94 | 193 | 156 | 0 | 0 | 0
20:00 | 35 | 0 | 130 | 0 | 350 | 0 | 0 | 345 | 304 |  | 0 | 350 | 150 | 0 | 0 | 15 | 85 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 69 | 0 | 47 | 17 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 50 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 0 | 0 | 51 | 100 | 97 | 50 | 19 | 18 | 80 | 0 | 0 | 270 | 265 | 181 | 36 | 126 | 33 | 53 | 0 | 25 | 0 | 0 | 0 | 22 | 10 | 33 | 22 | 156 | 154 | 95 | 22 | 0 | 60 | 44 | 52 | 49 | 100 | 100 | 66 | 40 | 40 | 0 | 17 | 32 | 8 | 280 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 97 | 0 | 100 | 200 | 10 | 0 | 7 | 70 | 105 | 0 | 0 | 0 | 0 |  | 913 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 150 | 29 | 16 | 0 | 60 | 0 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 161 | 0 | 152 | 0 | 96 | 0 | 173 | 0 | 361 | 70 | 0 | 113 | 72 | 107 | 0 | 0 | 0 |  | 6690 | 3318 | 10008 | 4084 | 913 | 1909 | 2332 | 358 | 95 | 161 | 156 | 0 | 0 | 102.32
21:00 | 35 | 0 | 130 | 0 | 320 | 0 | 0 | 346 | 300 |  | 0 | 350 | 150 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 69 | 0 | 47 | 0 | 17 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 50 | 100 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 51 | 100 | 64 | 19 | 0 | 20 | 80 | 0 | 0 | 270 | 270 | 180 | 36 | 120 | 33 | 53 | 0 | 25 | 0 | 0 | 0 | 22 | 10 | 33 | 22 | 156 | 155 | 72 | 22 | 0 | 60 | 44 | 53 | 49 | 100 | 100 | 67 | 77 | 40 | 0 | 17 | 31 | 8 | 270 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 60 | 0 | 30 | 168 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 913 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 130 | 28 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 163 | 0 | 150 | 0 | 95 | 0 | 172 | 0 | 368 | 67 | 0 | 113 | 68 | 107 | 0 | 0 | 0 |  | 6459 | 3270 | 9729 | 4269 | 913 | 1939 | 1932 | 358 | 95 | 67 | 156 | 0 | 0 | 102.32
22:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 351 | 300 |  | 0 | 350 | 150 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 34 | 0 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 50 | 100 | 0 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 51 | 50 | 6 | 18 | 0 | 37 | 80 | 0 | 0 | 270 | 270 | 190 | 36 | 120 | 33 | 54 | 0 | 25 | 0 | 0 | 0 | 22 | 10 | 33 | 22 | 146 | 152 | 0 | 22 | 0 | 60 | 44 | 53 | 49 | 100 | 100 | 66 | 77 | 40 | 0 | 17 | 31 | 8 | 280 | 24 | 11 | 0 | 70 | 0 | 0 | 200 | 0 | 34 | 0 | 0 | 50 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 920 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 141 | 27 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 170 | 0 | 153 | 0 | 95 | 0 | 165 | 0 | 382 | 35 | 0 | 104 | 69 | 56 | 0 | 0 | 0 |  | 5801 | 3156 | 8957 | 4278 | 920 | 1980 | 1129 | 358 | 95 | 51 | 146 | 0 | 0 | 102.18
23:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 345 | 300 |  | 0 | 350 | 150 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 47 | 50 | 100 | 0 | 0 | 204 | 0 | 120 | 0 |  | 0 | 0 | 51 | 50 | 0 | 18 | 18 | 38 | 80 | 0 | 0 | 280 | 275 | 172 | 36 | 125 | 33 | 53 | 0 | 25 | 0 | 0 | 0 | 22 | 10 | 33 | 22 | 140 | 154 | 0 | 22 | 0 | 60 | 44 | 53 | 49 | 100 | 101 | 66 | 40 | 40 | 0 | 17 | 31 | 9 | 290 | 24 | 11 | 0 | 70 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 17 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 920 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 26 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 163 | 0 | 153 | 0 | 95 | 0 | 163 | 0 | 381 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 5657 | 2883 | 8540 | 4300 | 920 | 1952 | 722 | 358 | 97 | 51 | 140 | 0 | 0 | 102.18
24:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 339 | 300 |  | 0 | 330 | 150 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 22 | 25 | 32 | 0 | 33 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 204 | 0 | 110 | 0 |  | 0 | 0 | 34 | 30 | 0 | 0 | 19 | 38 | 80 | 0 | 0 | 270 | 270 | 180 | 36 | 125 | 33 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 10 | 33 | 20 | 130 | 154 | 0 | 22 | 0 | 58 | 44 | 53 | 49 | 100 | 100 | 66 | 10 | 40 | 0 | 17 | 31 | 9 | 285 | 24 | 11 | 0 | 70 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 920 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 27 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 68 | 290 | 0 | 0 | 165 | 0 | 139 | 0 | 99 | 0 | 165 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5377 | 2806 | 8183 | 4207 | 920 | 1911 | 533 | 358 | 90 | 34 | 130 | 0 | 0 | 102.18
KWH | 790000 | 0 | 2504000 | 0 | 7582455 | 0 | 0 | 8641900 | 7231000 |  | 0 | 8597250 | 4988742 | 57600 | 13392 | 177792 | 1374560 | 0 | 0 | 0 | 34560 | 37728 | 433440 | 32936 | 733440 | 0 | 600624 | 194040 | 344479 | 191328 | 293868 | 600000 | 700020 | 739763 | 823500 | 100404 | 0 | 1018298 | 1176000 | 2400000 | 0 | 73832 | 5053553 | 0 | 2570933 | 0 |  | 0 | 0 | 412250 | 1034880 | 457920 | 365760 | 419808 | 465120 | 1957428 | 0 | 0 | 7173500 | 6845000 | 4316000 | 585454 | 2985370 | 682200 | 1024320 | 0 | 408316 | 0 | 0 | 42134 | 362556 | 152820 | 575100 | 507500 | 3080640 | 3581680 | 288000 | 400968 | 12750 | 1427000 | 1036560 | 619800 | 768456 | 2927356 | 2323000 | 1537344 | 709440 | 690840 | 0 | 269000 | 499620 | 164340 | 7422250 | 582408 | 211108 | 0 | 2870399 | 0 | 0 | 1768800 | 0 | 699840 | 126090 | 380160 | 848160 | 35127 | 0 | 85200 | 1144296 | 1960436 | 25680 | 0 | 114196 | 0 |  | 20401454 | 0 | 7858656 | 0 | 36480 | 0 | 0 | 0 | 53760 | 27904 | 186000 | 3621923 | 521693 | 70368 | 0 | 1256000 | 0 | 44992 | 0 | 187060 | 254780 | 74235 | 0 | 20640 | 0 | 364800 | 259632 | 208060 | 0 | 1555636 | 7012900 | 0 | 0 | 4418355 | 0 | 1179909 | 0 | 1312706 | 0 | 4428582 | 0 | 8967490 | 337920 | 0 | 580704 | 422208 | 554880 | 0 | 39496 | 131520 |  | 129495817 | 66390743 | 195886560 | 94392387 | 20401454 | 43539883 | 22345940 | 8568536 | 2194298 | 1159406 | 3080640 | 204016 | 0
Fuel Cost | 884800 | 0 | 2679280 | 0 | 5611016.7 | 0 | 0 | 6222168 | 5495560 |  | 0 | 6877800 | 4489867.8 | 587520 | 145035.36 | 1824145.92 | 1704454.4 | 0 | 0 | 0 | 383616 | 383316.48 | 4295390.4 | 345169.28 | 6674304 | 0 | 5621840.64 | 1860843.6 | 3286329.66 | 1905626.88 | 220401 | 450000 | 0 | 0 | 0 | 961870.32 | 0 | 264757.48 | 305760 | 3672000 | 0 | 709525.52 | 5306230.65 | 0 | 3265084.91 | 0 |  | 0 | 0 | 4324502.5 | 10648915.2 | 4354819.2 | 3423513.6 | 386223.36 | 1293033.6 | 2055299.4 | 0 | 0 | 5308390 | 5749800 | 3970720 | 573744.92 | 3970542.1 | 559404 | 1055049.6 | 0 | 583891.88 | 0 | 0 | 396059.6 | 369807.12 | 114615 | 1086939 | 380625 | 21256416 | 2936977.6 | 2738880 | 408987.36 | 209100 | 1940720 | 1409721.6 | 842928 | 960570 | 3629921.44 | 2137160 | 2290642.56 | 1248614.4 | 766832.4 | 0 | 427710 | 584555.4 | 386199 | 5269797.5 | 436806 | 160442.08 | 0 | 30053077.53 | 0 | 0 | 17015856 | 0 | 7061385.6 | 1455078.6 | 3543091.2 | 7955740.8 | 329139.99 | 0 | 747204 | 10195677.36 | 18526120.2 | 0 | 0 | 0 | 0 |  | 55083925.8 | 0 | 6129751.68 | 0 | 351667.2 | 0 | 0 | 0 | 623616 | 365542.4 | 1839540 | 2897538.4 | 808624.15 | 755752.32 | 0 | 2361280 | 0 | 501210.88 | 0 | 1851894 | 2642068.6 | 869291.85 | 0 | 205574.4 | 0 | 401280 | 428392.8 | 157501.42 | 0 | 9909401.32 | 28682761 | 0 | 0 | 3888152.4 | 0 | 1097315.37 | 0 | 2087202.54 | 0 | 3897152.16 | 0 | 6546267.7 | 3196723.2 | 0 | 5330862.72 | 3761873.28 | 5182579.2 | 0 | 0 | 0 |  | 273964962.7 | 151854742.79 | 425819705.49 | 86545659.27 | 55083925.8 | 39840265.33 | 170304424.51 | 38592162.32 | 570517.48 | 11962156.18 | 21256416 | 1664178.6 | 0
Yesterday Day Peak | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 375 | 305 |  | 0 | 400 | 230 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 20 | 0 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 40 | 50 | 100 | 0 | 0 | 226 | 0 | 146 | 0 |  | 0 | 0 | 0 | 50 | 0 | 18 | 19 | 2 | 80 | 0 | 0 | 320 | 290 | 198 | 36 | 125 | 33 | 50 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 19 | 128 | 148 | 0 | 22 | 2.2 | 60 | 44 | 5 | 30 | 130 | 104 | 60 | 10 | 40 | 0 | 17 | 28 | 10 | 320 | 24 | 11 | 0 | 152 | 0 | 0 | 40 | 0 | 10 | 19.7 | 0 | 8 | 0 | 0 | 0 | 70 | 105 | 4.6 | 0 | 0 | 0 |  | 930 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 63 | 290 | 0 | 0 | 181 | 0 | 0 | 0 | 40 | 0 | 185 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 28 |  | 8198.7 | DayPeak
Yesterday Evening Peak | 35 | 0 | 128 | 0 | 350 | 0 | 0 | 345 | 304 | 0 | 0 | 350 | 150 | 36 | 10 | 48 | 11 | 0 | 0 | 0 | 0 | 0 | 149 | 16 | 69 | 0 | 47 | 53 | 55 | 55 | 0 | 25 | 31 | 33 | 33 | 8 | 0 | 44 | 50 | 100 | 0 | 25 | 204 | 0 | 100 | 0 | 0 | 0 | 0 | 70 | 100 | 96 | 50 | 18 | 5 | 80 | 0 | 0 | 270 | 265 | 180 | 36 | 125 | 33 | 53 | 0 | 25 | 0 | 0 | 30 | 22 | 10 | 33 | 22 | 154 | 152 | 72 | 22 | 0 | 60 | 44 | 22 | 46 | 163 | 100 | 67 | 40 | 40 | 0 | 17 | 31 | 8 | 260 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 145 | 0 | 100 | 188 | 10 | 0 | 7 | 70 | 105 | 0 | 0 | 48 | 0 |  | 911 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 40 | 150 | 29 | 16 | 0 | 50 | 0 | 0 | 0 | 25 | 50 | 16 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 160 | 0 | 144 | 0 | 96 | 0 | 176 | 0 | 362 | 70 | 0 | 111 | 103 | 107 | 0 | 0 | 0 |  | 10244 | EvPeak
Forecast for Evening | 35 | 0 | 150 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 100 | 0 | 25 | 215 | 0 | 135 | 0 | 0 | 0 | 0 | 100 | 100 | 96 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 360 | 225 | 36 | 140 | 33 | 55 | 0 | 30 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 164 | 160 | 95 | 22 | 0 | 60 | 44 | 51 | 50 | 163 | 100 | 66 | 77 | 40 | 0 | 20 | 30 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 70 | 105 | 0 | 260 | 54 | 110 |  | 689 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 70 | 40 | 180 | 33 | 110 | 30 | 60 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 35 | 22 | 14 | 11 | 0 | 68 | 290 | 17 | 17 | 225 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 100 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 335 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 45 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 100 | 0 | 25 | 215 | 0 | 135 | 0 | 0 | 0 | 0 | 100 | 100 | 96 | 50 | 22 | 6 | 100 | 0 | 0 | 360 | 360 | 225 | 36 | 140 | 33 | 55 | 0 | 30 | 0 | 8 | 52 | 22 | 11 | 33 | 22 | 120 | 160 | 95 | 22 | 1.6 | 60 | 44 | 51 | 50 | 163 | 100 | 66 | 75 | 40 | 0 | 20 | 30 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 70 | 51 | 4.4 | 230 | 54 | 110 |  | 689 | 0 | 410 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 60 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 225 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 372 | 288 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 205 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 80 | 0 | 0 | 285 | 280 | 195 | 8 | 126 | 30 | 5 | 0 | 5 | 0 | 0 | 0 | 11 | 0 | 0 | 17 | 96 | 156 | 0 | 22 | 0.6 | 59 | 44 | 5 | 17 | 100 | 0 | 66 | 10 | 40 | 0 | 0 | 21 | 8 | 315 | 0 | 0 | 0 | 31 | 0 | 0 | 19 | 0 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1.8 | 0 | 0 | 0 | 0 | 520 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 13 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 5 | 0 | 68 | 290 | 0 | 0 | 171 | 0 | 0 | 0 | 12 | 0 | 177 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0
199
| Minimum Generation |  | 6567 | 6:00
| Highest Generation |  | 10244 | 19:00
| Day Peak Generation |  | 8198.7 | 12:00
| Evening Peak Generation |  | 10244 | 19:00
| HVDC Max Flow |  | 931 | 9:00
| HVDC EvPeak Flow |  | 911 | 19:00
| Load factor L.F |  | 79.68%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-10-31
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-10-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8198.7 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 6541 | MW
Evening Peak Generation : |  | 10244 | MW Hour : | 19:00 | Available Max Generation : |  | 14491 | MW
E.P. Demand (at gen end) : |  | 10244 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10400 | MW
Maximum Generation : |  | 10244 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4091 | MW
Total Gen. (MKWH) : |  | 195.8866 | System Load Factor : | 79.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 296 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-10-31
Actual : | 102.1 | Ft.(MSL) , | Rule curve : | 108.9 | Ft.( MSL )
Gas Consumed : | Total = | 1165.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 126385924.6
: |  | Coal : | 38592162.32 | Oil : | 182266580.69 | Total : | 347244667.61
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3696.9244 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1255.339 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1124.4179 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1015.8913 |  |  | 0 | 0%
) | 0 | 0:00 | 918.1097 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 740.8775 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 416.6041 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 190.818 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 571.3903 |  |  | 0 | 0%
Total | 0 |  | 9930.3722 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-1,3 & 5
4) Sirajganj 225 MW Unit-2
5) Raozan #2
6) Ashuganj unit-4 & 5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Jamalpur 132/33 kV T4 transformer was under shut down from 12:15 to 17:13 for tan delta test.
b) Tongi-Bashundhara 132 kV Ckt-2 was under shut down from 08:33 to 15:33 for A/M.
c) Mirpur-Uttara-18 132 kV Ckt was under shut down from 08:30 to 20:58 for A/M.
d) Kishoreganj 132/33 kV T1 transformer was under shut down from 09:42 to 12:49 for C/M.
e) Joypurhat 132/33 kV T4 transformer was under shut down from 08:37 to 17:15 for A/M.
f) After maintenance Siddhirganj 335 MW EGCB GT and ST were synchronized at 11:06 and 16:47 respectively.
g) Sirajganj unit-2 GT & ST were synchronized at 12:56 & 15:21 respectively for HRSG preservation test
and after completion of test ST & GT were shut down at 00:22(31/10/2019) & 00:37(31/10/2019) respectively.
h) Mirpur-Aminbazar 132 kV Ckt-1 was under shut down from 09:27 to 17:34 for A/M.
i) Madunaghat-Sikalbaha 132 kV Ckt was shut down at 07:14(31/10/2019).
j) Barishal-Patuakhali 132 kV Ckt was under shut down from 07:04(31/10/2019) to 08:17(31/10/2019) for CT loop |  |  |  |  | About 30 MW power interruption occurred under Patuakhali and Payra S/S
R/H maintenance at Patuakhali end. |  |  |  |  | area from 07:04(31/10/2019) to 08:17(31/10/2019).
k) Shahjibazar 330 MW CCPP GT-2 was shut down at 07:13(31/10/2019) for synchronizing ST.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-10-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 790000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 128 | 2504000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 7582455
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8641900 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 304 | 7231000 | Frequency control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8597250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 36 | 57600 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 4988742 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 10 | 13392 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 48 | 177792 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 16 | 32936 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 293868 | Engine tripped at 16:38
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 34560 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 11 | 1374560
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 37728 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 600624 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 194040
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 433440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 344479
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 191328
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 69 | 733440 | Low demand
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1300020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 739763
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 823500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 100404 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 2870399
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 145 | 699840
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 1144296 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2856 | 52533356
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 73832
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126090
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 365760
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 94 | 2194298 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 5053553
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2570933 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1960436
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 70 | 412250 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1034880
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 380160
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 419808
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 465120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 457920 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25680
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 48 | 114196
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1115 | 18054916
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1957428 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4316000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7173500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6845000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 682200 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1024320
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 585454 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 25 | 408316 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 35127 | Transformer over load
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 125 | 2985370
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 188 | 848160
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 362556
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 152820 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3080640
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 575100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 30 | 42134 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 507500
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1536 | 31581625
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 152 | 3581680 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 400968
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 288000 | High voltage
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 1768800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 7 | 85200 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 453 | 6137398
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1427000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 44 | 1036560
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 2927356
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2323000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 619800 | Engine problem
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 768456
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 211108
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1537344 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 709440 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 690840 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 269000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 31 | 499620 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 582408
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7422250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 164340
| Sylhet Area Total |  |  |  | 1949 | 933 | 21188522
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 911 | 20401454
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 36480 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 53760 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 27904 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 7858656 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 186000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 337920 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 103 | 422208
| Khulna Area Total |  |  |  | 2314 | 1454 | 29324382
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 70368 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 521693 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 150 | 3621923 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1312706
| Barisal Area Total |  |  |  | 462 | 291 | 5526690
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 1256000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 44992 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 254780
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 16 | 74235 | Low demand
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4418355 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 144 | 1179909 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 4428582 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 362 | 8967490 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 364800
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 259632
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 208060
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 20640 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 25 | 187060 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 111 | 580704
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 131520 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1141 | 22376759
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 68 | 1555636
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 290 | 7012900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 554880
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39496
| Rangpur Area Total |  |  |  | 605 | 465 | 9162912
| Total |  |  |  | 19018 | 10244 | 195886560
| Eastern Grid Total |  |  |  | 13454 | 6893 | 129495817
| Western Grid Total |  |  |  | 5564 | 3351 | 66390743
| National Grid Total |  |  |  | 19018 | 10244 | 195886560
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-10-30
(a) ENTIRE EASTERN GRID : |  | 6928 | MW | (b) ENTIRE WESTERN GRID : |  | 2843 | MW
i) Dhaka area |  | 3741 | MW | i) Khulna area |  | 1086 | MW
ii) Chittagong area |  | 1107 | MW | ii) Rajshahi area |  | 925 | MW
iii) Comilla area |  | 923 | MW | iii) Barisal area |  | 270 | MW
iv) Mymensingh area |  | 730 | MW | iv) Rangpur area |  | 562 | MW
v) Sylhet area |  | 427 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9771 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 1830 | Srimongal | 33 | 1830 | Bottail | 102 | 1800
Munsiganj | 94 | 1800 | Shahjibazar | 98 | 1830 | G.K Project | 42 | 1800
Sonargaon | 72 | 1000 | Fenchuganj | 33 | 1830 | Faridpur | 140 | 1830
Shyampur | 180 | 2300 | Kulawara | 40 | 1800 | Madaripur | 64 | 1800
Bhulta | 185 | 1830 | Sylhet | 131 | 1830 | Sariatpur | 44 | 1800
Madanganj | 42 | 100 | Chatak | 23 | 1830 | Gopalganj | 71 | 1900
Shitalakhya | 100 | 1400 | Sunamganj | 35 | 1830 | Bagerhat | 69 | 1800
Rahim steel | 20 | 1200 | Biani Bazar | 44 | 1830 | Mongla | 38 | 1000
Matuail | 96 | 900 | Comilla (S) | 160 | 1800 | Satkhira | 69 | 1800
Ghorasal | 77 | 1900 | Comilla(N) | 99 | 2100 | Gallamari | 40 | 1200
Narsingdi | 119 | 1930 | Chandpur | 83 | 1900 | Magura | 38 | 1800
Haripur (SBU) | 89 | 1700 | Feni | 122 | 1930 | Norail | 19 | 1830
Ullon | 65 | 1900 | Chowmuhani | 148 | 2000 | Chuadanga | 64 | 1800
Hasnabad | 175 | 1800 | Ashuganj | 49 | 2100 | Barisal(N) | 34 | 1900
Magbazar | 103 | 1300 | Daudkandi | 106 | 1800 | Barisal (S) | 86 | 1800
Maniknagar | 104 | 1800 | B.Baria | 122 | 1800 | Patuakhali | 87 | 1930
Bangabhaban | 19 | 1200 | Ramganj | 68 | 1900 | Bhandaria | 42 | 2000
Narinda | 90 | 1800 | Madunaghat | 54.5 | 1830 | Borhan Uddin | 31 | 1930
Dhanmondi | 148 | 1300 | Hathazari | 97 | 1800 | Ishurdi | 50 | 1830
Lalbag | 82 | 1800 | Khulshi | 187 | 1600 | Ruppur Paromanobik | 1 | 100
Madartek | 60 | 1900 | Halishahar | 138 | 1500 | Natore | 98 | 1800
Mirpur | 97 | 1800 | Baraulia | 160 | 600 | Bogra | 157 | 1830
Kalyanpur | 87 | 1800 | Sikalbaha | 31 | 1900 | Noagaon | 84 | 1930
Gulshan | 134 | 1300 | Dohazari | 76 | 1900 | Rajshahi | 104 | 1830
Uttara | 50 | 1800 | Cox'sbazar | 95 | 1830 | Rajshahi New | 9 | 1800
Uttara New | 36 | 1800 | Chandraghona | 28 | 1800 | C.Nawabganj | 55 | 1930
Kamrangirchar | 70 | 1800 | Kaptai | 4.6 | 1800 | Amnura | 23 | 1830
Savar | 125 | 1800 | A. Khaer Stl. | 5 | 400 | Pabna | 87 | 1800
Bhasantec | 146 | 1800 | Bakulia | 104 | 1800 | Shahjadpur | 84 | 1900
Agargaon | 50 | 1300 | Julda | 21 | 1830 | Serajganj | 74 | 1900
Satmosjid | 99 | 1800 | TK chemical | 14.5 | 1930 | Niyamatpur | 42 | 1900
Tongi | 141 | 1500 | Modern Steel | 12 | 200 | Joypurhat | 44 | 1830
Kabirpur | 188 | 1830 | Shahmirpur | 23 | 1800 | Sherpur(Bogura) | 32 | 1830
Basundhara | 94 | 1800 | Khagrachhari | 18 | 1800 | Mohastangor | 12 | 1800
Manikganj | 68 | 2000 | Matarbari | 28 | 1830 | Rangpur | 111 | 1830
Joydevpur | 194 | 1830 | Baroiar Hat | 22 | 1800 | Lalmonirhat | 43 | 1830
New Tongi | 96 | 1800 | Rangamati | 12 | 1800 | Saidpur | 86 | 1800
Korda | 228 | 1500 | Abul Khair 230 | 7 | 1200 | Purbasadipur | 78 | 1830
Dhamrai | 52 | 1830 | BSRM | 107 | 1700 | Thakurgaon | 56 | 1830
Valuka | 88 | 1500 | GPH Ispat | 0.09 | 1200 | Palashbari | 92 | 1800
Tangail | 147 | 1830 | Goalpara | 12 | 1830 | Barapukuria | 41 | 1800
Mymensing | 177 | 1800 | Central s/s | 87 | 1800 | Panchagar | 38 | 1900
Kishorganj | 98 | 1830 | Noapara | 52 | 1830 | Joldhaka | 20 | 1830
Netrokona | 81 | 1800 | Jessore | 98 | 1830 | Kurigram | 38 | 1800
Jamalpur | 87 | 1830 | Benapol | 30 | 1800
Sherpur | 78 | 1830 | Jhenida | 73 | 1830
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-10-30 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 388 | 18:30 | 379 | 9:00 | Kaliakoir | 369 | 14:00 | 357 | 11:00
Bheramara | 401 | 2:00 | 387 | 18:30 | Bhulta | 375 | 5:00 | 363 | 11:00
Ashuganj(N) | 380 | 7:00 | 368 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
Ghorasal | 228 | 19:00 | 220 | 14:00 | Hathazari | 215 | 7:00 | 210 | 16:00
Ishurdi | 236 | 1:00 | 226 | 9:00 | Megnaghat | 220 | 1:00 | 212 | 10:00
Ashuganj | 232 | 18:30 | 224 | 10:00 | Fenchuganj | 233 | 17:00 | 228 | 10:00
Serajganj | 231 | 3:00 | 229 | 8:00 | Siddhirganj | 220 | 5:00 | 213 | 10:00
Baghabari | 235 | 1:00 | 231 | 10:00 | Maniknagar | 218 | 2:00 | 210 | 11:00
Barapukuria | 230 | 5:00 | 226 | 11:00 | Old Airport | 217 | 2:00 | 209 | 11:00
Bogra | 232 | 5:00 | 226 | 12:00 | Barisal | 231 | 2:00 | 221 | 11:00
Khulna South | 230 | 24:00 | 209 | 13:00 | AKSML | 213 | 19:00 | 207 | 4:00
Rampura | 220 | 1:00 | 210 | 12:00 | BSRM | 216 | 18:30 | 209 | 10:00
Haripur | 219 | 5:00 | 212 | 10:00 | Bibiyana | 232 | 18:30 | 224 | 9:00
Hasnabad | 216 | 4:00 | 213 | 17:00 | Bhulta | 221 | 6:00 | 213 | 11:00
Aminbazar | 219 | 5:00 | 211 | 11:00 | Ashuganj (S) | 230 | 18:30 | 222 | 10:00
Tongi | 220 | 18:00 | 208 | 15:00 | Kaliakoir | 223 | 18:30 | 212 | 11:00
Comilla (N) | 226 | 8:00 | 220 | 11:00 | GPH | 214 | 19:00 | 207 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 600 | 126 | 1000 | Halishahar | 128 | 700 | 122 | 2000
Munsiganj | 132 | 1830 | 124 | 1000 | Baraulia | 128 | 1830 | 122 | 600
Megnaghat | 128 | 1830 | 124 | 1100 | Sikalbaha | 131 | 1830 | 124 | 500
Shyampur | 132 | 400 | 127 | 1000 | Dohazari | 129 | 1830 | 122 | 200
Bhulta | 125 | 1800 | 120 | 1100 | Cox'sbazar | 121 | 800 | 111 | 100
Madanganj | 133 | 1830 | 125 | 1100 | Chandraghona | 130 | 1800 | 124 | 1500
Shitalakhya | 134 | 1800 | 126 | 1200 | Kaptai | 130 | 1830 | 126 | 800
Rahim steal | 131 | 500 | 126 | 1200 | A. Khaer Stl. | 127 | 1900 | 124 | 100
Matuail | 130 | 600 | 125 | 900 | Bakulia | 129 | 1900 | 122 | 1100
Ghorasal | 135 | 100 | 132 | 1600 | Julda | 130 | 1830 | 124 | 400
Narsinghdi | 131 | 600 | 127 | 1200 | TK Chemical | 130 | 1900 | 125 | 500
Haripur (SBU) | 131 | 500 | 127 | 900 | Modern Steel | 129 | 1930 | 122 | 300
Ullon | 133 | 600 | 127 | 1200 | Shahmirpur | 131 | 1900 | 124 | 100
Hasnabad | 133 | 600 | 127 | 1200 | Khagrachhari | 129 | 1830 | 123 | 400
Magbazar | 134 | 600 | 127 | 1200 | Matarbari | 121 | 900 | 112 | 300
Maniknagar | 134 | 600 | 127 | 1500 | Baroiar Hat | 126 | 1800 | 122 | 1100
Bangabhaban | 134 | 600 | 127 | 1500 | Rangamati | 129 | 1830 | 124 | 1500
Narinda | 134 | 600 | 127 | 1500 | Goalpara | 135 | 600 | 126 | 1200
Dhanmondi | 133 | 600 | 127 | 1200 | Central s/s | 135 | 600 | 126 | 1200
Lalbag | 133 | 600 | 124 | 1200 | Noapara | 133 | 300 | 123 | 1200
Madartek | 133 | 600 | 127 | 1100 | Jessore | 130 | 600 | 124 | 800
Mirpur | 132 | 400 | 128 | 1500 | Benapol | 132 | 600 | 124 | 900
Kalyanpur | 135 | 300 | 130 | 1000 | Jhenida | 131 | 300 | 124 | 1800
Gulshan | 134 | 300 | 126 | 1100 | Bottail | 136 | 100 | 131 | 1200
Uttara | 132 | 400 | 124 | 1000 | G.K Project | 142 | 100 | 128 | 900
Uttara New | 132 | 200 | 121 | 1000 | Faridpur | 132 | 300 | 125 | 2000
Kamrangirchar | 132 | 500 | 124 | 1100 | Madaripur | 133 | 200 | 124 | 1100
Savar | 131 | 400 | 125 | 1100 | Sariatpur | 134 | 1700 | 125 | 1100
Bhasantec | 134 | 600 | 127 | 1100 | Gopalganj | 137 | 1700 | 125 | 1000
Agargaon | 135 | 500 | 128 | 1200 | Bagerhat | 134 | 300 | 121 | 1300
Satmosjid | 134 | 200 | 128 | 1100 | Mongla | 132 | 200 | 123 | 1000
Tongi | 133 | 1800 | 124 | 100 | Satkhira | 132 | 200 | 125 | 1200
Kabirpur | 131 | 1830 | 118 | 1100 | Gallamari | 136 | 200 | 126 | 1300
Basundhara | 130 | 1800 | 121 | 1500 | Magura | 133 | 700 | 123 | 1800
Manikganj | 136 | 1830 | 125 | 1100 | Norail | 132 | 500 | 122 | 1830
Joydevpur | 140 | 1900 | 129 | 1200 | Chuadanga | 131 | 500 | 120 | 1800
New Tongi | 132 | 1830 | 122 | 1100 | Barisal(N) | 137 | 1700 | 128 | 1100
Kodda | 130 | 1900 | 120 | 1000 | Barisal (S) | 135 | 1700 | 128 | 1100
Dhamrai | 129 | 2100 | 125 | 1300 | Patuakhali | 134 | 500 | 125 | 1100
Valuka | 126 | 1830 | 119 | 1300 | Bhandaria | 134 | 200 | 125 | 1000
Tangail | 130 | 100 | 124 | 1300 | Ishurdi | 140 | 500 | 135 | 1200
Mymensing | 129 | 2100 | 121 | 1300 | Ruppur Paromanobik | 140 | 300 | 134 | 1200
Kishorganj | 132 | 400 | 125 | 1300 | Natore | 137 | 400 | 130 | 1200
Netrokona | 128 | 2100 | 120 | 1300 | Bogra | 136 | 100 | 131 | 1300
Jamalpur | 139 | 1830 | 122 | 700 | Noagaon | 133 | 500 | 127 | 1300
Sherpur | 138 | 1830 | 122 | 800 | Rajshahi | 134 | 1800 | 124 | 1300
Srimongal | 135 | 100 | 132 | 1300 | Rajshahi New | 134 | 1800 | 124 | 1200
Shahjibazar | 133 | 300 | 130 | 1200 | C.Nawabganj | 131 | 1830 | 120 | 1200
Fenchuganj | 133 | 1700 | 124 | 2400 | Amnura | 135 | 1800 | 121 | 1200
Khulawara | 132 | 500 | 129 | 1800 | Pabna | 140 | 200 | 134 | 1200
Sylhet | 130 | 100 | 126 | 1800 | Shahjadpur | 142 | 100 | 138 | 900
Chatak | 131 | 200 | 125 | 1800 | Serajganj | 138 | 300 | 131 | 1100
Sunamganj | 130 | 700 | 123 | 1830 | Niyamatpur | 132 | 400 | 126 | 1300
Biani Bazar | 131 | 400 | 125 | 1800 | Joypurhat | 135 | 500 | 128 | 1300
Comilla(s) | 128 | 600 | 123 | 1800 | Sherpur(Bogura) | 136 | 100 | 131 | 1200
Comilla(n) | 133 | 1800 | 131 | 1000 | Mohastangor | 134 | 300 | 129 | 800
Chandpur | 130 | 700 | 128 | 1500 | Rangpur | 127 | 1700 | 121 | 1300
Feni | 125 | 800 | 122 | 2400 | Lalmonirhat | 125 | 600 | 117 | 1300
Chowmuhani | 123 | 800 | 120 | 1600 | Saidpur | 127 | 500 | 119 | 1830
Ashuganj | 136 | 800 | 133 | 1300 | Purbasadipur | 127 | 200 | 120 | 1400
Daudkandi | 129 | 700 | 125 | 1100 | Thakurgaon | 123 | 400 | 112 | 1830
B.Baria | 132 | 700 | 129 | 1200 | Palashbari | 133 | 400 | 123 | 1300
Ramganj | 125 | 1900 | 123 | 2200 | Barapukuria | 130 | 500 | 126 | 1100
Madanhat | 131 | 1900 | 126 | 300 | Panchagar | 122 | 600 | 108 | 1830
Hathazari | 130 | 1400 | 125 | 1500 | Joldhaka | 127 | 1700 | 118 | 1830
Khulshi | 128 | 1830 | 122 | 600 | Kurigram | 127 | 1700 | 118 | 1200
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-10-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 590 | 5377 | 2806 | 8183 |  |  |  | QF-LDC-12
0:30 | 565 | 5118.5 | 2730 | 7848.5 | Date: | 2019-10-30
1:00 | 540 | 4860 | 2654 | 7514
1:30 | 540 | 4862 | 2528.5 | 7390.5
2:00 | 540 | 4864 | 2403 | 7267
2:30 | 555 | 4720.5 | 2383.5 | 7104 | [5 empty] | Gen. at Eve. Peak | 10244 | 8095 MW (19:00 )
3:00 | 570 | 4577 | 2364 | 6941 | [6 empty] | 19:00
3:30 | 595 | 4480 | 2365.5 | 6845.5 | [5 empty] | Gen. at Day Peak | 8198.7 | 6206.6 MW (12:00 )
4:00 | 620 | 4383 | 2367 | 6750 | [6 empty] | 12:00
4:30 | 600 | 4371 | 2346.5 | 6717.5 | [5 empty] | Highest Generation | 10244
5:00 | 580 | 4359 | 2326 | 6685 | [6 empty] | 19:00
5:30 | 547 | 4307.5 | 2318.5 | 6626
6:00 | 514 | 4256 | 2311 | 6567
6:30 | 452 | 4311.8285 | 2338.85 | 6650.6785
7:00 | 390 | 4367.657 | 2366.7 | 6734.357
7:30 | 455 | 4396.2285 | 2365.3 | 6761.5285
8:00 | 520 | 4424.8 | 2363.9 | 6788.7
8:30 | 635 | 4499.9 | 2466.05 | 6965.95
9:00 | 750 | 4575 | 2568.2 | 7143.2
9:30 | 780 | 4738.5 | 2596.9 | 7335.4
10:00 | 810 | 4902 | 2625.6 | 7527.6
10:30 | 755 | 5058.8 | 2647.2 | 7706
11:00 | 700 | 5215.6 | 2668.8 | 7884.4
11:30 | 638 | 5359.55 | 2682 | 8041.55
12:00 | 576 | 5503.5 | 2695.2 | 8198.7
12:30 | 565 | 5558.5 | 2701.6 | 8260.1
13:00 | 554 | 5613.5 | 2708 | 8321.5
13:30 | 560 | 5574.85 | 2699.2 | 8274.05
14:00 | 566 | 5536.2 | 2690.4 | 8226.6
14:30 | 628 | 5557.375 | 2689 | 8246.375
15:00 | 690 | 5578.55 | 2687.6 | 8266.15
15:30 | 705 | 5575.805 | 2693.4 | 8269.205
16:00 | 720 | 5573.06 | 2699.2 | 8272.26
16:30 | 750 | 5520.78 | 2733.65 | 8254.43
17:00 | 780 | 5468.5 | 2768.1 | 8236.6
17:30 | 575 | 5893.25 | 3086.05 | 8979.3
18:00 | 370 | 6318 | 3404 | 9722
18:30 | 333 | 6605.5 | 3377.5 | 9983
19:00 | 296 | 6893 | 3351 | 10244
19:30 | 310 | 6737 | 3333 | 10070
20:00 | 330 | 6690 | 3318 | 10008 |  |  |  | Executive Engineer
20:30 | 355 | 6574.5 | 3294 | 9868.5 |  |  |  | Network Operation Division
21:00 | 380 | 6459 | 3270 | 9729
21:30 | 475 | 6130 | 3213 | 9343
22:00 | 570 | 5801 | 3156 | 8957 |  |  |  |  | Page 6 of 7
22:30 | 566 | 5729 | 3019.5 | 8748.5
23:00 | 562 | 5657 | 2883 | 8540
23:30 | 576 | 5517 | 2844.5 | 8361.5
24:00 | 590 | 5377 | 2806 | 8183
8095 MW (19:00 )
6206.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-10-30 |  | Energy | 195886560
[10 empty] | 2019-10-30 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4207 | 920 | 1911 | 533 | 358 | 90 | 34 | 0 | 130
0:30 | 3941.5 | 925 | 1893 | 493 | 356 | 93 | 21 | 0 | 126 | Date: | 2019-10-30
1:00 | 3676 | 930 | 1875 | 453 | 354 | 96 | 8 | 0 | 122
1:30 | 3673.5 | 807 | 1885.5 | 446 | 353.5 | 96 | 8 | 0 | 121 | [7 empty] | Total Energy | 195.8866 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3671 | 684 | 1896 | 439 | 353 | 96 | 8 | 0 | 120 | [7 empty] | Energy not Served | 0
2:30 | 3689 | 684 | 1777.5 | 375.5 | 354 | 96 | 8 | 0 | 120 | [7 empty] | Energy Requirement | 195.8866
3:00 | 3707 | 684 | 1659 | 312 | 355 | 96 | 8 | 0 | 120
3:30 | 3674.5 | 684 | 1614.5 | 296 | 354.5 | 96 | 8 | 0 | 118 | [6 empty] | Shortage
4:00 | 3642 | 684 | 1570 | 280 | 354 | 96 | 8 | 0 | 116
4:30 | 3632 | 684 | 1548.5 | 280 | 354 | 96 | 8 | 0 | 115
5:00 | 3622 | 684 | 1527 | 280 | 354 | 96 | 8 | 0 | 114
5:30 | 3575.5 | 684 | 1523 | 280 | 354.5 | 93 | 8 | 0 | 108
6:00 | 3529 | 684 | 1519 | 280 | 355 | 90 | 8 | 0 | 102
6:30 | 3601 | 684 | 1527.5 | 284.5 | 355 | 91 | 8 | 0 | 97 |  |  |  |  | Coal
7:00 | 3673 | 684 | 1536 | 289 | 355 | 92 | 8 | 0 | 92
7:30 | 3648.5 | 684 | 1534 | 332.5 | 355 | 93 | 8 | 0 | 96 |  |  |  | Oil |  |  |  | ,
8:00 | 3624 | 684 | 1532 | 376 | 355 | 94 | 8 | 0 | 100
8:30 | 3608.5 | 807.5 | 1536 | 432.5 | 354.5 | 94 | 8 | 0 | 105
9:00 | 3593 | 931 | 1540 | 489 | 354 | 94 | 8 | 0 | 110
9:30 | 3702 | 930.5 | 1563 | 544 | 354 | 94.5 | 8 | 0 | 112
10:00 | 3811 | 930 | 1586 | 599 | 354 | 95 | 8 | 0 | 114
10:30 | 3897.5 | 930 | 1636 | 646 | 353.5 | 92.5 | 8 | 0 | 116
11:00 | 3984 | 930 | 1686 | 693 | 353 | 90 | 8 | 0 | 118
11:30 | 3986.5 | 930 | 1768 | 759.5 | 353 | 90 | 4 | 0 | 123
12:00 | 3989 | 930 | 1850 | 826 | 353 | 90 | 0 | 0 | 128
12:30 | 4002 | 921 | 1878.5 | 852 | 353.5 | 90 | 4 | 0 | 128
13:00 | 4015 | 912 | 1907 | 878 | 354 | 90 | 8 | 0 | 128
13:30 | 4015 | 912 | 1907 | 878 | 354 | 90 | 8 | 0 | 128
14:00 | 4015 | 912 | 1907 | 878 | 354 | 90 | 8 | 0 | 128
14:30 | 4004.5 | 911.5 | 1917.5 | 859 | 354 | 89 | 4 | 0 | 131
15:00 | 3994 | 911 | 1928 | 840 | 354 | 88 | 0 | 0 | 134
15:30 | 3983 | 911.5 | 1940 | 849.5 | 354 | 86.5 | 0 | 0 | 132
16:00 | 3972 | 912 | 1952 | 859 | 354 | 85 | 0 | 0 | 130
16:30 | 3957 | 911 | 1897.5 | 905 | 354.5 | 85 | 11 | 0 | 129
17:00 | 3942 | 910 | 1843 | 951 | 355 | 85 | 22 | 0 | 128
17:30 | 3973.5 | 910.5 | 1831 | 1471 | 356.5 | 85.5 | 207 | 0 | 144
18:00 | 4005 | 911 | 1819 | 1991 | 358 | 86 | 392 | 0 | 160
18:30 | 3978 | 911 | 1862.5 | 2306.5 | 358 | 90 | 320 | 0 | 157
19:00 | 3951 | 911 | 1906 | 2622 | 358 | 94 | 248 | 0 | 154
19:30 | 4015 | 913 | 1898 | 2443 | 358 | 94 | 193 | 0 | 156
20:00 | 4084 | 913 | 1909 | 2332 | 358 | 95 | 161 | 0 | 156
20:30 | 4176.5 | 913 | 1924 | 2132 | 358 | 95 | 114 | 0 | 156
21:00 | 4269 | 913 | 1939 | 1932 | 358 | 95 | 67 | 0 | 156
21:30 | 4273.5 | 916.5 | 1959.5 | 1530.5 | 358 | 95 | 59 | 0 | 151
22:00 | 4278 | 920 | 1980 | 1129 | 358 | 95 | 51 | 0 | 146
22:30 | 4289 | 920 | 1966 | 925.5 | 358 | 96 | 51 | 0 | 143
23:00 | 4300 | 920 | 1952 | 722 | 358 | 97 | 51 | 0 | 140
23:30 | 4253.5 | 920 | 1931.5 | 627.5 | 358 | 93.5 | 42.5 | 0 | 135 | Max Temp. in Dhaka |  | 32.6° C
24:00 | 4207 | 920 | 1911 | 533 | 358 | 90 | 34 | 0 | 130
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-10-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 40 | 42 | 44 | 44 | 45 | 40 | 40 | 40 | 41 | 38 | 35 | 35 | 36 |  | 44 | 44 | 45 | 45 | 45 | 47 | 40 | 1018298
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1176000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 18 |  | 25 | 25 | 25 |  |  |  | 0 | 73832
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4.23 | 10.6 | 15.3 | 19 | 10.6 | 19.7 | 18.1 | 15.5 | 11.15 | 5.66 | 0.5 | [9 empty] | 126090
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 212 | 212 | 204 | 218 | 204 | 216 | 230 | 226 | 226 | 226 | 227 | 226 | 227 | 230 | 204 |  | 204 | 204 | 203 | 204 | 203 | 204 | 204 | 5053553
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 0 | 5 | 80 | 80 | 80 | 80 | 117 | 104 | 104 | 145 | 145 | 146 | 146 | 146 | 143 | 143 | 146 | 100 |  | 100 | 100 | 100 | 100 | 120 | 120 | 110 | 2570933
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 102 |  | 70 | 68 | 51 | 51 | 51 | 51 | 34 | 412250
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 46 | 81 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1960436
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | [11 empty] | 16 | 13 | 13 | 16 | 17 | 13 | 12 |  | 11 | 35 | 85 | 338 | 338 | 341 | 342 | 1374560
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 26 | 91 | 145 | 145 | 152 | 165 | 165 | 165 | 165 | 165 | 224 |  | 300 | 300 | 300 | 300 | 70 | 70 | 70 | 2870399
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 585454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 790000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 130 |  | 128 | 130 | 130 | 130 | 100 | 100 | 100 | 2504000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 350 | 350 | 350 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 300 | 320 | 320 | 350 | 350 | 350 | 350 | 380 |  | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 7582455
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1957428
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 32 | 32 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 682200
33 | Ashuganj 225 MW CCPP | 180 | 181 | 185 | 178 | 179 | 175 | 181 | 192 | 203 | 197 | 201 | 198 | 196 | 180 | 199 | 188 | 180 | 190 |  | 180 | 181 | 181 | 180 | 190 | 172 | 180 | 4316000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 290 | 290 | 280 | 305 | 275 | 280 | 290 | 305 | 290 | 290 | 270 | 295 | 270 | 265 | 275 |  | 265 | 265 | 265 | 270 | 270 | 275 | 270 | 6845000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 285 | 285 | 275 | 300 | 270 | 275 | 325 | 325 | 320 | 310 | 290 | 315 | 290 | 290 | 280 |  | 270 | 270 | 270 | 270 | 270 | 280 | 270 | 7173500
35 | Ashuganj 55 MW PP (Precision) | 51 | 52 | 5 | 5 | 5 | 5 | 5 | 42 | 52 | 51 | 49 | 50 | 49 | 50 | 50 | 50 | 52 | 53 |  | 53 | 53 | 53 | 53 | 54 | 53 | 54 | 1024320
36 | Chandpur 150 MW CCPP | 124 | 126 | 126 | 126 | 126 | 126 | 126 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 126 | 126 | 125 | 120 |  | 125 | 120 | 126 | 120 | 120 | 125 | 125 | 2985370
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 346 | 346 | 351 | 362 | 367 | 373 | 373 | 355 | 371 | 375 | 375 | 384 | 355 | 370 | 370 | 348 | 356 |  | 345 | 345 | 345 | 346 | 351 | 345 | 339 | 8641900
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 400 | 400 | 400 | 360 | 360 | 360 | 360 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 330 | 8597250
41 | Haripur 360MW CCPP(HPL) | 310 | 310 | 310 | 280 | 280 | 280 | 280 | 280 | 289 | 305 | 305 | 305 | 334 | 303 | 302 | 304 | 305 | 304 |  | 304 | 305 | 304 | 300 | 300 | 300 | 300 | 7231000
42 | RPCL 210MW CCPP | 155 | 154 | 154 | 154 | 154 | 156 | 154 | 156 | 153 | 150 | 150 | 148 | 149 | 149 | 148 | 149 | 151 | 150 |  | 152 | 154 | 154 | 155 | 152 | 154 | 154 | 3581680
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 1427000
45 | Fenchugonj CCPP Phase-2 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1036560
46 | Shajibazar 330 MW CCPP | 100 | 101 | 102 | 103 | 103 | 102 | 104 | 104 | 102 | 101 | 103 | 104 | 102 | 101 | 102 | 100 | 100 | 99 |  | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 2323000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 66 | 67 | 66 | 66 | 66 | 65 | 65 | 63 | 63 | 60 | 63 | 63 | 63 | 61 | 65 | 65 |  | 67 | 67 | 66 | 67 | 66 | 66 | 66 | 1537344
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 46 | 68 | 40 | 40 |  | 40 | 40 | 40 | 77 | 77 | 40 | 10 | 709440
49 | Shahjibazar 50MW PP (EPL) | 40 | 40 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 690840
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 17 | 17 | 0 | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 269000
52 | Sylhet 50MW PP (EPL) | 28 | 28 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 28 | 27 | 27 | 28 | 26 | 29 | 27 |  | 31 | 31 | 32 | 31 | 31 | 31 | 31 | 499620
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 0 |  |  |  |  | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 164340
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 0 |  |  | 0 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 211108
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 42 | 47 | 47 | 47 | 22 |  | 22 | 36 | 52 | 53 | 53 | 53 | 53 | 619800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 0 | [5 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 582408
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 300 | 300 | 320 | 315 | 315 | 315 | 310 | 315 | 320 | 320 | 325 | 300 | 305 | 310 | 300 | 275 |  | 260 | 290 | 280 | 270 | 280 | 290 | 285 | 7422250
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 55 |  | 55 | 55 | 55 |  |  |  |  | 191328
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 |  |  | 18 | 19 | 419808
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 0 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 293868
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 0 | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 400968
63 | Impoprt (Tripura) | 122 | 120 | 120 | 116 | 114 | 102 | 92 | 100 | 110 | 114 | 118 | 128 | 128 | 134 | 134 | 130 | 128 | 160 |  | 154 | 156 | 156 | 156 | 146 | 140 | 130 | 3080640
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 40 | 40 | 40 | 40 | 36 | 8 | 2 | 2 | 2 | 2 | 5 | 5 | 2 | 2 | 5 | 3 |  | 5 | 16 | 18 | 20 | 37 | 38 | 38 | 465120
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 0 | [5 empty] | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 362556
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 0 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 11 | 10 | 10 | 10 | 10 | 10 | 152820
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 0 | 0 |  |  | 0 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 575100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 16 | 16 | 16 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 507500
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 24 | 20 | 31 | 31 | 22 |  | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 700020
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 739763
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823500
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 19 | [7 empty] | 0 | 34560
78 | Gazipur 52 MW PP | [8 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 8 | [6 empty] | 100404
79 | Kodda 150MW PP | [16 empty] | 10 | 149 |  | 149 | 100 | 85 | 16 |  |  |  | 433440
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 17 |  | 72 | 95 | 95 | 72 | 0 | 0 |  | 288000
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 1 |  | 30 | 8 | 0 | 0 |  |  |  | 42134
| Gazipur 100 MW PP | 17 | 17 | 0 |  |  |  |  | 52 | 52 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 1144296
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.327 | 1.9 | 3.1 | 3.9 | 2.6 | 4.6 | 4.3 | 3.7 | 2.1 | 0.8 | 0 | 0 | [8 empty] | 25680
| Jodiac Power | [17 empty] | 22 |  | 48 | 54 |  |  |  |  | 0 | 114196
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 0 |  | 10 | 0 | 0 |  |  |  |  | 13392
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | [17 empty] | 0
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 11 |  | 16 | [6 empty] | 32936
86 | Meghnaghat CCPP(Summit) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4988742
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 7 |  | 36 | [5 empty] | 0 | 57600
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 30 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 90 |  | 100 | 100 | 100 | 100 | 50 | 50 | 30 | 1034880
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 49 | 49 | 49 | 49 | 20 | 23 |  | 46 | 46 | 49 | 49 | 49 | 49 | 49 | 768456
93 | Ashuganj 51 MW PP (Midland) | 25 | 25 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 10 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 35 | 408316
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 32 |  | 0 | 0 | [5 empty] | 37728
95 | Patenga 50MW PP (Baraka) | [7 empty] | 4 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 26 |  | 50 | 50 | 50 | 19 | 18 | 18 | 0 | 365760
96 | Chattogram 108 MW PP (ECPV) | 44 | 44 | 0 | [13 empty] | 4 | 38 |  | 96 | 97 | 97 | 64 | 6 |  |  | 457920
97 | Katpotti 52 MW PP (Sinha) | 32 | 18 | 18 | 6 | 6 | 6 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 22 |  | 47 | 47 | 47 | 47 | 34 | 28 | 33 | 600624
98 | Bosila 108MW PP(CLC) | [10 empty] | 40 | 70 | 69 | 69 | 69 | 69 | 69 | 69 |  | 69 | 69 | 69 | 69 | 24 |  | 0 | 733440
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 9 | 15 | 15 | 15 | 15 | 17 |  | 48 | 30 | 15 | 0 | 0 |  |  | 177792
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 17 |  |  | 0 | 344479
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 130 | 130 | 130 | 100 |  | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 2927356
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.3 | 1.6 | 2.1 | 2.4 | 2.2 | 1.1 | 2 | 1.3 | 0.6 | 0 | 0 | [8 empty] | 12750
103 | Kamalaghat 54 MW PP(Banco Energy) | [13 empty] | 17 | 17 | 17 | 17 | 53 |  | 53 | 17 | 17 |  |  |  | 0 | 194040
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 32 | 32 | 0 | [5 empty] | 14 | 16 | 31 | 40 | 40 | 58 | 70 | 70 | 70 | 127 |  | 200 | 200 | 200 | 200 | 200 | 140 | 110 | 1768800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [11 empty] | 10 | 45 | 45 | 45 | 45 | 45 | 61 |  | 145 | 100 | 97 | 60 | 34 | 28 | 0 | 699840
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 100 |  | 100 | 100 | 100 | 30 | 0 | 0 |  | 380160
116 | Chandpur 200MW (Desh energy) | [11 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 72 |  | 188 | 200 | 200 | 168 | 50 | 17 | 0 | 848160
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 3 |  | 10 | 10 | 10 |  |  |  |  | 35127
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 31 |  | 7 | 7 | 7 |  |  |  | 0 | 85200
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4860 | 4864 | 4577 | 4383 | 4359 | 4256 | 4367.657 | 4424.8 | 4575 | 4902 | 5215.6 | 5503.5 | 5613.5 | 5536.2 | 5578.55 | 5573.06 | 5468.5 | 6318 |  | 6893 | 6737 | 6690 | 6459 | 5801 | 5657 | 5377 | 129495817
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 1 | 16 |  | 16 | 0 | [5 empty] | 36480
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 2 | 39 |  | 4 | 0 | [5 empty] | 53760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 4 | 70 |  | 70 | 70 | 70 | 67 | 35 | 17 | 0 | 337920
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 0 |  |  | 70368
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 95 | 51 | 32 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 40 | 43 | 60 | 60 | 63 | 61 | 70 |  | 96 | 96 | 96 | 95 | 95 | 95 | 99 | 1312706
| Bhola 225 MW CCPP | 153 | 153 | 153 | 153 | 154 | 153 | 153 | 153 | 152 | 151 | 150 | 150 | 150 | 150 | 149 | 149 | 148 | 150 |  | 150 | 150 | 150 | 130 | 141 | 151 | 150 | 3621923
140 | Bhola 33 MW PP (Venture) | 25 | 21 | 21 | 21 | 21 | 19 | 18 | 16 | 16 | 17 | 17 | 21 | 21 | 22 | 21 | 19 | 21 | 28 |  | 29 | 29 | 29 | 28 | 27 | 26 | 27 | 521693
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 24 | 0 |  | 186000
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | 20 |  | 0 | [6 empty] | 27904
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 3 | 64 |  | 103 | 103 | 72 | 68 | 69 | 17 | 0 | 422208
146 | Bheramara HVDC | 930 | 684 | 684 | 684 | 684 | 684 | 684 | 684 | 931 | 930 | 930 | 930 | 912 | 913 | 911 | 912 | 910 | 911 |  | 911 | 913 | 913 | 913 | 920 | 920 | 920 | 20401454
147 | Bheramara 360 MW CCPP | 300 | 300 | 300 | 320 | 320 | 310 | 345 | 345 | 310 | 310 | 325 | 325 | 335 | 325 | 345 | 330 | 325 | 325 |  | 310 | 310 | 325 | 325 | 320 | 320 | 300 | 7858656
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 64 | 64 | 65 | 64 | 64 | 65 | 65 | 65 | 64 | 64 | 63 | 63 | 64 | 64 | 64 | 64 | 65 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1555636
152 | Barapukuria 275 MW TPP Unit-3 | 290 | 289 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7012900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 1256000
| Baghabari 50 MW Peaking PP | [12 empty] | 8 | 0 | 0 |  |  | 34 |  | 0 | 0 | [5 empty] | 44992
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 174 | 159 | 158 | 164 | 170 | 171 | 171 | 174 | 175 | 188 | 195 | 181 | 196 | 194 | 177 | 178 | 167 | 170 |  | 160 | 161 | 161 | 163 | 170 | 163 | 165 | 4418355
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [12 empty] | 5 | 10 | 10 | 15 | 53 | 117 |  | 144 | 151 | 152 | 150 | 153 | 153 | 139 | 1179909
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 172 | 173 | 170 | 167 | 172 | 172 | 171 | 176 | 168 | 175 | 194 | 185 | 185 | 169 | 177 | 182 | 177 | 179 |  | 176 | 173 | 173 | 172 | 165 | 163 | 165 | 4428582
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 348 | 363 | 370 | 370 | 370 | 369 | 391 | 380 | 380 | 381 | 381 | 382 | 384 | 382 | 384 | 383 | 343 | 379 |  | 362 | 361 | 361 | 368 | 382 | 381 | 380 | 8967490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 21 | 21 | 18 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 364800
163 | Bogura 20 MW PP (Energyprima) | 14 | 14 | 14 | 14 | 0 |  |  |  |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 259632
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 208060
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 40 |  | 50 | 50 | 50 | 50 | 30 | 12 | 0 | 254780
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 42 |  | 16 | 0 | 0 |  |  |  |  | 74235
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 20640
170 | Chapainawabganj 100 MW Peaking PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [5 empty] | 48 |  | 25 | 25 | 25 | 0 |  |  |  | 187060
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence) | [16 empty] | 6 | 83 |  | 111 | 113 | 113 | 113 | 104 |  | 0 | 580704
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 19 | 23 | 28 | 15 | 14 | 4 | 23 | 12 | 0 |  | 0 | [6 empty] | 131520
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [20 empty] | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 76 | 100 |  | 107 | 107 | 107 | 107 | 56 | 0 |  | 554880
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.7 | 2.9 | 4.2 | 5.6 | 6.8 | 6.2 | 6 | 4.4 | 2.6 | 1.2 | 0.1 | 0 |  | 0 | [6 empty] | 39496
178
178