## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-03 | Sunday
|  | Date (day): | 2019-11-03 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11710.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14352 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-02 | 2019-11-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 100 | 100 | 100 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 350 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 345 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 351 | 355 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 50 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 10 | 50 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 336 | 339 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 0 | 50 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 35 | 45 | 46
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 17 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 1 | 62 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 35 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 265 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 15 | 88 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 86 | 70 | 70 | 70 |  | 35 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2566 | 2859 | 3490 | 4252 | 806 | 654
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 105 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 20 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 91 | 92 | 94 | 94 | 136 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 104 | 140 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 51 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 10 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 12 | 20 | 45
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 9 | 83 | 50 | 96 |  | 12 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.63 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 260 |  |  | Transformer O/L
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 791.63 | 1003 | 1383 | 1628 | 386 | 110
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 160 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 340 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 33 | 33 |  | 12 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 55 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 35 | 35 | 36 | 36 | 160 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 33 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 87 | 100 | 100 |  |  | ST under maintenance
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 100 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 148 | 116 | 156
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 22 | 22 | 22
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1223 | 1476 | 1741 | 2200 | 458 | 28
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 155 | 146 | 170 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 53 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 48 | 200 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 225.2 | 419 | 408.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 58 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | Water problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 134 | 140 | 160 | 160 |  | 170 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 17 | 50 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 19 | 46 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 77 | 75 | 77 |  | 9 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 25 | 33 | 30 | 33 |  | 17 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 275 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 854 | 944 | 1101 | 1106 | 0 | 748
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 688 | 933 | 696 | 696
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 345 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 10 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 68 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1055 | 1560 | 1191 | 1927 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 28 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 174 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 60 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 253 | 315 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 60 | 60 | 60 | 40 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 204 | 171 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 210 | 182 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 426 | 425 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 50 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 919 | 1041 | 1539 | 1694 | 260 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 68 | 69 | 68 | 68
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 290 | 290 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 101 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 364 | 492 | 479 | 505 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 8250.83 | 10109 | 11710.6 | 14352 | 1952 | 1704
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7884.3622 | 9660 | 11190.4635 | 13714.5435
A. |  | 2019-11-02 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10109 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6419 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10109 | MW
3 | Day peak Generation : |  |  | 8250.83 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9660 | MW
4 | Evening peak Generation : |  |  | 10109 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 198.256 | MKWHr | By Solar | 0.21832 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 142.7637 | MKWHr |  | By Oil: | 24.3976 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.6585 | MKWHr |  | By Hydro: | 2.1657 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1952 | MW | Dhaka | 3698 | 3698 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1704 | MW | Chittagong | 1004 | 1004 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3656 | MW | Khulna | 1136 | 1136 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1148.4 | MMCFD |  |  | Rajshahi | 932 | 932 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129971222.504 | ii) Oil : | Taka | 235356044.58 | Comilla | 866 | 866 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 39143288.99 | Total | Taka | 404470556.074 | Mymensingh | 735 | 735 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 418 | 418 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 284 | MW (E to W) at | 19:00 | hrs | Barisal | 286 | 286 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 264 | MW at | 18:30 | hrs | Rangpur | 585 | 585 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.7° C |  |  | Total | 9660 | 9660 |  | 0
B. |  | 2019-11-03 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14352 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8300 | MW
4 | Reserve(Generation end) |  |  |  | 3752 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 207.8854 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6666 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1433 | MKWHr. | ii) HVDC Flow at Peak Time |  | 933 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9088 | MKWHr. | iii) Maximum HVDC Flow : |  | 935 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.81 | 101.86 |  | (b) Today: | 101.81 |  | (c) Rule Curve: |  | 108.38
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 100 | 0 | 380 | 0 | 0 | 345 | 363 |  | 0 | 400 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 17 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 40 | 50 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 340 | 320 | 180 | 16 | 90 | 33 | 55 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 114 | 207 | 0 | 22 | 0 | 59 | 0 | 5 | 5 | 100 | 128 | 40 | 10 | 40 | 0 | 0 | 7 | 0 | 265 | 0 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 0 |  | 680 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 23 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 193 | 0 | 0 | 0 | 62 | 0 | 195 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4967 | 2422 | 7389 | 4287 | 680 | 1736 | 127 | 355 | 90 | 0 | 114 | 0 | 0 | 101.88
2:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 345 | 359 |  | 0 | 370 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 40 | 50 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 310 | 290 | 186 | 16 | 90 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 21 | 112 | 207 | 0 | 22 | 0 | 60 | 0 | 5 | 5 | 100 | 128 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 534 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 163 | 0 | 0 | 0 | 62 | 0 | 193 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4600 | 2280 | 6880 | 4058 | 534 | 1681 | 50 | 355 | 90 | 0 | 112 | 0 | 0 | 101.88
3:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 345 | 304 |  | 0 | 370 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 39 | 50 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 270 | 290 | 181 | 16 | 90 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 21 | 110 | 207 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 129 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 305 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 160 | 0 | 0 | 0 | 32 | 0 | 191 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4476 | 2245 | 6721 | 3988 | 534 | 1621 | 24 | 355 | 89 | 0 | 110 | 0 | 0 | 101.87
4:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 345 | 304 |  | 0 | 330 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 39 | 50 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 270 | 290 | 179 | 16 | 90 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 21 | 104 | 208 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 128 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 157 | 0 | 0 | 0 | 32 | 0 | 183 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4372 | 2191 | 6563 | 3951 | 534 | 1518 | 12 | 355 | 89 | 0 | 104 | 0 | 0 | 101.87
5:00 | 35 | 0 | 102 | 0 | 250 | 0 | 0 | 343 | 304 |  | 0 | 330 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 38 | 50 | 110 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 270 | 290 | 180 | 16 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 21 | 102 | 209 | 0 | 0 | 0 | 58 | 0 | 5 | 5 | 100 | 128 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 530 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 155 | 0 | 0 | 0 | 12 | 0 | 183 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4258 | 2161 | 6419 | 3848 | 530 | 1484 | 12 | 355 | 88 | 0 | 102 | 0 | 0 | 101.86
6:00 | 35 | 0 | 102 | 0 | 250 | 0 | 0 | 348 | 304 |  | 0 | 330 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 38 | 50 | 110 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 270 | 290 | 181 | 16 | 80 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 21 | 92 | 209 | 0 | 0 | 0 | 58 | 0 | 5 | 5 | 100 | 128 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 530 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 168 | 0 | 0 | 0 | 12 | 0 | 181 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4275.1 | 2177 | 6452.1 | 3862 | 530 | 1513 | 12 | 355 | 88 | 0 | 92 | 0.1 | 0 | 101.86
7:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 362 | 264 |  | 0 | 330 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 39 | 50 | 110 | 0 | 0 | 216 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 305 | 325 | 200 | 16 | 70 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 84 | 208 | 0 | 0 | 0.2 | 58 | 0 | 5 | 5 | 100 | 137 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 |  | 530 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 290 | 0 | 0 | 176 | 0 | 0 | 0 | 12 | 0 | 177 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | 4290.5 | 2223.5 | 6514 | 3970 | 530 | 1468 | 12 | 355 | 89 | 0 | 84 | 6 | 0 | 101.85
8:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 374 | 303 |  | 0 | 330 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 50 | 110 | 0 | 0 | 217 | 0 | 112 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 80 | 0 | 0 | 310 | 325 | 201 | 16 | 30 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 90 | 192 | 0 | 0 | 0.6 | 59 | 0 | 5 | 5 | 100 | 133 | 40 | 10 | 5 | 0 | 0 | 7 | 0 | 310 | 0 | 8 | 0 | 5 | 0 | 0 | 29 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 35 | 18 | 2.01 | 0 | 0 | 0 |  | 530 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 17 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 66 | 290 | 0 | 0 | 191 | 0 | 0 | 0 | 11 | 0 | 184 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 |  | 4394.61 | 2333.3 | 6727.91 | 3968 | 530 | 1567 | 111 | 356 | 91 | 0 | 90 | 14.91 | 0 | 101.85
9:00 | 35 | 0 | 100 | 0 | 270 | 0 | 0 | 374 | 355 |  | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 50 | 110 | 0 | 0 | 205 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 19 | 3 | 80 | 0 | 0 | 305 | 305 | 192 | 16 | 30 | 20 | 5 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 0 | 15 | 100 | 176 | 0 | 20 | 1.6 | 60 | 0 | 5 | 5 | 130 | 129 | 65 | 10 | 5 | 0 | 0 | 7 | 0 | 320 | 0 | 8 | 0 | 67 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 70 | 34 | 3.34 | 0 | 0 | 0 |  | 541 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 68 | 290 | 0 | 0 | 203 | 0 | 0 | 0 | 27 | 0 | 194 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 4713.94 | 2393.1 | 7107.04 | 4032 | 541 | 1717 | 244 | 358 | 91 | 0 | 100 | 24.04 | 0 | 101.85
10:00 | 35 | 0 | 100 | 0 | 270 | 0 | 0 | 345 | 305 |  | 0 | 350 | 0 | 0 | 0 | 28 | 270 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 6 | 53 | 0 | 0 | 0 | 25 | 30 | 17 | 33 | 0 | 0 | 41 | 50 | 105 | 0 | 0 | 208 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 2 | 80 | 0 | 0 | 310 | 295 | 218 | 35 | 31 | 33 | 30 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 15 | 108 | 176 | 0 | 20 | 2 | 60 | 0 | 5 | 5 | 130 | 130 | 64 | 10 | 5 | 0 | 0 | 7 | 0 | 290 | 0 | 8 | 0 | 135 | 0 | 0 | 40 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 4.22 | 0 | 0 | 0 |  | 689 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 68 | 290 | 0 | 0 | 200 | 0 | 0 | 0 | 31 | 0 | 196 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 10 |  | 4877.22 | 2502.3 | 7379.52 | 3961 | 689 | 1691 | 452 | 358 | 91 | 0 | 108 | 29.52 | 0 | 101.85
11:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 367 | 315 |  | 0 | 380 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 6 | 53 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 41 | 50 | 105 | 0 | 0 | 219 | 0 | 115 | 0 |  | 0 | 0 | 0 | 10 | 0 | 5 | 19 | 2 | 80 | 0 | 0 | 325 | 325 | 202 | 35 | 32 | 33 | 30 | 0 | 5 | 0 | 0 | 0 | 19 | 8 | 0 | 22 | 114 | 171 | 0 | 20 | 2.2 | 60 | 0 | 5 | 5 | 130 | 141 | 63 | 10 | 5 | 0 | 0 | 7 | 0 | 310 | 0 | 8 | 0 | 165 | 0 | 0 | 40 | 0 | 6 | 19 | 0 | 0 | 0 | 0 | 0 | 82 | 68 | 4.63 | 0 | 0 | 0 |  | 689 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 68 | 290 | 0 | 0 | 205 | 0 | 0 | 0 | 31 | 0 | 200 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 50 |  | 5217.83 | 2561.8 | 7779.63 | 4175 | 689 | 1741 | 580 | 358 | 91 | 0 | 114 | 31.63 | 0 | 101.84
12:00 | 35 | 0 | 150 | 0 | 330 | 0 | 0 | 360 | 351 |  | 0 | 420 | 0 | 0 | 0 | 55 | 336 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 1 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 50 | 100 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 80 | 9 | 19 | 19 | 2 | 80 | 0 | 0 | 340 | 315 | 181 | 35 | 30 | 33 | 30 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 0 | 22 | 122 | 155 | 0 | 20 | 2.2 | 60 | 0 | 17 | 19 | 163 | 134 | 63 | 10 | 40 | 0 | 0 | 25 | 10 | 305 | 0 | 8 | 0 | 195 | 0 | 0 | 48 | 0 | 15 | 19 | 0 | 0 | 0 | 0 | 0 | 86 | 105 | 4.63 | 0 | 0 | 0 |  | 688 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 68 | 290 | 0 | 0 | 204 | 0 | 0 | 0 | 60 | 0 | 210 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 50 |  | 5659.83 | 2591 | 8250.83 | 4206 | 688 | 1958 | 796 | 358 | 91 | 0 | 122 | 31.83 | 0 | 101.84
13:00 | 35 | 0 | 154 | 0 | 330 | 0 | 0 | 350 | 355 |  | 0 | 380 | 0 | 0 | 0 | 42 | 337 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 50 | 100 | 0 | 0 | 179 | 0 | 139 | 0 |  | 0 | 0 | 0 | 90 | 24 | 28 | 19 | 4 | 80 | 0 | 0 | 330 | 305 | 180 | 35 | 85 | 33 | 54 | 0 | 24 | 0 | 0 | 0 | 22 | 8 | 16 | 22 | 126 | 155 | 0 | 20 | 2.1 | 60 | 0 | 47 | 46 | 130 | 147 | 65 | 30 | 40 | 0 | 0 | 30 | 10 | 280 | 0 | 8 | 0 | 215 | 0 | 0 | 60 | 0 | 15 | 18 | 10 | 0 | 0 | 0 | 0 | 89 | 105 | 4.27 | 0 | 0 | 0 |  | 689 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 68 | 290 | 0 | 0 | 202 | 0 | 0 | 0 | 95 | 0 | 206 | 0 | 379 | 35 | 0 | 0 | 0 | 0 | 0 | 5.6 | 42 |  | 5835.37 | 2590.6 | 8425.97 | 4229 | 689 | 1992 | 911 | 358 | 91 | 0 | 126 | 29.97 | 0 | 101.84
14:00 | 35 | 0 | 150 | 0 | 300 | 0 | 0 | 349 | 286 |  | 0 | 350 | 0 | 0 | 0 | 55 | 285 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 180 | 0 | 0 | 0 |  | 0 | 0 | 0 | 90 | 24 | 30 | 19 | 4 | 80 | 0 | 0 | 300 | 330 | 198 | 35 | 86 | 33 | 53 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 16 | 22 | 128 | 143 | 0 | 20 | 1.7 | 60 | 0 | 22 | 47 | 100 | 146 | 63 | 10 | 40 | 0 | 0 | 30 | 10 | 280 | 0 | 8 | 0 | 230 | 0 | 0 | 60 | 0 | 15 | 15.7 | 10 | 0 | 0 | 0 | 0 | 88 | 105 | 3.5 | 0 | 0 | 0 |  | 689 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 69 | 290 | 0 | 0 | 196 | 0 | 0 | 0 | 95 | 0 | 183 | 0 | 384 | 17 | 0 | 0 | 0 | 0 | 0 | 4.7 | 42 |  | 5474.9 | 2575.7 | 8050.6 | 4000 | 689 | 1835 | 922 | 359 | 92 | 0 | 128 | 25.6 | 0 | 101.83
15:00 | 35 | 0 | 150 | 0 | 300 | 0 | 0 | 382 | 306 |  | 0 | 350 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 43 | 50 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 90 | 29 | 30 | 19 | 2 | 80 | 0 | 0 | 315 | 320 | 185 | 35 | 87 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 15 | 22 | 130 | 143 | 0 | 20 | 0.3 | 60 | 0 | 22 | 47 | 100 | 150 | 62 | 10 | 40 | 0 | 0 | 30 | 10 | 320 | 0 | 8 | 0 | 230 | 0 | 0 | 60 | 0 | 16 | 14.4 | 30 | 0 | 0 | 0 | 0 | 88 | 105 | 2 | 0 | 0 | 0 |  | 736 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 69 | 290 | 0 | 0 | 203 | 0 | 0 | 0 | 94 | 0 | 184 | 0 | 415 | 17 | 0 | 0 | 0 | 0 | 0 | 4.2 | 52 |  | 5632.7 | 2724.2 | 8356.9 | 4140 | 736 | 1920 | 958 | 359 | 93 | 0 | 130 | 20.9 | 0 | 101.83
16:00 | 35 | 0 | 150 | 0 | 270 | 0 | 0 | 320 | 276 |  | 0 | 320 | 0 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 205 | 0 | 90 | 0 |  | 0 | 0 | 0 | 90 | 50 | 30 | 19 | 2 | 80 | 0 | 0 | 280 | 290 | 180 | 35 | 89 | 33 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 15 | 22 | 124 | 145 | 0 | 20 | 0.4 | 56 | 0 | 25 | 47 | 100 | 135 | 63 | 10 | 40 | 0 | 0 | 29 | 10 | 280 | 0 | 0 | 0 | 230 | 0 | 0 | 60 | 0 | 15 | 5.5 | 30 | 0 | 0 | 0 | 0 | 88 | 105 | 1 | 0 | 0 | 0 |  | 821 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 69 | 290 | 0 | 0 | 192 | 0 | 0 | 0 | 96 | 0 | 181 | 0 | 345 | 17 | 0 | 0 | 0 | 0 | 0 | 1.4 | 38 |  | 5407.9 | 2619.4 | 8027.3 | 3906 | 821 | 1753 | 964 | 359 | 92 | 0 | 124 | 8.3 | 0 | 101.83
17:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 280 | 277 |  | 0 | 320 | 0 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 42 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 0 | 33 | 0 | 0 | 42 | 50 | 100 | 0 | 0 | 192 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 50 | 30 | 19 | 3 | 80 | 0 | 0 | 305 | 310 | 188 | 35 | 87 | 33 | 53 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 15 | 22 | 124 | 159 | 0 | 20 | 0 | 59 | 0 | 25 | 5 | 100 | 132 | 63 | 10 | 40 | 0 | 0 | 12 | 10 | 280 | 0 | 0 | 0 | 230 | 0 | 0 | 65 | 0 | 16 | 0.3 | 30 | 0 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 821 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 173 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 69 | 290 | 0 | 0 | 173 | 0 | 0 | 0 | 97 | 0 | 172 | 0 | 383 | 17 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 5203.3 | 2602.7 | 7806 | 3774 | 821 | 1713 | 916 | 359 | 92 | 6 | 124 | 1 | 0 | 101.82
18:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 349 | 354 |  | 0 | 420 | 0 | 0 | 0 | 55 | 338 | 0 | 0 | 0 | 7 | 50 | 62 | 0 | 62 | 0 | 6 | 53 | 35 | 55 | 0 | 25 | 22 | 33 | 33 | 39 | 0 | 42 | 50 | 100 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 85 | 90 | 54 | 41 | 19 | 4 | 80 | 0 | 0 | 340 | 320 | 179 | 35 | 90 | 33 | 55 | 0 | 18 | 0 | 0 | 0 | 22 | 8 | 32 | 22 | 152 | 162 | 12 | 20 | 0 | 58 | 0 | 32 | 22 | 130 | 141 | 65 | 10 | 40 | 0 | 18 | 32 | 10 | 300 | 0 | 8 | 0 | 235 | 0 | 0 | 149 | 0 | 45 | 0 | 30 | 22 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 15 | 0 |  | 934 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 39 | 0 | 40 | 173 | 26 | 16 | 0 | 60 | 0 | 50 | 0 | 51 | 50 | 8 | 0 | 21 | 29 | 22 | 11 | 11 | 0 | 69 | 290 | 0 | 18 | 183 | 0 | 0 | 0 | 97 | 1 | 187 | 0 | 395 | 105 | 0 | 29 | 89 | 101 | 0 | 0 | 0 |  | 6427 | 3466 | 9893 | 4303 | 934 | 2013 | 1706 | 359 | 92 | 334 | 152 | 0 | 0 | 101.82
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 345 | 355 |  | 0 | 420 | 0 | 0 | 0 | 55 | 339 | 0 | 0 | 0 | 10 | 0 | 100 | 0 | 62 | 0 | 35 | 17 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 42 | 50 | 105 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 102 | 100 | 83 | 50 | 19 | 12 | 80 | 0 | 0 | 340 | 320 | 160 | 35 | 87 | 33 | 55 | 0 | 33 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 148 | 146 | 53 | 20 | 0 | 58 | 0 | 50 | 46 | 100 | 140 | 65 | 77 | 40 | 0 | 18 | 33 | 10 | 275 | 24 | 8 | 0 | 265 | 0 | 0 | 200 | 0 | 88 | 0 | 10 | 100 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 17 | 0 |  | 933 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 43 | 0 | 40 | 174 | 28 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 30 | 22 | 11 | 11 | 0 | 69 | 290 | 17 | 15 | 171 | 0 | 0 | 0 | 97 | 10 | 182 | 0 | 426 | 105 | 0 | 70 | 68 | 101 | 0 | 0 | 0 |  | 6701 | 3408 | 10109 | 4251 | 933 | 2125 | 1894 | 359 | 92 | 307 | 148 | 0 | 0 | 101.82
19:30 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 355 | 355 |  | 0 | 420 | 0 | 0 | 0 | 15 | 336 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 62 | 0 | 47 | 17 | 17 | 17 | 22 | 25 | 10 | 33 | 25 | 0 | 0 | 42 | 50 | 105 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 85 | 100 | 90 | 18 | 19 | 17 | 80 | 0 | 0 | 350 | 330 | 163 | 35 | 87 | 33 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 148 | 148 | 40 | 20 | 0 | 60 | 0 | 50 | 49 | 100 | 146 | 66 | 77 | 40 | 0 | 18 | 33 | 10 | 315 | 24 | 8 | 0 | 265 | 0 | 0 | 200 | 0 | 80 | 0 | 10 | 100 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 17 | 0 |  | 935 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 40 | 174 | 28 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 22 | 11 | 11 | 0 | 69 | 290 | 0 | 15 | 171 | 0 | 0 | 0 | 97 | 10 | 177 | 0 | 422 | 105 | 0 | 70 | 67 | 101 | 0 | 0 | 0 |  | 6593 | 3352 | 9945 | 4295 | 935 | 2171 | 1737 | 359 | 92 | 208 | 148 | 0 | 0 | 101.82
20:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 350 | 355 |  | 0 | 420 | 0 | 0 | 0 | 15 | 338 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 62 | 0 | 47 | 17 | 17 | 17 | 22 | 25 | 10 | 33 | 25 | 0 | 0 | 42 | 50 | 105 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 85 | 100 | 94 | 22 | 19 | 20 | 80 | 0 | 0 | 345 | 320 | 164 | 35 | 88 | 40 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 148 | 146 | 40 | 22 | 0 | 58 | 0 | 50 | 49 | 100 | 145 | 66 | 77 | 40 | 0 | 18 | 33 | 10 | 300 | 24 | 8 | 0 | 265 | 0 | 0 | 200 | 0 | 63 | 0 | 10 | 100 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 17 | 0 |  | 935 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 40 | 173 | 30 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 11 | 11 | 0 | 69 | 290 | 0 | 15 | 173 | 0 | 0 | 0 | 95 | 0 | 177 | 0 | 429 | 105 | 0 | 70 | 34 | 107 | 0 | 0 | 0 |  | 6559 | 3294 | 9853 | 4278 | 935 | 2166 | 1667 | 359 | 92 | 208 | 148 | 0 | 0 | 101.81
21:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 343 | 355 |  | 0 | 420 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 32 | 17 | 17 | 17 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 42 | 50 | 105 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 68 | 100 | 95 | 0 | 19 | 32 | 80 | 0 | 0 | 340 | 320 | 168 | 35 | 87 | 37 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 144 | 146 | 40 | 22 | 0 | 58 | 0 | 50 | 49 | 100 | 144 | 66 | 77 | 40 | 0 | 18 | 33 | 10 | 305 | 24 | 8 | 0 | 230 | 0 | 0 | 200 | 0 | 32 | 0 | 10 | 100 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 17 | 0 |  | 934 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 40 | 173 | 30 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 15 | 174 | 0 | 0 | 0 | 97 | 0 | 177 | 0 | 431 | 105 | 0 | 35 | 33 | 107 | 0 | 0 | 0 |  | 6344 | 3229 | 9573 | 4269 | 934 | 2191 | 1468 | 358 | 92 | 117 | 144 | 0 | 0 | 101.81
22:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 345 | 358 |  | 0 | 420 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 17 | 0 | 0 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 42 | 50 | 110 | 0 | 0 | 178 | 0 | 104 | 0 |  | 0 | 0 | 34 | 90 | 91 | 0 | 19 | 37 | 80 | 0 | 0 | 270 | 270 | 160 | 35 | 87 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 140 | 164 | 40 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 121 | 67 | 77 | 40 | 0 | 18 | 30 | 10 | 290 | 24 | 8 | 0 | 210 | 0 | 0 | 200 | 0 | 15 | 0 | 0 | 70 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 17 | 0 |  | 934 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 173 | 29 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 69 | 290 | 0 | 15 | 168 | 0 | 0 | 0 | 96 | 0 | 175 | 0 | 394 | 70 | 0 | 0 | 33 | 70 | 0 | 0 | 0 |  | 5989 | 3058 | 9047 | 4117 | 934 | 2141 | 1215 | 359 | 92 | 49 | 140 | 0 | 0 | 101.81
23:00 | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 345 | 361 |  | 0 | 420 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 41 | 50 | 110 | 0 | 0 | 179 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 91 | 0 | 19 | 37 | 80 | 0 | 0 | 270 | 270 | 161 | 35 | 87 | 37 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 130 | 165 | 0 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 127 | 67 | 77 | 40 | 0 | 18 | 33 | 10 | 280 | 24 | 8 | 0 | 214 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 934 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 27 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 167 | 0 | 0 | 0 | 98 | 0 | 160 | 0 | 339 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5859 | 2792 | 8651 | 4113 | 934 | 2083 | 942 | 358 | 91 | 0 | 130 | 0 | 0 | 101.81
24:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 347 | 358 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 41 | 50 | 110 | 0 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 90 | 50 | 0 | 19 | 40 | 80 | 0 | 0 | 270 | 270 | 161 | 35 | 87 | 37 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 124 | 180 | 0 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 124 | 67 | 77 | 40 | 0 | 18 | 33 | 10 | 290 | 24 | 8 | 0 | 115 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 105 | 0 | 0 | 0 | 0 |  | 935 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 174 | 0 | 0 | 0 | 96 | 0 | 163 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5507 | 2757 | 8264 | 4117 | 935 | 2110 | 529 | 358 | 91 | 0 | 124 | 0 | 0 | 101.81
KWH | 770000 | 0 | 2661000 | 0 | 7542827 | 0 | 0 | 8504320 | 7778000 |  | 0 | 9070250 | 0 | 0 | 0 | 548849 | 7334076 | 0 | 0 | 0 | 26880 | 409536 | 230400 | 0 | 399360 | 0 | 381312 | 673920 | 234267 | 193286 | 119124 | 600000 | 621900 | 690700 | 803000 | 48780 | 0 | 981731 | 1184000 | 2500000 | 0 | 0 | 4781595 | 0 | 2411850 | 0 |  | 0 | 0 | 395751 | 1190280 | 7574400 | 312480 | 454752 | 544320 | 1917884 | 0 | 0 | 7698900 | 7437000 | 4408000 | 702545 | 1727140 | 661840 | 897600 | 0 | 487688 | 0 | 0 | 0 | 344052 | 216360 | 278300 | 495600 | 2908800 | 4071680 | 221760 | 358206 | 14000 | 1405000 | 0 | 532800 | 654768 | 2841545 | 3150000 | 1353384 | 723840 | 710280 | 0 | 118000 | 458360 | 132480 | 7318800 | 145800 | 178320 | 0 | 3312000 | 0 | 0 | 1888800 | 0 | 367200 | 133785 | 183360 | 504480 | 0 | 0 | 0 | 1217520 | 1552284 | 30960 | 0 | 100798 | 0 |  | 17143272 | 0 | 8413632 | 0 | 34560 | 0 | 0 | 0 | 143040 | 0 | 205500 | 4144770 | 522302 | 36480 | 0 | 108500 | 0 | 29488 | 0 | 41524 | 296700 | 9878 | 0 | 34080 | 40821 | 332640 | 176292 | 195912 | 0 | 1635927 | 7022600 | 17000 | 62000 | 4647127 | 0 | 0 | 0 | 1535021 | 29760 | 4699682 | 0 | 9373966 | 616320 | 0 | 252960 | 240768 | 53880 | 0 | 39575 | 285120 |  | 135834865 | 62421097 | 198255962 | 97970233 | 17143272 | 44793497 | 23437558 | 8658527 | 2165731 | 960024 | 2908800 | 218320 | 0
Fuel Cost | 862400 | 0 | 2847270 | 0 | 5581691.98 | 0 | 0 | 6123110.4 | 5911280 |  | 0 | 7256200 | 0 | 0 | 0 | 5631190.74 | 9094254.24 | 0 | 0 | 0 | 298368 | 4160885.76 | 2283264 | 0 | 3634176 | 0 | 3569080.32 | 6462892.8 | 2234907.18 | 1925128.56 | 89343 | 450000 | 0 | 0 | 0 | 467312.4 | 0 | 255250.06 | 307840 | 3825000 | 0 | 0 | 5020674.75 | 0 | 3063049.5 | 0 |  | 0 | 0 | 4151427.99 | 12247981.2 | 72032544 | 2924812.8 | 418371.84 | 1513209.6 | 2013778.2 | 0 | 0 | 5697186 | 6247080 | 4055360 | 688494.1 | 2297096.2 | 542708.8 | 924528 | 0 | 697393.84 | 0 | 0 | 0 | 350933.04 | 162270 | 525987 | 371700 | 20070720 | 3338777.6 | 2108937.6 | 365370.12 | 229600 | 1910800 | 0 | 724608 | 818460 | 3523515.8 | 2898000 | 2016542.16 | 1273958.4 | 788410.8 | 0 | 187620 | 536281.2 | 311328 | 5196348 | 109350 | 135523.2 | 0 | 34676640 | 0 | 0 | 18170256 | 0 | 3705048 | 1543878.9 | 1708915.2 | 4732022.4 | 0 | 0 | 0 | 10848103.2 | 14669083.8 | 0 | 0 | 0 | 0 |  | 46286834.4 | 0 | 6562632.96 | 0 | 333158.4 | 0 | 0 | 0 | 1659264 | 0 | 2032395 | 3315816 | 809568.1 | 391795.2 | 0 | 203980 | 0 | 328496.32 | 0 | 411087.6 | 3076779 | 115671.38 | 0 | 339436.8 | 402086.85 | 365904 | 290881.8 | 148305.384 | 0 | 10420854.99 | 28722434 | 568650 | 1750260 | 4089471.76 | 0 | 0 | 0 | 2440683.39 | 502944 | 4135720.16 | 0 | 6842995.18 | 5830387.2 | 0 | 2322172.8 | 2145242.88 | 503239.2 | 0 | 0 | 0 |  | 335815530.68 | 137349148.754 | 473164679.434 | 89057174.294 | 46286834.4 | 40914048.21 | 223801507.82 | 39143288.99 | 563090.06 | 11554536.76 | 20070720 | 1773478.9 | 0
Yesterday Day Peak | 35 | 0 | 150 | 0 | 330 | 0 | 0 | 360 | 351 |  | 0 | 420 | 0 | 0 | 0 | 55 | 336 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 1 | 0 | 6 | 53 | 17 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 41 | 50 | 100 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 80 | 9 | 19 | 19 | 2 | 80 | 0 | 0 | 340 | 315 | 181 | 35 | 30 | 33 | 30 | 0 | 5 | 0 | 0 | 0 | 22 | 8 | 0 | 22 | 122 | 155 | 0 | 20 | 2.2 | 60 | 0 | 17 | 19 | 163 | 134 | 63 | 10 | 40 | 0 | 0 | 25 | 10 | 305 | 0 | 8 | 0 | 195 | 0 | 0 | 48 | 0 | 15 | 19 | 0 | 0 | 0 | 0 | 0 | 86 | 105 | 4.63 | 0 | 0 | 0 |  | 688 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 68 | 290 | 0 | 0 | 204 | 0 | 0 | 0 | 60 | 0 | 210 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 50 |  | 8250.83 | DayPeak
Yesterday Evening Peak | 35 | 0 | 100 | 0 | 350 | 0 | 0 | 345 | 355 | 0 | 0 | 420 | 0 | 0 | 0 | 55 | 339 | 0 | 0 | 0 | 10 | 0 | 100 | 0 | 62 | 0 | 35 | 17 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 42 | 50 | 105 | 0 | 0 | 204 | 0 | 104 | 0 | 0 | 0 | 0 | 102 | 100 | 83 | 50 | 19 | 12 | 80 | 0 | 0 | 340 | 320 | 160 | 35 | 87 | 33 | 55 | 0 | 33 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 148 | 146 | 53 | 20 | 0 | 58 | 0 | 50 | 46 | 100 | 140 | 65 | 77 | 40 | 0 | 18 | 33 | 10 | 275 | 24 | 8 | 0 | 265 | 0 | 0 | 200 | 0 | 88 | 0 | 10 | 100 | 0 | 0 | 0 | 70 | 105 | 0 | 0 | 17 | 0 |  | 933 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 43 | 0 | 40 | 174 | 28 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 30 | 22 | 11 | 11 | 0 | 69 | 290 | 17 | 15 | 171 | 0 | 0 | 0 | 97 | 10 | 182 | 0 | 426 | 105 | 0 | 70 | 68 | 101 | 0 | 0 | 0 |  | 10109 | EvPeak
Forecast for Evening | 35 | 0 | 100 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 110 | 0 | 25 | 215 | 0 | 0 | 145 | 0 | 0 | 0 | 100 | 100 | 96 | 50 | 19 | 45 | 100 | 0 | 0 | 360 | 360 | 225 | 36 | 100 | 33 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 156 | 160 | 95 | 22 | 0 | 60 | 0 | 51 | 50 | 163 | 160 | 66 | 77 | 40 | 0 | 20 | 33 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 70 | 105 | 0 | 260 | 54 | 110 |  | 696 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 70 | 40 | 180 | 33 | 110 | 30 | 60 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 35 | 22 | 14 | 11 | 0 | 68 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 100 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 50 | 50 | 30 | 335 | 0 |  | 0 | 50 | 50 | 100 | 50 | 70 | 0 | 45 | 17 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 110 | 0 | 25 | 215 | 0 | 0 | 140 | 0 | 0 | 0 | 80 | 100 | 50 | 20 | 19 | 20 | 80 | 0 | 0 | 360 | 360 | 225 | 36 | 100 | 33 | 55 | 0 | 30 | 0 | 8 | 0 | 22 | 11 | 33 | 22 | 116 | 170 | 0 | 22 | 1.6 | 60 | 0 | 51 | 50 | 163 | 160 | 66 | 75 | 40 | 0 | 20 | 30 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 0 | 115 | 70 | 51 | 5 | 230 | 54 | 50 |  | 696 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 60 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 210 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 425 | 0 | 100 | 113 | 0 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 369 | 360 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 31 | 33 | 0 | 0 | 0 | 40 | 50 | 110 | 0 | 0 | 205 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 80 | 0 | 0 | 295 | 280 | 194 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 94 | 180 | 0 | 0 | 0.5 | 30 | 0 | 11 | 5 | 100 | 133 | 66 | 5 | 5 | 0 | 0 | 12 | 10 | 310 | 0 | 8 | 0 | 3 | 0 | 0 | 7 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 1.5 | 0 | 0 | 0 | 0 | 591 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 67 | 290 | 0 | 0 | 186 | 0 | 0 | 0 | 22 | 0 | 177 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0
199
| Minimum Generation |  | 6419 | 5:00
| Highest Generation |  | 10109 | 19:00
| Day Peak Generation |  | 8250.83 | 12:00
| Evening Peak Generation |  | 10109 | 19:00
| HVDC Max Flow |  | 935 | 19:30
| HVDC EvPeak Flow |  | 933 | 19:00
| Load factor L.F |  | 81.72%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-03
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8250.83 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6666 | MW
Evening Peak Generation : |  | 10109 | MW Hour : | 19:00 | Available Max Generation : |  | 14352 | MW
E.P. Demand (at gen end) : |  | 10109 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10600 | MW
Maximum Generation : |  | 10109 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3752 | MW
Total Gen. (MKWH) : |  | 198.256 | System Load Factor : | 81.72% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 264 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-03
Actual : | 101.81 | Ft.(MSL) , | Rule curve : | 108.38 | Ft.( MSL )
Gas Consumed : | Total = | 1148.4 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129971222.504
: |  | Coal : | 39143288.99 | Oil : | 235356044.58 | Total : | 404470556.074
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3773.6947 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1282.0017 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1148.406 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1037.6017 |  |  | 0 | 0%
) | 0 | 0:00 | 937.7097 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 756.6954 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 424.7325 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 194.8717 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 583.5933 |  |  | 0 | 0%
Total | 0 |  | 10139.3067 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-1,3 & 5
4) Sirajganj 225 MW Unit-2
5) Raozan #2
6) Ashuganj unit-4 & 5
7) Chandpur CCPP ST
8)Sylhet 150 MW
9) Fenchuganj # 03 & 04
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Halishar 132/33 kV T-1, T-2, T-3 transformers tripped at 10:10 for capacitor bank snapped at B-phase loop |  |  |  |  | About 110 MW power interruption occurred under Halishar S/S area
at 33 kV feeder and were switched on at 10:29. |  |  |  |  | from 10:10 to 10:29.
b) Amnura-Chapainwabganj 100 MW 132 kV line was under shut down from 08:07 to 16:00 for A/M.
c) Baghabari 100 MW was shut down at 09:16 for on test basis.
d) Cumilla(s)-Surjamoninagar 132 kV Ckt-1 tripped at 11:40 from Cumilla(s) showing auto recloser blocked and
was switched on at 11:46.
e) Tongi(New)-Tongi P.P. 132 kV Ckt was under shut down from 09:01 to 13:35 for A/M.
f) Hathazari-Baroierhat 132 kV Ckt was under shut down from 07:57 to 15:46 for A/M.
g) Mirpur-Uttara 132 kV third phase was under shut down from 09:19 to 17:22 for A/M.
h) Halishahar-Kulsi 132 kV Ckt-1 was under shut down from 09:07 to 15:34 for A/M.
i) Maniknagar-Siddirganj 230 kV Ckt-2 & Maniknagar 230/132 kV T-2 transformer were under shut down from
08:07 to 17:21 for C/M.
j) Kishorganj-Mymensingh 132 kV Ckt was under shut down from 09:07 to 16:40 for A/M.
k) Jamalpur-United(Mymensingh) P.P. 132 kV Ckt-1 was under shut down from 08:09 to16:08 for A/M.
l) Sikalbaha-Anwara P.P. 230 kV Ckt-2 was under shut down from 09:39 to 22:18 for C/M.
m) Sherpur-United(Mymensingh) P.P. 132 kV Ckt-1 was under shut down from 08:12 to 16:28 for A/M.
n) Dhamrai-Kaliakoir 132 kV Ckt-1 was under shut down from 08:26 to 16:58 for A/M.
o) Mirpur-Aminbazar 132 kV Ckt-2 was under shut down from 08:30 to 13:18 for C/M.
p) Polashbari-Mohastangarh 132 kV Ckt-1 was under shut down from 08:10 to 16:38 for A/M.
q) Chuadanga 132/33 kV T-1 transformer was under shut down from 08:03 to 15:14 for A/M.
r) Khulna(c) 132/33 kV T-1 transformer was under shut down from 08:26 to 15:42 for A/M.
s) Khulna(s) 230/132 kV T-1 transformer was under shut down from 09:02 to 15:14 for A/M.
t) Madaripur 132 kV capacitor bank was shut down at 08:25 for A/M.
u) Barishal 230/132 kV T-2 transformer was under shut down from 09:26 to 15:15 for C/M.
v) Sitalakkha-Hasnabad 132 kV Ckt was under shut down from 09:26 to 15:15 for C/M.
w) Hasnabad 132 kV main bus was under shut down from 09:56 to 16:30 for A/M.
x) Chandpur CCPP St was synchronized at 12:46.
y) Faridpur-Madaripur 132 kV Ckt-1 was switched on at 16:45.
z) Tangail 132/33 kV T1 transformer was switched on at 16:59.
aa) Palasbari-Confidence Bogura 132 kV Ckt was under shut down from 18:11 to 21:45 due to over load
of Bogura-Mohastanghor ckt.
ab) Sikalbaha 150 MW was synchronized at 15:36.
ac) Baghabari 100 MW was synchronized at 14:56.
ad) Hasnabad 33 kv Bus along with T1 transformer were under shut down from 04:10(03/11/2019) to
05:03(03/11/2019) for D/W.
ae) Chandpur 150 MW tripped at 04:09(03/11/2019).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 770000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2661000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 7542827
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8504320 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 355 | 7778000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9070250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 548849
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 119124
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 10 | 26880 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 339 | 7334076
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 409536 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 35 | 381312 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 673920 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 230400 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 234267 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 193286
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 62 | 399360 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 1221900 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 690700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 48780 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 265 | 3312000 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 88 | 367200 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 1217520 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 2859 | 54538507
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 133785
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 312480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 2165731 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4781595
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2411850 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1552284
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 395751
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1190280
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 183360 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 454752
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 544320
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 83 | 7574400 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30960
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 100798 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1003 | 24332346
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1917884 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 160 | 4408000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 7698900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7437000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 661840 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 897600
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 35 | 702545 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 33 | 487688 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 1727140
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 504480 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 344052
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 216360 | Machine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2908800
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 278300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 495600
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1476 | 30686189
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 146 | 4071680 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 358206
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 53 | 221760 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14000
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 1888800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 419 | 6554446
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1405000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 2841545 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3150000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 532800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 654768
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 178320
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1353384 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 723840 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 710280 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 118000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 33 | 458360 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 145800
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7318800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 132480
| Sylhet Area Total |  |  |  | 1949 | 944 | 19723377
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 933 | 17143272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 34560 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 143040
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8413632 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 205500
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 10 | 29760 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 616320
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 68 | 240768 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1560 | 26826852
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 36480 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 522302
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 174 | 4144770 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1535021
| Barisal Area Total |  |  |  | 462 | 315 | 6238573
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 60 | 108500 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 29488 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 296700
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 9878 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 171 | 4647127 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4699682 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 426 | 9373966 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 40821
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 332640
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 176292
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 195912
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 34080 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 41524 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 252960 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 285120 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1041 | 20524690
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 69 | 1635927
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 290 | 7022600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 17000
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 62000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 101 | 53880
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39575
| Rangpur Area Total |  |  |  | 605 | 492 | 8830982
| Total |  |  |  | 19018 | 10109 | 198255962
| Eastern Grid Total |  |  |  | 13454 | 6701 | 135834865
| Western Grid Total |  |  |  | 5564 | 3408 | 62421097
| National Grid Total |  |  |  | 19018 | 10109 | 198255962
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-02
(a) ENTIRE EASTERN GRID : |  | 6721 | MW | (b) ENTIRE WESTERN GRID : |  | 2939 | MW
i) Dhaka area |  | 3698 | MW | i) Khulna area |  | 1136 | MW
ii) Chittagong area |  | 1004 | MW | ii) Rajshahi area |  | 932 | MW
iii) Comilla area |  | 866 | MW | iii) Barisal area |  | 286 | MW
iv) Mymensingh area |  | 735 | MW | iv) Rangpur area |  | 585 | MW
v) Sylhet area |  | 418 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9660 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 1500 | Srimongal | 34 | 1800 | Bottail | 102 | 1830
Munsiganj | 91 | 2000 | Shahjibazar | 102 | 1830 | G.K Project | 44 | 1830
Sonargaon | 68 | 2000 | Fenchuganj | 33 | 1800 | Faridpur | 140 | 1830
Shyampur | 172 | 1000 | Kulawara | 43 | 1800 | Madaripur | 65 | 1930
Bhulta | 175 | 1100 | Sylhet | 128 | 1800 | Sariatpur | 44 | 1900
Madanganj | 61 | 1900 | Chatak | 22 | 1800 | Gopalganj | 74 | 1830
Shitalakhya | 111 | 1600 | Sunamganj | 35 | 1900 | Bagerhat | 70 | 1800
Rahim steel | 10 | 1900 | Biani Bazar | 44 | 1800 | Mongla | 34 | 1000
Matuail | 88 | 1600 | Comilla (S) | 152 | 1800 | Satkhira | 76 | 1900
Ghorasal | 76 | 1800 | Comilla(N) | 89 | 1800 | Gallamari | 40 | 1800
Narsingdi | 122 | 1900 | Chandpur | 81 | 1900 | Magura | 40 | 1800
Haripur (SBU) | 84 | 2000 | Feni | 118 | 1800 | Norail | 25 | 1900
Ullon | 65 | 1800 | Chowmuhani | 138 | 1800 | Chuadanga | 68 | 1830
Hasnabad | 161 | 2000 | Ashuganj | 44 | 2400 | Barisal(N) | 34 | 1800
Magbazar | 97 | 1300 | Daudkandi | 102 | 1800 | Barisal (S) | 86 | 1800
Maniknagar | 96 | 1800 | B.Baria | 118 | 1900 | Patuakhali | 102 | 1930
Bangabhaban | 10 | 1200 | Ramganj | 64 | 1830 | Bhandaria | 44 | 1930
Narinda | 82 | 1100 | Madunaghat | 53 | 1800 | Borhan Uddin | 28 | 1930
Dhanmondi | 135 | 1300 | Hathazari | 91 | 1900 | Ishurdi | 52 | 1800
Lalbag | 80 | 1800 | Khulshi | 180 | 1500 | Ruppur Paromanobik | 1 | 100
Madartek | 61 | 1830 | Halishahar | 128 | 1500 | Natore | 94 | 1900
Mirpur | 96 | 1800 | Baraulia | 150 | 1200 | Bogra | 152 | 1830
Kalyanpur | 90 | 1830 | Sikalbaha | 22 | 2100 | Noagaon | 83 | 1900
Gulshan | 122 | 1300 | Dohazari | 83 | 1830 | Rajshahi | 105 | 2000
Uttara | 52 | 1800 | Cox'sbazar | 93 | 1800 | Rajshahi New | 10 | 1900
Uttara New | 38 | 1800 | Chandraghona | 26 | 1800 | C.Nawabganj | 52 | 1800
Kamrangirchar | 68 | 1800 | Kaptai | 4 | 1800 | Amnura | 24 | 1900
Savar | 128 | 1900 | A. Khaer Stl. | 20 | 2300 | Pabna | 27 | 1800
Bhasantec | 144 | 1800 | Bakulia | 97 | 1800 | Shahjadpur | 76 | 1900
Agargaon | 46 | 1800 | Julda | 18 | 700 | Serajganj | 75 | 1900
Satmosjid | 101 | 1800 | TK chemical | 13.5 | 100 | Niyamatpur | 42 | 1830
Tongi | 134 | 1800 | Modern Steel | 3 | 600 | Joypurhat | 44 | 1830
Kabirpur | 185 | 1800 | Shahmirpur | 29 | 1830 | Sherpur(Bogura) | 35 | 1800
Basundhara | 98 | 1830 | Khagrachhari | 18 | 1830 | Mohastangor | 12 | 1830
Manikganj | 82 | 1830 | Matarbari | 26 | 1800 | Rangpur | 104 | 1830
Joydevpur | 188 | 1830 | Baroiar Hat | 20 | 1800 | Lalmonirhat | 46 | 1830
New Tongi | 99 | 1800 | Rangamati | 12 | 1800 | Saidpur | 86 | 1830
Korda | 249 | 1800 | Abul Khair 230 | 126 | 1400 | Purbasadipur | 78 | 1800
Dhamrai | 46 | 1300 | BSRM | 97 | 100 | Thakurgaon | 57 | 1830
Valuka | 94 | 1800 | GPH Ispat | 0.09 | 1800 | Palashbari | 92 | 1830
Tangail | 149 | 1830 | Goalpara | 22 | 1000 | Barapukuria | 42 | 2000
Mymensing | 183 | 1830 | Central s/s | 81 | 1830 | Panchagar | 39 | 1800
Kishorganj | 197 | 1830 | Noapara | 48 | 1830 | Joldhaka | 20 | 1800
Netrokona | 78 | 1800 | Jessore | 102 | 1900 | Kurigram | 38 | 1800
Jamalpur | 94 | 1830 | Benapol | 32 | 1800
Sherpur | 72 | 1800 | Jhenida | 84 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-02 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 386 | 3:00 | 377 | 11:00 | Kaliakoir | 367 | 4:00 | 356 | 11:00
Bheramara | 402 | 1:00 | 385 | 18:30 | Bhulta | 376 | 4:00 | 365 | 11:00
Ashuganj(N) | 382 | 7:00 | 370 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
Ghorasal | 230 | 1:00 | 222 | 10:00 | Hathazari | 218 | 21:00 | 210 | 10:00
Ishurdi | 236 | 4:00 | 225 | 20:00 | Megnaghat | 219 | 5:00 | 214 | 13:00
Ashuganj | 230 | 1:00 | 225 | 10:00 | Fenchuganj | 232 | 9:00 | 227 | 11:00
Serajganj | 233 | 5:00 | 229 | 18:30 | Siddhirganj | 221 | 4:00 | 214 | 11:00
Baghabari | 236 | 6:00 | 232 | 10:00 | Maniknagar | 219 | 6:00 | 210 | 11:00
Barapukuria | 230 | 2:00 | 225 | 18:00 | Old Airport | 217 | 4:00 | 208 | 11:00
Bogra | 231 | 4:00 | 226 | 18:30 | Barisal | 232 | 16:00 | 221 | 10:00
Khulna South | 227 | 4:00 | 208 | 11:00 | AKSML | 213 | 17:00 | 204 | 15:00
Rampura | 220 | 4:00 | 211 | 10:00 | BSRM | 216 | 19:00 | 207 | 15:00
Haripur | 219 | 1:00 | 213 | 11:00 | Bibiyana | 229 | 22:00 | 223 | 14:00
Hasnabad | 220 | 4:00 | 210 | 9:00 | Bhulta | 221 | 3:00 | 214 | 11:00
Aminbazar | 219 | 6:00 | 210 | 11:00 | Ashuganj (S) | 229 | 4:00 | 224 | 11:00
Tongi | 215 | 18:00 | 207 | 10:00 | Kaliakoir | 222 | 4:00 | 214 | 11:00
Comilla (N) | 226 | 3:00 | 217 | 11:00 | GPH | 213 | 19:00 | 203 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 100 | 127 | 1100 | Halishahar | 130 | 1700 | 124 | 1100
Munsiganj | 130 | 600 | 126 | 1100 | Baraulia | 128 | 1800 | 120 | 1500
Megnaghat | 127 | 700 | 125 | 300 | Sikalbaha | 130 | 1800 | 124 | 1500
Shyampur | 132 | 100 | 128 | 1100 | Dohazari | 128 | 1900 | 121 | 1500
Bhulta | 125 | 300 | 120 | 1100 | Cox'sbazar | 121 | 800 | 114 | 200
Madanganj | 132 | 100 | 125 | 1930 | Chandraghona | 129 | 1800 | 125 | 1000
Shitalakhya | 133 | 100 | 126 | 1100 | Kaptai | 129 | 1700 | 125 | 1100
Rahim steal | 131 | 100 | 127 | 1100 | A. Khaer Stl. | 127 | 1830 | 123 | 1100
Matuail | 131 | 500 | 125 | 1100 | Bakulia | 128 | 1800 | 123 | 1000
Ghorasal | 136 | 1800 | 132 | 1000 | Julda | 129 | 2100 | 123 | 1100
Narsinghdi | 132 | 600 | 128 | 1100 | TK Chemical | 130 | 1900 | 126 | 1100
Haripur (SBU) | 131 | 400 | 128 | 1100 | Modern Steel | 129 | 1900 | 123 | 1000
Ullon | 133 | 600 | 128 | 1200 | Shahmirpur | 129 | 1830 | 122 | 1500
Hasnabad | 134 | 600 | 129 | 1200 | Khagrachhari | 128 | 1700 | 123 | 1500
Magbazar | 135 | 600 | 128 | 1200 | Matarbari | 122 | 900 | 119 | 1100
Maniknagar | 134 | 600 | 125 | 1200 | Baroiar Hat | 126 | 2200 | 120 | 1100
Bangabhaban | 134 | 600 | 125 | 1200 | Rangamati | 129 | 1900 | 124 | 1500
Narinda | 134 | 600 | 125 | 1200 | Goalpara | 136 | 300 | 124 | 1100
Dhanmondi | 133 | 600 | 128 | 1200 | Central s/s | 136 | 400 | 124 | 1100
Lalbag | 133 | 600 | 126 | 1200 | Noapara | 134 | 400 | 120 | 1100
Madartek | 134 | 600 | 128 | 1200 | Jessore | 132 | 500 | 120 | 1000
Mirpur | 134 | 500 | 123 | 1500 | Benapol | 132 | 400 | 122 | 1000
Kalyanpur | 134 | 300 | 125 | 1100 | Jhenida | 132 | 600 | 120 | 1100
Gulshan | 133 | 200 | 127 | 1100 | Bottail | 137 | 600 | 129 | 1830
Uttara | 131 | 400 | 122 | 1100 | G.K Project | 142 | 400 | 137 | 1830
Uttara New | 131 | 300 | 122 | 1100 | Faridpur | 134 | 600 | 125 | 1100
Kamrangirchar | 133 | 500 | 121 | 1100 | Madaripur | 135 | 600 | 122 | 1100
Savar | 131 | 400 | 122 | 1100 | Sariatpur | 134 | 600 | 121 | 1100
Bhasantec | 133 | 300 | 127 | 1100 | Gopalganj | 138 | 500 | 123 | 1100
Agargaon | 135 | 400 | 128 | 1100 | Bagerhat | 133 | 300 | 120 | 1100
Satmosjid | 134 | 300 | 127 | 1200 | Mongla | 132 | 400 | 118 | 1100
Tongi | 130 | 1800 | 125 | 1100 | Satkhira | 136 | 400 | 124 | 1100
Kabirpur | 129 | 1800 | 118 | 1000 | Gallamari | 137 | 400 | 123 | 1100
Basundhara | 128 | 1300 | 123 | 1100 | Magura | 133 | 600 | 120 | 1830
Manikganj | 134 | 1800 | 126 | 1000 | Norail | 131 | 500 | 117 | 1830
Joydevpur | 137 | 1900 | 131 | 1500 | Chuadanga | 130 | 600 | 115 | 1830
New Tongi | 130 | 1800 | 123 | 1000 | Barisal(N) | 138 | 400 | 126 | 1000
Kodda | 127 | 1830 | 120 | 1200 | Barisal (S) | 137 | 400 | 125 | 1100
Dhamrai | 130 | 200 | 123 | 1500 | Patuakhali | 134 | 700 | 120 | 1100
Valuka | 129 | 2300 | 118 | 1200 | Bhandaria | 135 | 600 | 121 | 1100
Tangail | 131 | 300 | 123 | 1200 | Ishurdi | 140 | 400 | 134 | 1930
Mymensing | 131 | 2300 | 121 | 1200 | Ruppur Paromanobik | 139 | 500 | 134 | 2000
Kishorganj | 130 | 400 | 126 | 1200 | Natore | 136 | 300 | 130 | 2000
Netrokona | 129 | 800 | 120 | 1200 | Bogra | 136 | 400 | 133 | 1800
Jamalpur | 137 | 2200 | 122 | 200 | Noagaon | 133 | 500 | 128 | 1930
Sherpur | 137 | 2200 | 120 | 100 | Rajshahi | 133 | 600 | 124 | 1100
Srimongal | 135 | 300 | 131 | 1100 | Rajshahi New | 133 | 500 | 125 | 1100
Shahjibazar | 134 | 2400 | 130 | 1100 | C.Nawabganj | 130 | 1800 | 122 | 1100
Fenchuganj | 131 | 600 | 128 | 1100 | Amnura | 134 | 1800 | 125 | 1100
Khulawara | 131 | 100 | 127 | 1000 | Pabna | 139 | 200 | 134 | 1000
Sylhet | 131 | 2400 | 124 | 1100 | Shahjadpur | 142 | 500 | 137 | 100
Chatak | 130 | 2400 | 123 | 1100 | Serajganj | 136 | 100 | 131 | 1100
Sunamganj | 128 | 700 | 122 | 1100 | Niyamatpur | 133 | 600 | 124 | 1930
Biani Bazar | 129 | 2400 | 124 | 1800 | Joypurhat | 134 | 300 | 128 | 1930
Comilla(s) | 127 | 700 | 123 | 1900 | Sherpur(Bogura) | 137 | 500 | 132 | 1000
Comilla(n) | 133 | 700 | 128 | 1100 | Mohastangor | 134 | 600 | 130 | 1700
Chandpur | 127 | 100 | 124 | 1100 | Rangpur | 128 | 300 | 121 | 1800
Feni | 125 | 800 | 119 | 1600 | Lalmonirhat | 123 | 600 | 115 | 1830
Chowmuhani | 123 | 800 | 117 | 1500 | Saidpur | 129 | 500 | 119 | 1800
Ashuganj | 136 | 800 | 134 | 1200 | Purbasadipur | 125 | 400 | 117 | 1830
Daudkandi | 128 | 700 | 123 | 1100 | Thakurgaon | 123 | 500 | 110 | 1830
B.Baria | 132 | 900 | 129 | 1100 | Palashbari | 132 | 300 | 124 | 1200
Ramganj | 122 | 700 | 113 | 1400 | Barapukuria | 130 | 200 | 125 | 1800
Madanhat | 131 | 2000 | 126 | 1000 | Panchagar | 122 | 600 | 105 | 1830
Hathazari | 130 | 600 | 126 | 200 | Joldhaka | 128 | 600 | 116 | 1830
Khulshi | 128 | 1830 | 121 | 1100 | Kurigram | 127 | 400 | 116 | 1830
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 504 | 5507 | 2757 | 8264 |  |  |  | QF-LDC-12
0:30 | 422 | 5237 | 2589.5 | 7826.5 | Date: | 2019-11-02
1:00 | 340 | 4967 | 2422 | 7389
1:30 | 375 | 4783.5 | 2351 | 7134.5
2:00 | 410 | 4600 | 2280 | 6880
2:30 | 415 | 4538 | 2262.5 | 6800.5 | [5 empty] | Gen. at Eve. Peak | 10109 | 10109 MW (19:00 )
3:00 | 420 | 4476 | 2245 | 6721 | [6 empty] | 19:00
3:30 | 440 | 4424 | 2218 | 6642 | [5 empty] | Gen. at Day Peak | 8250.83 | 8250.83 MW (12:00 )
4:00 | 460 | 4372 | 2191 | 6563 | [6 empty] | 12:00
4:30 | 455 | 4315 | 2176 | 6491 | [5 empty] | Highest Generation | 10109
5:00 | 450 | 4258 | 2161 | 6419 | [6 empty] | 19:00
5:30 | 450 | 4266.55 | 2169 | 6435.55
6:00 | 450 | 4275.1 | 2177 | 6452.1
6:30 | 379 | 4282.8 | 2200.25 | 6483.05
7:00 | 308 | 4290.5 | 2223.5 | 6514
7:30 | 374 | 4342.555 | 2278.4 | 6620.955
8:00 | 440 | 4394.61 | 2333.3 | 6727.91
8:30 | 500 | 4554.275 | 2363.2 | 6917.475
9:00 | 560 | 4713.94 | 2393.1 | 7107.04
9:30 | 605 | 4795.58 | 2447.7 | 7243.28
10:00 | 650 | 4877.22 | 2502.3 | 7379.52
10:30 | 635 | 5047.525 | 2532.05 | 7579.575
11:00 | 620 | 5217.83 | 2561.8 | 7779.63
11:30 | 533 | 5438.83 | 2576.4 | 8015.23
12:00 | 446 | 5659.83 | 2591 | 8250.83
12:30 | 411 | 5747.6 | 2590.8 | 8338.4
13:00 | 376 | 5835.37 | 2590.6 | 8425.97
13:30 | 463 | 5655.135 | 2583.15 | 8238.285
14:00 | 550 | 5474.9 | 2575.7 | 8050.6
14:30 | 595 | 5553.8 | 2649.95 | 8203.75
15:00 | 640 | 5632.7 | 2724.2 | 8356.9
15:30 | 630 | 5520.3 | 2671.8 | 8192.1
16:00 | 620 | 5407.9 | 2619.4 | 8027.3
16:30 | 610 | 5305.6 | 2611.05 | 7916.65
17:00 | 600 | 5203.3 | 2602.7 | 7806
17:30 | 475 | 5815.15 | 3034.35 | 8849.5
18:00 | 350 | 6427 | 3466 | 9893
18:30 | 317 | 6564 | 3437 | 10001
19:00 | 284 | 6701 | 3408 | 10109
19:30 | 290 | 6593 | 3352 | 9945
20:00 | 272 | 6559 | 3294 | 9853 |  |  |  | Executive Engineer
20:30 | 282 | 6451.5 | 3261.5 | 9713 |  |  |  | Network Operation Division
21:00 | 292 | 6344 | 3229 | 9573
21:30 | 329 | 6166.5 | 3143.5 | 9310
22:00 | 366 | 5989 | 3058 | 9047 |  |  |  |  | Page 6 of 7
22:30 | 378 | 5924 | 2925 | 8849
23:00 | 390 | 5859 | 2792 | 8651
23:30 | 447 | 5683 | 2774.5 | 8457.5
24:00 | 504 | 5507 | 2757 | 8264
10109 MW (19:00 )
8250.83 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-02 |  | Energy | 198255962
[10 empty] | 2019-11-02 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4117 | 935 | 2110 | 529 | 358 | 91 | 0 | 0 | 124
0:30 | 4202 | 807.5 | 1923 | 328 | 356.5 | 90.5 | 0 | 0 | 119 | Date: | 2019-11-02
1:00 | 4287 | 680 | 1736 | 127 | 355 | 90 | 0 | 0 | 114
1:30 | 4172.5 | 607 | 1708.5 | 88.5 | 355 | 90 | 0 | 0 | 113 | [7 empty] | Total Energy | 198.256 | Total Energy Gen 198.256 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 198.256 MKWHr
2:00 | 4058 | 534 | 1681 | 50 | 355 | 90 | 0 | 0 | 112 | [7 empty] | Energy not Served | 0
2:30 | 4023 | 534 | 1651 | 37 | 355 | 89.5 | 0 | 0 | 111 | [7 empty] | Energy Requirement | 198.256
3:00 | 3988 | 534 | 1621 | 24 | 355 | 89 | 0 | 0 | 110
3:30 | 3969.5 | 534 | 1569.5 | 18 | 355 | 89 | 0 | 0 | 107 | [6 empty] | Shortage
4:00 | 3951 | 534 | 1518 | 12 | 355 | 89 | 0 | 0 | 104
4:30 | 3899.5 | 532 | 1501 | 12 | 355 | 88.5 | 0 | 0 | 103
5:00 | 3848 | 530 | 1484 | 12 | 355 | 88 | 0 | 0 | 102
5:30 | 3855 | 530 | 1498.5 | 12 | 355 | 88 | 0 | 0 | 97
6:00 | 3862 | 530 | 1513 | 12 | 355 | 88 | 0 | 0 | 92
6:30 | 3916 | 530 | 1490.5 | 12 | 355 | 88.5 | 0 | 0 | 88 |  |  |  |  | Coal
7:00 | 3970 | 530 | 1468 | 12 | 355 | 89 | 0 | 0 | 84
7:30 | 3969 | 530 | 1517.5 | 61.5 | 355.5 | 90 | 0 | 0 | 87 |  |  |  | Oil |  |  |  | ,
8:00 | 3968 | 530 | 1567 | 111 | 356 | 91 | 0 | 0 | 90
8:30 | 4000 | 535.5 | 1642 | 177.5 | 357 | 91 | 0 | 0 | 95
9:00 | 4032 | 541 | 1717 | 244 | 358 | 91 | 0 | 0 | 100
9:30 | 3996.5 | 615 | 1704 | 348 | 358 | 91 | 0 | 0 | 104
10:00 | 3961 | 689 | 1691 | 452 | 358 | 91 | 0 | 0 | 108
10:30 | 4068 | 689 | 1716 | 516 | 358 | 91 | 0 | 0 | 111
11:00 | 4175 | 689 | 1741 | 580 | 358 | 91 | 0 | 0 | 114
11:30 | 4190.5 | 688.5 | 1849.5 | 688 | 358 | 91 | 0 | 0 | 118
12:00 | 4206 | 688 | 1958 | 796 | 358 | 91 | 0 | 0 | 122
12:30 | 4217.5 | 688.5 | 1975 | 853.5 | 358 | 91 | 0 | 0 | 124
13:00 | 4229 | 689 | 1992 | 911 | 358 | 91 | 0 | 0 | 126
13:30 | 4229 | 689 | 1992 | 911 | 358 | 91 | 0 | 0 | 126
14:00 | 4229 | 689 | 1992 | 911 | 358 | 91 | 0 | 0 | 126
14:30 | 4184.5 | 712.5 | 1956 | 934.5 | 358.5 | 92 | 0 | 0 | 128
15:00 | 4140 | 736 | 1920 | 958 | 359 | 93 | 0 | 0 | 130
15:30 | 4023 | 778.5 | 1836.5 | 961 | 359 | 92.5 | 0 | 0 | 127
16:00 | 3906 | 821 | 1753 | 964 | 359 | 92 | 0 | 0 | 124
16:30 | 3840 | 821 | 1733 | 940 | 359 | 92 | 3 | 0 | 124
17:00 | 3774 | 821 | 1713 | 916 | 359 | 92 | 6 | 0 | 124
17:30 | 4038.5 | 877.5 | 1863 | 1311 | 359 | 92 | 170 | 0 | 138
18:00 | 4303 | 934 | 2013 | 1706 | 359 | 92 | 334 | 0 | 152
18:30 | 4277 | 933.5 | 2069 | 1800 | 359 | 92 | 320.5 | 0 | 150
19:00 | 4251 | 933 | 2125 | 1894 | 359 | 92 | 307 | 0 | 148
19:30 | 4295 | 935 | 2171 | 1737 | 359 | 92 | 208 | 0 | 148
20:00 | 4278 | 935 | 2166 | 1667 | 359 | 92 | 208 | 0 | 148
20:30 | 4273.5 | 934.5 | 2178.5 | 1567.5 | 358.5 | 92 | 162.5 | 0 | 146
21:00 | 4269 | 934 | 2191 | 1468 | 358 | 92 | 117 | 0 | 144
21:30 | 4193 | 934 | 2166 | 1341.5 | 358.5 | 92 | 83 | 0 | 142
22:00 | 4117 | 934 | 2141 | 1215 | 359 | 92 | 49 | 0 | 140
22:30 | 4115 | 934 | 2112 | 1078.5 | 358.5 | 91.5 | 24.5 | 0 | 135
23:00 | 4113 | 934 | 2083 | 942 | 358 | 91 | 0 | 0 | 130
23:30 | 4115 | 934.5 | 2096.5 | 735.5 | 358 | 91 | 0 | 0 | 127 | Max Temp. in Dhaka |  | 32.7° C
24:00 | 4117 | 935 | 2110 | 529 | 358 | 91 | 0 | 0 | 124
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 198.256 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 198.256 MKWHr
Note on W13: Author:

## Generation
2019-11-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 39 | 39 | 38 | 38 | 39 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 43 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 981731
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1184000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 105 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 105 | 105 | 105 | 105 | 110 | 110 | 110 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0.1 | 4.4 | 10 | 15 | 18 | 19 | 19 | 18 | 15.7 | 14.4 | 5.5 | 0.3 | [9 empty] | 133785
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 203 | 204 | 204 | 204 | 216 | 217 | 205 | 208 | 219 | 204 | 179 | 180 | 217 | 205 | 192 | 203 |  | 204 | 205 | 204 | 204 | 178 | 179 | 204 | 4781595
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 105 | 104 | 104 | 105 | 105 | 109 | 112 | 115 | 109 | 115 | 139 | 139 | 0 | 0 | 90 | 104 | 139 |  | 104 | 104 | 104 | 104 | 104 | 104 | 135 | 2411850
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 0 | [16 empty] | 85 |  | 102 | 85 | 85 | 68 | 34 | 0 | 0 | 395751
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | [5 empty] | 18 | 34 | 34 | 68 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1552284
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 346 | 300 | 308 | 302 | 273 | 274 | 235 | 235 | 270 | 270 | 335 | 336 | 337 | 285 | 300 | 270 | 240 | 338 |  | 339 | 336 | 338 | 340 | 345 | 345 | 300 | 7334076
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 5 | 67 | 135 | 165 | 195 | 215 | 230 | 230 | 230 | 230 | 235 |  | 265 | 265 | 265 | 230 | 210 | 214 | 115 | 3312000
19 | Ashuganj 195MW PP (APSCL-United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 702545
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 770000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 102 | 102 | 100 | 100 | 100 | 100 | 100 | 150 | 154 | 150 | 150 | 150 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2661000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 380 | 320 | 320 | 300 | 250 | 250 | 250 | 250 | 270 | 270 | 300 | 330 | 330 | 300 | 300 | 270 | 250 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 7542827
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1917884
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 10 | 10 | 10 | 10 | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 40 | 37 | 37 | 37 | 37 | 661840
33 | Ashuganj 225 MW CCPP | 180 | 186 | 181 | 179 | 180 | 181 | 200 | 201 | 192 | 218 | 202 | 181 | 180 | 198 | 185 | 180 | 188 | 179 |  | 160 | 163 | 164 | 168 | 160 | 161 | 161 | 4408000
34 | Ashuganj 450 MW CCPP(South) | 320 | 290 | 290 | 290 | 290 | 290 | 325 | 325 | 305 | 295 | 325 | 315 | 305 | 330 | 320 | 290 | 310 | 320 |  | 320 | 330 | 320 | 320 | 270 | 270 | 270 | 7437000
| Ashuganj 450 MW CCPP(North) | 340 | 310 | 270 | 270 | 270 | 270 | 305 | 310 | 305 | 310 | 325 | 340 | 330 | 300 | 315 | 280 | 305 | 340 |  | 340 | 350 | 345 | 340 | 270 | 270 | 270 | 7698900
35 | Ashuganj 55 MW PP (Precision) | 55 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 54 | 53 | 51 | 52 | 53 | 55 |  | 55 | 55 | 55 | 56 | 55 | 56 | 56 | 897600
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 80 | 70 | 30 | 30 | 31 | 32 | 30 | 85 | 86 | 87 | 89 | 87 | 90 |  | 87 | 87 | 88 | 87 | 87 | 87 | 87 | 1727140
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 345 | 345 | 345 | 343 | 348 | 362 | 374 | 374 | 345 | 367 | 360 | 350 | 349 | 382 | 320 | 280 | 349 |  | 345 | 355 | 350 | 343 | 345 | 345 | 347 | 8504320
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 370 | 370 | 330 | 330 | 330 | 330 | 330 | 350 | 350 | 380 | 420 | 380 | 350 | 350 | 320 | 320 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 400 | 9070250
41 | Haripur 360MW CCPP(HPL) | 363 | 359 | 304 | 304 | 304 | 304 | 264 | 303 | 355 | 305 | 315 | 351 | 355 | 286 | 306 | 276 | 277 | 354 |  | 355 | 355 | 355 | 355 | 358 | 361 | 358 | 7778000
42 | RPCL 210MW CCPP | 207 | 207 | 207 | 208 | 209 | 209 | 208 | 192 | 176 | 176 | 171 | 155 | 155 | 143 | 143 | 145 | 159 | 162 |  | 146 | 148 | 146 | 146 | 164 | 165 | 180 | 4071680
43
44 | Fenchugonj CCPP Phase-1 | 59 | 60 | 60 | 60 | 58 | 58 | 58 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 56 | 59 | 58 |  | 58 | 60 | 58 | 58 | 60 | 60 | 60 | 1405000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 128 | 128 | 129 | 128 | 128 | 128 | 137 | 133 | 129 | 130 | 141 | 134 | 147 | 146 | 150 | 135 | 132 | 141 |  | 140 | 146 | 145 | 144 | 121 | 127 | 124 | 3150000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 64 | 63 | 63 | 65 | 63 | 62 | 63 | 63 | 65 |  | 65 | 66 | 66 | 66 | 67 | 67 | 67 | 1353384
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 10 | 10 | 10 | 10 | 10 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 723840
49 | Shahjibazar 50MW PP (EPL) | 40 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 710280
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [16 empty] | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 118000
52 | Sylhet 50MW PP (EPL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 25 | 30 | 30 | 30 | 29 | 12 | 32 |  | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 458360
53 | Sylhet 10MW PP (Desh) | 0 | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 132480
54 | Hobiganj 11MW PP Cofidence-E | 11 | 8 | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178320
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 17 | 47 | 22 | 22 | 25 | 25 | 32 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 532800
56 | Shahjahanulla 25 MW PP | [19 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 145800
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 280 | 305 | 280 | 270 | 300 | 300 | 310 | 320 | 290 | 310 | 305 | 280 | 280 | 320 | 280 | 280 | 300 |  | 275 | 315 | 300 | 305 | 290 | 280 | 290 | 7318800
58 | Nababganj 55 MW PP (Southern power ) | 17 | [16 empty] | 55 |  | 55 | 17 | 17 | 17 |  |  |  | 193286
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 454752
61 | Narshingdi 22 MW PP (Doreen) | [19 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 119124
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 358206
63 | Impoprt (Tripura) | 114 | 112 | 110 | 104 | 102 | 92 | 84 | 90 | 100 | 108 | 114 | 122 | 126 | 128 | 130 | 124 | 124 | 152 |  | 148 | 148 | 148 | 144 | 140 | 130 | 124 | 2908800
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 10 | 3 | 2 | 2 | 2 | 4 | 4 | 2 | 2 | 3 | 4 |  | 12 | 17 | 20 | 32 | 37 | 37 | 40 | 544320
65 | Feni 22MW PP (Doreen) | 22 | [7 empty] | 16 | 19 | 19 | 22 | 22 | 22 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 344052
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 216360
67 | Jangalia 33MW PP (Summit) | [12 empty] | 16 | 16 | 15 | 15 | 15 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 278300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495600
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 22 |  | 10 | 10 | 10 | 10 | 10 | 31 | 31 | 621900
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 17 | 28 | 28 | 28 | 28 | 28 | 33 | 0 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 690700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 803000
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 7 |  | 10 | 0 | [5 empty] | 26880
78 | Gazipur 52 MW PP | [17 empty] | 39 | [8 empty] | 48780
79 | Kodda 150MW PP | [17 empty] | 62 |  | 100 | 65 | 65 | 16 |  |  |  | 230400
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 12 |  | 53 | 40 | 40 | 40 | 40 | 0 | 0 | 221760
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | 17 | [6 empty] | 35 | 70 | 88 | 82 | 86 | 89 | 88 | 88 | 88 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 34 | 1217520
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.9 | 2.01 | 3.34 | 4.22 | 4.63 | 4.63 | 4.27 | 3.5 | 2 | 1 | 0 | 0 | [8 empty] | 30960
| Jodiac Power | [17 empty] | 15 |  | 17 | 17 | 17 | 17 | 17 |  |  | 100798
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 0 | [7 empty] | 0 | 10 | 80 | 90 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 1190280
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 19 | 46 | 47 | 47 | 47 | 5 | 22 |  | 46 | 49 | 49 | 49 | 49 | 49 | 49 | 654768
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 24 | 35 | 35 | 35 | 10 | 18 |  | 33 | 35 | 35 | 35 | 35 | 35 | 35 | 487688
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 |  | 0 | [6 empty] | 409536
95 | Patenga 50MW PP (Baraka) | [8 empty] | 2 | 18 | 5 | 19 | 28 | 30 | 30 | 30 | 30 | 41 |  | 50 | 18 | 22 |  |  |  |  | 312480
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 9 | 24 | 24 | 29 | 50 | 50 | 54 |  | 83 | 90 | 94 | 95 | 91 | 91 | 50 | 7574400
97 | Katpotti 52 MW PP (Sinha) | 33 | 33 | 24 | 12 | 12 | 12 | 12 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 35 | 47 | 47 | 32 | 27 |  |  | 381312
98 | Bosila 108MW PP(CLC) | [11 empty] | 1 | 40 | 40 | 40 | 40 | 42 | 62 |  | 62 | 62 | 62 | 16 |  |  |  | 399360
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 28 | 55 | 55 | 42 | 55 | 55 | 55 | 55 | 55 |  | 55 | 15 | 15 | 0 | 0 |  |  | 548849
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 17 | 17 | 17 |  |  |  | 234267
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 130 | 100 | 100 | 100 | 100 | 130 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2841545
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 0.6 | 1.6 | 2 | 2.2 | 2.2 | 2.1 | 1.7 | 0.3 | 0.4 | 0 | [9 empty] | 14000
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 673920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 | [6 empty] | 29 | 40 | 40 | 40 | 48 | 60 | 60 | 60 | 60 | 65 | 149 |  | 200 | 200 | 200 | 200 | 200 | 200 | 100 | 1888800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 6 | 15 | 15 | 15 | 16 | 15 | 16 | 45 |  | 88 | 80 | 63 | 32 | 15 | 0 | 0 | 367200
115 | Juldah 100 MW PP Unit-3 (Acorn) | [12 empty] | 10 | 10 | 30 | 30 | 30 | 30 |  | 10 | 10 | 10 | 10 | 0 | 0 |  | 183360
116 | Chandpur 200MW (Desh energy) | [16 empty] | 0 | 22 |  | 100 | 100 | 100 | 100 | 70 | 35 | 0 | 504480
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 4967 | 4600 | 4476 | 4372 | 4258 | 4275.1 | 4290.5 | 4394.61 | 4713.94 | 4877.22 | 5217.83 | 5659.83 | 5835.37 | 5474.9 | 5632.7 | 5407.9 | 5203.3 | 6427 |  | 6701 | 6593 | 6559 | 6344 | 5989 | 5859 | 5507 | 135834865
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 0 | 16 |  | 16 | 0 | [5 empty] | 34560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 6 | 39 |  | 43 | 43 | 43 | 18 | 0 |  |  | 143040
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 17 | 35 | 17 | 17 | 17 | 17 | 105 |  | 105 | 105 | 105 | 105 | 70 | 17 | 0 | 616320
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 0 | 16 |  | 16 | 16 | 0 |  |  |  |  | 36480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 62 | 62 | 32 | 32 | 12 | 12 | 12 | 11 | 27 | 31 | 31 | 60 | 95 | 95 | 94 | 96 | 97 | 97 |  | 97 | 97 | 95 | 97 | 96 | 98 | 96 | 1535021
| Bhola 225 MW CCPP | 166 | 173 | 173 | 173 | 173 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 173 | 174 | 174 | 170 | 173 | 173 |  | 174 | 174 | 173 | 173 | 173 | 155 | 174 | 4144770
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 22 | 22 | 21 | 20 | 19 | 17 | 16 | 19 | 18 | 19 | 20 | 21 | 20 | 18 | 20 | 26 |  | 28 | 28 | 30 | 30 | 29 | 27 | 22 | 522302
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 1 |  | 10 | 10 | 0 |  |  |  |  | 29760
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 205500
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 0 | 89 |  | 68 | 67 | 34 | 33 | 33 | 0 |  | 240768
146 | Bheramara HVDC | 680 | 534 | 534 | 534 | 530 | 530 | 530 | 530 | 541 | 689 | 689 | 688 | 689 | 689 | 736 | 821 | 821 | 934 |  | 933 | 935 | 935 | 934 | 934 | 934 | 935 | 17143272
147 | Bheramara 360 MW CCPP | 345 | 325 | 325 | 320 | 320 | 325 | 370 | 375 | 350 | 350 | 370 | 350 | 345 | 370 | 395 | 280 | 280 | 345 |  | 345 | 360 | 355 | 345 | 345 | 345 | 345 | 8413632
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 66 | 68 | 68 | 68 | 68 | 68 | 69 | 69 | 69 | 69 | 69 |  | 69 | 69 | 69 | 68 | 69 | 68 | 68 | 1635927
152 | Barapukuria 275 MW TPP Unit-3 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7022600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 |  |  |  |  | 30 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 108500
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 0 | [6 empty] | 29488
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 193 | 163 | 160 | 157 | 155 | 168 | 176 | 191 | 203 | 200 | 205 | 204 | 202 | 196 | 203 | 192 | 173 | 183 |  | 171 | 171 | 173 | 174 | 168 | 167 | 174 | 4647127
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 195 | 193 | 191 | 183 | 183 | 181 | 177 | 184 | 194 | 196 | 200 | 210 | 206 | 183 | 184 | 181 | 172 | 187 |  | 182 | 177 | 177 | 177 | 175 | 160 | 163 | 4699682
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 338 | 388 | 388 | 350 | 347 | 347 | 345 | 428 | 431 | 429 | 420 | 414 | 379 | 384 | 415 | 345 | 383 | 395 |  | 426 | 422 | 429 | 431 | 394 | 339 | 383 | 9373966
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 332640
163 | Bogura 20 MW PP (Energyprima) | 0 | [7 empty] | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 14 | 14 | 14 | 14 | 176292
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 195912
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 296700
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 0 | [6 empty] | 9878
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 29 |  | 30 | 0 | [5 empty] | 40821
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 21 |  | 8 | 8 | 0 | 0 | 0 | 0 |  | 34080
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 51 |  | 0 | [6 empty] | 41524
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence) | [17 empty] | 29 |  | 70 | 70 | 70 | 35 |  |  |  | 252960
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 10 | 50 | 50 | 42 | 42 | 52 | 38 | 0 | [9 empty] | 285120
173 | Rangpur 20 MW GTPP | [19 empty] | 17 | 0 | [5 empty] | 17000
175 | Saidpur 20 MW GTPP | [17 empty] | 18 |  | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 62000
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 101 |  | 101 | 101 | 107 | 107 | 70 | 35 | 0 | 53880
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.5 | 2.3 | 4.1 | 5.3 | 5.8 | 6 | 5.6 | 4.7 | 4.2 | 1.4 | 0.7 | [9 empty] | 39575
178
178