## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-04 | Monday
|  | Date (day): | 2019-11-04 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11884.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14545 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-03 | 2019-11-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 43 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 96 | 220 | 220 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 330 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 345 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 308 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 50 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 300 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 50 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 47 | 47
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 17 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 55 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 62 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 45 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 175 | 300 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 30 | 120 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2397 | 3067 | 3630 | 4391 | 806 | 636
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.13 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 50 | 20 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 133 | 132 | 130 | 130 | 100 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 222 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 147 | 140 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 51 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 70 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 7 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 88 | 50 | 96 |  | 12 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.9 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 784.03 | 1142 | 1399 | 1659 | 360 | 110
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 178 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 325 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 33 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 54 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 8 | 8 | 8 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 35 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 80 | 90 | 100 |  | 57 | ST under maintenance
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 190 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 150 | 116 | 156
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 22 | 22
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1293 | 1535 | 1703 | 2176 | 485 | 81
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 147 | 170 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 80 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.5 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 60 | 200 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 24 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 238.5 | 473 | 408.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | Water problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 150 | 160 | 300 | 300
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 74 | 74 | 74 |  | 12 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 29 | 33 | 32 | 33 |  | 17 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 275 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 865 | 964 | 1242 | 1243 | 0 | 581
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 689 | 691 | 696 | 696
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 45
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 400 | 245 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 68 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1089 | 1208 | 1191 | 1927 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 28 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 150 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 47 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 241 | 291 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 199 | 179 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 185 | 186 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 401 | 372 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 60 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 100 | 113 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 38 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 925 | 1104 | 1454 | 1604 | 320 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 68 | 68 | 68 | 68
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 290 | 290 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 364 | 471 | 479 | 505 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 8196.53 | 10255 | 11884.6 | 14545 | 2013 | 1572
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7823.2702 | 9788 | 11343.39 | 13882.6387
A. |  | 2019-11-03 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10255 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6666 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10255 | MW
3 | Day peak Generation : |  |  | 8196.53 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9788 | MW
4 | Evening peak Generation : |  |  | 10255 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 200.6498 | MKWHr | By Solar | 0.21257 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 147.911 | MKWHr |  | By Oil: | 22.4892 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.6327 | MKWHr |  | By Hydro: | 2.4951 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2013 | MW | Dhaka | 3768 | 3768 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1572 | MW | Chittagong | 1047 | 1047 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3585 | MW | Khulna | 1138 | 1138 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1157.09 | MMCFD |  |  | Rajshahi | 953 | 953 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 135425546.972 | ii) Oil : | Taka | 257568047.28 | Comilla | 906 | 906 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 38946052.34 | Total | Taka | 431939646.592 | Mymensingh | 708 | 708 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 427 | 427 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 284 | MW (E to W) at | 19:00 | hrs | Barisal | 269 | 269 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 264 | MW at | 18:30 | hrs | Rangpur | 572 | 572 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31° C |  |  | Total | 9788 | 9788 |  | 0
B. |  | 2019-11-04 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 30.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14545 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 4045 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 205.4434 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6783.1 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.9476 | MKWHr. | ii) HVDC Flow at Peak Time |  | 691 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9616 | MKWHr. | iii) Maximum HVDC Flow : |  | 752 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.76 | 101.81 |  | (b) Today: | 101.76 |  | (c) Rule Curve: |  | 108.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 347 | 322 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 41 | 50 | 110 | 0 | 0 | 203 | 0 | 0 | 135 |  | 0 | 0 | 0 | 20 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 270 | 270 | 168 | 35 | 87 | 37 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 118 | 182 | 0 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 128 | 67 | 74 | 40 | 0 | 18 | 33 | 10 | 290 | 24 | 8 | 0 | 45 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 0 |  | 752 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 68 | 290 | 0 | 0 | 174 | 0 | 0 | 0 | 96 | 0 | 161 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5235 | 2577 | 7812 | 3999 | 752 | 2069 | 290 | 358 | 91 | 135 | 118 | 0 | 0 | 101.81
2:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 350 | 322 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 50 | 110 | 0 | 0 | 203 | 0 | 0 | 134 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 275 | 275 | 170 | 35 | 87 | 37 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 112 | 183 | 0 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 128 | 67 | 74 | 40 | 0 | 18 | 33 | 10 | 300 | 4 | 8 | 0 | 15 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 68 | 0 | 0 | 0 | 0 |  | 591 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 67 | 290 | 0 | 0 | 178 | 0 | 0 | 0 | 96 | 0 | 164 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5108 | 2428 | 7536 | 3985 | 591 | 2080 | 185 | 357 | 92 | 134 | 112 | 0 | 0 | 101.81
3:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 355 | 322 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 43 | 50 | 110 | 0 | 0 | 204 | 0 | 0 | 133 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 80 | 0 | 0 | 270 | 270 | 166 | 35 | 87 | 37 | 56 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 110 | 195 | 0 | 22 | 0 | 60 | 0 | 11 | 49 | 100 | 128 | 67 | 5 | 40 | 0 | 0 | 10 | 10 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 |  | 592 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 67 | 290 | 0 | 0 | 177 | 0 | 0 | 0 | 95 | 0 | 165 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4755 | 2387 | 7142 | 3926 | 592 | 1855 | 76 | 357 | 93 | 133 | 110 | 0 | 0 | 101.81
4:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 353 | 322 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 33 | 16 | 0 | 0 | 44 | 50 | 110 | 0 | 0 | 209 | 0 | 0 | 110 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 80 | 0 | 0 | 280 | 285 | 175 | 16 | 87 | 37 | 56 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 104 | 197 | 0 | 0 | 0 | 60 | 0 | 11 | 5 | 100 | 127 | 67 | 5 | 5 | 0 | 0 | 10 | 10 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 |  | 591 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 68 | 290 | 0 | 0 | 173 | 0 | 0 | 0 | 21 | 0 | 164 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4587 | 2322 | 6909 | 3902 | 591 | 1692 | 58 | 358 | 94 | 110 | 104 | 0 | 0 | 101.81
5:00 | 35 | 0 | 100 | 0 | 280 | 0 | 0 | 352 | 322 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 50 | 110 | 0 | 0 | 207 | 0 | 0 | 105 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 80 | 0 | 0 | 270 | 270 | 164 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 197 | 0 | 0 | 0 | 60 | 0 | 11 | 5 | 100 | 127 | 68 | 5 | 5 | 0 | 0 | 10 | 10 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 |  | 591 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 68 | 290 | 0 | 0 | 172 | 0 | 0 | 0 | 21 | 0 | 163 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4368 | 2298 | 6666 | 3725 | 591 | 1644 | 51 | 358 | 92 | 105 | 100 | 0 | 0 | 101.81
6:00 | 35 | 0 | 100 | 0 | 280 | 0 | 0 | 371 | 322 |  | 0 | 370 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 110 | 0 | 0 | 208 | 0 | 0 | 103 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 80 | 0 | 0 | 290 | 290 | 177 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 98 | 197 | 0 | 0 | 0 | 30 | 0 | 11 | 5 | 100 | 129 | 67 | 5 | 5 | 0 | 0 | 10 | 10 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 |  | 592 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 68 | 290 | 0 | 0 | 182 | 0 | 0 | 0 | 21 | 0 | 173 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4333.1 | 2340 | 6673.1 | 3756 | 592 | 1625 | 51 | 358 | 90 | 103 | 98 | 0.1 | 0 | 101.81
7:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 366 | 358 |  | 0 | 330 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 110 | 0 | 0 | 213 | 0 | 0 | 103 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 80 | 0 | 0 | 295 | 290 | 194 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 88 | 156 | 0 | 0 | 0.5 | 30 | 0 | 11 | 5 | 100 | 134 | 67 | 5 | 5 | 0 | 0 | 12 | 10 | 305 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0.4 | 0 | 0 | 0 |  | 591 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 68 | 288 | 0 | 0 | 180 | 0 | 0 | 0 | 22 | 0 | 171 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 |  | 4353 | 2397.8 | 6750.8 | 3762 | 591 | 1669 | 86 | 356 | 90 | 103 | 88 | 5.8 | 0 | 101.81
8:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 369 | 360 |  | 0 | 330 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 31 | 33 | 0 | 0 | 0 | 40 | 50 | 110 | 0 | 0 | 205 | 0 | 0 | 103 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 80 | 0 | 0 | 295 | 280 | 194 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 94 | 180 | 0 | 0 | 0.5 | 30 | 0 | 11 | 5 | 100 | 133 | 66 | 5 | 5 | 0 | 0 | 12 | 10 | 310 | 0 | 8 | 0 | 3 | 0 | 0 | 7 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 1.5 | 0 | 0 | 0 |  | 591 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 67 | 290 | 0 | 0 | 186 | 0 | 0 | 0 | 22 | 0 | 177 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 |  | 4474.3 | 2398.4 | 6872.7 | 3830 | 591 | 1662 | 131 | 357 | 90 | 103 | 94 | 14.7 | 0 | 0
9:00 | 35 | 0 | 100 | 0 | 330 | 0 | 0 | 374 | 357 |  | 0 | 370 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 17 | 0 | 25 | 31 | 33 | 0 | 2 | 0 | 40 | 50 | 110 | 0 | 0 | 206 | 0 | 0 | 125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 270 | 325 | 218 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 11 | 0 | 0 | 15 | 102 | 176 | 0 | 20 | 0.7 | 29 | 0 | 11 | 23 | 100 | 129 | 65 | 5 | 40 | 0 | 17 | 31 | 10 | 315 | 16 | 8 | 0 | 50 | 0 | 0 | 31 | 0 | 2 | 14.82 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 3.2 | 0 | 0 | 0 |  | 600 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 14 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 67 | 290 | 0 | 0 | 194 | 0 | 0 | 0 | 21 | 0 | 181 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4840.72 | 2413.2 | 7253.92 | 3973 | 600 | 1766 | 218 | 357 | 90 | 125 | 102 | 22.92 | 0 | 0
10:00 | 35 | 0 | 101 | 0 | 330 | 0 | 0 | 345 | 356 |  | 0 | 370 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 31 | 33 | 0 | 8 | 0 | 41 | 50 | 100 | 0 | 0 | 205 | 0 | 0 | 139 |  | 0 | 0 | 0 | 10 | 0 | 5 | 19 | 4 | 80 | 0 | 0 | 270 | 320 | 183 | 16 | 0 | 30 | 52 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 112 | 160 | 0 | 22 | 1.6 | 32 | 0 | 11 | 49 | 100 | 122 | 65 | 5 | 40 | 0 | 17 | 29 | 10 | 285 | 16 | 8 | 0 | 145 | 0 | 0 | 60 | 0 | 30 | 18.39 | 0 | 0 | 0 | 0 | 0 | 70 | 105 | 4.1 | 0 | 0 | 0 |  | 689 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 8 | 0 | 66 | 290 | 0 | 0 | 178 | 0 | 0 | 0 | 21 | 0 | 170 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 5142.09 | 2462.2 | 7604.29 | 3895 | 689 | 1809 | 484 | 356 | 91 | 139 | 112 | 29.29 | 0 | 0
11:00 | 35 | 0 | 101 | 0 | 330 | 0 | 0 | 350 | 354 |  | 0 | 370 | 0 | 0 | 0 | 10 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 31 | 17 | 0 | 8 | 0 | 83 | 50 | 100 | 0 | 0 | 214 | 0 | 0 | 140 |  | 0 | 0 | 0 | 10 | 0 | 24 | 16 | 3 | 80 | 0 | 0 | 280 | 330 | 190 | 16 | 90 | 33 | 52 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 120 | 157 | 0 | 22 | 2.5 | 60 | 0 | 11 | 49 | 100 | 124 | 63 | 5 | 40 | 0 | 17 | 28 | 9 | 310 | 16 | 8 | 0 | 145 | 0 | 0 | 60 | 0 | 30 | 19.5 | 0 | 0 | 0 | 0 | 0 | 70 | 105 | 4.9 | 0 | 0 | 0 |  | 689 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 8 | 0 | 67 | 290 | 0 | 0 | 192 | 0 | 0 | 0 | 21 | 0 | 202 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 |  | 5381.9 | 2565 | 7946.9 | 4093 | 689 | 1835 | 547 | 357 | 133 | 140 | 120 | 32.9 | 0 | 0
12:00 | 35 | 0 | 96 | 0 | 330 | 0 | 0 | 370 | 345 |  | 0 | 420 | 0 | 0 | 0 | 15 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 28 | 25 | 8 | 8 | 0 | 83 | 50 | 100 | 0 | 0 | 222 | 0 | 0 | 147 |  | 0 | 0 | 0 | 10 | 0 | 24 | 16 | 3 | 80 | 0 | 0 | 260 | 350 | 207 | 16 | 90 | 33 | 54 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 126 | 154 | 0 | 22 | 2.5 | 58 | 0 | 11 | 49 | 100 | 150 | 63 | 5 | 40 | 0 | 17 | 29 | 9 | 310 | 16 | 8 | 0 | 175 | 0 | 0 | 60 | 0 | 30 | 19.13 | 0 | 0 | 0 | 0 | 0 | 88 | 105 | 4.9 | 0 | 0 | 0 |  | 689 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 8 | 0 | 68 | 290 | 0 | 0 | 199 | 0 | 0 | 0 | 47 | 0 | 185 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 38 |  | 5577.53 | 2619 | 8196.53 | 4191 | 689 | 1898 | 622 | 358 | 133 | 147 | 126 | 32.53 | 0 | 0
13:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 360 | 352 |  | 0 | 450 | 0 | 0 | 0 | 26 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 24 | 25 | 25 | 8 | 0 | 84 | 50 | 100 | 0 | 0 | 205 | 0 | 0 | 139 |  | 0 | 0 | 0 | 40 | 10 | 24 | 19 | 7 | 100 | 0 | 0 | 325 | 320 | 185 | 45 | 90 | 33 | 54 | 0 | 14 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 126 | 139 | 0 | 22 | 1.8 | 56 | 0 | 53 | 49 | 163 | 144 | 63 | 76 | 40 | 0 | 17 | 30 | 9 | 290 | 16 | 8 | 0 | 175 | 0 | 0 | 100 | 0 | 32 | 18 | 0 | 0 | 0 | 0 | 0 | 88 | 105 | 4.2 | 0 | 0 | 0 |  | 689 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 67 | 290 | 0 | 0 | 205 | 0 | 0 | 0 | 52 | 0 | 205 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 17 |  | 5898 | 2595.6 | 8493.6 | 4162 | 689 | 2163 | 694 | 357 | 134 | 139 | 126 | 29.6 | 0 | 0
14:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 347 | 304 |  | 0 | 400 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 31 | 15 | 25 | 8 | 0 | 84 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 140 |  | 0 | 0 | 0 | 40 | 15 | 24 | 19 | 3 | 100 | 0 | 0 | 325 | 325 | 160 | 45 | 90 | 30 | 53 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 134 | 139 | 0 | 22 | 1.4 | 58 | 0 | 53 | 49 | 100 | 138 | 63 | 76 | 40 | 0 | 17 | 29 | 9 | 280 | 16 | 8 | 0 | 177 | 0 | 0 | 100 | 0 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 88 | 105 | 3.4 | 0 | 0 | 0 |  | 691 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 67 | 290 | 0 | 0 | 201 | 0 | 0 | 0 | 53 | 0 | 192 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 12 |  | 5658.8 | 2557.1 | 8215.9 | 4041 | 691 | 1995 | 700 | 357 | 134 | 140 | 134 | 23.9 | 0 | 0
15:00 | 35 | 0 | 121 | 0 | 330 | 0 | 0 | 365 | 306 |  | 0 | 400 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 35 | 17 | 17 | 10 | 25 | 31 | 25 | 25 | 8 | 0 | 84 | 50 | 100 | 0 | 0 | 211 | 0 | 0 | 140 |  | 0 | 0 | 0 | 60 | 12 | 24 | 19 | 2 | 80 | 0 | 0 | 340 | 335 | 192 | 8 | 90 | 30 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 134 | 142 | 0 | 22 | 1.43 | 58 | 0 | 53 | 47 | 100 | 143 | 63 | 76 | 40 | 0 | 17 | 29 | 9 | 320 | 16 | 8 | 0 | 175 | 0 | 0 | 100 | 0 | 32 | 11 | 0 | 5 | 0 | 0 | 0 | 88 | 105 | 2.37 | 0 | 0 | 0 |  | 691 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 68 | 290 | 0 | 0 | 202 | 0 | 0 | 0 | 52 | 0 | 204 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 15 |  | 5840.8 | 2582.6 | 8423.4 | 4196 | 691 | 2003 | 749 | 358 | 134 | 140 | 134 | 18.4 | 0 | 0
16:00 | 35 | 0 | 128 | 0 | 330 | 0 | 0 | 348 | 305 |  | 0 | 400 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 31 | 33 | 25 | 8 | 0 | 84 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 140 |  | 0 | 0 | 0 | 60 | 12 | 24 | 19 | 2 | 80 | 0 | 0 | 325 | 315 | 179 | 8 | 90 | 30 | 53 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 134 | 143 | 0 | 22 | 0.5 | 58 | 0 | 53 | 49 | 100 | 144 | 65 | 50 | 40 | 0 | 17 | 30 | 7 | 270 | 24 | 8 | 0 | 178 | 0 | 0 | 100 | 0 | 35 | 5 | 0 | 50 | 0 | 0 | 0 | 88 | 105 | 1.06 | 0 | 0 | 0 |  | 691 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 70 | 290 | 0 | 0 | 173 | 0 | 0 | 0 | 53 | 0 | 189 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 9 |  | 5775.56 | 2480.3 | 8255.86 | 4089 | 691 | 1882 | 818 | 360 | 134 | 140 | 134 | 7.86 | 0 | 0
17:00 | 35 | 0 | 120 | 0 | 330 | 0 | 0 | 358 | 304 |  | 0 | 360 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 31 | 33 | 25 | 8 | 0 | 82 | 50 | 100 | 0 | 0 | 208 | 0 | 0 | 104 |  | 0 | 0 | 0 | 60 | 12 | 24 | 19 | 2 | 80 | 0 | 0 | 345 | 290 | 194 | 8 | 91 | 30 | 53 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 124 | 144 | 0 | 22 | 0 | 57 | 0 | 8 | 46 | 100 | 147 | 65 | 10 | 40 | 0 | 17 | 30 | 9 | 280 | 24 | 8 | 0 | 178 | 0 | 0 | 80 | 0 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 174 | 22 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 69 | 290 | 0 | 0 | 191 | 0 | 0 | 0 | 54 | 0 | 174 | 0 | 423 | 0 | 0 | 0 | 0 | 55 | 0 | 0.1 | 4 |  | 5601 | 2546.1 | 8147.1 | 4087 | 691 | 1795 | 845 | 359 | 132 | 114 | 124 | 0.1 | 0 | 0
18:00 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 370 | 357 |  | 0 | 450 | 0 | 0 | 0 | 35 | 340 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 60 | 0 | 7 | 53 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 10 | 0 | 82 | 50 | 100 | 0 | 1 | 205 | 0 | 0 | 140 |  | 0 | 0 | 102 | 90 | 49 | 34 | 19 | 5 | 80 | 0 | 0 | 325 | 320 | 179 | 8 | 80 | 37 | 54 | 0 | 28 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 154 | 146 | 20 | 22 | 0 | 55 | 0 | 47 | 49 | 163 | 139 | 65 | 74 | 40 | 0 | 17 | 33 | 9 | 285 | 24 | 8 | 0 | 203 | 0 | 0 | 151 | 0 | 53 | 0 | 70 | 90 | 0 | 0 | 15 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 43 | 0 | 0 | 0 | 39 | 6 | 40 | 150 | 28 | 16 | 0 | 0 | 0 | 50 | 0 | 60 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 196 | 0 | 0 | 0 | 81 | 2 | 188 | 0 | 423 | 105 | 0 | 60 | 102 | 102 | 0 | 0 | 4 |  | 6747 | 3146 | 9893 | 4113 | 691 | 2170 | 1828 | 358 | 132 | 447 | 154 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 345 | 308 |  | 0 | 450 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 62 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 45 | 0 | 82 | 50 | 100 | 0 | 25 | 204 | 0 | 0 | 140 |  | 0 | 0 | 102 | 100 | 88 | 50 | 19 | 7 | 80 | 0 | 0 | 325 | 320 | 178 | 8 | 80 | 37 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 150 | 147 | 80 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 160 | 65 | 74 | 40 | 0 | 17 | 33 | 9 | 275 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 120 | 0 | 70 | 190 | 0 | 0 | 24 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 43 | 0 | 40 | 150 | 28 | 16 | 0 | 0 | 0 | 50 | 0 | 60 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 179 | 0 | 0 | 0 | 97 | 0 | 186 | 0 | 372 | 105 | 0 | 100 | 68 | 113 | 0 | 0 | 0 |  | 7181 | 3074 | 10255 | 4069 | 691 | 2025 | 2380 | 358 | 132 | 450 | 150 | 0 | 0 | 0
19:30 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 347 | 308 |  | 0 | 450 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 62 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 82 | 50 | 100 | 0 | 8 | 204 | 0 | 0 | 140 |  | 0 | 0 | 102 | 100 | 90 | 50 | 19 | 3 | 80 | 0 | 0 | 325 | 325 | 178 | 8 | 90 | 37 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 150 | 147 | 80 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 172 | 66 | 74 | 40 | 0 | 17 | 33 | 9 | 300 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 100 | 0 | 70 | 200 | 0 | 0 | 8 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 173 | 28 | 0 | 0 | 0 | 0 | 42 | 0 | 34 | 50 | 0 | 0 | 25 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 180 | 0 | 0 | 0 | 95 | 0 | 187 | 0 | 405 | 105 | 0 | 113 | 68 | 113 | 0 | 0 | 0 |  | 7142 | 2999 | 10141 | 4127 | 691 | 2077 | 2238 | 358 | 132 | 368 | 150 | 0 | 0 | 0
20:00 | 35 | 0 | 221 | 0 | 330 | 0 | 0 | 345 | 305 |  | 0 | 450 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 62 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 0 | 8 | 204 | 0 | 0 | 140 |  | 0 | 0 | 102 | 100 | 95 | 50 | 19 | 11 | 80 | 0 | 0 | 325 | 320 | 178 | 8 | 80 | 37 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 150 | 148 | 91 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 248 | 67 | 74 | 40 | 0 | 17 | 34 | 9 | 310 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 112 | 0 | 70 | 200 | 0 | 0 | 8 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 173 | 28 | 0 | 0 | 0 | 0 | 30 | 0 | 34 | 50 | 0 | 0 | 25 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 186 | 0 | 377 | 105 | 0 | 113 | 67 | 113 | 0 | 0 | 0 |  | 7168 | 2959 | 10127 | 4191 | 691 | 2067 | 2224 | 358 | 90 | 356 | 150 | 0 | 0 | 0
21:00 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 345 | 307 |  | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 62 | 0 | 47 | 35 | 18 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 140 |  | 0 | 0 | 85 | 100 | 97 | 41 | 19 | 22 | 80 | 0 | 0 | 325 | 320 | 178 | 8 | 90 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 142 | 148 | 72 | 22 | 0 | 60 | 0 | 47 | 49 | 100 | 303 | 66 | 74 | 40 | 0 | 17 | 34 | 9 | 305 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 56 | 0 | 30 | 88 | 0 | 0 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 167 | 28 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 69 | 290 | 0 | 0 | 183 | 0 | 0 | 0 | 97 | 0 | 186 | 0 | 424 | 53 | 0 | 113 | 34 | 85 | 0 | 0 | 0 |  | 6806 | 2810 | 9616 | 4251 | 691 | 2120 | 1714 | 359 | 90 | 249 | 142 | 0 | 0 | 0
22:00 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 345 | 307 |  | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 47 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 139 |  | 0 | 0 | 68 | 70 | 60 | 21 | 19 | 30 | 80 | 0 | 0 | 325 | 320 | 178 | 8 | 90 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 138 | 153 | 16 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 290 | 67 | 74 | 40 | 0 | 17 | 35 | 9 | 290 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 24 | 0 | 10 | 34 | 0 | 0 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 692 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 152 | 26 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 184 | 0 | 0 | 0 | 98 | 0 | 188 | 0 | 380 | 0 | 0 | 113 | 17 | 50 | 0 | 0 | 0 |  | 6490 | 2610 | 9100 | 4232 | 692 | 2072 | 1303 | 358 | 90 | 215 | 138 | 0 | 0 | 0
23:00 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 346 | 307 |  | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 39 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 139 |  | 0 | 0 | 51 | 70 | 31 | 0 | 19 | 38 | 80 | 0 | 0 | 320 | 325 | 186 | 8 | 90 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 132 | 153 | 8 | 22 | 0 | 60 | 0 | 47 | 49 | 100 | 301 | 66 | 74 | 40 | 0 | 17 | 34 | 9 | 280 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 165 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 67 | 290 | 0 | 0 | 188 | 0 | 0 | 0 | 96 | 0 | 188 | 0 | 415 | 0 | 0 | 35 | 17 | 20 | 0 | 0 | 0 |  | 6071 | 2541 | 8612 | 4268 | 691 | 2098 | 787 | 357 | 89 | 190 | 132 | 0 | 0 | 0
24:00 | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 351 | 307 |  | 0 | 450 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 39 | 50 | 100 | 0 | 0 | 204 | 0 | 0 | 112 |  | 0 | 0 | 17 | 70 | 31 | 0 | 19 | 38 | 80 | 0 | 0 | 325 | 310 | 165 | 8 | 86 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 124 | 154 | 0 | 22 | 0 | 60 | 0 | 47 | 49 | 100 | 300 | 66 | 10 | 40 | 0 | 17 | 35 | 9 | 295 | 24 | 8 | 0 | 95 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 67 | 290 | 0 | 0 | 197 | 0 | 0 | 0 | 95 | 0 | 195 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5799 | 2461 | 8260 | 4254 | 691 | 2066 | 550 | 357 | 89 | 129 | 124 | 0 | 0 | 0
KWH | 775000 | 0 | 3226000 | 0 | 7634727 | 0 | 0 | 8658950 | 7795000 |  | 0 | 9721375 | 0 | 0 | 0 | 327242 | 7454930 | 0 | 0 | 0 | 0 | 0 | 156960 | 0 | 419520 | 0 | 228192 | 760320 | 361770 | 405297 | 232416 | 600000 | 685800 | 743700 | 621100 | 138504 | 0 | 1307062 | 1188000 | 2500000 | 0 | 39486 | 4931602 | 0 | 0 | 3106613 |  | 0 | 0 | 525376 | 965040 | 563520 | 392640 | 442128 | 389280 | 1996972 | 0 | 0 | 7691600 | 7525000 | 7406000 | 451636 | 1528050 | 681840 | 1115040 | 0 | 541856 | 0 | 0 | 0 | 365148 | 154080 | 583400 | 436220 | 2961600 | 3857760 | 348480 | 405216 | 11800 | 1240000 | 0 | 753000 | 951480 | 2792241 | 3593000 | 1552704 | 960960 | 778680 | 0 | 322000 | 615500 | 223920 | 7358700 | 358200 | 198192 | 0 | 3276870 | 0 | 0 | 2224800 | 0 | 649440 | 137025 | 243840 | 862080 | 0 | 0 | 64800 | 1505256 | 1921963 | 27480 | 0 | 0 | 0 |  | 15947636 | 0 | 8056800 | 0 | 68180 | 0 | 0 | 0 | 78240 | 4224 | 237750 | 4183315 | 508200 | 24000 | 0 | 1001000 | 0 | 130656 | 0 | 149676 | 243690 | 18148 | 0 | 105120 | 0 | 341280 | 239508 | 198666 | 0 | 1595782 | 7036900 | 0 | 0 | 4756627 | 0 | 0 | 0 | 1430868 | 23040 | 4611573 | 0 | 9732763 | 386400 | 0 | 574368 | 285696 | 532800 | 0 | 36268 | 139200 |  | 137971379 | 62678374 | 200649753 | 101209716 | 15947636 | 46701287 | 18337452 | 8632682 | 2495062 | 4151745 | 2961600 | 212573 | 0
Fuel Cost | 868000 | 0 | 3451820 | 0 | 5649697.98 | 0 | 0 | 6234444 | 5924200 |  | 0 | 7777100 | 0 | 0 | 0 | 3357502.92 | 9244113.2 | 0 | 0 | 0 | 0 | 0 | 1555473.6 | 0 | 3817632 | 0 | 2135877.12 | 7291468.8 | 3451285.8 | 4036758.12 | 174312 | 450000 | 0 | 0 | 0 | 1326868.32 | 0 | 339836.12 | 308880 | 3825000 | 0 | 379460.46 | 5178182.1 | 0 | 0 | 69867726.37 |  | 0 | 0 | 5511194.24 | 9930261.6 | 5359075.2 | 3675110.4 | 406757.76 | 1082198.4 | 2096820.6 | 0 | 0 | 5691784 | 6321000 | 6813520 | 442603.28 | 2032306.5 | 559108.8 | 1148491.2 | 0 | 774854.08 | 0 | 0 | 0 | 372450.96 | 115560 | 1102626 | 327165 | 20435040 | 3163363.2 | 3314044.8 | 413320.32 | 193520 | 1686400 | 0 | 1024080 | 1189350 | 3462378.84 | 3305560 | 2313528.96 | 1691289.6 | 864334.8 | 0 | 511980 | 720135 | 526212 | 5224677 | 268650 | 150625.92 | 0 | 34308828.9 | 0 | 0 | 21402576 | 0 | 6552849.6 | 1581268.5 | 2272588.8 | 8086310.4 | 0 | 0 | 568296 | 13411830.96 | 18162550.35 | 0 | 0 | 0 | 0 |  | 43058617.2 | 0 | 6284304 | 0 | 657255.2 | 0 | 0 | 0 | 907584 | 55334.4 | 2351347.5 | 3346652 | 787710 | 257760 | 0 | 1881880 | 0 | 1455507.84 | 0 | 1481792.4 | 2527065.3 | 212513.08 | 0 | 1046995.2 | 0 | 375408 | 395188.2 | 150390.162 | 0 | 10165131.34 | 28780921 | 0 | 0 | 4185831.76 | 0 | 0 | 0 | 2275080.12 | 389376 | 4058184.24 | 0 | 7104916.99 | 3655344 | 0 | 5272698.24 | 2545551.36 | 4976352 | 0 | 0 | 0 |  | 357214116.88 | 140642691.532 | 497856808.412 | 92635339.462 | 43058617.2 | 42790207.51 | 176733434.43 | 38946052.34 | 648716.12 | 80834612.85 | 20435040 | 1774788.5 | 0
Yesterday Day Peak | 35 | 0 | 96 | 0 | 330 | 0 | 0 | 370 | 345 |  | 0 | 420 | 0 | 0 | 0 | 15 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 28 | 25 | 8 | 8 | 0 | 83 | 50 | 100 | 0 | 0 | 222 | 0 | 0 | 147 |  | 0 | 0 | 0 | 10 | 0 | 24 | 16 | 3 | 80 | 0 | 0 | 260 | 350 | 207 | 16 | 90 | 33 | 54 | 0 | 5 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 126 | 154 | 0 | 22 | 2.5 | 58 | 0 | 11 | 49 | 100 | 150 | 63 | 5 | 40 | 0 | 17 | 29 | 9 | 310 | 16 | 8 | 0 | 175 | 0 | 0 | 60 | 0 | 30 | 19.13 | 0 | 0 | 0 | 0 | 0 | 88 | 105 | 4.9 | 0 | 0 | 0 |  | 689 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 8 | 0 | 68 | 290 | 0 | 0 | 199 | 0 | 0 | 0 | 47 | 0 | 185 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 38 |  | 8196.53 | DayPeak
Yesterday Evening Peak | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 345 | 308 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 62 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 45 | 0 | 82 | 50 | 100 | 0 | 25 | 204 | 0 | 0 | 140 | 0 | 0 | 0 | 102 | 100 | 88 | 50 | 19 | 7 | 80 | 0 | 0 | 325 | 320 | 178 | 8 | 80 | 37 | 54 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 150 | 147 | 80 | 22 | 0 | 60 | 0 | 50 | 49 | 100 | 160 | 65 | 74 | 40 | 0 | 17 | 33 | 9 | 275 | 24 | 8 | 0 | 300 | 0 | 0 | 200 | 0 | 120 | 0 | 70 | 190 | 0 | 0 | 24 | 88 | 105 | 0 | 0 | 0 | 0 |  | 691 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 43 | 0 | 40 | 150 | 28 | 16 | 0 | 0 | 0 | 50 | 0 | 60 | 50 | 8 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 179 | 0 | 0 | 0 | 97 | 0 | 186 | 0 | 372 | 105 | 0 | 100 | 68 | 113 | 0 | 0 | 0 |  | 10255 | EvPeak
Forecast for Evening | 35 | 0 | 220 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 |  | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 80 | 50 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 96 | 50 | 19 | 15 | 100 | 0 | 0 | 360 | 360 | 225 | 8 | 100 | 37 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 156 | 160 | 95 | 22 | 0 | 60 | 0 | 51 | 50 | 163 | 300 | 66 | 74 | 40 | 0 | 20 | 33 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 88 | 105 | 0 | 300 | 54 | 110 |  | 696 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 45 | 70 | 40 | 180 | 33 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 35 | 22 | 14 | 11 | 0 | 68 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 220 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 50 | 50 | 30 | 335 | 0 |  | 0 | 50 | 50 | 100 | 50 | 70 | 0 | 47 | 17 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 80 | 50 | 100 | 0 | 25 | 215 | 0 | 140 | 0 | 0 | 0 | 0 | 80 | 100 | 50 | 20 | 19 | 10 | 80 | 0 | 0 | 360 | 360 | 225 | 8 | 90 | 33 | 55 | 0 | 30 | 0 | 8 | 0 | 22 | 11 | 33 | 22 | 116 | 170 | 0 | 22 | 1.6 | 60 | 0 | 51 | 50 | 163 | 300 | 66 | 74 | 40 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 0 | 115 | 88 | 51 | 5 | 230 | 54 | 50 |  | 696 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 68 | 290 | 0 | 0 | 210 | 0 | 0 | 0 | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 113 | 0 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 220 | 0 | 330 | 0 | 0 | 351 | 252 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 21 | 33 | 17 | 0 | 0 | 35 | 50 | 100 | 0 | 0 | 184 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 275 | 280 | 175 | 8 | 91 | 30 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 8 | 15 | 98 | 154 | 0 | 20 | 1 | 60 | 0 | 5 | 5 | 100 | 300 | 66 | 10 | 5 | 0 | 0 | 12 | 0 | 310 | 16 | 8 | 0 | 15 | 0 | 0 | 19 | 0 | 9 | 9.9 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 1.8 | 0 | 0 | 0 | 0 | 589 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 67 | 289 | 0 | 0 | 176 | 0 | 0 | 0 | 24 | 0 | 164 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0
199
| Minimum Generation |  | 6666 | 5:00
| Highest Generation |  | 10255 | 19:00
| Day Peak Generation |  | 8196.53 | 12:00
| Evening Peak Generation |  | 10255 | 19:00
| HVDC Max Flow |  | 752 | 1:00
| HVDC EvPeak Flow |  | 691 | 19:00
| Load factor L.F |  | 81.53%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8196.53 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 6783.1 | MW
Evening Peak Generation : |  | 10255 | MW Hour : | 19:00 | Available Max Generation : |  | 14545 | MW
E.P. Demand (at gen end) : |  | 10255 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 10255 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4045 | MW
Total Gen. (MKWH) : |  | 200.6498 | System Load Factor : | 81.53% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 264 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-04
Actual : | 101.76 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : | Total = | 1157.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 135425546.972
: |  | Coal : | 38946052.34 | Oil : | 257568047.28 | Total : | 431939646.592
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3734.3579 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1268.3399 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1136.1145 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1026.4774 |  |  | 0 | 0%
) | 0 | 0:00 | 927.6668 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 748.5903 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 420.5676 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 192.7946 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 577.3405 |  |  | 0 | 0%
Total | 0 |  | 10032.2494 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-1,3 & 5
4) Sirajganj 225 MW Unit-2
5) Raozan #2
6) Ashuganj unit-4 & 5
7) Chandpur CCPP ST
8)Sylhet 150 MW
9) Fenchuganj # 03 & 04
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Bogura-Sherpur 132 kV Ckt-1 was shut down at 12:46 for C/M.
b) Hathazari-Baroierhat 132 kV Ckt-1 was under shut down from 08:07 to 16:08 for A/M.
c) Aminbazar-Hasnabad 230 kV Ckt-2 was under shut down from 09:16 to 20:19 for A/M.
d) Modunaghat-TK 132 kV CKt was under shut down from 08:08 to 15:35 for A/M.
e) Halisahar-Khulshi 132 kV Ckt-1 was under shut down from 09:08 to 14:59 for A/M.
f) Maniknagar 230/132 kV T-2 transformer was under shut down from 08:18 to 17:28 for A/M.
g) Tangail 132/33 kV T-1 transformer was under shut down from 08:12 to 16:17 for A/M.
h) Kishorganj-Mymensingh 132 kV Ckt-1 was under shut down from 09:04 to 16:58 for A/M.
i) Jamalpur-UMPL 132 kV Ckt-1 was under shut down from 08:10 to 15:45 for A/M.
j) Sherpur-UMPL 132 kV Ckt-1 was under shut down from 08:04 to 16:49 for A/M.
k) Dhamrai-Kaliakoir 132 kV Ckt-1 was under shut down from 08:41 to 17:18 for A/M.
l) Dhamrai 132/33 kV T-1 transformer was shut down at 08:35 for A/M.
m) Amnura-Amnura P/P 132 kV Ckt-1 was under shut down from 08:01 to 15:50 for A/M.
n) Chuadanga 132/33 kV T-2 transformer was under shut down from 08:01 to 14:06 for A/M.
o) Khulna (c) 132/33 kV T-1 transformer was under shut down from 08:02 to 16:24 for A/M.
p) Khulna(s) 230/132 kV T-2 transformer was under shut down from 08:45 to 16:43 for A/M.
q) Barishal 230/132 kV T-2 transformer was under shut down from 08:14 to 15:45 for A/M.
r) Chandpur 150 MW GT synchronized at 10:32.
s) Chattak-Sunamganj 132 kV Ckt tripped at 09:15 from both ends showing distance Z2 at B-phase of
Chattak end and distance, directional O/C relay at Sunamganj and was switched on at 09:30.
t) Barishal(n) 132/33 kV T-5 transformer tripped at 12:25 showing PRD and was switched on at 16:51.
u) Shariatpur 132/33 kV T-1 transformer with 33 kV bus-1 were under shut down from 14:24 to 16:01 for |  |  |  |  | About 15 MW power interruption occurred under Shariatpur S/S area
replacement of 33/0.4 kV auxiliary transformer. |  |  |  |  | from 14:24 to 16:01.
v) GPH Ispat s/s 230/33/11 kV T-1 transformer was under shut down from 15:38 to 16:50 for oil leakage
maintenance.
w) Baghabari 100 MW was shut down at 17:22 for gas shortage.
x) Modunaghat-TK Chemical 132 kV Ckt was shut down at 07:24(04/11/2019) for A/M.
y) Hasnabad-Lalbagh 132 kV Ckt was shut down at 06:32(04/11/2019) for A/M.
z) Hasnabad 230/132 kV auto transformer-1 was under shut down from 06:25(04/11/2019) to 10:20 for C/M.
aa) Chattak-Sunamganj 132 kV Ckt was under shut down from 07:19(04/11/2019) to 08:38 for bird nest
removing.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 775000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 3226000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 7634727
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8658950 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 308 | 7795000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9721375
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 327242
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 232416
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7454930 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 228192 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 760320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 55 | 156960 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 361770
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 405297
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 62 | 419520 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1285800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 743700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 621100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 45 | 138504 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3276870
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 120 | 649440 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1505256 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 3067 | 56378369
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 39486
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137025
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 392640
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 132 | 2495062 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4931602
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3106613 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1921963
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 525376
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 965040
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 243840 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 442128
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 389280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 88 | 563520 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27480
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1142 | 18681055
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1996972 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 178 | 7406000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7691600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7525000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 681840 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1115040
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 451636 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 541856 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1528050
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 190 | 862080
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 365148
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 154080 | Machine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 2961600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 583400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 436220
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1535 | 34300522
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 147 | 3857760 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 405216
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 80 | 348480 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 2224800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 24 | 64800 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 473 | 6912856
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1240000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 2792241 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3593000 | GT-1 under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 753000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 951480
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 198192
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1552704 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 960960 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 778680 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 322000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 33 | 615500 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 358200
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7358700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 223920
| Sylhet Area Total |  |  |  | 1949 | 964 | 21698577
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 691 | 15947636 | Sembcorp PP under maint.
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 68180 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 78240
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 4224 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 8056800 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 237750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 23040 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 386400
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 68 | 285696 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1208 | 25087966
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 24000 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 508200
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 150 | 4183315 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1430868
| Barisal Area Total |  |  |  | 462 | 291 | 6146383
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 1001000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 130656
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 243690
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 18148 | Low demand
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 179 | 4756627 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4611573 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 372 | 9732763 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 341280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 239508
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 198666
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 105120
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 60 | 149676 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 100 | 574368
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 139200 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1104 | 22242275
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 68 | 1595782
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 290 | 7036900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 532800
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36268
| Rangpur Area Total |  |  |  | 605 | 471 | 9201750
| Total |  |  |  | 19018 | 10255 | 200649753
| Eastern Grid Total |  |  |  | 13454 | 7181 | 137971379
| Western Grid Total |  |  |  | 5564 | 3074 | 62678374
| National Grid Total |  |  |  | 19018 | 10255 | 200649753
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-03
(a) ENTIRE EASTERN GRID : |  | 6856 | MW | (b) ENTIRE WESTERN GRID : |  | 2932 | MW
i) Dhaka area |  | 3768 | MW | i) Khulna area |  | 1138 | MW
ii) Chittagong area |  | 1047 | MW | ii) Rajshahi area |  | 953 | MW
iii) Comilla area |  | 906 | MW | iii) Barisal area |  | 269 | MW
iv) Mymensingh area |  | 708 | MW | iv) Rangpur area |  | 572 | MW
v) Sylhet area |  | 427 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9788 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 1200 | Srimongal | 34 | 1930 | Bottail | 102 | 1830
Munsiganj | 98 | 2000 | Shahjibazar | 100 | 1930 | G.K Project | 44 | 1830
Sonargaon | 68 | 1930 | Fenchuganj | 38 | 1800 | Faridpur | 142 | 1900
Shyampur | 180 | 2400 | Kulawara | 41 | 1900 | Madaripur | 64 | 2000
Bhulta | 180 | 1900 | Sylhet | 131 | 1800 | Sariatpur | 46 | 1830
Madanganj | 52 | 100 | Chatak | 22 | 1800 | Gopalganj | 76 | 1830
Shitalakhya | 109 | 1200 | Sunamganj | 37 | 1900 | Bagerhat | 70 | 1800
Rahim steel | 23 | 1500 | Biani Bazar | 43 | 1800 | Mongla | 32 | 900
Matuail | 90 | 1200 | Comilla (S) | 154 | 1800 | Satkhira | 76 | 1800
Ghorasal | 74 | 1830 | Comilla(N) | 93 | 1830 | Gallamari | 42 | 1300
Narsingdi | 126 | 1830 | Chandpur | 82 | 1830 | Magura | 41 | 1800
Haripur (SBU) | 88 | 2100 | Feni | 116 | 1830 | Norail | 26 | 1830
Ullon | 68 | 1800 | Chowmuhani | 152 | 1800 | Chuadanga | 70 | 1800
Hasnabad | 175 | 1830 | Ashuganj | 43 | 2300 | Barisal(N) | 34 | 1900
Magbazar | 109 | 1500 | Daudkandi | 106 | 2000 | Barisal (S) | 86 | 1800
Maniknagar | 106 | 1600 | B.Baria | 120 | 1830 | Patuakhali | 85 | 2000
Bangabhaban | 20 | 1400 | Ramganj | 64 | 1830 | Bhandaria | 42 | 1800
Narinda | 90 | 1700 | Madunaghat | 54 | 1830 | Borhan Uddin | 28 | 1830
Dhanmondi | 143 | 1200 | Hathazari | 95 | 1800 | Ishurdi | 53 | 1800
Lalbag | 84 | 1300 | Khulshi | 166 | 1830 | Ruppur Paromanobik | 1 | 100
Madartek | 62 | 1830 | Halishahar | 138 | 1400 | Natore | 99 | 1830
Mirpur | 97 | 1800 | Baraulia | 160 | 1200 | Bogra | 158 | 1900
Kalyanpur | 102 | 2000 | Sikalbaha | 30 | 1500 | Noagaon | 86 | 1900
Gulshan | 136 | 1300 | Dohazari | 94 | 1930 | Rajshahi | 110 | 1830
Uttara | 53 | 1800 | Cox'sbazar | 86 | 2300 | Rajshahi New | 10 | 1830
Uttara New | 38 | 1800 | Chandraghona | 26 | 1830 | C.Nawabganj | 55 | 1830
Kamrangirchar | 70 | 1800 | Kaptai | 4 | 1900 | Amnura | 25 | 1830
Savar | 123 | 1830 | A. Khaer Stl. | 16 | 400 | Pabna | 88 | 1800
Bhasantec | 150 | 1800 | Bakulia | 104 | 1200 | Shahjadpur | 79 | 1800
Agargaon | 53 | 1300 | Julda | 18 | 700 | Serajganj | 75 | 1900
Satmosjid | 91 | 1800 | TK chemical | 17 | 1800 | Niyamatpur | 43 | 1830
Tongi | 130 | 1800 | Modern Steel | 10 | 1400 | Joypurhat | 44 | 1830
Kabirpur | 196 | 1200 | Shahmirpur | 29 | 1800 | Sherpur(Bogura) | 37 | 1800
Basundhara | 103 | 1800 | Khagrachhari | 20 | 1800 | Mohastangor | 12 | 1800
Manikganj | 80 | 1800 | Matarbari | 27 | 1900 | Rangpur | 108 | 1930
Joydevpur | 186 | 1830 | Baroiar Hat | 22 | 1800 | Lalmonirhat | 44 | 1830
New Tongi | 106 | 1800 | Rangamati | 12 | 1800 | Saidpur | 84 | 1830
Korda | 236 | 1800 | Abul Khair 230 | 136 | 1200 | Purbasadipur | 82 | 1830
Dhamrai | 49 | 1900 | BSRM | 53 | 1830 | Thakurgaon | 59 | 1830
Valuka | 86 | 1930 | GPH Ispat | 0.11 | 1700 | Palashbari | 86 | 1800
Tangail | 154 | 1830 | Goalpara | 23 | 1830 | Barapukuria | 42 | 1830
Mymensing | 162 | 1800 | Central s/s | 81 | 1830 | Panchagar | 40 | 1800
Kishorganj | 94 | 1830 | Noapara | 49 | 1800 | Joldhaka | 19 | 2000
Netrokona | 75 | 1900 | Jessore | 107 | 1830 | Kurigram | 40 | 1800
Jamalpur | 97 | 1800 | Benapol | 32 | 1830
Sherpur | 74 | 1900 | Jhenida | 86 | 1830
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-03 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 386 | 3:00 | 377 | 11:00 | Kaliakoir | 367 | 4:00 | 356 | 11:00
Bheramara | 402 | 1:00 | 385 | 18:30 | Bhulta | 376 | 4:00 | 365 | 11:00
Ashuganj(N) | 382 | 7:00 | 370 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 11:00
Ghorasal | 230 | 1:00 | 222 | 10:00 | Hathazari | 218 | 21:00 | 210 | 10:00
Ishurdi | 236 | 4:00 | 225 | 20:00 | Megnaghat | 219 | 5:00 | 214 | 13:00
Ashuganj | 230 | 1:00 | 225 | 10:00 | Fenchuganj | 232 | 9:00 | 227 | 11:00
Serajganj | 233 | 5:00 | 229 | 18:30 | Siddhirganj | 221 | 4:00 | 214 | 11:00
Baghabari | 236 | 6:00 | 232 | 10:00 | Maniknagar | 219 | 6:00 | 210 | 11:00
Barapukuria | 230 | 2:00 | 225 | 18:00 | Old Airport | 217 | 4:00 | 208 | 11:00
Bogra | 231 | 4:00 | 226 | 18:30 | Barisal | 232 | 16:00 | 221 | 10:00
Khulna South | 227 | 4:00 | 208 | 11:00 | AKSML | 213 | 17:00 | 204 | 15:00
Rampura | 220 | 4:00 | 211 | 10:00 | BSRM | 216 | 19:00 | 207 | 15:00
Haripur | 219 | 1:00 | 213 | 11:00 | Bibiyana | 229 | 22:00 | 223 | 14:00
Hasnabad | 220 | 4:00 | 210 | 9:00 | Bhulta | 221 | 3:00 | 214 | 11:00
Aminbazar | 219 | 6:00 | 210 | 11:00 | Ashuganj (S) | 229 | 4:00 | 224 | 11:00
Tongi | 215 | 18:00 | 207 | 10:00 | Kaliakoir | 222 | 4:00 | 214 | 11:00
Comilla (N) | 226 | 3:00 | 217 | 11:00 | GPH | 213 | 19:00 | 203 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 130 | 300 | 125 | 1100 | Halishahar | 132 | 1900 | 125 | 900
Munsiganj | 131 | 1800 | 124 | 1100 | Baraulia | 129 | 1900 | 123 | 1200
Megnaghat | 127 | 1800 | 124 | 700 | Sikalbaha | 132 | 1900 | 127 | 100
Shyampur | 132 | 2000 | 125 | 1200 | Dohazari | 128 | 700 | 123 | 1100
Bhulta | 123 | 200 | 118 | 1200 | Cox'sbazar | 123 | 1800 | 115 | 100
Madanganj | 133 | 1830 | 124 | 900 | Chandraghona | 131 | 1830 | 126 | 1200
Shitalakhya | 133 | 400 | 124 | 1200 | Kaptai | 130 | 1830 | 126 | 1200
Rahim steal | 131 | 400 | 126 | 1100 | A. Khaer Stl. | 130 | 1930 | 124 | 700
Matuail | 130 | 600 | 123 | 1200 | Bakulia | 130 | 1830 | 124 | 900
Ghorasal | 136 | 1800 | 133 | 1500 | Julda | 131 | 1930 | 125 | 1000
Narsinghdi | 132 | 900 | 129 | 1100 | TK Chemical | 131 | 1830 | 126 | 800
Haripur (SBU) | 131 | 100 | 125 | 1200 | Modern Steel | 130 | 1800 | 124 | 1300
Ullon | 132 | 300 | 126 | 1700 | Shahmirpur | 131 | 1830 | 124 | 800
Hasnabad | 133 | 1800 | 127 | 1100 | Khagrachhari | 130 | 1900 | 125 | 1200
Magbazar | 134 | 600 | 125 | 1500 | Matarbari | 125 | 1800 | 119 | 100
Maniknagar | 135 | 1930 | 123 | 1100 | Baroiar Hat | 126 | 2100 | 120 | 1300
Bangabhaban | 135 | 1930 | 123 | 1100 | Rangamati | 130 | 1830 | 126 | 200
Narinda | 135 | 1930 | 123 | 1100 | Goalpara | 137 | 100 | 124 | 1200
Dhanmondi | 132 | 300 | 126 | 1700 | Central s/s | 136 | 500 | 124 | 1200
Lalbag | 132 | 500 | 125 | 1200 | Noapara | 135 | 200 | 121 | 1200
Madartek | 133 | 500 | 126 | 1200 | Jessore | 134 | 400 | 118 | 1200
Mirpur | 134 | 200 | 123 | 1600 | Benapol | 135 | 200 | 121 | 1300
Kalyanpur | 133 | 200 | 126 | 1100 | Jhenida | 134 | 300 | 121 | 1200
Gulshan | 132 | 300 | 125 | 1200 | Bottail | 136 | 300 | 130 | 1200
Uttara | 131 | 100 | 122 | 1200 | G.K Project | 142 | 100 | 137 | 1200
Uttara New | 130 | 300 | 124 | 1200 | Faridpur | 134 | 300 | 126 | 2000
Kamrangirchar | 131 | 400 | 122 | 1200 | Madaripur | 135 | 1830 | 125 | 2100
Savar | 131 | 500 | 121 | 1200 | Sariatpur | 134 | 700 | 126 | 1200
Bhasantec | 132 | 600 | 124 | 1200 | Gopalganj | 139 | 1830 | 126 | 1200
Agargaon | 133 | 400 | 126 | 1200 | Bagerhat | 137 | 1900 | 124 | 1200
Satmosjid | 133 | 500 | 125 | 1200 | Mongla | 133 | 1800 | 120 | 1200
Tongi | 133 | 1800 | 125 | 1500 | Satkhira | 136 | 100 | 123 | 1300
Kabirpur | 134 | 1900 | 119 | 1500 | Gallamari | 138 | 300 | 125 | 1200
Basundhara | 132 | 1900 | 121 | 1200 | Magura | 134 | 500 | 120 | 1200
Manikganj | 137 | 1830 | 126 | 1300 | Norail | 132 | 600 | 118 | 1300
Joydevpur | 136 | 1800 | 130 | 1700 | Chuadanga | 131 | 600 | 116 | 1300
New Tongi | 132 | 1830 | 122 | 1200 | Barisal(N) | 140 | 300 | 131 | 1200
Kodda | 135 | 1900 | 120 | 1500 | Barisal (S) | 138 | 300 | 130 | 1200
Dhamrai | 129 | 2000 | 122 | 1200 | Patuakhali | 135 | 400 | 125 | 1200
Valuka | 129 | 600 | 119 | 1200 | Bhandaria | 135 | 300 | 126 | 1200
Tangail | 130 | 2300 | 124 | 1200 | Ishurdi | 140 | 100 | 134 | 1100
Mymensing | 131 | 2300 | 122 | 1200 | Ruppur Paromanobik | 137 | 600 | 135 | 1000
Kishorganj | 131 | 500 | 126 | 1200 | Natore | 135 | 100 | 130 | 1200
Netrokona | 129 | 2300 | 122 | 1200 | Bogra | 135 | 200 | 132 | 1200
Jamalpur | 139 | 1800 | 124 | 1200 | Noagaon | 133 | 500 | 129 | 1100
Sherpur | 138 | 1900 | 124 | 1100 | Rajshahi | 133 | 1830 | 125 | 1200
Srimongal | 135 | 100 | 131 | 1100 | Rajshahi New | 134 | 1830 | 125 | 1200
Shahjibazar | 134 | 100 | 131 | 1700 | C.Nawabganj | 130 | 1800 | 120 | 1200
Fenchuganj | 133 | 100 | 130 | 1100 | Amnura | 136 | 1800 | 123 | 1100
Khulawara | 132 | 300 | 128 | 1700 | Pabna | 140 | 300 | 134 | 1200
Sylhet | 132 | 200 | 126 | 1200 | Shahjadpur | 140 | 100 | 138 | 1100
Chatak | 131 | 200 | 125 | 1700 | Serajganj | 137 | 400 | 131 | 1100
Sunamganj | 130 | 200 | 123 | 1800 | Niyamatpur | 131 | 400 | 127 | 1830
Biani Bazar | 129 | 100 | 125 | 1700 | Joypurhat | 133 | 400 | 129 | 1300
Comilla(s) | 129 | 600 | 123 | 1000 | Sherpur(Bogura) | 136 | 200 | 132 | 1400
Comilla(n) | 133 | 1830 | 129 | 1100 | Mohastangor | 133 | 200 | 129 | 1200
Chandpur | 135 | 1930 | 121 | 1000 | Rangpur | 128 | 600 | 121 | 1300
Feni | 126 | 2000 | 121 | 1000 | Lalmonirhat | 122 | 500 | 117 | 1200
Chowmuhani | 125 | 700 | 118 | 1500 | Saidpur | 127 | 400 | 120 | 1300
Ashuganj | 136 | 700 | 134 | 1200 | Purbasadipur | 127 | 600 | 115 | 1800
Daudkandi | 128 | 700 | 123 | 1500 | Thakurgaon | 122 | 400 | 112 | 1800
B.Baria | 133 | 500 | 130 | 1200 | Palashbari | 131 | 2000 | 124 | 1200
Ramganj | 126 | 2000 | 120 | 1700 | Barapukuria | 130 | 400 | 126 | 1200
Madanhat | 132 | 1830 | 126 | 1300 | Panchagar | 120 | 500 | 109 | 1800
Hathazari | 131 | 1800 | 126 | 900 | Joldhaka | 128 | 600 | 119 | 1830
Khulshi | 129 | 2000 | 123 | 1100 | Kurigram | 126 | 200 | 119 | 1200
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 504 | 5799 | 2461 | 8260 |  |  |  | QF-LDC-12
0:30 | 422 | 5517 | 2519 | 8036 | Date: | 2019-11-03
1:00 | 340 | 5235 | 2577 | 7812
1:30 | 375 | 5171.5 | 2502.5 | 7674
2:00 | 410 | 5108 | 2428 | 7536
2:30 | 415 | 4931.5 | 2407.5 | 7339 | [5 empty] | Gen. at Eve. Peak | 10255 | 10255 MW (19:00 )
3:00 | 420 | 4755 | 2387 | 7142 | [6 empty] | 19:00
3:30 | 440 | 4671 | 2354.5 | 7025.5 | [5 empty] | Gen. at Day Peak | 8196.53 | 8196.53 MW (12:00 )
4:00 | 460 | 4587 | 2322 | 6909 | [6 empty] | 12:00
4:30 | 455 | 4477.5 | 2310 | 6787.5 | [5 empty] | Highest Generation | 10255
5:00 | 450 | 4368 | 2298 | 6666 | [6 empty] | 19:00
5:30 | 450 | 4350.55 | 2319 | 6669.55
6:00 | 450 | 4333.1 | 2340 | 6673.1
6:30 | 379 | 4343.05 | 2368.9 | 6711.95
7:00 | 308 | 4353 | 2397.8 | 6750.8
7:30 | 374 | 4413.65 | 2398.1 | 6811.75
8:00 | 440 | 4474.3 | 2398.4 | 6872.7
8:30 | 500 | 4657.51 | 2405.8 | 7063.31
9:00 | 560 | 4840.72 | 2413.2 | 7253.92
9:30 | 605 | 4991.405 | 2437.7 | 7429.105
10:00 | 650 | 5142.09 | 2462.2 | 7604.29
10:30 | 635 | 5261.995 | 2513.6 | 7775.595
11:00 | 620 | 5381.9 | 2565 | 7946.9
11:30 | 533 | 5479.715 | 2592 | 8071.715
12:00 | 446 | 5577.53 | 2619 | 8196.53
12:30 | 411 | 5737.765 | 2607.3 | 8345.065
13:00 | 376 | 5898 | 2595.6 | 8493.6
13:30 | 463 | 5778.4 | 2576.35 | 8354.75
14:00 | 550 | 5658.8 | 2557.1 | 8215.9
14:30 | 595 | 5749.8 | 2569.85 | 8319.65
15:00 | 640 | 5840.8 | 2582.6 | 8423.4
15:30 | 630 | 5808.18 | 2531.45 | 8339.63
16:00 | 620 | 5775.56 | 2480.3 | 8255.86
16:30 | 610 | 5688.28 | 2513.2 | 8201.48
17:00 | 600 | 5601 | 2546.1 | 8147.1
17:30 | 475 | 6174 | 2846.05 | 9020.05
18:00 | 350 | 6747 | 3146 | 9893
18:30 | 317 | 6964 | 3110 | 10074
19:00 | 284 | 7181 | 3074 | 10255
19:30 | 290 | 7142 | 2999 | 10141
20:00 | 272 | 7168 | 2959 | 10127 |  |  |  | Executive Engineer
20:30 | 282 | 6987 | 2884.5 | 9871.5 |  |  |  | Network Operation Division
21:00 | 292 | 6806 | 2810 | 9616
21:30 | 329 | 6648 | 2710 | 9358
22:00 | 366 | 6490 | 2610 | 9100 |  |  |  |  | Page 6 of 7
22:30 | 378 | 6280.5 | 2575.5 | 8856
23:00 | 390 | 6071 | 2541 | 8612
23:30 | 447 | 5935 | 2501 | 8436
24:00 | 504 | 5799 | 2461 | 8260
10255 MW (19:00 )
8196.53 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-03 |  | Energy | 200649753
[10 empty] | 2019-11-03 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4254 | 691 | 2066 | 550 | 357 | 89 | 129 | 0 | 124
0:30 | 4126.5 | 721.5 | 2067.5 | 420 | 357.5 | 90 | 132 | 0 | 121 | Date: | 2019-11-03
1:00 | 3999 | 752 | 2069 | 290 | 358 | 91 | 135 | 0 | 118
1:30 | 3992 | 671.5 | 2074.5 | 237.5 | 357.5 | 91.5 | 134.5 | 0 | 115 | [7 empty] | Total Energy | 200.6498 | Total Energy Gen 200.650 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 200.650 MKWHr
2:00 | 3985 | 591 | 2080 | 185 | 357 | 92 | 134 | 0 | 112 | [7 empty] | Energy not Served | 0
2:30 | 3955.5 | 591.5 | 1967.5 | 130.5 | 357 | 92.5 | 133.5 | 0 | 111 | [7 empty] | Energy Requirement | 200.6498
3:00 | 3926 | 592 | 1855 | 76 | 357 | 93 | 133 | 0 | 110
3:30 | 3914 | 591.5 | 1773.5 | 67 | 357.5 | 93.5 | 121.5 | 0 | 107 | [6 empty] | Shortage
4:00 | 3902 | 591 | 1692 | 58 | 358 | 94 | 110 | 0 | 104
4:30 | 3813.5 | 591 | 1668 | 54.5 | 358 | 93 | 107.5 | 0 | 102
5:00 | 3725 | 591 | 1644 | 51 | 358 | 92 | 105 | 0 | 100
5:30 | 3740.5 | 591.5 | 1634.5 | 51 | 358 | 91 | 104 | 0 | 99
6:00 | 3756 | 592 | 1625 | 51 | 358 | 90 | 103 | 0 | 98
6:30 | 3759 | 591.5 | 1647 | 68.5 | 357 | 90 | 103 | 0 | 93 |  |  |  |  | Coal
7:00 | 3762 | 591 | 1669 | 86 | 356 | 90 | 103 | 0 | 88
7:30 | 3796 | 591 | 1665.5 | 108.5 | 356.5 | 90 | 103 | 0 | 91 |  |  |  | Oil |  |  |  | ,
8:00 | 3830 | 591 | 1662 | 131 | 357 | 90 | 103 | 0 | 94
8:30 | 3901.5 | 595.5 | 1714 | 174.5 | 357 | 90 | 114 | 0 | 98
9:00 | 3973 | 600 | 1766 | 218 | 357 | 90 | 125 | 0 | 102
9:30 | 3934 | 644.5 | 1787.5 | 351 | 356.5 | 90.5 | 132 | 0 | 107
10:00 | 3895 | 689 | 1809 | 484 | 356 | 91 | 139 | 0 | 112
10:30 | 3994 | 689 | 1822 | 515.5 | 356.5 | 112 | 139.5 | 0 | 116
11:00 | 4093 | 689 | 1835 | 547 | 357 | 133 | 140 | 0 | 120
11:30 | 4142 | 689 | 1866.5 | 584.5 | 357.5 | 133 | 143.5 | 0 | 123
12:00 | 4191 | 689 | 1898 | 622 | 358 | 133 | 147 | 0 | 126
12:30 | 4176.5 | 689 | 2030.5 | 658 | 357.5 | 133.5 | 143 | 0 | 126
13:00 | 4162 | 689 | 2163 | 694 | 357 | 134 | 139 | 0 | 126
13:30 | 4162 | 689 | 2163 | 694 | 357 | 134 | 139 | 0 | 126
14:00 | 4162 | 689 | 2163 | 694 | 357 | 134 | 139 | 0 | 126
14:30 | 4179 | 690 | 2083 | 721.5 | 357.5 | 134 | 139.5 | 0 | 130
15:00 | 4196 | 691 | 2003 | 749 | 358 | 134 | 140 | 0 | 134
15:30 | 4142.5 | 691 | 1942.5 | 783.5 | 359 | 134 | 140 | 0 | 134
16:00 | 4089 | 691 | 1882 | 818 | 360 | 134 | 140 | 0 | 134
16:30 | 4088 | 691 | 1838.5 | 831.5 | 359.5 | 133 | 127 | 0 | 129
17:00 | 4087 | 691 | 1795 | 845 | 359 | 132 | 114 | 0 | 124
17:30 | 4100 | 691 | 1982.5 | 1336.5 | 358.5 | 132 | 280.5 | 0 | 139
18:00 | 4113 | 691 | 2170 | 1828 | 358 | 132 | 447 | 0 | 154
18:30 | 4091 | 691 | 2097.5 | 2104 | 358 | 132 | 448.5 | 0 | 152
19:00 | 4069 | 691 | 2025 | 2380 | 358 | 132 | 450 | 0 | 150
19:30 | 4127 | 691 | 2077 | 2238 | 358 | 132 | 368 | 0 | 150
20:00 | 4191 | 691 | 2067 | 2224 | 358 | 90 | 356 | 0 | 150
20:30 | 4221 | 691 | 2093.5 | 1969 | 358.5 | 90 | 302.5 | 0 | 146
21:00 | 4251 | 691 | 2120 | 1714 | 359 | 90 | 249 | 0 | 142
21:30 | 4241.5 | 691.5 | 2096 | 1508.5 | 358.5 | 90 | 232 | 0 | 140
22:00 | 4232 | 692 | 2072 | 1303 | 358 | 90 | 215 | 0 | 138
22:30 | 4250 | 691.5 | 2085 | 1045 | 357.5 | 89.5 | 202.5 | 0 | 135
23:00 | 4268 | 691 | 2098 | 787 | 357 | 89 | 190 | 0 | 132
23:30 | 4261 | 691 | 2082 | 668.5 | 357 | 89 | 159.5 | 0 | 128 | Max Temp. in Dhaka |  | 31° C
24:00 | 4254 | 691 | 2066 | 550 | 357 | 89 | 129 | 0 | 124
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 200.650 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 200.650 MKWHr
Note on W13: Author:

## Generation
2019-11-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 41 | 42 | 43 | 44 | 42 | 40 | 40 | 40 | 40 | 41 | 83 | 83 | 84 | 84 | 84 | 84 | 82 | 82 |  | 82 | 82 | 40 | 40 | 40 | 39 | 39 | 1307062
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1188000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 25 | 8 | 8 | 0 |  |  |  | 39486
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0.1 | 4.1 | 10.3 | 14.82 | 18.39 | 19.5 | 19.13 | 18 | 15 | 11 | 5 | 0 | [9 empty] | 137025
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 204 | 209 | 207 | 208 | 213 | 205 | 206 | 205 | 214 | 222 | 205 | 204 | 211 | 204 | 208 | 205 |  | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 4931602
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 135 | 134 | 133 | 110 | 105 | 103 | 103 | 103 | 125 | 139 | 140 | 147 | 139 | 140 | 140 | 140 | 104 | 140 |  | 140 | 140 | 140 | 140 | 139 | 139 | 112 | 3106613
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 102 |  | 102 | 102 | 102 | 85 | 68 | 51 | 17 | 525376
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 68 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1921963
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 340 | 339 | 339 | 336 | 330 | 336 | 300 | 300 | 300 | 300 | 340 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7454930
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | 15 | 0 |  |  |  |  | 3 | 50 | 145 | 145 | 175 | 175 | 177 | 175 | 178 | 178 | 203 |  | 300 | 300 | 300 | 300 | 300 | 145 | 95 | 3276870
19 | Ashuganj 195MW PP (APSCL-United) | 35 | 35 | 35 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 45 | 45 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 451636
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 775000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 101 | 96 | 100 | 100 | 121 | 128 | 120 | 220 |  | 220 | 220 | 221 | 220 | 220 | 220 | 220 | 3226000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 280 | 280 | 300 | 300 | 330 | 330 | 330 | 330 | 300 | 300 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7634727
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1996972
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 10 | 10 | 10 | 10 | 10 | 30 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 681840
33 | Ashuganj 225 MW CCPP | 168 | 170 | 166 | 175 | 164 | 177 | 194 | 194 | 218 | 183 | 190 | 207 | 185 | 160 | 192 | 179 | 194 | 179 |  | 178 | 178 | 178 | 178 | 178 | 186 | 165 | 7406000
34 | Ashuganj 450 MW CCPP(South) | 270 | 275 | 270 | 285 | 270 | 290 | 290 | 280 | 325 | 320 | 330 | 350 | 320 | 325 | 335 | 315 | 290 | 320 |  | 320 | 325 | 320 | 320 | 320 | 325 | 310 | 7525000
| Ashuganj 450 MW CCPP(North) | 270 | 275 | 270 | 280 | 270 | 290 | 295 | 295 | 270 | 270 | 280 | 260 | 325 | 325 | 340 | 325 | 345 | 325 |  | 325 | 325 | 325 | 325 | 325 | 320 | 325 | 7691600
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 10 | 10 | 10 | 10 | 10 | 52 | 52 | 54 | 54 | 53 | 51 | 53 | 53 | 54 |  | 54 | 54 | 54 | 55 | 55 | 55 | 55 | 1115040
36 | Chandpur 150 MW CCPP | 87 | 87 | 87 | 87 | 0 | [5 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 80 |  | 80 | 90 | 80 | 90 | 90 | 90 | 86 | 1528050
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 347 | 350 | 355 | 353 | 352 | 371 | 366 | 369 | 374 | 345 | 350 | 370 | 360 | 347 | 365 | 348 | 358 | 370 |  | 345 | 347 | 345 | 345 | 345 | 346 | 351 | 8658950
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 370 | 330 | 330 | 370 | 370 | 370 | 420 | 450 | 400 | 400 | 400 | 360 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9721375
41 | Haripur 360MW CCPP(HPL) | 322 | 322 | 322 | 322 | 322 | 322 | 358 | 360 | 357 | 356 | 354 | 345 | 352 | 304 | 306 | 305 | 304 | 357 |  | 308 | 308 | 305 | 307 | 307 | 307 | 307 | 7795000
42 | RPCL 210MW CCPP | 182 | 183 | 195 | 197 | 197 | 197 | 156 | 180 | 176 | 160 | 157 | 154 | 139 | 139 | 142 | 143 | 144 | 146 |  | 147 | 147 | 148 | 148 | 153 | 153 | 154 | 3857760
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 29 | 32 | 60 | 58 | 56 | 58 | 58 | 58 | 57 | 55 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1240000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 128 | 128 | 128 | 127 | 127 | 129 | 134 | 133 | 129 | 122 | 124 | 150 | 144 | 138 | 143 | 144 | 147 | 139 |  | 160 | 172 | 248 | 303 | 290 | 301 | 300 | 3593000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 68 | 67 | 67 | 66 | 65 | 65 | 63 | 63 | 63 | 63 | 63 | 65 | 65 | 65 |  | 65 | 66 | 67 | 66 | 67 | 66 | 66 | 1552704
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 76 | 76 | 76 | 50 | 10 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 10 | 960960
49 | Shahjibazar 50MW PP (EPL) | 40 | 40 | 40 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 778680
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 18 | 18 | 0 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 322000
52 | Sylhet 50MW PP (EPL) | 33 | 33 | 10 | 10 | 10 | 10 | 12 | 12 | 31 | 29 | 28 | 29 | 30 | 29 | 29 | 30 | 30 | 33 |  | 33 | 33 | 34 | 34 | 35 | 34 | 35 | 615500
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 223920
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 198192
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 53 | 53 | 53 | 53 | 8 | 47 |  | 50 | 50 | 50 | 47 | 50 | 47 | 47 | 753000
56 | Shahjahanulla 25 MW PP | 24 | 4 | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 358200
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 290 | 300 | 300 | 310 | 305 | 310 | 315 | 285 | 310 | 310 | 290 | 280 | 320 | 270 | 280 | 285 |  | 275 | 300 | 310 | 305 | 290 | 280 | 295 | 7358700
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 0 |  |  |  | 405297
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442128
61 | Narshingdi 22 MW PP (Doreen) | 22 | [11 empty] | 22 | 0 | 10 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 232416
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | [5 empty] | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 405216
63 | Impoprt (Tripura) | 118 | 112 | 110 | 104 | 100 | 98 | 88 | 94 | 102 | 112 | 120 | 126 | 126 | 134 | 134 | 134 | 124 | 154 |  | 150 | 150 | 150 | 142 | 138 | 132 | 124 | 2961600
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 10 | 3 | 4 | 3 | 3 | 7 | 3 | 2 | 2 | 2 | 5 |  | 7 | 3 | 11 | 22 | 30 | 38 | 38 | 389280
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | [5 empty] | 11 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 365148
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 154080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | [7 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 583400
68 | Cumilla 25 MW PP (Summit) | 22 | 22 | 22 | 22 | 22 | 19 | 10 | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 18 | 21 | 21 | 21 | 21 | 21 | 436220
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 28 | 24 | 31 | 31 | 31 | 31 | 19 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 685800
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 25 | 25 | 15 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 743700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 16 | 33 | 33 | 33 |  |  |  |  | 8 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 621100
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 45 | 16 | [5 empty] | 138504
79 | Kodda 150MW PP | [17 empty] | 50 |  | 55 | 50 | 50 | 16 |  |  |  | 156960
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 20 |  | 80 | 80 | 91 | 72 | 16 | 8 | 0 | 348480
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 70 | 70 | 70 | 70 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 52 | 52 | 1505256
| Kaptai 7 MW Solar PP | [6 empty] | 0.4 | 1.5 | 3.2 | 4.1 | 4.9 | 4.9 | 4.2 | 3.4 | 2.37 | 1.06 | [10 empty] | 27480
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 0 | [6 empty] | 0 | 10 | 10 | 10 | 40 | 40 | 60 | 60 | 60 | 90 |  | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 965040
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 5 | 5 | 5 | 5 | 5 | 23 | 49 | 49 | 49 | 49 | 49 | 47 | 49 | 46 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 951480
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14 | 35 | 35 | 10 | 10 | 28 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 541856
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [9 empty] | 5 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 34 |  | 50 | 50 | 50 | 41 | 21 |  |  | 392640
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 10 | 15 | 12 | 12 | 12 | 49 |  | 88 | 90 | 95 | 97 | 60 | 31 | 31 | 563520
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 7 |  | 47 | 47 | 47 | 47 | 47 |  |  | 228192
98 | Bosila 108MW PP(CLC) | [14 empty] | 26 | 50 | 50 | 60 |  | 62 | 62 | 62 | 62 | 61 |  |  | 419520
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 10 | 15 | 26 | 30 | 30 | 30 | 30 | 35 |  | 55 | 55 | 30 | 0 |  |  |  | 327242
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 18 |  |  |  | 361770
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 100 | 100 | 100 | 100 | 163 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2792241
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.5 | 0.5 | 0.7 | 1.6 | 2.5 | 2.5 | 1.8 | 1.4 | 1.43 | 0.5 | [10 empty] | 11800
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 53 |  | 53 | 35 | 35 | 35 | 35 | 35 | 35 | 760320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 50 | 50 | 7 | 7 |  |  |  | 7 | 31 | 60 | 60 | 60 | 100 | 100 | 100 | 100 | 80 | 151 |  | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 2224800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 2 | 30 | 30 | 30 | 32 | 32 | 32 | 35 | 32 | 53 |  | 120 | 100 | 112 | 56 | 24 | 0 |  | 649440
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 70 |  | 70 | 70 | 70 | 30 | 10 | 0 |  | 243840
116 | Chandpur 200MW (Desh energy) | [14 empty] | 5 | 50 | 50 | 90 |  | 190 | 200 | 200 | 88 | 34 | 17 | 0 | 862080
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 15 |  | 24 | 8 | 8 | 0 |  |  |  | 64800
Anwara 300 MW PP (United)
120 | Eastern Zone Total | 5235 | 5108 | 4755 | 4587 | 4368 | 4333.1 | 4353 | 4474.3 | 4840.72 | 5142.09 | 5381.9 | 5577.53 | 5898 | 5658.8 | 5840.8 | 5775.56 | 5601 | 6747 |  | 7181 | 7142 | 7168 | 6806 | 6490 | 6071 | 5799 | 137971379
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 43 |  | 16 | 0 | [5 empty] | 68180
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 10 | 39 |  | 43 | 0 | [5 empty] | 78240
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 105 |  | 105 | 105 | 105 | 53 | 0 |  |  | 386400
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 0 | [5 empty] | 24000
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 96 | 95 | 21 | 21 | 21 | 22 | 22 | 21 | 21 | 21 | 47 | 52 | 53 | 52 | 53 | 54 | 81 |  | 97 | 95 | 97 | 97 | 98 | 96 | 95 | 1430868
| Bhola 225 MW CCPP | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 173 | 173 | 174 | 174 | 174 | 150 |  | 150 | 173 | 173 | 167 | 152 | 165 | 173 | 4183315
140 | Bhola 33 MW PP (Venture) | 21 | 21 | 22 | 20 | 20 | 20 | 19 | 18 | 14 | 18 | 20 | 20 | 21 | 21 | 20 | 20 | 22 | 28 |  | 28 | 28 | 28 | 28 | 26 | 25 | 25 | 508200
141 | Noapara 100 MW PP (Bangla Trac) | [17 empty] | 2 |  | 0 | [6 empty] | 23040
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 237750
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 6 |  | 0 | [6 empty] | 4224
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 102 |  | 68 | 68 | 67 | 34 | 17 | 17 | 0 | 285696
146 | Bheramara HVDC | 752 | 591 | 592 | 591 | 591 | 592 | 591 | 591 | 600 | 689 | 689 | 689 | 689 | 691 | 691 | 691 | 691 | 691 |  | 691 | 691 | 691 | 691 | 692 | 691 | 691 | 15947636
147 | Bheramara 360 MW CCPP | 355 | 360 | 355 | 370 | 350 | 370 | 380 | 370 | 365 | 345 | 360 | 400 | 345 | 340 | 340 | 320 | 305 | 245 |  | 245 | 245 | 245 | 245 | 245 | 245 | 240 | 8056800
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 68 | 67 | 67 | 68 | 68 | 68 | 68 | 67 | 67 | 66 | 67 | 68 | 67 | 67 | 68 | 70 | 69 | 68 |  | 68 | 68 | 68 | 69 | 68 | 67 | 67 | 1595782
152 | Barapukuria 275 MW TPP Unit-3 | 290 | 290 | 290 | 290 | 290 | 290 | 288 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7036900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 40 | 0 | [8 empty] | 1001000
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 42 | 30 | 8 | 8 | 0 |  | 130656
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 174 | 178 | 177 | 173 | 172 | 182 | 180 | 186 | 194 | 178 | 192 | 199 | 205 | 201 | 202 | 173 | 191 | 196 |  | 179 | 180 | 180 | 183 | 184 | 188 | 197 | 4756627
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 161 | 164 | 165 | 164 | 163 | 173 | 171 | 177 | 181 | 170 | 202 | 185 | 205 | 192 | 204 | 189 | 174 | 188 |  | 186 | 187 | 186 | 186 | 188 | 188 | 195 | 4611573
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 382 | 383 | 382 | 383 | 381 | 382 | 433 | 430 | 432 | 421 | 425 | 401 | 422 | 409 | 419 | 396 | 423 | 423 |  | 372 | 405 | 377 | 424 | 380 | 415 | 432 | 9732763
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 20 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 341280
163 | Bogura 20 MW PP (Energyprima) | 14 | 14 | 0 | 0 | 0 | 0 |  |  | 0 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 239508
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 198666
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 12 | 12 | 12 | 243690
166 | Katakhali 50 MW PP (Northern) | [16 empty] | 0 | 8 |  | 8 | 0 | [5 empty] | 18148
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 0 | 52 |  | 52 | 25 | 25 | 0 |  |  |  | 105120
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 0 | 60 |  | 60 | 34 | 34 | 0 |  |  |  | 149676
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 0 | 60 |  | 100 | 113 | 113 | 113 | 113 | 35 |  | 574368
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 34 | 38 | 17 | 12 | 15 | 9 | 4 | 4 | [8 empty] | 139200
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 55 | 102 |  | 113 | 113 | 113 | 85 | 50 | 20 | 0 | 532800
177 | Sympa Solar Power 8MW | [6 empty] | 0.8 | 2.4 | 4.2 | 5.2 | 6 | 6 | 5.6 | 4.1 | 3.6 | 1.3 | 0.1 | 0 | [8 empty] | 36268
178
178