## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-08 | Friday
|  | Date (day): | 2019-11-08 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12112.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14913 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-07 | 2019-11-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1 & 2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 131 | 100 | 130 | 130
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 350 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 309 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 354 | 358 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 360 | 225 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 98 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 309 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 47 | 48 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 84 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 53 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 30 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 175 | 195 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 63 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2132 | 2529 | 3693 | 4367 | 706 | 678
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 105 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 11 | 20 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 77 | 77 | 87 | 87 | 143 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 104 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 61 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 8 | 30 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 96 | 95 | 50 | 98 |  | 10 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.82 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 16 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 51 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 806.82 | 906 | 1255 | 1448 | 393 | 333
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 90 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 143 | 145 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 330 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 300 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 33 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 51 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 16 | 16 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 35 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 88 | 80 | 90 |  | 57
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 40 | 65 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 6 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 148 | 100 | 145
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 22 | 22
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1183 | 1456 | 1677 | 2163 | 485 | 81
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 149 | 155 | 170 | 180 | 22 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 4 | 92 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 21 | 200 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 7 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 176.4 | 476 | 408.6 | 612 | 22 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 59 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 0 | 0 |  |  | Water problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 301 | 287 | 300 | 300
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 50 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 27 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 66 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 77 | 77 | 77 |  | 9 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 5 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 6 | 33 | 32 | 36 |  | 14 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 285 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 138 | 0 | 140 | 140 |  | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1039 | 1086 | 1379 | 1383 | 0 | 575
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 929 | 929 | 682 | 941
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 305 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 18 | 90 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1257 | 1433 | 1177 | 2167 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 27 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 173 | 154 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 88 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 205 | 285 | 378 | 448 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 50 | 60 | 60 | 100 |  | Machine problem
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 48
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 184 | 193 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 147 | 220 | 220 | 220 |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 189 | 197 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 408 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 11 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1028 | 1099 | 1734 | 1888 | 320 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 290 | 290 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 104 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 295.5 | 409 | 411 | 437 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 8122.72 | 9679 | 12112.6 | 14913 | 1926 | 1831
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7750.1105 | 9235 | 11556.9647 | 14228.9033
A. |  | 2019-11-07 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 9679 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6459 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9679 | MW
3 | Day peak Generation : |  |  | 8122.72 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9235 | MW
4 | Evening peak Generation : |  |  | 9679 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 191.4952 | MKWHr | By Solar | 0.15293 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 138.7914 | MKWHr |  | By Oil: | 20.3445 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 7.0133 | MKWHr |  | By Hydro: | 1.7482 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1926 | MW | Dhaka | 3599 | 3599 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1831 | MW | Chittagong | 1009 | 1009 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3757 | MW | Khulna | 1036 | 1036 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1155.073 | MMCFD |  |  | Rajshahi | 841 | 841 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129114723.886 | ii) Oil : | Taka | 192262236.47 | Comilla | 858 | 858 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 28684397 | Total | Taka | 350061357.356 | Mymensingh | 695 | 695 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.099 | MKWHr. | Sylhet | 384 | 384 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 330 | MW (E to W) at | 19:00 | hrs | Barisal | 265 | 265 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 280 | MW at | 19:30 | hrs | Rangpur | 548 | 548 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.7° C |  |  | Total | 9235 | 9235 |  | 0
B. |  | 2019-11-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 30.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14913 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7000 | MW
4 | Reserve(Generation end) |  |  |  | 5913 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 178.0615 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6253.9 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.512 | MKWHr. | ii) HVDC Flow at Peak Time |  | 929 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9328 | MKWHr. | iii) Maximum HVDC Flow : |  | 931 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.29 | 101.44 |  | (b) Today: | 101.29 |  | (c) Rule Curve: |  | 108.3
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 300 |  | 0 | 360 | 0 | 0 | 0 | 0 | 300 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 40 | 115 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 70 | 60 | 0 | 19 | 39 | 80 | 0 | 0 | 330 | 270 | 144 | 8 | 88 | 37 | 55 | 0 | 7 | 0 | 0 | 0 | 19 | 6 | 0 | 21 | 120 | 156 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 290 | 67 | 10 | 5 | 0 | 0 | 8 | 0 | 260 | 0 | 11 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 10 | 0 | 0 | 138 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 820 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 24 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 189 | 0 | 166 | 0 | 63 | 0 | 192 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4705 | 2635 | 7340 | 4077 | 820 | 1591 | 362 | 290 | 80 | 0 | 120 | 0 | 0 | 101.49
2:00 | 35 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 300 |  | 0 | 360 | 0 | 0 | 0 | 0 | 300 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 35 | 40 | 115 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 70 | 64 | 0 | 19 | 40 | 80 | 0 | 0 | 330 | 265 | 145 | 8 | 87 | 37 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 108 | 156 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 265 | 40 | 10 | 5 | 0 | 0 | 8 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 139 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 724 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 184 | 0 | 168 | 0 | 23 | 0 | 185 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4524 | 2442 | 6966 | 3987 | 724 | 1485 | 297 | 290 | 75 | 0 | 108 | 0 | 0 | 101.48
3:00 | 35 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 300 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 35 | 40 | 115 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 70 | 44 | 0 | 19 | 40 | 80 | 0 | 0 | 330 | 270 | 145 | 8 | 88 | 37 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 100 | 156 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 265 | 40 | 10 | 5 | 0 | 0 | 8 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 137 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 723 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 291 | 0 | 0 | 170 | 0 | 170 | 0 | 12 | 0 | 172 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4392 | 2410 | 6802 | 3970 | 723 | 1383 | 260 | 291 | 75 | 0 | 100 | 0 | 0 | 101.47
4:00 | 35 | 0 | 125 | 0 | 250 | 0 | 0 | 0 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 300 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 35 | 40 | 115 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 50 | 44 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 270 | 145 | 8 | 89 | 10 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 98 | 157 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 263 | 40 | 10 | 5 | 0 | 0 | 8 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 140 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 723 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 290 | 0 | 0 | 161 | 0 | 169 | 0 | 11 | 0 | 166 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4240 | 2391 | 6631 | 3829 | 723 | 1388 | 228 | 290 | 75 | 0 | 98 | 0 | 0 | 101.46
5:00 | 35 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 225 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 40 | 115 | 0 | 0 | 0 | 0 | 110 | 0 |  | 0 | 0 | 0 | 50 | 44 | 0 | 19 | 40 | 80 | 0 | 0 | 265 | 275 | 147 | 8 | 87 | 10 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 90 | 158 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 272 | 40 | 10 | 5 | 0 | 0 | 8 | 0 | 260 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 102 | 0 | 0 | 0 | 0 |  | 723 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 21 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 290 | 0 | 0 | 164 | 0 | 172 | 0 | 11 | 0 | 171 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4101 | 2358 | 6459 | 3737 | 723 | 1324 | 215 | 290 | 80 | 0 | 90 | 0 | 0 | 101.45
6:00 | 35 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 225 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 40 | 115 | 0 | 0 | 0 | 0 | 112 | 0 |  | 0 | 0 | 0 | 50 | 44 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 270 | 147 | 8 | 87 | 10 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 90 | 157 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 266 | 40 | 10 | 5 | 0 | 0 | 8 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0.06 | 0 | 0 | 0 | 138 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 723 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 289 | 0 | 0 | 170 | 0 | 172 | 0 | 11 | 0 | 175 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4132.06 | 2360 | 6492.06 | 3725 | 723 | 1372 | 213 | 289 | 80 | 0 | 90 | 0.06 | 0 | 101.44
7:00 | 35 | 0 | 131 | 0 | 250 | 0 | 0 | 0 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 225 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 37 | 40 | 115 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 44 | 0 | 19 | 37 | 80 | 0 | 0 | 280 | 290 | 148 | 8 | 0 | 10 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 18 | 90 | 156 | 0 | 0 | 0.2 | 60 | 0 | 5 | 5 | 100 | 280 | 63 | 10 | 5 | 0 | 0 | 6 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.17 | 0 | 0 | 0 | 140 | 0 | 5 | 105 | 0.646 | 0 | 0 | 0 |  | 723 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 290 | 0 | 0 | 171 | 0 | 172 | 0 | 12 | 0 | 179 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | 4179.016 | 2507.5 | 6686.516 | 3778 | 723 | 1463 | 263 | 290 | 77 | 0 | 90 | 2.516 | 0 | 0
8:00 | 35 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 225 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 37 | 40 | 115 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 44 | 0 | 19 | 11 | 80 | 0 | 0 | 295 | 305 | 146 | 8 | 0 | 10 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 15 | 96 | 156 | 0 | 0 | 0.8 | 60 | 0 | 5 | 5 | 100 | 312 | 66 | 10 | 5 | 0 | 0 | 6 | 0 | 310 | 0 | 11 | 0 | 16 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 0 | 139 | 0 | 88 | 105 | 1.5 | 0 | 0 | 0 |  | 723 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 290 | 0 | 0 | 175 | 0 | 167 | 0 | 12 | 0 | 175 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 |  | 4345.3 | 2519.2 | 6864.5 | 3846 | 723 | 1457 | 363 | 290 | 77 | 0 | 96 | 12.5 | 0 | 101.58
9:00 | 35 | 0 | 136 | 0 | 300 | 0 | 0 | 0 | 344 |  | 0 | 320 | 0 | 0 | 0 | 0 | 268 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 37 | 40 | 115 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 84 | 0 | 19 | 4 | 80 | 0 | 0 | 260 | 270 | 147 | 8 | 0 | 33 | 40 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 15 | 104 | 154 | 0 | 0 | 1.7 | 60 | 0 | 5 | 5 | 100 | 295 | 66 | 10 | 5 | 0 | 0 | 6 | 0 | 300 | 0 | 11 | 0 | 49 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 0 | 140 | 0 | 88 | 105 | 3.25 | 0 | 0 | 0 |  | 723 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 17 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 184 | 0 | 173 | 0 | 11 | 0 | 174 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 |  | 4626.95 | 2491.5 | 7118.45 | 3893 | 723 | 1553 | 462 | 290 | 77 | 0 | 104 | 16.45 | 0 | 101.58
10:00 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 314 |  | 0 | 350 | 0 | 0 | 0 | 15 | 261 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 96 | 5 | 19 | 4 | 80 | 0 | 0 | 260 | 270 | 144 | 8 | 0 | 33 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 15 | 110 | 152 | 0 | 0 | 2.1 | 58 | 0 | 5 | 5 | 100 | 296 | 65 | 10 | 5 | 0 | 0 | 6 | 0 | 280 | 0 | 8 | 0 | 134 | 0 | 0 | 7 | 0 | 36 | 10 | 40 | 0 | 0 | 140 | 0 | 88 | 105 | 4.11 | 0 | 6 | 0 |  | 930 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 195 | 0 | 173 | 0 | 11 | 0 | 171 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 4695.21 | 2702.8 | 7398.01 | 3792 | 930 | 1547 | 668 | 290 | 40 | 0 | 110 | 21.01 | 0 | 101.57
11:00 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 314 |  | 0 | 350 | 0 | 0 | 0 | 15 | 268 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 30 | 33 | 17 | 0 | 0 | 38 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 95 | 24 | 19 | 2 | 80 | 0 | 0 | 310 | 315 | 144 | 8 | 0 | 33 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 32 | 15 | 116 | 149 | 0 | 0 | 2.4 | 60 | 0 | 5 | 5 | 100 | 302 | 63 | 10 | 5 | 0 | 0 | 6 | 0 | 305 | 0 | 11 | 0 | 175 | 0 | 0 | 7 | 0 | 100 | 19 | 90 | 12 | 0 | 141 | 0 | 88 | 105 | 4.73 | 0 | 17 | 0 |  | 929 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 175 | 0 | 168 | 0 | 13 | 0 | 170 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 |  | 5103.13 | 2713.5 | 7816.63 | 3911 | 929 | 1579 | 882 | 290 | 78 | 0 | 116 | 31.63 | 0 | 101.57
12:00 | 0 | 0 | 131 | 0 | 330 | 0 | 0 | 0 | 354 |  | 0 | 350 | 0 | 0 | 0 | 30 | 300 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 27 | 33 | 25 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 96 | 26 | 19 | 4 | 80 | 0 | 0 | 320 | 325 | 143 | 8 | 0 | 33 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 15 | 122 | 149 | 4 | 0 | 2.4 | 60 | 0 | 5 | 5 | 130 | 301 | 63 | 10 | 5 | 0 | 0 | 6 | 0 | 305 | 0 | 11 | 0 | 175 | 0 | 0 | 21 | 0 | 100 | 20 | 100 | 40 | 0 | 138 | 0 | 88 | 105 | 2.82 | 0 | 17 | 0 |  | 929 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 184 | 0 | 168 | 0 | 12 | 0 | 189 | 0 | 419 | 0 | 0 | 0 | 18 | 0 | 0 | 5.5 | 0 |  | 5337.22 | 2785.5 | 8122.72 | 4009 | 929 | 1691 | 974 | 290 | 77 | 0 | 122 | 30.72 | 0 | 101.56
13:00 | 0 | 0 | 130 | 0 | 330 | 0 | 0 | 0 | 351 |  | 0 | 350 | 0 | 0 | 0 | 30 | 300 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 27 | 33 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 95 | 25 | 19 | 2 | 80 | 25 | 0 | 320 | 315 | 122 | 8 | 50 | 33 | 47 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 21 | 124 | 149 | 16 | 0 | 2.2 | 58 | 0 | 5 | 5 | 130 | 286 | 60 | 10 | 5 | 0 | 17 | 32 | 10 | 300 | 0 | 11 | 0 | 177 | 0 | 0 | 62 | 0 | 100 | 0 | 100 | 70 | 0 | 140 | 0 | 88 | 105 | 4.31 | 0 | 17 | 0 |  | 930 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 178 | 0 | 168 | 0 | 12 | 0 | 168 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0 |  | 5481.51 | 2724.1 | 8205.61 | 4015 | 930 | 1719 | 1039 | 290 | 77 | 0 | 124 | 11.61 | 0 | 101.56
14:00 | 0 | 0 | 132 | 0 | 300 | 0 | 0 | 0 | 323 |  | 0 | 320 | 0 | 0 | 0 | 30 | 270 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 27 | 33 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 90 | 94 | 25 | 19 | 4 | 80 | 75 | 0 | 320 | 290 | 126 | 8 | 50 | 30 | 48 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 21 | 126 | 151 | 16 | 0 | 1.4 | 60 | 0 | 5 | 5 | 100 | 291 | 65 | 10 | 5 | 0 | 17 | 31 | 10 | 280 | 0 | 11 | 0 | 145 | 0 | 0 | 70 | 0 | 86 | 14.7 | 100 | 40 | 0 | 142 | 0 | 88 | 105 | 3.4 | 0 | 17 | 0 |  | 929 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 172 | 0 | 161 | 0 | 13 | 0 | 162 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 |  | 5306.5 | 2658.3 | 7964.8 | 3971 | 929 | 1578 | 970 | 290 | 77 | 0 | 126 | 23.8 | 0 | 101.55
15:00 | 0 | 0 | 132 | 0 | 300 | 0 | 0 | 0 | 324 |  | 0 | 320 | 0 | 0 | 0 | 30 | 270 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 30 | 0 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 90 | 93 | 25 | 19 | 2 | 80 | 80 | 0 | 335 | 305 | 143 | 8 | 50 | 33 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 21 | 120 | 150 | 16 | 0 | 1.3 | 60 | 0 | 5 | 5 | 100 | 288 | 63 | 10 | 5 | 0 | 17 | 29 | 10 | 300 | 0 | 11 | 0 | 145 | 0 | 0 | 70 | 0 | 70 | 4.4 | 100 | 34 | 0 | 139 | 0 | 88 | 105 | 2.5 | 0 | 17 | 0 |  | 930 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 180 | 0 | 160 | 0 | 13 | 0 | 174 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 5299.2 | 2724.8 | 8024 | 4043 | 930 | 1606 | 947 | 290 | 77 | 0 | 120 | 11 | 0 | 0
16:00 | 0 | 0 | 134 | 0 | 300 | 0 | 0 | 25 | 322 |  | 0 | 320 | 0 | 0 | 0 | 30 | 270 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 90 | 0 | 19 | 3 | 80 | 80 | 0 | 310 | 290 | 145 | 8 | 50 | 33 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 21 | 130 | 149 | 16 | 0 | 0.5 | 59 | 0 | 5 | 5 | 100 | 305 | 65 | 10 | 5 | 0 | 17 | 30 | 10 | 290 | 0 | 11 | 0 | 145 | 0 | 0 | 70 | 0 | 70 | 1.8 | 100 | 34 | 0 | 140 | 0 | 88 | 105 | 0.5 | 0 | 17 | 0 |  | 929 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 13 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 173 | 0 | 165 | 0 | 12 | 0 | 171 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 5225.8 | 2662.2 | 7888 | 3993 | 929 | 1546 | 919 | 290 | 77 | 0 | 130 | 4 | 0 | 0
17:00 | 0 | 0 | 125 | 0 | 300 | 0 | 0 | 50 | 285 |  | 0 | 320 | 0 | 0 | 0 | 30 | 240 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 25 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 90 | 90 | 8 | 19 | 4 | 80 | 80 | 0 | 260 | 290 | 146 | 8 | 80 | 33 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 21 | 126 | 150 | 16 | 0 | 0 | 59 | 0 | 5 | 5 | 130 | 284 | 64 | 10 | 5 | 0 | 17 | 29 | 10 | 290 | 0 | 11 | 0 | 145 | 0 | 0 | 93 | 0 | 70 | 0 | 100 | 42 | 0 | 139 | 0 | 88 | 105 | 0 | 0 | 17 | 0 |  | 929 | 0 | 305 | 0 | 7 | 0 | 0 | 0 | 19 | 0 | 0 | 151 | 22 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 150 | 0 | 167 | 0 | 13 | 0 | 176 | 0 | 357 | 17 | 0 | 0 | 39 | 0 | 0 | 0.1 | 0 |  | 5185 | 2700.1 | 7885.1 | 3905 | 929 | 1510 | 1029 | 290 | 77 | 19 | 126 | 0.1 | 0 | 0
18:00 | 0 | 0 | 99 | 0 | 350 | 0 | 0 | 146 | 357 |  | 0 | 360 | 0 | 7 | 0 | 15 | 315 | 0 | 115 | 0 | 6 | 0 | 45 | 0 | 70 | 0 | 47 | 53 | 55 | 55 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 14 | 0 | 0 | 104 | 0 |  | 0 | 0 | 68 | 100 | 90 | 31 | 19 | 4 | 80 | 90 | 0 | 330 | 290 | 146 | 8 | 85 | 37 | 10 | 0 | 13 | 0 | 0 | 5 | 19 | 6 | 33 | 21 | 154 | 151 | 72 | 22 | 0 | 60 | 0 | 26 | 16 | 130 | 288 | 65 | 74 | 40 | 0 | 17 | 33 | 10 | 290 | 24 | 11 | 0 | 212 | 0 | 0 | 182 | 0 | 77 | 0 | 100 | 105 | 0 | 0 | 0 | 88 | 105 | 0 | 16 | 50 | 20 |  | 929 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 39 | 0 | 40 | 154 | 27 | 16 | 0 | 60 | 0 | 0 | 0 | 51 | 50 | 8 | 0 | 0 | 0 | 22 | 3 | 8 | 0 | 0 | 290 | 0 | 0 | 165 | 0 | 147 | 0 | 21 | 0 | 168 | 0 | 417 | 53 | 0 | 40 | 90 | 109 | 0 | 0 | 0 |  | 6431 | 3233 | 9664 | 4153 | 929 | 1861 | 1997 | 290 | 77 | 203 | 154 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 0 | 350 | 0 | 0 | 309 | 358 |  | 0 | 360 | 0 | 0 | 0 | 0 | 309 | 0 | 98 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 48 | 17 | 17 | 17 | 0 | 25 | 28 | 30 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 61 | 100 | 95 | 11 | 19 | 8 | 80 | 90 | 0 | 330 | 300 | 145 | 8 | 88 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 148 | 155 | 92 | 22 | 0 | 59 | 0 | 50 | 27 | 100 | 287 | 66 | 77 | 40 | 0 | 17 | 33 | 10 | 285 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 63 | 0 | 100 | 65 | 0 | 0 | 7 | 88 | 105 | 0 | 16 | 54 | 51 |  | 929 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 154 | 27 | 16 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 11 | 11 | 0 | 0 | 290 | 0 | 15 | 193 | 0 | 147 | 0 | 88 | 0 | 197 | 0 | 408 | 53 | 0 | 35 | 90 | 104 | 0 | 0 | 0 |  | 6453 | 3226 | 9679 | 4357 | 929 | 1998 | 1720 | 290 | 77 | 160 | 148 | 0 | 0 | 0
19:30 | 0 | 0 | 100 | 0 | 350 | 0 | 0 | 342 | 358 |  | 0 | 360 | 0 | 0 | 0 | 0 | 305 | 0 | 98 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 47 | 17 | 17 | 17 | 22 | 25 | 31 | 28 | 16 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 34 | 100 | 97 | 0 | 19 | 11 | 80 | 90 | 0 | 330 | 310 | 147 | 8 | 90 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 148 | 175 | 92 | 22 | 0 | 59 | 0 | 51 | 27 | 100 | 267 | 66 | 77 | 40 | 0 | 17 | 33 | 10 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 24 | 0 | 100 | 52 | 0 | 140 | 0 | 88 | 105 | 0 | 0 | 54 | 34 |  | 929 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 151 | 28 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 13 | 11 | 0 | 0 | 290 | 0 | 0 | 192 | 0 | 153 | 0 | 92 | 0 | 196 | 0 | 395 | 35 | 0 | 35 | 75 | 113 | 0 | 0 | 0 |  | 6498 | 3128 | 9626 | 4547 | 929 | 1989 | 1562 | 290 | 77 | 84 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 0 | 350 | 0 | 0 | 343 | 356 |  | 0 | 360 | 0 | 0 | 0 | 0 | 304 | 0 | 98 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 47 | 17 | 0 | 17 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 134 | 0 |  | 0 | 0 | 17 | 100 | 97 | 0 | 19 | 17 | 80 | 90 | 0 | 330 | 270 | 145 | 8 | 90 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 150 | 161 | 92 | 22 | 0 | 60 | 0 | 53 | 27 | 100 | 272 | 66 | 77 | 40 | 0 | 17 | 33 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 27 | 0 | 100 | 52 | 0 | 140 | 0 | 88 | 105 | 0 | 0 | 54 | 0 |  | 929 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 172 | 27 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 13 | 11 | 0 | 0 | 290 | 0 | 0 | 193 | 0 | 150 | 0 | 92 | 0 | 196 | 0 | 395 | 35 | 0 | 0 | 75 | 113 | 0 | 0 | 0 |  | 6394 | 3111 | 9505 | 4563 | 929 | 1984 | 1479 | 290 | 77 | 33 | 150 | 0 | 0 | 0
21:00 | 0 | 0 | 100 | 0 | 350 | 0 | 0 | 343 | 355 |  | 0 | 360 | 0 | 0 | 0 | 0 | 298 | 0 | 98 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 134 | 0 |  | 0 | 0 | 17 | 90 | 98 | 0 | 19 | 24 | 80 | 90 | 0 | 260 | 270 | 146 | 8 | 90 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 144 | 161 | 92 | 22 | 0 | 60 | 0 | 53 | 27 | 100 | 265 | 66 | 77 | 40 | 0 | 17 | 33 | 10 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 40 | 0 | 140 | 0 | 70 | 105 | 0 | 0 | 54 | 0 |  | 929 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 172 | 26 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 187 | 0 | 149 | 0 | 95 | 0 | 181 | 0 | 369 | 35 | 0 | 0 | 59 | 83 | 0 | 0 | 0 |  | 6210 | 3039 | 9249 | 4469 | 929 | 2000 | 1313 | 290 | 77 | 27 | 144 | 0 | 0 | 0
22:00 | 0 | 0 | 100 | 0 | 260 | 0 | 0 | 316 | 330 |  | 0 | 300 | 0 | 0 | 0 | 0 | 220 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 0 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 134 | 0 |  | 0 | 0 | 0 | 90 | 98 | 0 | 19 | 27 | 80 | 90 | 0 | 260 | 270 | 146 | 8 | 90 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 138 | 163 | 65 | 20 | 0 | 60 | 0 | 53 | 27 | 100 | 264 | 66 | 77 | 40 | 0 | 17 | 33 | 10 | 285 | 24 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 0 | 0 | 140 | 0 | 70 | 105 | 0 | 0 | 51 | 0 |  | 929 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 164 | 27 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 178 | 0 | 146 | 0 | 94 | 0 | 181 | 0 | 369 | 17 | 0 | 0 | 36 | 19 | 0 | 0 | 0 |  | 5764 | 2889 | 8653 | 4253 | 929 | 1903 | 1063 | 290 | 77 | 0 | 138 | 0 | 0 | 101.36
23:00 | 0 | 0 | 100 | 0 | 260 | 0 | 0 | 280 | 300 |  | 0 | 280 | 0 | 0 | 0 | 0 | 220 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 22 | 25 | 22 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 135 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 19 | 30 | 80 | 90 | 0 | 260 | 270 | 147 | 8 | 90 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 134 | 159 | 24 | 22 | 0 | 60 | 0 | 53 | 27 | 100 | 267 | 65 | 77 | 40 | 0 | 17 | 33 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 0 | 0 | 140 | 0 | 70 | 105 | 0 | 0 | 22 | 0 |  | 930 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 150 | 26 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 13 | 8 | 0 | 0 | 290 | 0 | 0 | 172 | 0 | 163 | 0 | 95 | 0 | 170 | 0 | 369 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 5493 | 2816 | 8309 | 4193 | 930 | 1859 | 825 | 290 | 78 | 0 | 134 | 0 | 0 | 101.35
24:00 | 0 | 0 | 100 | 0 | 260 | 0 | 0 | 280 | 300 |  | 0 | 280 | 0 | 0 | 0 | 0 | 220 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 25 | 31 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 19 | 31 | 80 | 90 | 0 | 260 | 270 | 30 | 8 | 92 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 130 | 165 | 0 | 22 | 0 | 58 | 0 | 53 | 27 | 100 | 262 | 65 | 77 | 40 | 0 | 17 | 33 | 10 | 295 | 0 | 11 | 0 | 45 | 0 | 0 | 140 | 0 | 0 | 0 | 50 | 0 | 0 | 138 | 0 | 54 | 105 | 0 | 0 | 0 | 0 |  | 931 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 25 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 290 | 0 | 0 | 171 | 0 | 168 | 0 | 95 | 0 | 168 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5181 | 2748 | 7929 | 4067 | 931 | 1829 | 604 | 290 | 78 | 0 | 130 | 0 | 0 | 0
KWH | 324000 | 0 | 2936000 | 0 | 6954382 | 0 | 0 | 2053630 | 7446000 |  | 0 | 8051125 | 0 | 9600 | 0 | 287334 | 6491230 | 0 | 2884000 | 0 | 3840 | 0 | 165120 | 0 | 82560 | 0 | 775200 | 159480 | 227100 | 120022 | 87552 | 600000 | 678240 | 740900 | 782100 | 4584 | 0 | 776220 | 972000 | 2700000 | 0 | 15651 | 0 | 0 | 3172862 | 0 |  | 0 | 0 | 164832 | 2014440 | 1920960 | 186720 | 457296 | 470880 | 1917884 | 920235 | 0 | 7514900 | 6977000 | 3464000 | 200727 | 1465720 | 721728 | 917760 | 0 | 402372 | 0 | 0 | 8808 | 147348 | 145800 | 447000 | 493530 | 2932800 | 3637560 | 568320 | 153216 | 13800 | 1426000 | 0 | 417600 | 386928 | 2760815 | 6490000 | 1428576 | 731520 | 453960 | 0 | 224000 | 480280 | 121320 | 7316500 | 145632 | 256992 | 0 | 2566799 | 0 | 0 | 1903200 | 0 | 813600 | 76140 | 1413120 | 576480 | 8363 | 3043000 | 30000 | 1466604 | 2524970 | 27840 | 27600 | 439664 | 105381 |  | 20512000 | 0 | 7830720 | 0 | 39360 | 0 | 0 | 0 | 63360 | 0 | 218625 | 4070135 | 508900 | 32520 | 0 | 1334000 | 0 | 0 | 0 | 57936 | 147230 | 6377 | 0 | 7200 | 0 | 101280 | 79488 | 188928 | 0 | 0 | 7013300 | 0 | 13000 | 4533509 | 0 | 4115900 | 0 | 872361 | 0 | 4474382 | 0 | 8641727 | 216000 | 0 | 120000 | 399600 | 432960 | 0 | 35148 | 0 |  | 125429252 | 66065946 | 191495198 | 98429887 | 20512000 | 40361543 | 19880272 | 7013300 | 1748220 | 464248 | 2932800 | 152928 | 0
Fuel Cost | 362880 | 0 | 3141520 | 0 | 5146242.68 | 0 | 0 | 1478613.6 | 5658960 |  | 0 | 6440900 | 0 | 97920 | 0 | 2948046.84 | 8049125.2 | 0 | 3605000 | 0 | 42624 | 0 | 1636339.2 | 0 | 751296 | 0 | 7255872 | 1529413.2 | 2166534 | 1195419.12 | 65664 | 450000 | 0 | 0 | 0 | 43914.72 | 0 | 201817.2 | 252720 | 4131000 | 0 | 150406.11 | 0 | 0 | 4029534.74 | 0 |  | 0 | 0 | 1729087.68 | 20728587.6 | 18268329.6 | 1747699.2 | 420712.32 | 1309046.4 | 2013778.2 | 966246.75 | 0 | 5561026 | 5860680 | 3186880 | 196712.46 | 1949407.6 | 591816.96 | 945292.8 | 0 | 575391.96 | 0 | 0 | 82795.2 | 150294.96 | 109350 | 844830 | 370147.5 | 20236320 | 2982799.2 | 5404723.2 | 156280.32 | 226320 | 1939360 | 0 | 567936 | 483660 | 3423410.6 | 5970800 | 2128578.24 | 1287475.2 | 503895.6 | 0 | 356160 | 561927.6 | 285102 | 5194715 | 109224 | 195313.92 | 0 | 26874385.53 | 0 | 0 | 18308784 | 0 | 8209224 | 878655.6 | 13170278.4 | 5407382.4 | 78361.31 | 2860420 | 263100 | 13067441.64 | 23860966.5 | 0 | 254472 | 0 | 0 |  | 55382400 | 0 | 6107961.6 | 0 | 379430.4 | 0 | 0 | 0 | 734976 | 0 | 2162201.25 | 3256108 | 788795 | 349264.8 | 0 | 2507920 | 0 | 0 | 0 | 573566.4 | 1526775.1 | 74674.67 | 0 | 71712 | 0 | 111408 | 131155.2 | 143018.496 | 0 | 0 | 28684397 | 0 | 366990 | 3989487.92 | 0 | 3827787 | 0 | 1387053.99 | 0 | 3937456.16 | 0 | 6308460.71 | 2043360 | 0 | 1101600 | 3560436 | 4043846.4 | 0 | 0 | 0 |  | 293687348.06 | 133552242.096 | 427239590.156 | 92953425.366 | 55382400 | 36161298.52 | 187221277.19 | 28684397 | 454537.2 | 5040959.28 | 20236320 | 1104975.6 | 0
Yesterday Day Peak | 0 | 0 | 131 | 0 | 330 | 0 | 0 | 0 | 354 |  | 0 | 350 | 0 | 0 | 0 | 30 | 300 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 25 | 27 | 33 | 25 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 96 | 26 | 19 | 4 | 80 | 0 | 0 | 320 | 325 | 143 | 8 | 0 | 33 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 15 | 122 | 149 | 4 | 0 | 2.4 | 60 | 0 | 5 | 5 | 130 | 301 | 63 | 10 | 5 | 0 | 0 | 6 | 0 | 305 | 0 | 11 | 0 | 175 | 0 | 0 | 21 | 0 | 100 | 20 | 100 | 40 | 0 | 138 | 0 | 88 | 105 | 2.82 | 0 | 17 | 0 |  | 929 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 290 | 0 | 0 | 184 | 0 | 168 | 0 | 12 | 0 | 189 | 0 | 419 | 0 | 0 | 0 | 18 | 0 | 0 | 5.5 | 0 |  | 8122.72 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 0 | 350 | 0 | 0 | 309 | 358 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 309 | 0 | 98 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 48 | 17 | 17 | 17 | 0 | 25 | 28 | 30 | 33 | 0 | 0 | 37 | 40 | 105 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 61 | 100 | 95 | 11 | 19 | 8 | 80 | 90 | 0 | 330 | 300 | 145 | 8 | 88 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 6 | 33 | 21 | 148 | 155 | 92 | 22 | 0 | 59 | 0 | 50 | 27 | 100 | 287 | 66 | 77 | 40 | 0 | 17 | 33 | 10 | 285 | 24 | 11 | 0 | 195 | 0 | 0 | 200 | 0 | 63 | 0 | 100 | 65 | 0 | 0 | 7 | 88 | 105 | 0 | 16 | 54 | 51 |  | 929 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 154 | 27 | 16 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 11 | 11 | 0 | 0 | 290 | 0 | 15 | 193 | 0 | 147 | 0 | 88 | 0 | 197 | 0 | 408 | 53 | 0 | 35 | 90 | 104 | 0 | 0 | 0 |  | 9679 | EvPeak
Forecast for Evening | 0 | 0 | 130 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 37 | 50 | 110 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 98 | 50 | 19 | 40 | 100 | 0 | 0 | 360 | 360 | 225 | 16 | 90 | 37 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 145 | 180 | 95 | 22 | 0 | 60 | 0 | 51 | 44 | 163 | 300 | 66 | 77 | 40 | 0 | 20 | 36 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 140 | 115 | 88 | 105 | 0 | 300 | 54 | 110 |  | 941 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 33 | 110 | 30 | 60 | 0 | 50 | 48 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 0 | 0 | 130 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 100 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 37 | 50 | 110 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 20 | 19 | 30 | 80 | 0 | 0 | 360 | 360 | 225 | 16 | 80 | 33 | 55 | 0 | 30 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 100 | 170 | 0 | 22 | 1.6 | 60 | 0 | 51 | 44 | 163 | 300 | 66 | 77 | 40 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 140 | 115 | 88 | 105 | 5 | 230 | 54 | 50 |  | 682 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 33 | 70 | 0 | 60 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 220 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 113 | 0 | 113 | 0 | 8
Generation at 08:00(Today) | 0 | 0 | 100 | 0 | 230 | 0 | 0 | 261 | 250 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 30 | 25 | 0 | 19 | 29 | 80 | 0 | 0 | 260 | 270 | 216 | 8 | 80 | 34 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 78 | 163 | 0 | 0 | 0.4 | 60 | 0 | 5 | 5 | 100 | 265 | 20 | 10 | 5 | 0 | 0 | 7 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 0 | 0 | 139 | 0 | 17 | 68 | 0.9 | 0 | 0 | 0 | 0 | 578 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 13 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 20 | 14 | 5 | 0 | 0 | 290 | 0 | 0 | 140 | 0 | 148 | 0 | 12 | 0 | 167 | 0 | 229 | 0 | 0 | 0 | 0 | 50 | 0 | 1.7 | 0 | 0
199
| Minimum Generation |  | 6459 | 5:00
| Highest Generation |  | 9679 | 19:00
| Day Peak Generation |  | 8122.72 | 12:00
| Evening Peak Generation |  | 9679 | 19:00
| HVDC Max Flow |  | 931 | 24:00
| HVDC EvPeak Flow |  | 929 | 19:00
| Load factor L.F |  | 82.44%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-08
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8122.72 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 6253.9 | MW
Evening Peak Generation : |  | 9679 | MW Hour : | 19:00 | Available Max Generation : |  | 14913 | MW
E.P. Demand (at gen end) : |  | 9679 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 9679 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5913 | MW
Total Gen. (MKWH) : |  | 191.4952 | System Load Factor : | 82.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 280 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-08
Actual : | 101.29 | Ft.(MSL) , | Rule curve : | 108.3 | Ft.( MSL )
Gas Consumed : | Total = | 1155.073 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129114723.886
: |  | Coal : | 28684397 | Oil : | 192262236.47 | Total : | 350061357.356
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3207.2814 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1085.2833 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 971.4211 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 877.4212 |  |  | 0 | 0%
) | 0 | 0:00 | 793.1001 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 639.9902 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 364.7611 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 164.9631 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 493.5591 |  |  | 0 | 0%
Total | 0 |  | 8597.7807 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-1,2,3 & 5
4) Raozan #2
5) Ashuganj unit-4 & 5
6) Chandpur CCPP ST
7)Sylhet 150 MW
8) Fenchuganj # 03 & 04
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ghorasal unit-2 tripped at 09:45.
b) Chandpur CCPP GT was synchronized at 11:47.
c) Hathazari-Baroihat 132 kV Ckt-1 was under shut down from 08:47 to 16:42 for A/M.
d) Aminbazar-Mirpur 132 kV Ckt-2 was under shut down from 09:57 to 17:35 for A/M.
e) Sikalbaha-TK Chemical 132 kV Ckt was under shut down from 08:54 to 14:10 for A/M.
f) Mymensingh-Kishorganj 132 kV Ckt-1 was under shut down from 09:05 to 17:29 for A/M.
g) Rangamati 132/33 kV T-1 transformer was under shut down from 11:53 to 14:56 for A/M.
h) Meghnaghat-Haripur 230 kV Ckt-1 was under shut down from 08:21 to 13:52 for A/M.
i) Naogaon-Bogura 132 kV Ckt-2 was under shut down from 08:50 to 15:27 for A/M.
j) Manuknagar 230/132 kV T-1 transformer was under shut down from 08:20 to 16:18 for A/M.
k) Hasnabad 132/33 kV T-5 transformer was under shut down from 07:05 to for A/M.
l) Khulna (c) 132/33 kV T-3 transformer was under shut down from 08:07 to 16:51 for A/M.
m) Bogura-Mohasthangarh 132 kV Ckt-1 was under shut down from 09:30 to for A/M.
n) Barisal 230 kV bus bar-2 was under shut down from 08:40 to 14:40 for A/M.
o) Khulna(S) 230/132 kV T-2 transformer was under shut down from 08:41 to 13:10 for A/M.
p) Haripur 412 MW Gt was synchronized at 15:05.
q) Haripur 412 MW STG was synchronized at 17:01.
r) Ashuganj unit-4 was tripped at 00:18(08/11/2019) due to hydraulic control oil problem
s) Ashuganj 225 MW CCPP STG was synchronized at 02:27(08/11/2019).
t) Bogura(N) 132 kV main bus was shut down at 06:06(08/11/2019) for D/W.
u) B.Baria 132 kV bus & 132/33 kV T2 transformer were shut down at 06:56(08/11/2019) for C/M.
v) Ghorasal 230/132 kV AT-1 transformer was shut down at 07:04(08/11/2019) for C/M.
w) Hasnabad 132/33 kV T-5 transformer was shut down at 07:20(08/11/2019) for A/M.
x) Meghnaghat 450 MW GT2 was shut down at 07:04(08/11/2019) for S/S work.
y) Meghnaghat 230 kV S/S Bus-2 was shut down at 07:30(08/11/2019) for DS work.
z) Hathazari 132/33 kV T2 transformer was shut down at 07:42(08/11/2019) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 324000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2936000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 6954382
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 309 | 2053630
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 358 | 7446000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8051125 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 9600 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 287334 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 87552 | Reserve
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 98 | 2884000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 3840 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 309 | 6491230
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 775200 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 159480 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 84 | 165120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 227100 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 120022 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 82560 | Low demand
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1278240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 740900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 782100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 4584 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 2566799 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 63 | 813600 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1466604 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 2529 | 46711002
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 15651
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 76140
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 11 | 186720
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 77 | 1748220 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 3172862 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2524970
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 61 | 164832 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2014440
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1413120
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 457296
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 470880
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 1920960 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27840
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 27600 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 439664
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 51 | 105381 | Low demand
| Chattogram area Total |  |  |  | 2166 | 906 | 17466576
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1917884 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 90 | 920235 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 145 | 3464000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7514900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6977000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 721728 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 917760
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 402372 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 8363 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 88 | 1465720
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 65 | 576480 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 147348
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 6 | 145800 | Machine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2932800
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 447000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 8808 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 493530
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1456 | 29262455
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 155 | 3637560 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 153216
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 92 | 568320
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 1903200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 7 | 30000 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 476 | 6306096
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1426000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 2760815 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 287 | 6490000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 417600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 27 | 386928
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 256992
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1428576 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 731520 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 453960 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 224000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 33 | 480280 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 145632
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7316500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 3043000 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 121320
| Sylhet Area Total |  |  |  | 1949 | 1086 | 25683123
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 929 | 20512000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 39360 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 63360 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 7830720 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 218625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 216000 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 90 | 399600 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1433 | 29279665
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 32520 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 508900
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 154 | 4070135 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 88 | 872361
| Barisal Area Total |  |  |  | 462 | 285 | 5483916
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 1334000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 147230 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 6377 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 193 | 4533509 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 147 | 4115900 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 197 | 4474382 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 8641727 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 101280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 79488
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 188928
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 7200
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 57936 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 120000 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1099 | 23807957
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 290 | 7013300
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 13000 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 104 | 432960
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35148
| Rangpur Area Total |  |  |  | 605 | 409 | 7494408
| Total |  |  |  | 19018 | 9679 | 191495198
| Eastern Grid Total |  |  |  | 13454 | 6453 | 125429252
| Western Grid Total |  |  |  | 5564 | 3226 | 66065946
| National Grid Total |  |  |  | 19018 | 9679 | 191495198
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-07
(a) ENTIRE EASTERN GRID : |  | 6545 | MW | (b) ENTIRE WESTERN GRID : |  | 2690 | MW
i) Dhaka area |  | 3599 | MW | i) Khulna area |  | 1036 | MW
ii) Chittagong area |  | 1009 | MW | ii) Rajshahi area |  | 841 | MW
iii) Comilla area |  | 858 | MW | iii) Barisal area |  | 265 | MW
iv) Mymensingh area |  | 695 | MW | iv) Rangpur area |  | 548 | MW
v) Sylhet area |  | 384 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9235 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 1700 | Srimongal | 32 | 1800 | Bottail | 96 | 1800
Munsiganj | 84 | 1800 | Shahjibazar | 92 | 1800 | G.K Project | 40 | 1800
Sonargaon | 71 | 1830 | Fenchuganj | 33 | 1800 | Faridpur | 132 | 1900
Shyampur | 180 | 100 | Kulawara | 35 | 1800 | Madaripur | 61 | 2100
Bhulta | 173 | 1500 | Sylhet | 116 | 1800 | Sariatpur | 40 | 1830
Madanganj | 51 | 1700 | Chatak | 19 | 1800 | Gopalganj | 67 | 1830
Shitalakhya | 108 | 1100 | Sunamganj | 32 | 2000 | Bagerhat | 66 | 1830
Rahim steel | 21 | 1400 | Biani Bazar | 37 | 1900 | Mongla | 34 | 100
Matuail | 90 | 1200 | Comilla (S) | 154 | 1800 | Satkhira | 66 | 1830
Ghorasal | 73 | 1800 | Comilla(N) | 77 | 1800 | Gallamari | 41 | 1300
Narsingdi | 126 | 1900 | Chandpur | 78 | 2000 | Magura | 36 | 1800
Haripur (SBU) | 80 | 300 | Feni | 115 | 1800 | Norail | 22 | 1830
Ullon | 62 | 1800 | Chowmuhani | 140 | 1930 | Chuadanga | 64 | 1800
Hasnabad | 137 | 1900 | Ashuganj | 47 | 2200 | Barisal(N) | 35 | 2100
Magbazar | 104 | 1200 | Daudkandi | 108 | 1830 | Barisal (S) | 82 | 1800
Maniknagar | 108 | 1800 | B.Baria | 106 | 1830 | Patuakhali | 85 | 1900
Bangabhaban | 19 | 1300 | Ramganj | 68 | 1800 | Bhandaria | 40 | 2000
Narinda | 90 | 1400 | Madunaghat | 51 | 1830 | Borhan Uddin | 28 | 2100
Dhanmondi | 140 | 1200 | Hathazari | 88 | 1800 | Ishurdi | 48 | 1800
Lalbag | 82 | 1800 | Khulshi | 184 | 1200 | Ruppur Paromanobik | 1 | 100
Madartek | 60 | 2000 | Halishahar | 138 | 1800 | Natore | 88 | 1800
Mirpur | 92 | 1800 | Baraulia | 101 | 1500 | Bogra | 147 | 1830
Kalyanpur | 99 | 1800 | Sikalbaha | 22 | 1830 | Noagaon | 80 | 1800
Gulshan | 136 | 1300 | Dohazari | 82 | 2000 | Rajshahi | 96 | 1900
Uttara | 52 | 1800 | Cox'sbazar | 91 | 1800 | Rajshahi New | 9 | 1900
Uttara New | 37 | 1800 | Chandraghona | 28 | 1200 | C.Nawabganj | 51 | 1800
Kamrangirchar | 66 | 1800 | Kaptai | 4 | 1800 | Amnura | 22 | 1800
Savar | 118 | 1800 | A. Khaer Stl. | 0 | 0 | Pabna | 79 | 1800
Bhasantec | 146 | 1800 | Bakulia | 104 | 1800 | Shahjadpur | 74 | 1930
Agargaon | 49 | 1300 | Julda | 21 | 1830 | Serajganj | 64 | 1830
Satmosjid | 87 | 1800 | TK chemical | 15 | 1830 | Niyamatpur | 41 | 1800
Tongi | 137 | 1830 | Modern Steel | 13 | 1100 | Joypurhat | 40 | 1830
Kabirpur | 187 | 1800 | Shahmirpur | 28 | 1800 | Sherpur(Bogura) | 32 | 1800
Basundhara | 97 | 1800 | Khagrachhari | 16 | 1800 | Mohastangor | 11 | 1800
Manikganj | 76 | 1900 | Matarbari | 28 | 1900 | Rangpur | 108 | 1800
Joydevpur | 185 | 1830 | Baroiar Hat | 20 | 1800 | Lalmonirhat | 38 | 2000
New Tongi | 96 | 1800 | Rangamati | 12 | 1800 | Saidpur | 83 | 1800
Korda | 225 | 1800 | Abul Khair 230 | 130 | 800 | Purbasadipur | 78 | 1830
Dhamrai | 54 | 1800 | BSRM | 109 | 1200 | Thakurgaon | 56 | 1830
Valuka | 92 | 1800 | GPH Ispat | 2 | 1800 | Palashbari | 87 | 1800
Tangail | 157 | 1800 | Goalpara | 21 | 1830 | Barapukuria | 40 | 1800
Mymensing | 173 | 1800 | Central s/s | 69 | 1900 | Panchagar | 39 | 1800
Kishorganj | 84 | 2100 | Noapara | 45 | 1830 | Joldhaka | 19 | 1800
Netrokona | 73 | 1800 | Jessore | 96 | 1830 | Kurigram | 35 | 1800
Jamalpur | 86 | 1800 | Benapol | 30 | 1830
Sherpur | 72 | 1800 | Jhenida | 78 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-07 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 384 | 4:00 | 375 | 15:00 | Kaliakoir | 364 | 4:00 | 352 | 10:00
Bheramara | 402 | 1:00 | 386 | 18:00 | Bhulta | 370 | 6:00 | 357 | 10:00
Ashuganj(N) | 374 | 2:00 | 363 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 10:00
Ghorasal | 222 | 21:00 | 220 | 1:00 | Hathazari | 219 | 18:00 | 212 | 10:00
Ishurdi | 236 | 4:00 | 227 | 11:00 | Megnaghat | 218 | 1:00 | 208 | 10:00
Ashuganj | 227 | 4:00 | 220 | 10:00 | Fenchuganj | 231 | 1:00 | 226 | 10:00
Serajganj | 233 | 4:00 | 229 | 10:00 | Siddhirganj | 218 | 3:00 | 210 | 10:00
Baghabari | 236 | 1:00 | 231 | 12:00 | Maniknagar | 216 | 4:00 | 207 | 16:00
Barapukuria | 230 | 4:00 | 224 | 12:00 | Old Airport | 214 | 4:00 | 206 | 10:00
Bogra | 231 | 5:00 | 225 | 12:00 | Barisal | 230 | 1:00 | 221 | 14:00
Khulna South | 228 | 4:00 | 212 | 13:00 | AKSML | 214 | 17:00 | 209 | 2:00
Rampura | 218 | 4:00 | 210 | 10:00 | BSRM | 215 | 18:00 | 209 | 15:00
Haripur | 215 | 1:00 | 210 | 10:00 | Bibiyana | 228 | 3:00 | 224 | 11:00
Hasnabad | 215 | 4:00 | 210 | 14:00 | Bhulta | 219 | 6:00 | 210 | 10:00
Aminbazar | 215 | 4:00 | 207 | 12:00 | Ashuganj (S) | 226 | 4:00 | 220 | 10:00
Tongi | 212 | 4:00 | 206 | 10:00 | Kaliakoir | 219 | 3:00 | 212 | 10:00
Comilla (N) | 223 | 1:00 | 217 | 10:00 | GPH | 214 | 18:00 | 209 | 5:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 130 | 300 | 123 | 1200 | Halishahar | 131 | 1800 | 126 | 900
Munsiganj | 130 | 1800 | 122 | 1200 | Baraulia | 128 | 700 | 124 | 1500
Megnaghat | 125 | 100 | 122 | 1200 | Sikalbaha | 131 | 1800 | 126 | 1500
Shyampur | 130 | 400 | 124 | 1200 | Dohazari | 130 | 1800 | 125 | 100
Bhulta | 124 | 300 | 117 | 1200 | Cox'sbazar | 122 | 800 | 114 | 2000
Madanganj | 130 | 600 | 123 | 1000 | Chandraghona | 130 | 1800 | 127 | 1000
Shitalakhya | 131 | 500 | 123 | 1200 | Kaptai | 130 | 100 | 127 | 700
Rahim steal | 130 | 500 | 124 | 1100 | A. Khaer Stl. | 127 | 100 | 115 | 400
Matuail | 130 | 100 | 122 | 1200 | Bakulia | 129 | 1800 | 126 | 100
Ghorasal | 135 | 1000 | 130 | 1500 | Julda | 131 | 1830 | 126 | 600
Narsinghdi | 130 | 300 | 124 | 1200 | TK Chemical | 130 | 1900 | 124 | 900
Haripur (SBU) | 130 | 600 | 124 | 1000 | Modern Steel | 129 | 1800 | 125 | 200
Ullon | 132 | 600 | 125 | 1200 | Shahmirpur | 131 | 1800 | 126 | 100
Hasnabad | 132 | 600 | 125 | 1200 | Khagrachhari | 129 | 300 | 126 | 1000
Magbazar | 132 | 600 | 125 | 1200 | Matarbari | 122 | 900 | 117 | 2000
Maniknagar | 132 | 600 | 125 | 1200 | Baroiar Hat | 126 | 1830 | 120 | 1000
Bangabhaban | 132 | 600 | 125 | 1200 | Rangamati | 129 | 800 | 127 | 900
Narinda | 132 | 600 | 125 | 1200 | Goalpara | 137 | 400 | 125 | 1300
Dhanmondi | 132 | 600 | 125 | 1200 | Central s/s | 137 | 600 | 126 | 1300
Lalbag | 131 | 600 | 121 | 1200 | Noapara | 135 | 600 | 123 | 1300
Madartek | 131 | 600 | 124 | 1200 | Jessore | 132 | 600 | 121 | 1300
Mirpur | 133 | 600 | 124 | 1500 | Benapol | 134 | 500 | 121 | 1200
Kalyanpur | 133 | 600 | 127 | 1100 | Jhenida | 134 | 600 | 123 | 1800
Gulshan | 132 | 600 | 124 | 1200 | Bottail | 138 | 600 | 131 | 1100
Uttara | 130 | 600 | 122 | 1200 | G.K Project | 143 | 600 | 139 | 1100
Uttara New | 130 | 600 | 123 | 1200 | Faridpur | 133 | 600 | 126 | 1300
Kamrangirchar | 130 | 600 | 121 | 1200 | Madaripur | 134 | 200 | 124 | 1500
Savar | 130 | 600 | 122 | 1000 | Sariatpur | 135 | 100 | 123 | 1500
Bhasantec | 133 | 600 | 125 | 1200 | Gopalganj | 137 | 100 | 126 | 1300
Agargaon | 134 | 600 | 126 | 1200 | Bagerhat | 136 | 600 | 121 | 1300
Satmosjid | 133 | 600 | 126 | 1200 | Mongla | 131 | 600 | 122 | 1100
Tongi | 131 | 800 | 125 | 1500 | Satkhira | 137 | 600 | 125 | 1200
Kabirpur | 127 | 800 | 120 | 900 | Gallamari | 137 | 600 | 126 | 1300
Basundhara | 127 | 1800 | 121 | 1500 | Magura | 135 | 600 | 122 | 1200
Manikganj | 134 | 1300 | 127 | 1600 | Norail | 133 | 600 | 121 | 1800
Joydevpur | 133 | 1900 | 127 | 1300 | Chuadanga | 132 | 500 | 119 | 1800
New Tongi | 128 | 1300 | 123 | 1500 | Barisal(N) | 137 | 100 | 131 | 1100
Kodda | 130 | 1300 | 125 | 1830 | Barisal (S) | 136 | 1300 | 130 | 1200
Dhamrai | 128 | 900 | 121 | 1100 | Patuakhali | 135 | 600 | 127 | 2000
Valuka | 127 | 2200 | 113 | 1100 | Bhandaria | 135 | 600 | 122 | 1400
Tangail | 129 | 400 | 119 | 1100 | Ishurdi | 140 | 300 | 134 | 1000
Mymensing | 130 | 2200 | 116 | 1100 | Ruppur Paromanobik | 138 | 700 | 135 | 1100
Kishorganj | 128 | 2300 | 122 | 1200 | Natore | 136 | 200 | 130 | 1300
Netrokona | 129 | 2300 | 115 | 1200 | Bogra | 137 | 500 | 130 | 1300
Jamalpur | 138 | 2100 | 118 | 1000 | Noagaon | 133 | 500 | 125 | 1300
Sherpur | 136 | 1830 | 115 | 1000 | Rajshahi | 132 | 300 | 125 | 1200
Srimongal | 135 | 100 | 128 | 1200 | Rajshahi New | 134 | 1800 | 125 | 1200
Shahjibazar | 134 | 700 | 127 | 1200 | C.Nawabganj | 129 | 1800 | 120 | 1100
Fenchuganj | 132 | 600 | 127 | 1100 | Amnura | 133 | 1800 | 122 | 1100
Khulawara | 132 | 100 | 126 | 1200 | Pabna | 139 | 200 | 134 | 1100
Sylhet | 129 | 500 | 123 | 1200 | Shahjadpur | 141 | 100 | 138 | 900
Chatak | 129 | 600 | 122 | 1200 | Serajganj | 136 | 300 | 130 | 1100
Sunamganj | 129 | 600 | 120 | 1200 | Niyamatpur | 133 | 400 | 125 | 1100
Biani Bazar | 130 | 100 | 123 | 1200 | Joypurhat | 135 | 200 | 125 | 1200
Comilla(s) | 127 | 100 | 122 | 1600 | Sherpur(Bogura) | 137 | 300 | 130 | 1100
Comilla(n) | 133 | 700 | 127 | 1100 | Mohastangor | 134 | 400 | 128 | 1200
Chandpur | 127 | 1400 | 126 | 700 | Rangpur | 128 | 400 | 121 | 1200
Feni | 123 | 1700 | 118 | 1000 | Lalmonirhat | 126 | 400 | 116 | 1300
Chowmuhani | 122 | 700 | 117 | 1600 | Saidpur | 128 | 500 | 120 | 1300
Ashuganj | 134 | 100 | 131 | 1800 | Purbasadipur | 128 | 600 | 115 | 1800
Daudkandi | 127 | 700 | 122 | 1000 | Thakurgaon | 120 | 100 | 113 | 1800
B.Baria | 130 | 700 | 125 | 1100 | Palashbari | 132 | 200 | 125 | 1400
Ramganj | 122 | 700 | 118 | 1500 | Barapukuria | 130 | 400 | 124 | 1200
Madanhat | 131 | 1800 | 127 | 200 | Panchagar | 124 | 400 | 109 | 1830
Hathazari | 131 | 1800 | 127 | 1000 | Joldhaka | 127 | 500 | 119 | 1300
Khulshi | 128 | 1800 | 124 | 1100 | Kurigram | 128 | 500 | 120 | 1100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 630 | 5181 | 2748 | 7929 |  |  |  | QF-LDC-12
0:30 | 635 | 4943 | 2691.5 | 7634.5 | Date: | 2019-11-07
1:00 | 640 | 4705 | 2635 | 7340
1:30 | 645 | 4614.5 | 2538.5 | 7153
2:00 | 650 | 4524 | 2442 | 6966
2:30 | 655 | 4458 | 2426 | 6884 | [5 empty] | Gen. at Eve. Peak | 9679 | 9679 MW (19:00 )
3:00 | 660 | 4392 | 2410 | 6802 | [6 empty] | 19:00
3:30 | 660 | 4316 | 2400.5 | 6716.5 | [5 empty] | Gen. at Day Peak | 8122.72 | 8122.72 MW (12:00 )
4:00 | 660 | 4240 | 2391 | 6631 | [6 empty] | 12:00
4:30 | 655 | 4170.5 | 2374.5 | 6545 | [5 empty] | Highest Generation | 9679
5:00 | 650 | 4101 | 2358 | 6459 | [6 empty] | 19:00
5:30 | 625 | 4116.53 | 2359 | 6475.53
6:00 | 600 | 4132.06 | 2360 | 6492.06
6:30 | 565 | 4155.538 | 2433.75 | 6589.288
7:00 | 530 | 4179.016 | 2507.5 | 6686.516
7:30 | 530 | 4262.158 | 2513.35 | 6775.508
8:00 | 530 | 4345.3 | 2519.2 | 6864.5
8:30 | 635 | 4486.125 | 2505.35 | 6991.475
9:00 | 740 | 4626.95 | 2491.5 | 7118.45
9:30 | 815 | 4661.08 | 2597.15 | 7258.23
10:00 | 890 | 4695.21 | 2702.8 | 7398.01
10:30 | 845 | 4899.17 | 2708.15 | 7607.32
11:00 | 800 | 5103.13 | 2713.5 | 7816.63
11:30 | 750 | 5220.175 | 2749.5 | 7969.675
12:00 | 700 | 5337.22 | 2785.5 | 8122.72
12:30 | 660 | 5409.365 | 2754.8 | 8164.165
13:00 | 620 | 5481.51 | 2724.1 | 8205.61
13:30 | 665 | 5394.005 | 2691.2 | 8085.205
14:00 | 710 | 5306.5 | 2658.3 | 7964.8
14:30 | 765 | 5302.85 | 2691.55 | 7994.4
15:00 | 820 | 5299.2 | 2724.8 | 8024
15:30 | 810 | 5262.5 | 2693.5 | 7956
16:00 | 800 | 5225.8 | 2662.2 | 7888
16:30 | 770 | 5205.4 | 2681.15 | 7886.55
17:00 | 740 | 5185 | 2700.1 | 7885.1
17:30 | 560 | 5808 | 2966.55 | 8774.55
18:00 | 380 | 6431 | 3233 | 9664
18:30 | 355 | 6442 | 3229.5 | 9671.5
19:00 | 330 | 6453 | 3226 | 9679
19:30 | 280 | 6498 | 3128 | 9626
20:00 | 290 | 6394 | 3111 | 9505 |  |  |  | Executive Engineer
20:30 | 325 | 6302 | 3075 | 9377 |  |  |  | Network Operation Division
21:00 | 360 | 6210 | 3039 | 9249
21:30 | 400 | 5987 | 2964 | 8951
22:00 | 440 | 5764 | 2889 | 8653 |  |  |  |  | Page 6 of 7
22:30 | 520 | 5628.5 | 2852.5 | 8481
23:00 | 600 | 5493 | 2816 | 8309
23:30 | 615 | 5337 | 2782 | 8119
24:00 | 630 | 5181 | 2748 | 7929
9679 MW (19:00 )
8122.72 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-07 |  | Energy | 191495198
[10 empty] | 2019-11-07 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4067 | 931 | 1829 | 604 | 290 | 78 | 0 | 0 | 130
0:30 | 4072 | 875.5 | 1710 | 483 | 290 | 79 | 0 | 0 | 125 | Date: | 2019-11-07
1:00 | 4077 | 820 | 1591 | 362 | 290 | 80 | 0 | 0 | 120
1:30 | 4032 | 772 | 1538 | 329.5 | 290 | 77.5 | 0 | 0 | 114 | [7 empty] | Total Energy | 191.4952 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3987 | 724 | 1485 | 297 | 290 | 75 | 0 | 0 | 108 | [7 empty] | Energy not Served | 0
2:30 | 3978.5 | 723.5 | 1434 | 278.5 | 290.5 | 75 | 0 | 0 | 104 | [7 empty] | Energy Requirement | 191.4952
3:00 | 3970 | 723 | 1383 | 260 | 291 | 75 | 0 | 0 | 100
3:30 | 3899.5 | 723 | 1385.5 | 244 | 290.5 | 75 | 0 | 0 | 99 | [6 empty] | Shortage
4:00 | 3829 | 723 | 1388 | 228 | 290 | 75 | 0 | 0 | 98
4:30 | 3783 | 723 | 1356 | 221.5 | 290 | 77.5 | 0 | 0 | 94
5:00 | 3737 | 723 | 1324 | 215 | 290 | 80 | 0 | 0 | 90
5:30 | 3731 | 723 | 1348 | 214 | 289.5 | 80 | 0 | 0 | 90
6:00 | 3725 | 723 | 1372 | 213 | 289 | 80 | 0 | 0 | 90
6:30 | 3751.5 | 723 | 1417.5 | 238 | 289.5 | 78.5 | 0 | 0 | 90 |  |  |  |  | Coal
7:00 | 3778 | 723 | 1463 | 263 | 290 | 77 | 0 | 0 | 90
7:30 | 3812 | 723 | 1460 | 313 | 290 | 77 | 0 | 0 | 93 |  |  |  | Oil |  |  |  | ,
8:00 | 3846 | 723 | 1457 | 363 | 290 | 77 | 0 | 0 | 96
8:30 | 3869.5 | 723 | 1505 | 412.5 | 290 | 77 | 0 | 0 | 100
9:00 | 3893 | 723 | 1553 | 462 | 290 | 77 | 0 | 0 | 104
9:30 | 3842.5 | 826.5 | 1550 | 565 | 290 | 58.5 | 0 | 0 | 107
10:00 | 3792 | 930 | 1547 | 668 | 290 | 40 | 0 | 0 | 110
10:30 | 3851.5 | 929.5 | 1563 | 775 | 290 | 59 | 0 | 0 | 113
11:00 | 3911 | 929 | 1579 | 882 | 290 | 78 | 0 | 0 | 116
11:30 | 3960 | 929 | 1635 | 928 | 290 | 77.5 | 0 | 0 | 119
12:00 | 4009 | 929 | 1691 | 974 | 290 | 77 | 0 | 0 | 122
12:30 | 4012 | 929.5 | 1705 | 1006.5 | 290 | 77 | 0 | 0 | 123
13:00 | 4015 | 930 | 1719 | 1039 | 290 | 77 | 0 | 0 | 124
13:30 | 4015 | 930 | 1719 | 1039 | 290 | 77 | 0 | 0 | 124
14:00 | 4015 | 930 | 1719 | 1039 | 290 | 77 | 0 | 0 | 124
14:30 | 4029 | 930 | 1662.5 | 993 | 290 | 77 | 0 | 0 | 122
15:00 | 4043 | 930 | 1606 | 947 | 290 | 77 | 0 | 0 | 120
15:30 | 4018 | 929.5 | 1576 | 933 | 290 | 77 | 0 | 0 | 125
16:00 | 3993 | 929 | 1546 | 919 | 290 | 77 | 0 | 0 | 130
16:30 | 3949 | 929 | 1528 | 974 | 290 | 77 | 9.5 | 0 | 128
17:00 | 3905 | 929 | 1510 | 1029 | 290 | 77 | 19 | 0 | 126
17:30 | 4029 | 929 | 1685.5 | 1513 | 290 | 77 | 111 | 0 | 140
18:00 | 4153 | 929 | 1861 | 1997 | 290 | 77 | 203 | 0 | 154
18:30 | 4255 | 929 | 1929.5 | 1858.5 | 290 | 77 | 181.5 | 0 | 151
19:00 | 4357 | 929 | 1998 | 1720 | 290 | 77 | 160 | 0 | 148
19:30 | 4547 | 929 | 1989 | 1562 | 290 | 77 | 84 | 0 | 148
20:00 | 4563 | 929 | 1984 | 1479 | 290 | 77 | 33 | 0 | 150
20:30 | 4516 | 929 | 1992 | 1396 | 290 | 77 | 30 | 0 | 147
21:00 | 4469 | 929 | 2000 | 1313 | 290 | 77 | 27 | 0 | 144
21:30 | 4361 | 929 | 1951.5 | 1188 | 290 | 77 | 13.5 | 0 | 141
22:00 | 4253 | 929 | 1903 | 1063 | 290 | 77 | 0 | 0 | 138
22:30 | 4223 | 929.5 | 1881 | 944 | 290 | 77.5 | 0 | 0 | 136
23:00 | 4193 | 930 | 1859 | 825 | 290 | 78 | 0 | 0 | 134
23:30 | 4130 | 930.5 | 1844 | 714.5 | 290 | 78 | 0 | 0 | 132 | Max Temp. in Dhaka |  | 30.7° C
24:00 | 4067 | 931 | 1829 | 604 | 290 | 78 | 0 | 0 | 130
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Hydro
Note on W13: Author:

## Generation
2019-11-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 35 | 35 | 35 | 40 | 40 | 37 | 37 | 37 | 0 | 38 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 776220
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 110 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 110 | 110 | 110 | 110 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 14 | [8 empty] | 15651
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0.06 | 1.17 | 8 | 8 | 10 | 19 | 20 | 0 | 14.7 | 4.4 | 1.8 | 0 | [9 empty] | 76140
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 148 | 148 | 147 | 148 | 110 | 112 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 146 | 140 | 104 | 105 | 104 |  | 104 | 104 | 134 | 134 | 134 | 135 | 148 | 3172862
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 68 |  | 61 | 34 | 17 | 17 | 0 |  |  | 164832
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 102 | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2524970
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 145 | 145 | 145 | 120 | 100 | 100 | 100 | 100 | 140 | 100 | 100 | 100 | 100 | 100 | 105 | 105 | 80 | 115 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 2884000
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 225 | 225 | 225 | 225 | 268 | 261 | 268 | 300 | 300 | 270 | 270 | 270 | 240 | 315 |  | 309 | 305 | 304 | 298 | 220 | 220 | 220 | 6491230
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 0 | 16 | 49 | 134 | 175 | 175 | 177 | 145 | 145 | 145 | 145 | 212 |  | 195 | 195 | 195 | 195 | 145 | 45 | 45 | 2566799
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | [16 empty] | 324000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 125 | 130 | 130 | 131 | 130 | 136 | 130 | 130 | 131 | 130 | 132 | 132 | 134 | 125 | 99 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2936000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 300 | 300 | 300 | 330 | 330 | 300 | 300 | 300 | 300 | 350 |  | 350 | 350 | 350 | 350 | 260 | 260 | 260 | 6954382
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1917884
29 | Ashuganj TPP Unit- 4 | [12 empty] | 25 | 75 | 80 | 80 | 80 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 920235
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 10 | 10 | 10 | 10 | 10 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 33 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 721728
33 | Ashuganj 225 MW CCPP | 144 | 145 | 145 | 145 | 147 | 147 | 148 | 146 | 147 | 144 | 144 | 143 | 122 | 126 | 143 | 145 | 146 | 146 |  | 145 | 147 | 145 | 146 | 146 | 147 | 30 | 3464000
34 | Ashuganj 450 MW CCPP(South) | 270 | 265 | 270 | 270 | 275 | 270 | 290 | 305 | 270 | 270 | 315 | 325 | 315 | 290 | 305 | 290 | 290 | 290 |  | 300 | 310 | 270 | 270 | 270 | 270 | 270 | 6977000
| Ashuganj 450 MW CCPP(North) | 330 | 330 | 330 | 260 | 265 | 260 | 280 | 295 | 260 | 260 | 310 | 320 | 320 | 320 | 335 | 310 | 260 | 330 |  | 330 | 330 | 330 | 260 | 260 | 260 | 260 | 7514900
35 | Ashuganj 55 MW PP (Precision) | 55 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 54 | 51 | 51 | 47 | 48 | 49 | 10 | 10 | 10 |  | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 917760
36 | Chandpur 150 MW CCPP | 88 | 87 | 88 | 89 | 87 | 87 | 0 | 0 |  |  |  |  | 50 | 50 | 50 | 50 | 80 | 85 |  | 88 | 90 | 90 | 90 | 90 | 90 | 92 | 1465720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [15 empty] | 25 | 50 | 146 |  | 309 | 342 | 343 | 343 | 316 | 280 | 280 | 2053630
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 350 | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 360 |  | 360 | 360 | 360 | 360 | 300 | 280 | 280 | 8051125
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 260 | 260 | 260 | 260 | 260 | 260 | 344 | 314 | 314 | 354 | 351 | 323 | 324 | 322 | 285 | 357 |  | 358 | 358 | 356 | 355 | 330 | 300 | 300 | 7446000
42 | RPCL 210MW CCPP | 156 | 156 | 156 | 157 | 158 | 157 | 156 | 156 | 154 | 152 | 149 | 149 | 149 | 151 | 150 | 149 | 150 | 151 |  | 155 | 175 | 161 | 161 | 163 | 159 | 165 | 3637560
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 58 | 60 | 60 | 59 | 59 | 60 |  | 59 | 59 | 60 | 60 | 60 | 60 | 58 | 1426000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 290 | 265 | 265 | 263 | 272 | 266 | 280 | 312 | 295 | 296 | 302 | 301 | 286 | 291 | 288 | 305 | 284 | 288 |  | 287 | 267 | 272 | 265 | 264 | 267 | 262 | 6490000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 40 | 40 | 40 | 40 | 40 | 63 | 66 | 66 | 65 | 63 | 63 | 60 | 65 | 63 | 65 | 64 | 65 |  | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 1428576
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 74 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 731520
49 | Shahjibazar 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 453960
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 224000
52 | Sylhet 50MW PP (EPL) | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 32 | 31 | 29 | 30 | 29 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 480280
53 | Sylhet 10MW PP (Desh) | 0 | [11 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 121320
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256992
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 26 |  | 50 | 51 | 53 | 53 | 53 | 53 | 53 | 417600
56 | Shahjahanulla 25 MW PP | 0 | [16 empty] | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 145632
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 280 | 270 | 275 | 260 | 310 | 290 | 310 | 300 | 280 | 305 | 305 | 300 | 280 | 300 | 290 | 290 | 290 |  | 285 | 300 | 290 | 300 | 285 | 290 | 295 | 7316500
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 55 |  | 17 | 17 | 17 |  |  |  |  | 120022
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 457296
61 | Narshingdi 22 MW PP (Doreen) | [20 empty] | 22 | 22 | 22 | 22 | 22 | 0 | 87552
62 | Tangail 22 MW PP (Doreen) | 0 | [16 empty] | 22 |  | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 153216
63 | Impoprt (Tripura) | 120 | 108 | 100 | 98 | 90 | 90 | 90 | 96 | 104 | 110 | 116 | 122 | 124 | 126 | 120 | 130 | 126 | 154 |  | 148 | 148 | 150 | 144 | 138 | 134 | 130 | 2932800
64 | Malancha, Ctg. EPZ (United) | 39 | 40 | 40 | 40 | 40 | 40 | 37 | 11 | 4 | 4 | 2 | 4 | 2 | 4 | 2 | 3 | 4 | 4 |  | 8 | 11 | 17 | 24 | 27 | 30 | 31 | 470880
65 | Feni 22MW PP (Doreen) | 19 | 0 | [15 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 147348
66 | Feni 11 MW PP (Doreen) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 145800
67 | Jangalia 33MW PP (Summit) | [10 empty] | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 447000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 493530
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 27 | 27 | 27 | 30 | 30 | 30 | 22 |  | 28 | 31 | 31 | 31 | 31 | 22 | 31 | 678240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 28 | 33 | 33 |  | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 740900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 782100
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 6 | [8 empty] | 3840
78 | Gazipur 52 MW PP | [26 empty] | 4584
79 | Kodda 150MW PP | [17 empty] | 45 |  | 84 | 50 | 16 | 10 | 0 |  |  | 165120
80 | Jamalpur 95 MW PP(Powerpac) | [11 empty] | 4 | 16 | 16 | 16 | 16 | 16 | 72 |  | 92 | 92 | 92 | 92 | 65 | 24 | 0 | 568320
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 0 |  |  |  |  | 5 |  | 0 | [6 empty] | 8808
| Gazipur 100 MW PP | 17 | 17 | 0 |  |  | 0 | 5 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 70 | 70 | 70 | 54 | 1466604
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.646 | 1.5 | 3.25 | 4.11 | 4.73 | 2.82 | 4.31 | 3.4 | 2.5 | 0.5 | 0 | 0 | [8 empty] | 27840
| Jodiac Power | [9 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 |  | 54 | 54 | 54 | 54 | 51 | 22 | 0 | 439664
| Karnaphuli Power Ltd. | [17 empty] | 20 |  | 51 | 34 | [5 empty] | 105381
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 7 | [8 empty] | 9600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 70 | 70 | 70 | 50 | 50 | 50 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 2014440
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 386928
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 13 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 402372
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [9 empty] | 5 | 24 | 26 | 25 | 25 | 25 |  | 8 | 31 |  | 11 | [6 empty] | 186720
96 | Chattogram 108 MW PP (ECPV) | 60 | 64 | 44 | 44 | 44 | 44 | 44 | 44 | 84 | 96 | 95 | 96 | 95 | 94 | 93 | 90 | 90 | 90 |  | 95 | 97 | 97 | 98 | 98 | 97 | 97 | 1920960
97 | Katpotti 52 MW PP (Sinha) | 30 | 24 | 24 | 12 | 12 | 12 | 12 | 13 | 39 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 48 | 47 | 47 | 18 | 18 | 6 | 6 | 775200
98 | Bosila 108MW PP(CLC) | 40 | 0 | [15 empty] | 70 | [8 empty] | 82560
99 | Madanganj-55 MW PP(Summit) | [8 empty] | 0 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 15 |  | 0 | [6 empty] | 287334
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 55 |  | 17 | 17 | [5 empty] | 227100
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 130 | 130 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2760815
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 0.8 | 1.7 | 2.1 | 2.4 | 2.4 | 2.2 | 1.4 | 1.3 | 0.5 | 0 | 0 | [8 empty] | 13800
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 53 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 159480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 30 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 21 | 62 | 70 | 70 | 70 | 93 | 182 |  | 200 | 200 | 200 | 200 | 200 | 200 | 140 | 1903200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 0 | 36 | 100 | 100 | 100 | 86 | 70 | 70 | 70 | 77 |  | 63 | 24 | 27 | 0 |  |  |  | 813600
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | 0 |  |  |  |  | 40 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 1413120
116 | Chandpur 200MW (Desh energy) | [10 empty] | 12 | 40 | 70 | 40 | 34 | 34 | 42 | 105 |  | 65 | 52 | 52 | 40 | 0 |  |  | 576480
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 8363
118 | Bibiyana-III 400 MW CCPP | 138 | 139 | 137 | 140 | 140 | 138 | 140 | 139 | 140 | 140 | 141 | 138 | 140 | 142 | 139 | 140 | 139 | 0 |  | 0 | 140 | 140 | 140 | 140 | 140 | 138 | 3043000
| Jamalpur 115 MW PP (United) | [19 empty] | 7 | [6 empty] | 30000
| Anwara 300 MW PP (United) | [17 empty] | 16 |  | 16 | [6 empty] | 27600
120 | Eastern Zone Total | 4705 | 4524 | 4392 | 4240 | 4101 | 4132.06 | 4179.016 | 4345.3 | 4626.95 | 4695.21 | 5103.13 | 5337.22 | 5481.51 | 5306.5 | 5299.2 | 5225.8 | 5185 | 6431 |  | 6453 | 6498 | 6394 | 6210 | 5764 | 5493 | 5181 | 125429252
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 7 | 16 |  | 16 | [6 empty] | 39360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 19 | 39 |  | 0 | [6 empty] | 63360
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 17 | 53 |  | 53 | 35 | 35 | 35 | 17 | 0 |  | 216000
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | [6 empty] | 32520
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 63 | 23 | 12 | 11 | 11 | 11 | 12 | 12 | 11 | 11 | 13 | 12 | 12 | 13 | 13 | 12 | 13 | 21 |  | 88 | 92 | 92 | 95 | 94 | 95 | 95 | 872361
| Bhola 225 MW CCPP | 171 | 171 | 171 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 173 | 150 | 150 | 173 | 149 | 151 | 154 |  | 154 | 151 | 172 | 172 | 164 | 150 | 167 | 4070135
140 | Bhola 33 MW PP (Venture) | 24 | 22 | 21 | 21 | 21 | 20 | 19 | 18 | 17 | 18 | 19 | 20 | 20 | 20 | 21 | 13 | 22 | 27 |  | 27 | 28 | 27 | 26 | 27 | 26 | 25 | 508900
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 32 | 32 | 32 | 0 | 218625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [11 empty] | 18 | 0 |  |  |  | 39 | 90 |  | 90 | 75 | 75 | 59 | 36 | 17 | 0 | 399600
146 | Bheramara HVDC | 820 | 724 | 723 | 723 | 723 | 723 | 723 | 723 | 723 | 930 | 929 | 929 | 930 | 929 | 930 | 929 | 929 | 929 |  | 929 | 929 | 929 | 929 | 929 | 930 | 931 | 20512000
147 | Bheramara 360 MW CCPP | 310 | 305 | 310 | 310 | 315 | 310 | 335 | 350 | 305 | 310 | 325 | 310 | 310 | 310 | 325 | 305 | 305 | 310 |  | 305 | 305 | 305 | 310 | 310 | 310 | 310 | 7830720
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 290 | 290 | 291 | 290 | 290 | 289 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7013300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 60 | 60 | 60 | 50 | 50 | 50 | 50 | 60 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1334000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 189 | 184 | 170 | 161 | 164 | 170 | 171 | 175 | 184 | 195 | 175 | 184 | 178 | 172 | 180 | 173 | 150 | 165 |  | 193 | 192 | 193 | 187 | 178 | 172 | 171 | 4533509
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 166 | 168 | 170 | 169 | 172 | 172 | 172 | 167 | 173 | 173 | 168 | 168 | 168 | 161 | 160 | 165 | 167 | 147 |  | 147 | 153 | 150 | 149 | 146 | 163 | 168 | 4115900
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | [12 empty] | 0 | 0
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 185 | 172 | 166 | 171 | 175 | 179 | 175 | 174 | 171 | 170 | 189 | 168 | 162 | 174 | 171 | 176 | 168 |  | 197 | 196 | 196 | 181 | 181 | 170 | 168 | 4474382
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 342 | 302 | 302 | 303 | 254 | 253 | 369 | 370 | 371 | 370 | 379 | 419 | 425 | 389 | 398 | 396 | 357 | 417 |  | 408 | 395 | 395 | 369 | 369 | 369 | 368 | 8641727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | [16 empty] | 22 |  | 22 | 0 | 0 | 22 | 22 | 21 |  | 101280
163 | Bogura 20 MW PP (Energyprima) | 0 | [16 empty] | 3 |  | 11 | 13 | 13 | 14 | 14 | 13 |  | 79488
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 188928
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 25 | 25 | 25 | 25 | 0 |  |  | 147230
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 6377
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 7200
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 51 |  | 0 | 0 | [5 empty] | 57936
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 40 |  | 35 | 35 | [5 empty] | 120000
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 15 | 0 | [5 empty] | 13000
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 109 |  | 104 | 113 | 113 | 83 | 19 | 0 |  | 432960
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.5 | 2.2 | 3.5 | 4.8 | 5.5 | 5.5 | 5.1 | 4.3 | 2.8 | 1.2 | 0.1 | [9 empty] | 35148
178
178