## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-10 | Sunday
|  | Date (day): | 2019-11-10 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11823.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14292 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-09 | 2019-11-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 101 | 150 | 100 | 100
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 380 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 348 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 357 | 322 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 90 | 60 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 285 | 235 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 2 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 24 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 26 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 30 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 16 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 88 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2130 | 2387 | 3923 | 4372 | 706 | 643
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0.7 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 18 | 20 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 77 | 87 | 87 | 143 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 90 | 149 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 90 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 10 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 16 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 40 | 15 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 91 | 71 | 50 | 98 |  | 10 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1.8 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 720.5 | 703 | 1240 | 1433 | 393 | 333
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 80 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 180 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 365 | 320 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 310 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 33 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 48 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 43 | 16 | 16 | 152 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 35 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 84 | 80 | 90 |  | 73 | Machine Problem
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 1 | 70 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 13 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 6 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 122 | 115 | 149
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 15 | 22 | 22
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1364 | 1421 | 1692 | 2167 | 450 | 97
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 157 | 143 | 170 | 200 | 2 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 16 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 177.2 | 279 | 408.6 | 632 | 2 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 0 | 30
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 312 | 286 | 300 | 300
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 20 | 49 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 1 | 77 | 77 | 77 |  | 9 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 20 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 6 | 32 | 32 | 36 |  | 14 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 85 | 217 | 226 | 226 |  | 174
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 994 | 1378 | 1465 | 1499 | 0 | 349
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 443 | 443 | 450 | 450
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 13 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 310 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 36 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 793 | 855 | 945 | 1676 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 22 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 145 | 123 | 140 | 140
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 52 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 173 | 197 | 338 | 408 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 30 | 60 | 60 |  | 71
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Machine problem.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 48
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 201 | 183 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Under S/D
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 203 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 406 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 3 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 3 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 26 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 806 | 1066 | 1401 | 1668 | 320 | 79
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 34 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 152.8 | 183 | 411 | 437 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 7310.5 | 8469 | 11823.6 | 14292 | 1871 | 1586
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6860.7692 | 7948 | 11096.2301 | 13412.7779
A. |  | 2019-11-09 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8469 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5475 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8469 | MW
3 | Day peak Generation : |  |  | 7310.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7948 | MW
4 | Evening peak Generation : |  |  | 8469 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 167.1497 | MKWHr | By Solar | 0.043296 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 139.3257 | MKWHr |  | By Oil: | 8.8022 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.6816 | MKWHr |  | By Hydro: | 1.757 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1871 | MW | Dhaka | 3082 | 3082 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1586 | MW | Chittagong | 805 | 805 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3457 | MW | Khulna | 878 | 878 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1090.03 | MMCFD |  |  | Rajshahi | 812 | 812 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 126659947.586 | ii) Oil : | Taka | 85860989.51 | Comilla | 705 | 705 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15057744 | Total | Taka | 227578681.096 | Mymensingh | 589 | 589 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.4775 | MKWHr. | Sylhet | 348 | 348 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -256 | MW (E to W) at | 19:00 | hrs | Barisal | 185 | 185 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -368 | MW at | 18:00 | hrs | Rangpur | 544 | 544 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.7° C |  |  | Total | 7948 | 7948 |  | 0
B. |  | 2019-11-10 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14292 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6500 | MW
4 | Reserve(Generation end) |  |  |  | 5792 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 167.7615 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5021 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.9229 | MKWHr. | ii) HVDC Flow at Peak Time |  | 443 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.617 | MKWHr. | iii) Maximum HVDC Flow : |  | 621 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.2 | 101.24 |  | (b) Today: | 101.2 |  | (c) Rule Curve: |  | 108.1
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 350 | 270 |  | 0 | 360 | 0 | 0 | 0 | 0 | 200 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 260 | 250 | 167 | 8 | 89 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 196 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 274 | 40 | 1 | 5 | 0 | 0 | 10 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 621 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 13 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 155 | 0 | 164 | 0 | 13 | 0 | 175 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4228 | 2215 | 6443 | 3901 | 621 | 1495 | 105 | 150 | 75 | 0 | 96 | 0 | 0 | 101.24
2:00 | 35 | 0 | 101 | 0 | 230 | 0 | 0 | 350 | 270 |  | 0 | 360 | 0 | 0 | 0 | 0 | 200 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 260 | 250 | 160 | 8 | 85 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 92 | 207 | 0 | 0 | 0 | 59 | 0 | 5 | 5 | 100 | 268 | 40 | 1 | 5 | 0 | 0 | 10 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 445 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 12 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 159 | 0 | 0 | 0 | 12 | 0 | 175 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4232 | 1856 | 6088 | 3716 | 445 | 1505 | 105 | 150 | 75 | 0 | 92 | 0 | 0 | 101.24
3:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 349 | 270 |  | 0 | 360 | 0 | 0 | 0 | 0 | 170 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 260 | 250 | 160 | 8 | 80 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 92 | 210 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 239 | 40 | 1 | 5 | 0 | 0 | 8 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 445 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 10 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 156 | 0 | 0 | 0 | 12 | 0 | 176 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4124 | 1795 | 5919 | 3621 | 445 | 1431 | 105 | 150 | 75 | 0 | 92 | 0 | 0 | 101.24
4:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 349 | 250 |  | 0 | 320 | 0 | 0 | 0 | 0 | 170 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 265 | 255 | 169 | 8 | 85 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 90 | 105 | 0 | 0 | 0 | 60 | 0 | 5 | 5 | 100 | 237 | 40 | 1 | 5 | 0 | 0 | 7 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 68 | 0 | 0 | 0 | 0 |  | 445 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 157 | 0 | 0 | 0 | 12 | 0 | 164 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3910 | 1704 | 5614 | 3405 | 445 | 1381 | 68 | 150 | 75 | 0 | 90 | 0 | 0 | 101.24
5:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 356 | 250 |  | 0 | 320 | 0 | 0 | 0 | 0 | 170 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 101 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 280 | 265 | 177 | 8 | 90 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 90 | 106 | 0 | 0 | 0 | 40 | 0 | 5 | 5 | 100 | 237 | 40 | 1 | 5 | 0 | 0 | 5 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 445 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 166 | 0 | 0 | 0 | 12 | 0 | 178 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3910 | 1565 | 5475 | 3353 | 445 | 1345 | 17 | 150 | 75 | 0 | 90 | 0 | 0 | 101.24
6:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 375 | 250 |  | 0 | 320 | 0 | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 280 | 270 | 178 | 8 | 90 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 88 | 106 | 0 | 0 | 0 | 40 | 0 | 5 | 5 | 100 | 235 | 54 | 1 | 5 | 0 | 0 | 10 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 445 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 174 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4007 | 1613 | 5620 | 3499 | 445 | 1363 | 0 | 150 | 75 | 0 | 88 | 0 | 0 | 101.24
7:00 | 35 | 0 | 100 | 0 | 230 | 0 | 0 | 383 | 280 |  | 0 | 350 | 0 | 0 | 0 | 0 | 230 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 290 | 275 | 182 | 8 | 90 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 106 | 0 | 0 | 0.1 | 40 | 0 | 5 | 5 | 100 | 236 | 55 | 1 | 5 | 0 | 0 | 7 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 |  | 446 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 176 | 0 | 0 | 0 | 12 | 0 | 186 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 |  | 4179.8 | 1690.4 | 5870.2 | 3655 | 446 | 1460 | 0 | 150 | 75 | 0 | 80 | 4.2 | 0 | 101.24
8:00 | 35 | 0 | 101 | 0 | 250 | 0 | 0 | 382 | 300 |  | 0 | 390 | 0 | 0 | 0 | 0 | 255 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 80 | 0 | 0 | 300 | 285 | 201 | 8 | 90 | 37 | 5 | 0 | 7 | 0 | 0 | 0 | 19 | 0 | 0 | 10 | 86 | 157 | 0 | 22 | 0.1 | 38 | 0 | 5 | 5 | 100 | 237 | 55 | 1 | 5 | 0 | 0 | 7 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 | 85 | 0 | 0 | 3 | 1.1 | 0 | 0 | 0 |  | 446 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 12 | 0 | 190 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 |  | 4432 | 1802.5 | 6234.5 | 3899 | 446 | 1569 | 3 | 150 | 75 | 0 | 86 | 6.5 | 0 | 101.23
9:00 | 35 | 0 | 101 | 0 | 320 | 0 | 0 | 373 | 332 |  | 0 | 390 | 0 | 0 | 0 | 0 | 278 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 25 | 0 | 0 | 35 | 40 | 100 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 13 | 80 | 0 | 0 | 260 | 250 | 190 | 8 | 83 | 37 | 45 | 0 | 7 | 0 | 0 | 0 | 19 | 0 | 15 | 10 | 92 | 159 | 0 | 0 | 0.3 | 40 | 0 | 5 | 5 | 130 | 300 | 55 | 1 | 20 | 0 | 0 | 7 | 0 | 305 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 7 | 2.1 | 0 | 0 | 0 | 85 | 0 | 52 | 51 | 1.2 | 0 | 0 | 0 |  | 443 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 191 | 0 | 0 | 0 | 12 | 0 | 202 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 |  | 4727.6 | 1930.6 | 6658.2 | 4042 | 443 | 1712 | 137 | 150 | 75 | 0 | 92 | 7.2 | 0 | 101.23
10:00 | 35 | 0 | 101 | 0 | 320 | 0 | 0 | 363 | 361 |  | 0 | 390 | 0 | 0 | 0 | 0 | 284 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 26 | 29 | 0 | 0 | 34 | 40 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 75 | 1 | 0 | 19 | 9 | 100 | 0 | 0 | 320 | 250 | 180 | 8 | 80 | 37 | 52 | 0 | 7 | 0 | 0 | 0 | 19 | 6 | 33 | 14 | 94 | 165 | 0 | 22 | 0.3 | 40 | 0 | 5 | 5 | 163 | 293 | 65 | 1 | 20 | 0 | 0 | 6 | 0 | 305 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 17 | 0 | 29 | 0 | 0 | 85 | 0 | 52 | 105 | 1.8 | 0 | 0 | 0 |  | 443 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 189 | 0 | 0 | 0 | 12 | 0 | 201 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4945.1 | 1886.2 | 6831.3 | 3964 | 443 | 1791 | 309 | 150 | 74 | 0 | 94 | 6.3 | 0 | 101.23
11:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 357 | 359 |  | 0 | 390 | 0 | 0 | 0 | 0 | 284 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 29 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 90 | 58 | 15 | 17 | 7 | 100 | 0 | 0 | 340 | 260 | 192 | 8 | 87 | 37 | 50 | 0 | 7 | 0 | 0 | 0 | 19 | 0 | 33 | 14 | 106 | 180 | 0 | 22 | 0.4 | 40 | 0 | 5 | 5 | 130 | 301 | 65 | 1 | 20 | 0 | 0 | 6 | 0 | 270 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 85 | 0 | 52 | 105 | 2.1 | 0 | 9 | 0 |  | 443 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 186 | 0 | 0 | 0 | 12 | 0 | 202 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 |  | 5081.5 | 1874.4 | 6955.9 | 4039 | 443 | 1684 | 453 | 150 | 75 | 0 | 106 | 5.9 | 0 | 0
12:00 | 35 | 0 | 101 | 0 | 320 | 0 | 0 | 375 | 357 |  | 0 | 390 | 0 | 0 | 0 | 0 | 285 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 90 | 0 |  | 0 | 0 | 0 | 90 | 91 | 18 | 17 | 10 | 100 | 0 | 0 | 365 | 320 | 199 | 8 | 85 | 37 | 50 | 0 | 7 | 0 | 0 | 0 | 19 | 6 | 33 | 14 | 120 | 157 | 0 | 20 | 0.2 | 40 | 0 | 5 | 20 | 130 | 312 | 65 | 1 | 20 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.7 | 100 | 1 | 0 | 85 | 0 | 52 | 105 | 1.8 | 0 | 17 | 0 |  | 443 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 150 | 0 | 0 | 201 | 0 | 0 | 0 | 13 | 0 | 197 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 5385.7 | 1924.8 | 7310.5 | 4281 | 443 | 1745 | 491 | 150 | 75 | 0 | 120 | 5.5 | 0 | 0
13:00 | 35 | 0 | 98 | 0 | 320 | 0 | 0 | 390 | 359 |  | 0 | 390 | 0 | 0 | 0 | 0 | 280 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 26 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 90 | 0 |  | 0 | 0 | 0 | 90 | 91 | 18 | 16 | 10 | 100 | 0 | 0 | 335 | 365 | 183 | 8 | 84 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 19 | 6 | 33 | 14 | 124 | 153 | 0 | 22 | 0.2 | 40 | 0 | 5 | 40 | 130 | 301 | 65 | 1 | 40 | 0 | 0 | 22 | 0 | 315 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | 0 | 85 | 0 | 52 | 105 | 0.9 | 0 | 17 | 0 |  | 443 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 5 | 0 | 0 | 150 | 0 | 0 | 202 | 0 | 0 | 0 | 54 | 0 | 197 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 |  | 5445.1 | 1985.4 | 7430.5 | 4239 | 443 | 1898 | 497 | 150 | 75 | 0 | 124 | 4.5 | 0 | 0
14:00 | 35 | 0 | 97 | 0 | 320 | 0 | 0 | 355 | 302 |  | 0 | 360 | 0 | 0 | 0 | 0 | 278 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 115 | 0 |  | 0 | 0 | 0 | 90 | 91 | 18 | 17 | 13 | 100 | 0 | 0 | 320 | 320 | 180 | 8 | 87 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 19 | 6 | 33 | 14 | 132 | 144 | 0 | 22 | 0.2 | 40 | 0 | 5 | 49 | 130 | 302 | 67 | 5 | 40 | 0 | 0 | 22 | 0 | 280 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 3 | 0 | 85 | 0 | 52 | 105 | 1.1 | 0 | 0 | 0 |  | 442 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 5 | 0 | 0 | 150 | 0 | 0 | 184 | 0 | 0 | 0 | 54 | 0 | 192 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 5193.3 | 1930 | 7123.3 | 4149 | 442 | 1754 | 417 | 150 | 75 | 0 | 132 | 4.3 | 0 | 0
15:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 361 | 302 |  | 0 | 360 | 0 | 0 | 0 | 0 | 258 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 16 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 100 | 91 | 18 | 16 | 7 | 100 | 0 | 0 | 320 | 320 | 179 | 8 | 81 | 37 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 33 | 14 | 124 | 143 | 0 | 22 | 0.1 | 40 | 0 | 7 | 49 | 130 | 292 | 65 | 5 | 40 | 0 | 0 | 22 | 0 | 300 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 6 | 0 | 75 | 0 | 52 | 105 | 0.6 | 0 | 0 | 0 |  | 443 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 190 | 0 | 0 | 0 | 52 | 0 | 203 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 |  | 5165.7 | 1898.2 | 7063.9 | 4072 | 443 | 1764 | 434 | 149 | 75 | 0 | 124 | 2.9 | 0 | 0
16:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 372 | 301 |  | 0 | 360 | 0 | 0 | 0 | 0 | 247 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 100 | 65 | 0 | 16 | 7 | 100 | 0 | 0 | 350 | 350 | 201 | 8 | 91 | 37 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 8 | 14 | 120 | 143 | 0 | 22 | 0.1 | 40 | 0 | 5 | 10 | 100 | 314 | 40 | 5 | 10 | 0 | 0 | 12 | 0 | 310 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 0 | 84 | 0 | 52 | 105 | 0.1 | 0 | 0 | 0 |  | 443 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 194 | 0 | 0 | 0 | 13 | 0 | 210 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 12 |  | 5052.2 | 1945.7 | 6997.9 | 4243 | 443 | 1583 | 384 | 149 | 75 | 0 | 120 | 0.9 | 0 | 0
17:00 | 35 | 0 | 140 | 0 | 370 | 0 | 0 | 400 | 322 |  | 0 | 410 | 0 | 0 | 0 | 0 | 291 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 0 | 17 | 13 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 68 | 0 | 16 | 35 | 100 | 0 | 0 | 325 | 320 | 191 | 8 | 89 | 37 | 10 | 0 | 7 | 0 | 0 | 0 | 0 | 11 | 8 | 0 | 132 | 143 | 0 | 22 | 0 | 60 | 0 | 5 | 18 | 130 | 292 | 65 | 5 | 10 | 0 | 0 | 24 | 0 | 320 | 0 | 0 | 0 | 14 | 0 | 0 | 12 | 0 | 0 | 0 | 20 | 14 | 1 | 84 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 443 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 205 | 0 | 0 | 0 | 12 | 0 | 212 | 0 | 407 | 0 | 0 | 2 | 0 | 30 | 0 | 0.1 | 0 |  | 5410 | 1988.1 | 7398.1 | 4352 | 443 | 1773 | 474 | 149 | 75 | 0 | 132 | 0.1 | 0 | 0
18:00 | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 349 | 322 |  | 0 | 410 | 0 | 13 | 0 | 5 | 233 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 17 | 55 | 55 | 22 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 17 | 90 | 95 | 8 | 16 | 40 | 100 | 0 | 0 | 320 | 310 | 180 | 43 | 80 | 37 | 48 | 0 | 35 | 0 | 0 | 5 | 0 | 11 | 33 | 15 | 146 | 144 | 16 | 22 | 0 | 60 | 0 | 53 | 49 | 163 | 284 | 67 | 77 | 40 | 0 | 17 | 31 | 0 | 290 | 16 | 11 | 0 | 40 | 0 | 0 | 100 | 0 | 7 | 0 | 60 | 72 | 10 | 119 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 443 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 123 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 26 | 50 | 0 | 0 | 0 | 11 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 0 | 0 | 53 | 0 | 200 | 0 | 406 | 35 | 0 | 30 | 36 | 34 | 0 | 0 | 0 |  | 6192 | 2212 | 8404 | 4265 | 443 | 2116 | 1095 | 149 | 77 | 113 | 146 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 348 | 322 |  | 0 | 420 | 0 | 0 | 0 | 15 | 235 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 47 | 17 | 35 | 35 | 22 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 17 | 90 | 71 | 18 | 16 | 40 | 100 | 0 | 0 | 320 | 310 | 180 | 43 | 84 | 37 | 48 | 0 | 35 | 0 | 0 | 0 | 13 | 11 | 33 | 15 | 122 | 143 | 16 | 20 | 0 | 60 | 0 | 53 | 49 | 163 | 286 | 67 | 77 | 40 | 0 | 17 | 32 | 0 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 100 | 0 | 16 | 0 | 10 | 70 | 0 | 217 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 443 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 123 | 22 | 0 | 0 | 0 | 30 | 50 | 0 | 26 | 50 | 0 | 0 | 0 | 36 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 183 | 0 | 0 | 0 | 52 | 0 | 203 | 0 | 406 | 53 | 0 | 35 | 36 | 34 | 0 | 0 | 0 |  | 6168 | 2301 | 8469 | 4413 | 443 | 2128 | 995 | 149 | 77 | 142 | 122 | 0 | 0 | 0
19:30 | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 346 | 282 |  | 0 | 370 | 0 | 0 | 0 | 0 | 238 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 17 | 35 | 35 | 22 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 90 | 51 | 18 | 16 | 40 | 100 | 0 | 0 | 330 | 320 | 194 | 43 | 88 | 37 | 48 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 130 | 144 | 16 | 22 | 0 | 60 | 0 | 53 | 49 | 100 | 300 | 67 | 77 | 40 | 0 | 17 | 32 | 0 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 52 | 0 | 225 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 443 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 144 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 26 | 50 | 0 | 0 | 0 | 35 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 188 | 0 | 0 | 0 | 52 | 0 | 210 | 0 | 421 | 53 | 0 | 35 | 36 | 35 | 0 | 0 | 0 |  | 5896 | 2329 | 8225 | 4532 | 443 | 2010 | 810 | 149 | 77 | 74 | 130 | 0 | 0 | 0
20:00 | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 356 | 283 |  | 0 | 370 | 0 | 0 | 0 | 0 | 240 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 17 | 17 | 0 | 22 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 60 | 51 | 18 | 16 | 40 | 100 | 0 | 0 | 330 | 320 | 190 | 43 | 88 | 37 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 130 | 140 | 16 | 22 | 0 | 60 | 0 | 53 | 49 | 100 | 298 | 67 | 77 | 40 | 0 | 17 | 32 | 0 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 52 | 0 | 225 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 442 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 9 | 0 | 0 | 0 | 40 | 0 | 0 | 26 | 50 | 0 | 0 | 0 | 34 | 21 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 191 | 0 | 0 | 0 | 53 | 0 | 207 | 0 | 431 | 53 | 0 | 35 | 35 | 35 | 0 | 0 | 0 |  | 5825 | 2305 | 8130 | 4529 | 442 | 2000 | 743 | 149 | 77 | 60 | 130 | 0 | 0 | 0
21:00 | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 348 | 284 |  | 0 | 370 | 0 | 0 | 0 | 0 | 251 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 17 | 0 | 0 | 22 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 10 | 25 | 16 | 0 | 40 | 100 | 0 | 0 | 320 | 310 | 181 | 43 | 81 | 37 | 50 | 0 | 35 | 0 | 0 | 0 | 18 | 11 | 33 | 15 | 122 | 140 | 16 | 22 | 0 | 60 | 0 | 53 | 49 | 100 | 290 | 67 | 77 | 40 | 0 | 17 | 32 | 0 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 45 | 0 | 226 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 442 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 21 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 0 | 0 | 52 | 0 | 205 | 0 | 425 | 35 | 0 | 35 | 36 | 35 | 0 | 0 | 0 |  | 5649 | 2184 | 7833 | 4432 | 442 | 1987 | 624 | 149 | 77 | 0 | 122 | 0 | 0 | 0
22:00 | 35 | 0 | 150 | 0 | 354 | 0 | 0 | 346 | 286 |  | 0 | 370 | 0 | 0 | 0 | 0 | 273 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 10 | 6 | 5 | 16 | 40 | 100 | 0 | 0 | 320 | 265 | 180 | 43 | 82 | 37 | 49 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 120 | 143 | 0 | 22 | 0 | 60 | 0 | 53 | 49 | 100 | 245 | 67 | 30 | 40 | 0 | 17 | 32 | 0 | 260 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 45 | 0 | 225 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 443 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 5 | 0 | 0 | 149 | 0 | 0 | 178 | 0 | 0 | 0 | 52 | 0 | 195 | 0 | 391 | 17 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 5250 | 1985 | 7235 | 4296 | 443 | 1873 | 277 | 149 | 77 | 0 | 120 | 0 | 0 | 101.36
23:00 | 35 | 0 | 150 | 0 | 320 | 0 | 0 | 346 | 284 |  | 0 | 330 | 0 | 0 | 0 | 0 | 266 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 0 | 320 | 265 | 186 | 43 | 83 | 37 | 48 | 0 | 7 | 0 | 0 | 0 | 19 | 0 | 8 | 15 | 104 | 148 | 0 | 22 | 0 | 60 | 0 | 5 | 49 | 100 | 247 | 40 | 10 | 40 | 0 | 0 | 6 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 443 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 156 | 0 | 0 | 0 | 27 | 0 | 164 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4794 | 1884 | 6678 | 4153 | 443 | 1720 | 34 | 149 | 75 | 0 | 104 | 0 | 0 | 101.35
24:00 | 35 | 0 | 100 | 0 | 320 | 0 | 0 | 347 | 284 |  | 0 | 330 | 0 | 0 | 0 | 0 | 266 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 26 | 30 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 100 | 0 | 0 | 320 | 260 | 170 | 8 | 87 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 102 | 162 | 0 | 22 | 0 | 60 | 0 | 5 | 5 | 100 | 238 | 40 | 10 | 5 | 0 | 0 | 6 | 0 | 295 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 443 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 158 | 0 | 0 | 0 | 12 | 0 | 165 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4472 | 1845 | 6317 | 4031 | 443 | 1517 | 0 | 149 | 75 | 0 | 102 | 0 | 0 | 0
KWH | 832000 | 0 | 2731000 | 0 | 7244400 | 0 | 0 | 8732670 | 7191000 |  | 0 | 8818125 | 0 | 18240 | 0 | 24829 | 5882984 | 0 | 1866000 | 0 | 0 | 0 | 0 | 0 | 56640 | 0 | 330000 | 80280 | 126517 | 128083 | 84996 | 600000 | 545940 | 716700 | 712300 | 0 | 0 | 792960 | 964000 | 2600000 | 0 | 0 | 0 | 0 | 2792686 | 0 |  | 0 | 0 | 27555 | 1007880 | 845760 | 156480 | 395184 | 762240 | 2273780 | 0 | 0 | 7684600 | 7055000 | 4440000 | 418181 | 2049470 | 599184 | 764160 | 0 | 338584 | 0 | 0 | 6475 | 218088 | 104400 | 411400 | 340590 | 2616960 | 3526160 | 67200 | 317808 | 0 | 1173000 | 0 | 373200 | 593496 | 2990397 | 6309000 | 1319808 | 438720 | 585000 | 0 | 37000 | 355700 | 0 | 7405700 | 144792 | 66912 | 0 | 256964 | 0 | 0 | 477600 | 0 | 60480 | 15930 | 476160 | 290440 | 0 | 2837000 | 0 | 788844 | 1955409 | 0 | 0 | 61213 | 0 |  | 10922909 | 0 | 7513920 | 0 | 0 | 0 | 0 | 0 | 25920 | 0 | 0 | 3630404 | 309400 | 0 | 0 | 223000 | 204000 | 75187 | 0 | 79280 | 217690 | 0 | 0 | 0 | 88938 | 178560 | 151092 | 138078 | 0 | 0 | 3681600 | 0 | 0 | 4576145 | 375073 | 0 | 0 | 643222 | 0 | 4850936 | 0 | 9227600 | 186720 | 0 | 148032 | 187632 | 160320 | 0 | 27366 | 14400 |  | 119312254 | 47837424 | 167149678 | 97781335 | 10922909 | 41544377 | 8130288 | 3681600 | 1756960 | 671953 | 2616960 | 43296 | 0
Fuel Cost | 931840 | 0 | 2922170 | 0 | 5360856 | 0 | 0 | 6287522.4 | 5465160 |  | 0 | 7054500 | 0 | 186048 | 0 | 254745.54 | 7294900.16 | 0 | 2332500 | 0 | 0 | 0 | 0 | 0 | 515424 | 0 | 3088800 | 769885.2 | 1206972.18 | 1275706.68 | 63747 | 450000 | 0 | 0 | 0 | 0 | 0 | 206169.6 | 250640 | 3978000 | 0 | 0 | 0 | 0 | 3546711.22 | 0 |  | 0 | 0 | 289051.95 | 10371085.2 | 8043177.6 | 1464652.8 | 363569.28 | 2119027.2 | 2387469 | 0 | 0 | 5686604 | 5926200 | 4084800 | 409817.38 | 2725795.1 | 491330.88 | 787084.8 | 0 | 484175.12 | 0 | 0 | 60865 | 222449.76 | 78300 | 777546 | 255442.5 | 18057024 | 2891451.2 | 639072 | 324164.16 | 0 | 1595280 | 0 | 507552 | 741870 | 3708092.28 | 5804280 | 1966513.92 | 772147.2 | 649350 | 0 | 58830 | 416169 | 0 | 5258047 | 108594 | 50853.12 | 0 | 2690413.08 | 0 | 0 | 4594512 | 0 | 610243.2 | 183832.2 | 4437811.2 | 2724327.2 | 0 | 2666780 | 0 | 7028600.04 | 18478615.05 | 0 | 0 | 0 | 0 |  | 29491854.3 | 0 | 5860857.6 | 0 | 0 | 0 | 0 | 0 | 300672 | 0 | 0 | 2904323.2 | 479570 | 0 | 0 | 419240 | 383520 | 837583.18 | 0 | 784872 | 2257445.3 | 0 | 0 | 0 | 876039.3 | 196416 | 249301.8 | 104525.046 | 0 | 0 | 15057744 | 0 | 0 | 4027007.6 | 5779874.93 | 0 | 0 | 1022722.98 | 0 | 4268823.68 | 0 | 6736148 | 1766371.2 | 0 | 1358933.76 | 1671801.12 | 1497388.8 | 0 | 0 | 0 |  | 187435165.4 | 88333035.796 | 275768201.196 | 89602796.826 | 29491854.3 | 37057150.76 | 76992896.15 | 15057744 | 456809.6 | 8868093.36 | 18057024 | 183832.2 | 0
Yesterday Day Peak | 35 | 0 | 101 | 0 | 320 | 0 | 0 | 375 | 357 |  | 0 | 390 | 0 | 0 | 0 | 0 | 285 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 24 | 26 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 90 | 0 |  | 0 | 0 | 0 | 90 | 91 | 18 | 17 | 10 | 100 | 0 | 0 | 365 | 320 | 199 | 8 | 85 | 37 | 50 | 0 | 7 | 0 | 0 | 0 | 19 | 6 | 33 | 14 | 120 | 157 | 0 | 20 | 0.2 | 40 | 0 | 5 | 20 | 130 | 312 | 65 | 1 | 20 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.7 | 100 | 1 | 0 | 85 | 0 | 52 | 105 | 1.8 | 0 | 17 | 0 |  | 443 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 150 | 0 | 0 | 201 | 0 | 0 | 0 | 13 | 0 | 197 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 7310.5 | DayPeak
Yesterday Evening Peak | 35 | 0 | 150 | 0 | 380 | 0 | 0 | 348 | 322 | 0 | 0 | 420 | 0 | 0 | 0 | 15 | 235 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 47 | 17 | 35 | 35 | 22 | 25 | 24 | 26 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 17 | 90 | 71 | 18 | 16 | 40 | 100 | 0 | 0 | 320 | 310 | 180 | 43 | 84 | 37 | 48 | 0 | 35 | 0 | 0 | 0 | 13 | 11 | 33 | 15 | 122 | 143 | 16 | 20 | 0 | 60 | 0 | 53 | 49 | 163 | 286 | 67 | 77 | 40 | 0 | 17 | 32 | 0 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 100 | 0 | 16 | 0 | 10 | 70 | 0 | 217 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 443 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 123 | 22 | 0 | 0 | 0 | 30 | 50 | 0 | 26 | 50 | 0 | 0 | 0 | 36 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 183 | 0 | 0 | 0 | 52 | 0 | 203 | 0 | 406 | 53 | 0 | 35 | 36 | 34 | 0 | 0 | 0 |  | 8469 | EvPeak
Forecast for Evening | 35 | 0 | 100 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 37 | 50 | 110 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 98 | 50 | 19 | 25 | 100 | 0 | 0 | 360 | 360 | 225 | 16 | 90 | 37 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 149 | 200 | 95 | 22 | 0 | 60 | 30 | 51 | 44 | 163 | 300 | 66 | 77 | 40 | 0 | 20 | 36 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 226 | 115 | 88 | 105 | 0 | 300 | 54 | 110 |  | 450 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 140 | 33 | 110 | 30 | 0 | 60 | 50 | 48 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 100 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 100 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 37 | 50 | 110 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 20 | 19 | 15 | 80 | 0 | 0 | 360 | 360 | 225 | 16 | 80 | 33 | 55 | 0 | 30 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 115 | 170 | 0 | 22 | 1.6 | 60 | 0 | 51 | 44 | 163 | 300 | 66 | 77 | 40 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 226 | 115 | 88 | 105 | 5 | 230 | 54 | 50 |  | 450 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 140 | 33 | 70 | 0 | 0 | 60 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 220 | 0 | 0 | 240 | 251 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 8 | 25 | 0 | 0 | 35 | 40 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 295 | 300 | 180 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 86 | 128 | 0 | 0 | 0.2 | 0 | 0 | 5 | 5 | 100 | 260 | 5 | 10 | 5 | 0 | 0 | 7 | 0 | 315 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3.94 | 0 | 0 | 0 | 226 | 0 | 17 | 12 | 1.933 | 0 | 0 | 0 | 0 | 444 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5475 | 5:00
| Highest Generation |  | 8469 | 19:00
| Day Peak Generation |  | 7310.5 | 12:00
| Evening Peak Generation |  | 8469 | 19:00
| HVDC Max Flow |  | 621 | 1:00
| HVDC EvPeak Flow |  | 443 | 19:00
| Load factor L.F |  | 82.24%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7310.5 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5021 | MW
Evening Peak Generation : |  | 8469 | MW Hour : | 19:00 | Available Max Generation : |  | 14292 | MW
E.P. Demand (at gen end) : |  | 8469 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 8469 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5792 | MW
Total Gen. (MKWH) : |  | 167.1497 | System Load Factor : | 82.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -368 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-10
Actual : | 101.2 | Ft.(MSL) , | Rule curve : | 108.1 | Ft.( MSL )
Gas Consumed : | Total = | 1090.03 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 126659947.586
: |  | Coal : | 15057744 | Oil : | 85860989.51 | Total : | 227578681.096
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2984.5844 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1007.9395 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 901.8358 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 814.4429 |  |  | 0 | 0%
) | 0 | 0:00 | 736.2439 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 594.1052 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 341.1822 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 153.204 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 458.1604 |  |  | 0 | 0%
Total | 0 |  | 7991.6983 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1&2. | 9) Sirajganj unit-2
2) Sylhet-150 MW.
3) Ghorasal Unit-1,3 & 5
4) Raozan #2
5) Ashuganj unit-4 & 5
6) Chandpur CCPP ST
7)Sylhet 150 MW
8) Fenchuganj # 03 & 04
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sikalbaha 150 MW tripped at 09:28 due to cooling temperature high and was synchronized at 11:30.
b) Bogura(O)-Naogaon 132 kV Ckt-2 was shut down from 09:10 to 15:40 for A/M.
c) After maintenance Bibiyana #03 ST was synchronized at 17:47.
d) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 05:43 from both ends showing 67N gen trip at Sirajganj end & 67N trip
Circuit supervision relay at Ashuganj end and was switched on at 10:44.
e) Ashuganj 230/132 kV OTA-12 tripped at 05:43 showing E/F relay at 230 kV side & abnormal at 132 kV side.
f) Raozan #01 tripped at 06:55 due to Boiler tripping and was synchronized at 08:41.
g) Bagerhat-Bhandaria 132 kV Ckt tripped at 07:07 from both end showing dist Z1 from both end and was switched
on at 07:50(10/11/19).
h) Bogura-Mohasthangarh 132 kV Ckt-1 was under shut down since at 07:27 for red hot maintenance at B phase CT
connector of Bogura end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 832000 | #1 under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 2731000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7244400
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 348 | 8732670 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 322 | 7191000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8818125
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 18240 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 24829 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 84996
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 60 | 1866000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 235 | 5882984 | machine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 330000 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 80280 | Low demand.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 126517 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 128083 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 24 | 56640 | low demand
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1145940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 716700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 712300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 256964 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 16 | 60480 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 788844 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2387 | 47828992
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 15930
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 156480 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 77 | 1756960 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 149 | 2792686 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1955409
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 27555 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1007880 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 476160 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 395184
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 762240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 71 | 845760 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 0
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 61213 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 703 | 12853457
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2273780 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4440000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7684600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7055000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 599184 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 48 | 764160
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 43 | 418181 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 338584 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 84 | 2049470
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 70 | 290440 | Low demand.
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 218088
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 104400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2616960
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 411400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 6475 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 340590
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1421 | 29611312
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 143 | 3526160 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 317808
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 67200 | Low demand.
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 0
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 477600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 279 | 4388768
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1173000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 2990397
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 286 | 6309000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 373200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 593496
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 66912
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1319808 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 438720 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 585000 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 37000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 32 | 355700 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 144792
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7405700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 217 | 2837000 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0
| Sylhet Area Total |  |  |  | 1949 | 1378 | 24629725
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 443 | 10922909 | Low demand
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 13 | 25920 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 7513920 | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 186720 | Low demand.
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 36 | 187632 | Low demand
| Khulna Area Total |  |  |  | 2314 | 855 | 18837101
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 309400
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 123 | 3630404 | FGMO
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 52 | 643222 | Low demand
| Barisal Area Total |  |  |  | 462 | 197 | 4583026
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 30 | 204000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 223000 | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 75187
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 217690
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 183 | 4576145 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 203 | 4850936 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 406 | 9227600 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 88938
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 178560
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 151092
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 138078
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 26 | 79280 | Low demand.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 148032 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 14400 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1066 | 20172938
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3681600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 34 | 160320
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 27366
| Rangpur Area Total |  |  |  | 605 | 183 | 3869286
| Total |  |  |  | 19018 | 8469 | 166774605
| Eastern Grid Total |  |  |  | 13454 | 6168 | 119312254
| Western Grid Total |  |  |  | 5564 | 2301 | 47462351
| National Grid Total |  |  |  | 19018 | 8469 | 166774605
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-09
(a) ENTIRE EASTERN GRID : |  | 5529 | MW | (b) ENTIRE WESTERN GRID : |  | 2419 | MW
i) Dhaka area |  | 3082 | MW | i) Khulna area |  | 878 | MW
ii) Chittagong area |  | 805 | MW | ii) Rajshahi area |  | 812 | MW
iii) Comilla area |  | 705 | MW | iii) Barisal area |  | 185 | MW
iv) Mymensingh area |  | 589 | MW | iv) Rangpur area |  | 544 | MW
v) Sylhet area |  | 348 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7948 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 900 | Srimongal | 28 | 1800 | Bottail | 92 | 1800
Munsiganj | 81 | 2000 | Shahjibazar | 75 | 1930 | G.K Project | 34 | 1800
Sonargaon | 64 | 1700 | Fenchuganj | 23 | 1800 | Faridpur | 122 | 1830
Shyampur | 164 | 900 | Kulawara | 34 | 1830 | Madaripur | 58 | 1900
Bhulta | 161 | 1900 | Sylhet | 109 | 1800 | Sariatpur | 34 | 1900
Madanganj | 36 | 1830 | Chatak | 17 | 1900 | Gopalganj | 60 | 1800
Shitalakhya | 87 | 1200 | Sunamganj | 30 | 1800 | Bagerhat | 45 | 1700
Rahim steel | 10 | 600 | Biani Bazar | 39 | 1800 | Mongla | 26 | 100
Matuail | 86 | 1000 | Comilla (S) | 146 | 1800 | Satkhira | 42 | 1800
Ghorasal | 64 | 1830 | Comilla(N) | 77 | 2000 | Gallamari | 32 | 1830
Narsingdi | 90 | 100 | Chandpur | 68 | 2000 | Magura | 36 | 1800
Haripur (SBU) | 83 | 900 | Feni | 98 | 1930 | Norail | 20 | 1830
Ullon | 56 | 2000 | Chowmuhani | 116 | 1830 | Chuadanga | 58 | 1800
Hasnabad | 120 | 1400 | Ashuganj | 39 | 2100 | Barisal(N) | 32 | 1900
Magbazar | 84 | 1300 | Daudkandi | 90 | 1930 | Barisal (S) | 66 | 1830
Maniknagar | 84 | 1300 | B.Baria | 94 | 1800 | Patuakhali | 76 | 1900
Bangabhaban | 11 | 1300 | Ramganj | 54 | 1800 | Bhandaria | 26 | 2100
Narinda | 80 | 1400 | Madunaghat | 53 | 1200 | Borhan Uddin | 24 | 2200
Dhanmondi | 118 | 1300 | Hathazari | 74 | 1900 | Ishurdi | 44 | 1800
Lalbag | 75 | 1300 | Khulshi | 164 | 1100 | Ruppur Paromanobik | 1 | 100
Madartek | 48 | 1500 | Halishahar | 112 | 1400 | Natore | 78 | 1800
Mirpur | 84 | 1800 | Baraulia | 84 | 2400 | Bogra | 141 | 1800
Kalyanpur | 90 | 1800 | Sikalbaha | 17 | 1100 | Noagaon | 77 | 1900
Gulshan | 106 | 1300 | Dohazari | 72 | 100 | Rajshahi | 94 | 2000
Uttara | 43 | 1300 | Cox'sbazar | 68 | 2000 | Rajshahi New | 9 | 2000
Uttara New | 31 | 1830 | Chandraghona | 24 | 1830 | C.Nawabganj | 53 | 1930
Kamrangirchar | 64 | 1800 | Kaptai | 4 | 1700 | Amnura | 22 | 1800
Savar | 110 | 1200 | A. Khaer Stl. | 0 | 0 | Pabna | 69 | 1900
Bhasantec | 121 | 1800 | Bakulia | 85 | 1800 | Shahjadpur | 61 | 1900
Agargaon | 40 | 1800 | Julda | 17 | 900 | Serajganj | 59 | 1900
Satmosjid | 77 | 1800 | TK chemical | 12 | 100 | Niyamatpur | 41 | 1900
Tongi | 125 | 1100 | Modern Steel | 7 | 1200 | Joypurhat | 42 | 1900
Kabirpur | 161 | 1100 | Shahmirpur | 22 | 1200 | Sherpur(Bogura) | 32 | 1900
Basundhara | 84 | 1800 | Khagrachhari | 18 | 1800 | Mohastangor | 10 | 2000
Manikganj | 59 | 1930 | Matarbari | 23 | 1900 | Rangpur | 108 | 1800
Joydevpur | 158 | 1830 | Baroiar Hat | 18 | 1700 | Lalmonirhat | 41 | 1800
New Tongi | 89 | 1800 | Rangamati | 10 | 1700 | Saidpur | 85 | 1800
Korda | 189 | 1700 | Abul Khair 230 | 134 | 1200 | Purbasadipur | 75 | 1800
Dhamrai | 44 | 1800 | BSRM | 101 | 800 | Thakurgaon | 54 | 1900
Valuka | 82 | 1600 | GPH Ispat | 6.2 | 1300 | Palashbari | 79 | 1900
Tangail | 123 | 1830 | Goalpara | 20 | 1200 | Barapukuria | 40 | 1930
Mymensing | 147 | 1930 | Central s/s | 54 | 1200 | Panchagar | 36 | 1800
Kishorganj | 76 | 1900 | Noapara | 45 | 1930 | Joldhaka | 19 | 1830
Netrokona | 63 | 1800 | Jessore | 86 | 1800 | Kurigram | 34 | 1800
Jamalpur | 83 | 1830 | Benapol | 26 | 1830
Sherpur | 64 | 1800 | Jhenida | 72 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-09 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 389 | 19:00 | 379 | 18:30 | Kaliakoir | 370 | 5:00 | 358 | 12:00
Bheramara | 407 | 3:00 | 402 | 1:00 | Bhulta | 378 | 3:00 | 367 | 12:00
a f | 380 | 3:00 | 371 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
Ghorasal | 228 | 21:00 | 225 | 7:00 | Hathazari | 223 | 18:00 | 210 | 10:00
Ishurdi | 241 | 24:00 | 230 | 10:00 | Megnaghat | 221 | 18:00 | 217 | 9:00
Ashuganj | 230 | 2:00 | 225 | 24:00 | Fenchuganj | 235 | 18:00 | 229 | 11:00
Serajganj | 231 | 1:00 | 230 | 8:00 | Siddhirganj | 222 | 3:00 | 215 | 12:00
Baghabari | 238 | 5:00 | 233 | 17:00 | Maniknagar | 220 | 3:00 | 214 | 12:00
Barapukuria | 230 | 3:00 | 220 | 18:00 | Old Airport | 220 | 3:00 | 211 | 12:00
Bogra | 232 | 5:00 | 224 | 18:00 | Barisal | 234 | 3:00 | 222 | 12:00
Khulna South | 240 | 21:00 | 228 | 9:00 | AKSML | 219 | 18:00 | 206 | 10:00
Rampura | 221 | 3:00 | 217 | 12:00 | BSRM | 221 | 18:00 | 210 | 10:00
Haripur | 220 | 3:00 | 215 | 12:00 | Bibiyana | 232 | 18:00 | 226 | 12:00
Hasnabad | 219 | 6:00 | 213 | 16:00 | Bhulta | 223 | 19:30 | 216 | 12:00
Aminbazar | 220 | 4:00 | 212 | 12:00 | Ashuganj (S) | 231 | 19:00 | 225 | 11:00
Tongi | 216 | 18:30 | 207 | 11:00 | Kaliakoir | 224 | 3:00 | 213 | 16:00
Comilla (N) | 228 | 18:00 | 221 | 13:00 | GPH | 220 | 18:00 | 206 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 1800 | 129 | 1200 | Halishahar | 134 | 1800 | 123 | 1000
Munsiganj | 133 | 1800 | 127 | 1100 | Baraulia | 133 | 1800 | 123 | 800
Megnaghat | 130 | 400 | 127 | 1100 | Sikalbaha | 134 | 1800 | 122 | 800
Shyampur | 134 | 1900 | 129 | 1200 | Dohazari | 132 | 1800 | 116 | 100
Bhulta | 126 | 300 | 122 | 1200 | Cox'sbazar | 128 | 300 | 118 | 700
Madanganj | 132 | 1830 | 127 | 100 | Chandraghona | 133 | 1800 | 124 | 1000
Shitalakhya | 136 | 300 | 127 | 1200 | Kaptai | 132 | 1800 | 127 | 700
Rahim steal | 133 | 300 | 129 | 1200 | A. Khaer Stl. | 130 | 1700 | 124 | 400
Matuail | 132 | 1800 | 128 | 1000 | Bakulia | 132 | 1800 | 121 | 1000
Ghorasal | 135 | 100 | 134 | 1100 | Julda | 133 | 1800 | 123 | 1000
Narsinghdi | 132 | 600 | 129 | 1100 | TK Chemical | 132 | 1800 | 124 | 700
Haripur (SBU) | 133 | 400 | 129 | 1200 | Modern Steel | 133 | 1800 | 123 | 700
Ullon | 134 | 600 | 130 | 1400 | Shahmirpur | 134 | 1800 | 122 | 1000
Hasnabad | 135 | 600 | 130 | 1400 | Khagrachhari | 131 | 1800 | 123 | 1000
Magbazar | 136 | 400 | 123 | 1200 | Matarbari | 130 | 1400 | 118 | 100
Maniknagar | 135 | 600 | 130 | 1600 | Baroiar Hat | 130 | 1800 | 123 | 1000
Bangabhaban | 135 | 600 | 130 | 1600 | Rangamati | 132 | 1800 | 124 | 1000
Narinda | 135 | 600 | 130 | 1600 | Goalpara | 140 | 400 | 127 | 1200
Dhanmondi | 134 | 600 | 130 | 1400 | Central s/s | 140 | 400 | 126 | 1200
Lalbag | 135 | 500 | 126 | 1200 | Noapara | 137 | 300 | 125 | 1800
Madartek | 135 | 500 | 130 | 1200 | Jessore | 136 | 300 | 123 | 1800
Mirpur | 134 | 600 | 129 | 1400 | Benapol | 138 | 300 | 125 | 1800
Kalyanpur | 137 | 600 | 131 | 1200 | Jhenida | 137 | 300 | 123 | 1800
Gulshan | 134 | 600 | 129 | 1200 | Bottail | 140 | 400 | 130 | 1800
Uttara | 135 | 1900 | 127 | 1200 | G.K Project | 142 | 300 | 137 | 1800
Uttara New | 133 | 600 | 127 | 1200 | Faridpur | 136 | 300 | 127 | 1700
Kamrangirchar | 135 | 400 | 127 | 1200 | Madaripur | 135 | 500 | 126 | 1600
Savar | 134 | 300 | 126 | 1200 | Sariatpur | 136 | 500 | 124 | 1600
Bhasantec | 136 | 300 | 130 | 1200 | Gopalganj | 137 | 600 | 127 | 1600
Agargaon | 137 | 300 | 130 | 1200 | Bagerhat | 140 | 300 | 126 | 1600
Satmosjid | 137 | 300 | 130 | 1200 | Mongla | 137 | 200 | 125 | 1200
Tongi | 132 | 1830 | 125 | 1100 | Satkhira | 142 | 300 | 126 | 1200
Kabirpur | 129 | 1800 | 120 | 1200 | Gallamari | 142 | 300 | 127 | 1200
Basundhara | 131 | 1800 | 123 | 1200 | Magura | 137 | 400 | 124 | 1800
Manikganj | 134 | 1800 | 127 | 1200 | Norail | 137 | 300 | 122 | 1800
Joydevpur | 135 | 400 | 130 | 1200 | Chuadanga | 134 | 400 | 120 | 1800
New Tongi | 131 | 1800 | 124 | 1200 | Barisal(N) | 140 | 300 | 132 | 1600
Kodda | 130 | 1900 | 120 | 1200 | Barisal (S) | 139 | 300 | 130 | 1600
Dhamrai | 130 | 2100 | 125 | 1200 | Patuakhali | 136 | 100 | 127 | 1600
Valuka | 128 | 1900 | 121 | 1300 | Bhandaria | 140 | 300 | 126 | 1600
Tangail | 130 | 1800 | 126 | 100 | Ishurdi | 141 | 500 | 134 | 1800
Mymensing | 130 | 1900 | 124 | 900 | Ruppur Paromanobik | 140 | 500 | 133 | 1800
Kishorganj | 130 | 1900 | 125 | 100 | Natore | 137 | 500 | 130 | 1800
Netrokona | 128 | 1800 | 123 | 1300 | Bogra | 137 | 500 | 130 | 1800
Jamalpur | 132 | 1900 | 121 | 1300 | Noagaon | 134 | 600 | 127 | 1200
Sherpur | 131 | 1800 | 120 | 1200 | Rajshahi | 133 | 600 | 127 | 1200
Srimongal | 135 | 1800 | 131 | 1200 | Rajshahi New | 133 | 600 | 126 | 1700
Shahjibazar | 135 | 1800 | 131 | 100 | C.Nawabganj | 125 | 600 | 122 | 1700
Fenchuganj | 133 | 1830 | 128 | 100 | Amnura | 132 | 2000 | 124 | 1200
Khulawara | 133 | 1900 | 128 | 100 | Pabna | 140 | 600 | 134 | 1800
Sylhet | 130 | 1800 | 125 | 1200 | Shahjadpur | 143 | 600 | 139 | 1200
Chatak | 130 | 2100 | 125 | 100 | Serajganj | 138 | 600 | 132 | 1200
Sunamganj | 130 | 2200 | 124 | 100 | Niyamatpur | 133 | 600 | 125 | 1800
Biani Bazar | 130 | 2400 | 125 | 100 | Joypurhat | 135 | 400 | 127 | 1200
Comilla(s) | 129 | 2200 | 124 | 1200 | Sherpur(Bogura) | 138 | 400 | 132 | 1800
Comilla(n) | 136 | 1800 | 131 | 1000 | Mohastangor | 134 | 600 | 126 | 1800
Chandpur | 133 | 1800 | 127 | 700 | Rangpur | 128 | 600 | 118 | 1800
Feni | 128 | 1800 | 124 | 1100 | Lalmonirhat | 125 | 600 | 113 | 1800
Chowmuhani | 128 | 700 | 122 | 1100 | Saidpur | 128 | 600 | 117 | 1800
Ashuganj | 135 | 800 | 133 | 1600 | Purbasadipur | 128 | 600 | 113 | 1900
Daudkandi | 130 | 1800 | 127 | 1300 | Thakurgaon | 124 | 600 | 112 | 1830
B.Baria | 132 | 1930 | 130 | 1600 | Palashbari | 131 | 600 | 121 | 1800
Ramganj | 124 | 2100 | 121 | 1000 | Barapukuria | 130 | 600 | 120 | 1800
Madanhat | 132 | 1800 | 126 | 700 | Panchagar | 122 | 600 | 103 | 1800
Hathazari | 151 | 1830 | 120 | 500 | Joldhaka | 126 | 500 | 115 | 1800
Khulshi | 130 | 1500 | 121 | 1000 | Kurigram | 127 | 300 | 115 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 208 | 4472 | 1845 | 6317 |  |  |  | QF-LDC-12
0:30 | 329 | 4350 | 2030 | 6380 | Date: | 2019-11-09
1:00 | 450 | 4228 | 2215 | 6443
1:30 | 390 | 4230 | 2035.5 | 6265.5
2:00 | 330 | 4232 | 1856 | 6088
2:30 | 330 | 4178 | 1825.5 | 6003.5 | [5 empty] | Gen. at Eve. Peak | 8469 | 8469 MW (19:00 )
3:00 | 330 | 4124 | 1795 | 5919 | [6 empty] | 19:00
3:30 | 335 | 4017 | 1749.5 | 5766.5 | [5 empty] | Gen. at Day Peak | 7310.5 | 7310.5 MW (12:00 )
4:00 | 340 | 3910 | 1704 | 5614 | [6 empty] | 12:00
4:30 | 305 | 3910 | 1634.5 | 5544.5 | [5 empty] | Highest Generation | 8469
5:00 | 270 | 3910 | 1565 | 5475 | [6 empty] | 19:00
5:30 | 240 | 3958.5 | 1589 | 5547.5
6:00 | 210 | 4007 | 1613 | 5620
6:30 | 145 | 4093.4 | 1651.7 | 5745.1
7:00 | 80 | 4179.8 | 1690.4 | 5870.2
7:30 | 125 | 4305.9 | 1746.45 | 6052.35
8:00 | 170 | 4432 | 1802.5 | 6234.5
8:30 | 200 | 4579.8 | 1866.55 | 6446.35
9:00 | 230 | 4727.6 | 1930.6 | 6658.2
9:30 | 231 | 4836.35 | 1908.4 | 6744.75
10:00 | 232 | 4945.1 | 1886.2 | 6831.3
10:30 | 180 | 5013.3 | 1880.3 | 6893.6
11:00 | 128 | 5081.5 | 1874.4 | 6955.9
11:30 | 93 | 5233.6 | 1899.6 | 7133.2
12:00 | 58 | 5385.7 | 1924.8 | 7310.5
12:30 | 66 | 5415.4 | 1955.1 | 7370.5
13:00 | 74 | 5445.1 | 1985.4 | 7430.5
13:30 | 99 | 5319.2 | 1957.7 | 7276.9
14:00 | 124 | 5193.3 | 1930 | 7123.3
14:30 | 172 | 5179.5 | 1914.1 | 7093.6
15:00 | 220 | 5165.7 | 1898.2 | 7063.9
15:30 | 240 | 5108.95 | 1921.95 | 7030.9
16:00 | 260 | 5052.2 | 1945.7 | 6997.9
16:30 | 143 | 5231.1 | 1966.9 | 7198
17:00 | 26 | 5410 | 1988.1 | 7398.1
17:30 | 197 | 5801 | 2100.05 | 7901.05
18:00 | 368 | 6192 | 2212 | 8404
18:30 | 312 | 6180 | 2256.5 | 8436.5
19:00 | 256 | 6168 | 2301 | 8469
19:30 | 210 | 5896 | 2329 | 8225
20:00 | 154 | 5825 | 2305 | 8130 |  |  |  | Executive Engineer
20:30 | 90 | 5737 | 2244.5 | 7981.5 |  |  |  | Network Operation Division
21:00 | 26 | 5649 | 2184 | 7833
21:30 | 16 | 5449.5 | 2084.5 | 7534
22:00 | 6 | 5250 | 1985 | 7235 |  |  |  |  | Page 6 of 7
22:30 | 53 | 5022 | 1934.5 | 6956.5
23:00 | 100 | 4794 | 1884 | 6678
23:30 | 154 | 4633 | 1864.5 | 6497.5
24:00 | 208 | 4472 | 1845 | 6317
8469 MW (19:00 )
7310.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-09 |  | Energy | 167149678
[10 empty] | 2019-11-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4031 | 443 | 1517 | 0 | 149 | 75 | 0 | 0 | 102
0:30 | 3966 | 532 | 1506 | 52.5 | 149.5 | 75 | 0 | 0 | 99 | Date: | 2019-11-09
1:00 | 3901 | 621 | 1495 | 105 | 150 | 75 | 0 | 0 | 96
1:30 | 3808.5 | 533 | 1500 | 105 | 150 | 75 | 0 | 0 | 94 | [7 empty] | Total Energy | 167.1497 | Total Energy Gen 167.150 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.150 MKWHr
2:00 | 3716 | 445 | 1505 | 105 | 150 | 75 | 0 | 0 | 92 | [7 empty] | Energy not Served | 0
2:30 | 3668.5 | 445 | 1468 | 105 | 150 | 75 | 0 | 0 | 92 | [7 empty] | Energy Requirement | 167.1497
3:00 | 3621 | 445 | 1431 | 105 | 150 | 75 | 0 | 0 | 92
3:30 | 3513 | 445 | 1406 | 86.5 | 150 | 75 | 0 | 0 | 91 | [6 empty] | Shortage
4:00 | 3405 | 445 | 1381 | 68 | 150 | 75 | 0 | 0 | 90
4:30 | 3379 | 445 | 1363 | 42.5 | 150 | 75 | 0 | 0 | 90
5:00 | 3353 | 445 | 1345 | 17 | 150 | 75 | 0 | 0 | 90
5:30 | 3426 | 445 | 1354 | 8.5 | 150 | 75 | 0 | 0 | 89
6:00 | 3499 | 445 | 1363 | 0 | 150 | 75 | 0 | 0 | 88
6:30 | 3577 | 445.5 | 1411.5 | 0 | 150 | 75 | 0 | 0 | 84 |  |  |  |  | Coal
7:00 | 3655 | 446 | 1460 | 0 | 150 | 75 | 0 | 0 | 80
7:30 | 3777 | 446 | 1514.5 | 1.5 | 150 | 75 | 0 | 0 | 83 |  |  |  | Oil |  |  |  | ,
8:00 | 3899 | 446 | 1569 | 3 | 150 | 75 | 0 | 0 | 86
8:30 | 3970.5 | 444.5 | 1640.5 | 70 | 150 | 75 | 0 | 0 | 89
9:00 | 4042 | 443 | 1712 | 137 | 150 | 75 | 0 | 0 | 92
9:30 | 4003 | 443 | 1751.5 | 223 | 150 | 74.5 | 0 | 0 | 93
10:00 | 3964 | 443 | 1791 | 309 | 150 | 74 | 0 | 0 | 94
10:30 | 4001.5 | 443 | 1737.5 | 381 | 150 | 74.5 | 0 | 0 | 100
11:00 | 4039 | 443 | 1684 | 453 | 150 | 75 | 0 | 0 | 106
11:30 | 4160 | 443 | 1714.5 | 472 | 150 | 75 | 0 | 0 | 113
12:00 | 4281 | 443 | 1745 | 491 | 150 | 75 | 0 | 0 | 120
12:30 | 4260 | 443 | 1821.5 | 494 | 150 | 75 | 0 | 0 | 122
13:00 | 4239 | 443 | 1898 | 497 | 150 | 75 | 0 | 0 | 124
13:30 | 4239 | 443 | 1898 | 497 | 150 | 75 | 0 | 0 | 124
14:00 | 4239 | 443 | 1898 | 497 | 150 | 75 | 0 | 0 | 124
14:30 | 4155.5 | 443 | 1831 | 465.5 | 149.5 | 75 | 0 | 0 | 124
15:00 | 4072 | 443 | 1764 | 434 | 149 | 75 | 0 | 0 | 124
15:30 | 4157.5 | 443 | 1673.5 | 409 | 149 | 75 | 0 | 0 | 122
16:00 | 4243 | 443 | 1583 | 384 | 149 | 75 | 0 | 0 | 120
16:30 | 4297.5 | 443 | 1678 | 429 | 149 | 75 | 0 | 0 | 126
17:00 | 4352 | 443 | 1773 | 474 | 149 | 75 | 0 | 0 | 132
17:30 | 4308.5 | 443 | 1944.5 | 784.5 | 149 | 76 | 56.5 | 0 | 139
18:00 | 4265 | 443 | 2116 | 1095 | 149 | 77 | 113 | 0 | 146
18:30 | 4339 | 443 | 2122 | 1045 | 149 | 77 | 127.5 | 0 | 134
19:00 | 4413 | 443 | 2128 | 995 | 149 | 77 | 142 | 0 | 122
19:30 | 4532 | 443 | 2010 | 810 | 149 | 77 | 74 | 0 | 130
20:00 | 4529 | 442 | 2000 | 743 | 149 | 77 | 60 | 0 | 130
20:30 | 4480.5 | 442 | 1993.5 | 683.5 | 149 | 77 | 30 | 0 | 126
21:00 | 4432 | 442 | 1987 | 624 | 149 | 77 | 0 | 0 | 122
21:30 | 4364 | 442.5 | 1930 | 450.5 | 149 | 77 | 0 | 0 | 121
22:00 | 4296 | 443 | 1873 | 277 | 149 | 77 | 0 | 0 | 120
22:30 | 4224.5 | 443 | 1796.5 | 155.5 | 149 | 76 | 0 | 0 | 112
23:00 | 4153 | 443 | 1720 | 34 | 149 | 75 | 0 | 0 | 104
23:30 | 4092 | 443 | 1618.5 | 17 | 149 | 75 | 0 | 0 | 103 | Max Temp. in Dhaka |  | 30.7° C
24:00 | 4031 | 443 | 1517 | 0 | 149 | 75 | 0 | 0 | 102
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 167.150 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.150 MKWHr
Note on W13: Author:

## Generation
2019-11-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 |  | 37 | 37 | 37 | 37 | 37 | 35 | 35 | 792960
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3.5 | 2.8 | 2.1 |  |  | 0.7 | [14 empty] | 15930
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 105 | 105 | 105 | 105 | 101 | 110 | 147 | 146 | 146 | 0 | 0 | 90 | 90 | 115 | 147 | 147 | 145 | 149 |  | 149 | 147 | 147 | 147 | 148 | 148 | 148 | 2792686
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | 0 | 0 |  |  |  |  | 27555
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 68 | 17 | 0 |  | 3 | 51 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 34 | 0 | 1955409
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 80 | 80 | 70 | 40 | 40 | 90 | 90 | 90 | 97 | 97 | 90 | 90 | 90 | 90 | 85 | 90 | 100 | 63 |  | 60 | 40 | 40 | 40 | 32 | 40 | 40 | 1866000
17 | Siddhirganj 335 MW CCPP | 200 | 200 | 170 | 170 | 170 | 170 | 230 | 255 | 278 | 284 | 284 | 285 | 280 | 278 | 258 | 247 | 291 | 233 |  | 235 | 238 | 240 | 251 | 273 | 266 | 266 | 5882984
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 0 | 17 | 30 | 24 | 15 | 15 | 14 | 14 | 14 | 14 | 40 |  | 30 | 0 | 0 |  |  |  |  | 256964
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 418181
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 832000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 101 | 101 | 101 | 100 | 101 | 98 | 97 | 100 | 100 | 140 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 100 | 2731000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 370 | 380 |  | 380 | 380 | 380 | 380 | 354 | 320 | 320 | 7244400
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2273780
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 5 | 599184
33 | Ashuganj 225 MW CCPP | 167 | 160 | 160 | 169 | 177 | 178 | 182 | 201 | 190 | 180 | 192 | 199 | 183 | 180 | 179 | 201 | 191 | 180 |  | 180 | 194 | 190 | 181 | 180 | 186 | 170 | 4440000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 255 | 265 | 270 | 275 | 285 | 250 | 250 | 260 | 320 | 365 | 320 | 320 | 350 | 320 | 310 |  | 310 | 320 | 320 | 310 | 265 | 265 | 260 | 7055000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 265 | 280 | 280 | 290 | 300 | 260 | 320 | 340 | 365 | 335 | 320 | 320 | 350 | 325 | 320 |  | 320 | 330 | 330 | 320 | 320 | 320 | 320 | 7684600
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 52 | 50 | 50 | 51 | 51 | 50 | 10 | 10 | 48 |  | 48 | 48 | 50 | 50 | 49 | 48 | 5 | 764160
36 | Chandpur 150 MW CCPP | 89 | 85 | 80 | 85 | 90 | 90 | 90 | 90 | 83 | 80 | 87 | 85 | 84 | 87 | 81 | 91 | 89 | 80 |  | 84 | 88 | 88 | 81 | 82 | 83 | 87 | 2049470
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 350 | 349 | 349 | 356 | 375 | 383 | 382 | 373 | 363 | 357 | 375 | 390 | 355 | 361 | 372 | 400 | 349 |  | 348 | 346 | 356 | 348 | 346 | 346 | 347 | 8732670
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 360 | 320 | 320 | 320 | 350 | 390 | 390 | 390 | 390 | 390 | 390 | 360 | 360 | 360 | 410 | 410 |  | 420 | 370 | 370 | 370 | 370 | 330 | 330 | 8818125
41 | Haripur 360MW CCPP(HPL) | 270 | 270 | 270 | 250 | 250 | 250 | 280 | 300 | 332 | 361 | 359 | 357 | 359 | 302 | 302 | 301 | 322 | 322 |  | 322 | 282 | 283 | 284 | 286 | 284 | 284 | 7191000
42 | RPCL 210MW CCPP | 196 | 207 | 210 | 105 | 106 | 106 | 106 | 157 | 159 | 165 | 180 | 157 | 153 | 144 | 143 | 143 | 143 | 144 |  | 143 | 144 | 140 | 140 | 143 | 148 | 162 | 3526160
43
44 | Fenchugonj CCPP Phase-1 | 60 | 59 | 60 | 60 | 40 | 40 | 40 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1173000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 274 | 268 | 239 | 237 | 237 | 235 | 236 | 237 | 300 | 293 | 301 | 312 | 301 | 302 | 292 | 314 | 292 | 284 |  | 286 | 300 | 298 | 290 | 245 | 247 | 238 | 6309000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 54 | 55 | 55 | 55 | 65 | 65 | 65 | 65 | 67 | 65 | 40 | 65 | 67 |  | 67 | 67 | 67 | 67 | 67 | 40 | 40 | 1319808
48 | Shahjibazar 86MW PP (Shahjibazar) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 5 | 5 | 77 |  | 77 | 77 | 77 | 77 | 30 | 10 | 10 | 438720
49 | Shahjibazar 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 10 | 10 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 5 | 585000
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [16 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 37000
52 | Sylhet 50MW PP (EPL) | 10 | 10 | 8 | 7 | 5 | 10 | 7 | 7 | 7 | 6 | 6 | 6 | 22 | 22 | 22 | 12 | 24 | 31 |  | 32 | 32 | 32 | 32 | 32 | 6 | 6 | 355700
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11MW PP Cofidence-E | 0 | [12 empty] | 0 |  | 0 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 66912
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 53 |  | 53 | 53 | 53 | 53 | 53 | 5 | 5 | 373200
56 | Shahjahanulla 25 MW PP | [17 empty] | 16 |  | 16 | 24 | 24 | 24 | 0 |  |  | 144792
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 295 | 265 | 265 | 305 | 320 | 315 | 315 | 305 | 305 | 270 | 310 | 315 | 280 | 300 | 310 | 320 | 290 |  | 290 | 310 | 300 | 290 | 260 | 290 | 295 | 7405700
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 13 | 55 |  | 35 | 35 | [5 empty] | 128083
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 17 | 17 | 16 | 17 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 0 | 16 | 16 | 16 | 395184
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 0 |  |  | 84996
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 22 |  | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 317808
63 | Impoprt (Tripura) | 96 | 92 | 92 | 90 | 90 | 88 | 80 | 86 | 92 | 94 | 106 | 120 | 124 | 132 | 124 | 120 | 132 | 146 |  | 122 | 130 | 130 | 122 | 120 | 104 | 102 | 2616960
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 40 | 40 | 42 | 13 | 13 | 9 | 7 | 10 | 10 | 13 | 7 | 7 | 35 | 40 |  | 40 | 40 | 40 | 40 | 40 | 42 | 15 | 762240
65 | Feni 22MW PP (Doreen) | [7 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [5 empty] | 13 | 19 | 19 | 18 | 19 | 19 | 0 | 218088
66 | Feni 11 MW PP (Doreen) | [9 empty] | 6 |  | 6 | 6 | 6 | 6 | 6 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 104400
67 | Jangalia 33MW PP (Summit) | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 15 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 33 |  | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 411400
68 | Cumilla 25 MW PP (Summit) | 21 | 18 | 15 | 15 | 10 | 8 | 5 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 340590
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 24 | 24 | 20 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 31 | 545940
71 | Maona 33 MW PP(Summit) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 716700
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 29 | 29 | 33 | 33 | 33 | 16 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 712300
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 0 | 0 |  | 67200
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 5 |  | 0 | 0 | [5 empty] | 6475
| Gazipur 100 MW PP | [8 empty] | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 88 |  | 88 | 52 | 52 | 52 | 17 |  |  | 788844
| Kaptai 7 MW Solar PP | [6 empty] | 0.2 | 1.1 | 1.2 | 1.8 | 2.1 | 1.8 | 0.9 | 1.1 | 0.6 | 0.1
| Jodiac Power | [10 empty] | 9 | 17 | 17 | [13 empty] | 61213
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 0 | 13 | [8 empty] | 18240
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 0 | 10 | 75 | 90 | 90 | 90 | 90 | 100 | 100 | 90 | 90 |  | 90 | 90 | 60 | 10 | 10 | 0 |  | 1007880
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 40 | 49 | 49 | 10 | 18 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 5 | 593496
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 35 |  | 35 | 35 | 35 | 35 | 35 | 7 | 7 | 338584
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [10 empty] | 15 | 18 | 18 | 18 | 18 |  |  | 8 |  | 18 | 18 | 18 | 16 | 5 |  |  | 156480
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 1 | 58 | 91 | 91 | 91 | 91 | 65 | 68 | 95 |  | 71 | 51 | 51 | 25 | 6 |  |  | 845760
97 | Katpotti 52 MW PP (Sinha) | [11 empty] | 2 | 6 | 14 | 18 | 18 | 18 | 29 |  | 47 | 30 | 47 | 47 | 47 |  |  | 330000
98 | Bosila 108MW PP(CLC) | [16 empty] | 18 | 40 |  | 24 | [6 empty] | 56640
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 5 |  | 15 | 0 | 0 |  |  |  |  | 24829
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 35 | 35 | 17 |  |  |  |  | 126517
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 130 | 130 | 130 | 130 | 130 | 100 | 130 | 163 |  | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 2990397
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 80280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 12 | 100 |  | 100 | 100 | 100 | 100 | 7 |  |  | 477600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 7 | 17 | 0 | 0 | [5 empty] | 7 |  | 16 | 0 | 0 |  |  |  |  | 60480
115 | Juldah 100 MW PP Unit-3 (Acorn) | [9 empty] | 29 | 100 | 100 | 100 | 30 | 30 | 10 | 20 | 60 |  | 10 | 0 | 0 |  |  |  |  | 476160
116 | Chandpur 200MW (Desh energy) | [11 empty] | 1 | 3 | 3 | 6 | 8 | 14 | 72 |  | 70 | 52 | 52 | 45 | 45 | 0 |  | 290440
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 1 | 10 | [8 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 84 | 86 | 85 | 84 | 82 | 84 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 75 | 84 | 84 | 119 |  | 217 | 225 | 225 | 226 | 225 | 227 | 228 | 2837000
| Jamalpur 115 MW PP (United) | [26 empty] | 0
Anwara 300 MW PP (United)
120 | Eastern Zone Total | 4228 | 4232 | 4124 | 3910 | 3910 | 4007 | 4179.8 | 4432 | 4727.6 | 4945.1 | 5081.5 | 5385.7 | 5445.1 | 5193.3 | 5165.7 | 5052.2 | 5410 | 6192 |  | 6168 | 5896 | 5825 | 5649 | 5250 | 4794 | 4472 | 119312254
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 9 |  | 13 | 13 | 0 |  |  |  |  | 25920
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 35 |  | 53 | 53 | 53 | 35 | 17 | 0 |  | 186720
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 13 | 54 | 54 | 52 | 13 | 12 | 53 |  | 52 | 52 | 53 | 52 | 52 | 27 | 12 | 643222
| Bhola 225 MW CCPP | 173 | 160 | 148 | 172 | 172 | 172 | 172 | 171 | 172 | 130 | 144 | 145 | 135 | 142 | 124 | 144 | 143 | 123 |  | 123 | 144 | 144 | 125 | 134 | 141 | 123 | 3630404
140 | Bhola 33 MW PP (Venture) | 13 | 12 | 10 | 9 | 9 | 9 | 8 | 12 | 12 | 12 | 15 | 15 | 17 | 18 | 16 | 16 | 14 | 20 |  | 22 | 22 | 9 | 12 | 8 | 13 | 12 | 309400
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 36 |  | 36 | 36 | 35 | 36 | 18 | 0 |  | 187632
146 | Bheramara HVDC | 621 | 445 | 445 | 445 | 445 | 445 | 446 | 446 | 443 | 443 | 443 | 443 | 443 | 442 | 443 | 443 | 443 | 443 |  | 443 | 443 | 442 | 442 | 443 | 443 | 443 | 10922909
147 | Bheramara 360 MW CCPP | 315 | 310 | 305 | 250 | 160 | 195 | 225 | 250 | 320 | 305 | 315 | 350 | 330 | 330 | 305 | 350 | 330 | 310 |  | 310 | 330 | 325 | 305 | 310 | 310 | 310 | 7513920
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3681600
153 | Baghabari 71 MW GTPP | [19 empty] | 30 | 40 | 40 | 50 | 50 | 50 | 50 | 204000
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 0 | 0 | 0 | [20 empty] | 223000
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 0 | 0 |  |  |  |  | 75187
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 155 | 159 | 156 | 157 | 166 | 174 | 176 | 180 | 191 | 189 | 186 | 201 | 202 | 184 | 190 | 194 | 205 | 180 |  | 183 | 188 | 191 | 182 | 178 | 156 | 158 | 4576145
158 | Sirajgonj 225MW CCPP Unit-1(Oil) | [26 empty] | 375073
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 164 | 0 | 0 | 0 | 0 | 0
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 175 | 176 | 164 | 178 | 185 | 186 | 190 | 202 | 201 | 202 | 197 | 197 | 192 | 203 | 210 | 212 | 200 |  | 203 | 210 | 207 | 205 | 195 | 164 | 165 | 4850936
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 368 | 365 | 325 | 337 | 265 | 264 | 307 | 381 | 417 | 432 | 396 | 397 | 432 | 393 | 392 | 392 | 407 | 406 |  | 406 | 421 | 431 | 425 | 391 | 418 | 410 | 9227600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 |  | 22 | 22 | 21 | 21 | 21 | 3 | 3 | 178560
163 | Bogura 20 MW PP (Energyprima) | [11 empty] | 3 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 5 | 5 | 151092
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 138078
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 50 | 0 |  |  | 217690
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 11 |  | 36 | 35 | 34 | 0 |  |  |  | 88938
169 | Natore 52 MW PP (Rajlanka) | [22 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 26 |  | 26 | 26 | 26 | 0 | 0 |  |  | 79280
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 2 | 30 |  | 35 | 35 | 35 | 35 |  |  |  | 148032
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 12 | 0 | [9 empty] | 14400
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 30 | 34 |  | 34 | 35 | 35 | 35 | 0 |  |  | 160320
177 | Sympa Solar Power 8MW | [6 empty] | 0.4 | 2.5 | 3.6 | 4.2 | 3.4 | 2.8 | 3.4 | 3 | 2.2 | 0.7 | 0.1 | [9 empty] | 27366
178
178