## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-12 | Tuesday
|  | Date (day): | 2019-11-12 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12048.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14785 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-11 | 2019-11-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 101 | 0 | 0 | 0 |  |  | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 340 | 330 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 344 | 344 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 323 | 303 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 350 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 5 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 161 | 118 | 150 | 200 | 10 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 300 | 300
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 48 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 30 | 54 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 53 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 28 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 14 | 200 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 68 | 16 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 90 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2003 | 2126 | 3887 | 4339 | 606 | 641
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20.9 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 22 | 20 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 78 | 87 | 87 | 143 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 149 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 50 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 5 | 15 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 42 | 97 | 50 | 98 |  | 10 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 658.1 | 800 | 1240 | 1433 | 393 | 333
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 180 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 340 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 270 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 33 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 52 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 16 | 16 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 87 | 81 | 80 | 90 |  | 73 | Machine Problem
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 50 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 124 | 113 | 149
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 4 | 18 | 22 | 22
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1162 | 1411 | 1690 | 2167 | 485 | 97
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 156 | 170 | 200
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 16 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 160 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 276.4 | 332 | 408.6 | 632 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 58 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 0 | 0
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 0 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 286 | 238 | 300 | 300
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 28 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 67 | 68 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 68 | 76 | 77 | 77 |  | 9 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 32 | 38 | 32 | 36 |  | 14 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 285 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 227 | 341 | 310 | 341 |  | 59 | Machine Problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1284 | 1429 | 1386 | 1584 | 0 | 234
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 441 | 778 | 840 | 939
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 310 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 48 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 751 | 1209 | 1335 | 2165 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 11 | 18 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 81 | 92 | 92
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 22 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 43 | 121 | 290 | 360 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Machine problem.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 48
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 154 | 197 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 156 | 188 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 384 | 347 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 43 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 842 | 1045 | 1401 | 1668 | 320 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 251 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 163.7 | 364 | 411 | 437 | 0 | 85
| Total |  |  |  |  | 19428 | 18905 | 7183.2 | 8837 | 12048.6 | 14785 | 1804 | 1398
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6812.5381 | 8381 | 11426.8775 | 14022.0759
A. |  | 2019-11-11 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 8837 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4949 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8837 | MW
3 | Day peak Generation : |  |  | 7183.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8381 | MW
4 | Evening peak Generation : |  |  | 8837 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 163.9461 | MKWHr | By Solar | 0.14259 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 129.8274 | MKWHr |  | By Oil: | 12.4788 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.7874 | MKWHr |  | By Hydro: | 1.7434 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1804 | MW | Dhaka | 3445 | 3445 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1398 | MW | Chittagong | 899 | 899 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3202 | MW | Khulna | 779 | 779 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1074.71 | MMCFD |  |  | Rajshahi | 850 | 850 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 116800080.416 | ii) Oil : | Taka | 120360335.58 | Comilla | 713 | 713 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19580466 | Total | Taka | 256740881.996 | Mymensingh | 674 | 674 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 341 | 341 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 296 | MW (E to W) at | 19:00 | hrs | Barisal | 134 | 134 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 130 | MW at | 13:00 | hrs | Rangpur | 546 | 546 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.3° C |  |  | Total | 8381 | 8381 |  | 0
B. |  | 2019-11-12 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 29.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14785 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7600 | MW
4 | Reserve(Generation end) |  |  |  | 5185 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 178.1014 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5848 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.8065 | MKWHr. | ii) HVDC Flow at Peak Time |  | 778 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.16 | MKWHr. | iii) Maximum HVDC Flow : |  | 783 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.47 | 101.36 |  | (b) Today: | 101.47 |  | (c) Rule Curve: |  | 108
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 101 | 0 | 250 | 0 | 0 | 345 | 269 |  | 0 | 280 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 8 | 33 | 0 | 0 | 32 | 40 | 105 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 60 | 0 | 0 | 240 | 225 | 155 | 8 | 53 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 158 | 0 | 0 | 0 | 25 | 0 | 5 | 5 | 100 | 242 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 442 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3842 | 1544 | 5386 | 3305 | 442 | 1337 | 0 | 160 | 72 | 0 | 70 | 0 | 0 | 101.26
2:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 345 | 203 |  | 0 | 280 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 33 | 0 | 0 | 32 | 40 | 105 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 60 | 0 | 0 | 240 | 225 | 159 | 8 | 51 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 68 | 157 | 0 | 0 | 0 | 25 | 0 | 5 | 5 | 100 | 250 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 439 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3652 | 1533 | 5185 | 3161 | 439 | 1285 | 0 | 160 | 72 | 0 | 68 | 0 | 0 | 101.28
3:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 353 | 203 |  | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 33 | 0 | 0 | 33 | 40 | 105 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 60 | 0 | 0 | 240 | 230 | 156 | 8 | 51 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 156 | 0 | 0 | 0 | 25 | 0 | 5 | 5 | 100 | 240 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 439 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3546 | 1530 | 5076 | 3037 | 439 | 1299 | 0 | 160 | 73 | 0 | 68 | 0 | 0 | 101.3
4:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 312 | 203 |  | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 33 | 0 | 0 | 33 | 40 | 105 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 240 | 230 | 156 | 8 | 49 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 157 | 0 | 0 | 0 | 25 | 0 | 5 | 5 | 100 | 239 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 439 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3496 | 1524 | 5020 | 2995 | 439 | 1287 | 0 | 160 | 73 | 0 | 66 | 0 | 0 | 101.32
5:00 | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 280 | 202 |  | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 33 | 0 | 0 | 34 | 40 | 105 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 60 | 0 | 0 | 240 | 230 | 156 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 157 | 0 | 0 | 0 | 25 | 0 | 5 | 5 | 100 | 238 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 442 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3424 | 1525 | 4949 | 2932 | 442 | 1275 | 0 | 160 | 74 | 0 | 66 | 0 | 0 | 101.34
6:00 | 35 | 0 | 101 | 0 | 250 | 0 | 0 | 280 | 202 |  | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 33 | 0 | 0 | 34 | 40 | 105 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 60 | 0 | 0 | 240 | 235 | 170 | 8 | 51 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 157 | 0 | 0 | 0 | 25 | 0 | 5 | 5 | 100 | 238 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 442 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3470 | 1557 | 5027 | 2952 | 442 | 1335 | 0 | 160 | 74 | 0 | 64 | 0 | 0 | 101.36
7:00 | 35 | 0 | 100 | 0 | 280 | 0 | 0 | 320 | 240 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 33 | 0 | 0 | 34 | 40 | 105 | 0 | 0 | 0 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 0 | 0 | 290 | 250 | 180 | 8 | 50 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 64 | 158 | 0 | 0 | 0.2 | 25 | 0 | 5 | 5 | 100 | 260 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 |  | 442 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 3713.3 | 1596.2 | 5309.5 | 3159 | 442 | 1410 | 0 | 160 | 74 | 0 | 64 | 0.5 | 0 | 101.38
8:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 371 | 274 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 8 | 33 | 0 | 0 | 34 | 40 | 105 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 80 | 0 | 0 | 290 | 290 | 201 | 8 | 90 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 68 | 157 | 0 | 0 | 1 | 25 | 0 | 5 | 5 | 100 | 302 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 2.6 | 0 | 0 | 0 | 226 | 0 | 5 | 14 | 0.4 | 0 | 0 | 0 |  | 442 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 |  | 4063 | 1716.6 | 5779.6 | 3521 | 442 | 1466 | 43 | 160 | 74 | 0 | 68 | 5.6 | 0 | 101.19
9:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 365 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 8 | 33 | 0 | 0 | 40 | 40 | 105 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 30 | 0 | 0 | 16 | 2 | 80 | 0 | 0 | 270 | 275 | 190 | 8 | 90 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 11 | 0 | 0 | 4 | 80 | 154 | 0 | 0 | 1.7 | 40 | 0 | 5 | 5 | 130 | 298 | 40 | 5 | 5 | 0 | 0 | 7 | 0 | 315 | 0 | 0 | 0 | 3 | 0 | 0 | 52 | 0 | 0 | 10.8 | 0 | 0 | 0 | 227 | 0 | 70 | 55 | 0.7 | 0 | 0 | 0 |  | 441 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 |  | 4457.2 | 1796.9 | 6254.1 | 3682 | 441 | 1548 | 248 | 160 | 80 | 0 | 80 | 15.1 | 0 | 101.19
10:00 | 35 | 0 | 100 | 0 | 300 | 0 | 0 | 349 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 24 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 90 | 0 | 0 | 16 | 3 | 80 | 0 | 0 | 265 | 275 | 193 | 8 | 90 | 5 | 5 | 0 | 7 | 0 | 0 | 0 | 19 | 5 | 0 | 4 | 82 | 154 | 0 | 22 | 2.1 | 60 | 0 | 5 | 5 | 130 | 299 | 40 | 5 | 5 | 0 | 17 | 7 | 0 | 310 | 24 | 8 | 0 | 14 | 0 | 0 | 80 | 0 | 0 | 8.7 | 0 | 0 | 0 | 227 | 0 | 70 | 105 | 1.9 | 0 | 0 | 0 |  | 441 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 386 | 0 | 0 | 0 | 18 | 0 | 0 | 2.4 | 0 |  | 4732.7 | 1813.4 | 6546.1 | 3784 | 441 | 1545 | 444 | 160 | 75 | 0 | 82 | 15.1 | 0 | 101.19
11:00 | 35 | 0 | 101 | 0 | 340 | 0 | 0 | 351 | 360 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 27 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 50 | 0 |  | 0 | 0 | 0 | 90 | 3 | 2 | 16 | 2 | 80 | 0 | 0 | 260 | 265 | 180 | 8 | 80 | 27 | 49 | 0 | 11 | 0 | 0 | 0 | 19 | 5 | 33 | 4 | 86 | 152 | 0 | 22 | 0.7 | 58 | 0 | 28 | 28 | 100 | 285 | 67 | 60 | 40 | 0 | 17 | 31 | 0 | 300 | 24 | 8 | 0 | 14 | 0 | 0 | 88 | 0 | 21 | 6.6 | 40 | 0 | 0 | 228 | 0 | 70 | 105 | 3.4 | 0 | 0 | 0 |  | 441 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 0 | 0 | 160 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 |  | 5100.7 | 1834.4 | 6935.1 | 3807 | 441 | 1822 | 528 | 160 | 75 | 0 | 86 | 16.1 | 0 | 101.18
12:00 | 35 | 0 | 101 | 0 | 340 | 0 | 0 | 344 | 323 |  | 0 | 380 | 0 | 0 | 0 | 5 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 27 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 90 | 42 | 18 | 16 | 4 | 80 | 0 | 0 | 260 | 265 | 180 | 8 | 87 | 37 | 47 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 4 | 96 | 152 | 0 | 22 | 2.4 | 58 | 0 | 28 | 49 | 100 | 286 | 67 | 68 | 40 | 0 | 17 | 32 | 0 | 280 | 24 | 8 | 0 | 14 | 0 | 0 | 100 | 0 | 68 | 20.9 | 40 | 0 | 0 | 227 | 0 | 70 | 105 | 2.2 | 0 | 0 | 0 |  | 441 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 |  | 5383.5 | 1799.7 | 7183.2 | 3882 | 441 | 1819 | 681 | 160 | 75 | 0 | 96 | 29.2 | 0 | 101.18
13:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 353 | 323 |  | 0 | 380 | 0 | 0 | 0 | 15 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 27 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 90 | 97 | 18 | 16 | 4 | 80 | 0 | 0 | 270 | 260 | 187 | 8 | 84 | 37 | 48 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 4 | 88 | 149 | 0 | 22 | 1.8 | 59 | 0 | 28 | 49 | 100 | 288 | 66 | 70 | 40 | 0 | 17 | 34 | 0 | 300 | 24 | 8 | 0 | 14 | 0 | 0 | 100 | 0 | 70 | 13.1 | 40 | 0 | 0 | 227 | 0 | 70 | 105 | 5.2 | 0 | 0 | 0 |  | 441 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 55 | 0 | 0 | 39 | 50 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 159 | 0 | 0 | 163 | 0 | 0 | 0 | 5 | 0 | 195 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 |  | 5367.1 | 1891.9 | 7259 | 3830 | 441 | 1853 | 748 | 159 | 75 | 39 | 88 | 26 | 0 | 101.18
14:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 347 | 262 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 27 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 16 | 6 | 80 | 0 | 0 | 270 | 305 | 161 | 8 | 90 | 37 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 4 | 90 | 152 | 0 | 22 | 1.9 | 60 | 0 | 50 | 46 | 100 | 239 | 67 | 70 | 40 | 0 | 17 | 37 | 0 | 290 | 24 | 8 | 0 | 15 | 0 | 0 | 100 | 0 | 57 | 16.06 | 10 | 0 | 0 | 227 | 0 | 70 | 105 | 4.606 | 0 | 0 | 0 |  | 441 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 55 | 0 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 160 | 0 | 0 | 158 | 0 | 0 | 0 | 13 | 0 | 173 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 |  | 5116.566 | 1887.4 | 7003.966 | 3723 | 441 | 1789 | 657 | 160 | 75 | 42 | 90 | 26.966 | 0 | 101.18
15:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 369 | 303 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 0 | 17 | 0 | 22 | 25 | 27 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 16 | 4 | 80 | 0 | 0 | 285 | 285 | 176 | 8 | 90 | 37 | 48 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 10 | 94 | 151 | 0 | 0 | 1.3 | 60 | 0 | 52 | 49 | 100 | 254 | 66 | 70 | 40 | 0 | 17 | 36 | 0 | 320 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 48 | 11.77 | 10 | 0 | 0 | 228 | 0 | 70 | 105 | 2.83 | 0 | 0 | 0 |  | 441 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 16 | 0 | 0 | 55 | 0 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 172 | 0 | 0 | 181 | 0 | 0 | 0 | 20 | 0 | 173 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 5284.9 | 1950 | 7234.9 | 3834 | 441 | 1909 | 649 | 172 | 75 | 42 | 94 | 18.9 | 0 | 101.4
16:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 350 | 303 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 6 | 0 | 17 | 0 | 22 | 25 | 27 | 28 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 19 | 4 | 80 | 0 | 0 | 270 | 270 | 163 | 8 | 86 | 37 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 90 | 152 | 0 | 0 | 0.5 | 60 | 0 | 53 | 49 | 100 | 245 | 67 | 70 | 40 | 0 | 18 | 11 | 0 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 42 | 5.2 | 10 | 0 | 0 | 229 | 0 | 70 | 105 | 0.767 | 0 | 0 | 0 |  | 441 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 232 | 0 | 0 | 170 | 0 | 0 | 0 | 21 | 0 | 161 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 5153.467 | 1993.7 | 7147.167 | 3769 | 441 | 1859 | 632 | 232 | 75 | 42 | 90 | 7.167 | 0 | 101.18
17:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 351 | 303 |  | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 6 | 14 | 35 | 5 | 22 | 25 | 27 | 28 | 33 | 0 | 0 | 34 | 40 | 110 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 16 | 90 | 97 | 2 | 19 | 4 | 80 | 0 | 0 | 270 | 270 | 162 | 8 | 80 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 21 | 0 | 33 | 12 | 94 | 154 | 12 | 0 | 0 | 59 | 0 | 11 | 49 | 100 | 244 | 67 | 20 | 40 | 0 | 18 | 13 | 0 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 35 | 0.17 | 10 | 3 | 1 | 227 | 0 | 70 | 105 | 0 | 0 | 1 | 0 |  | 441 | 0 | 310 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 16 | 0 | 0 | 60 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 250 | 0 | 0 | 173 | 0 | 0 | 0 | 22 | 0 | 171 | 0 | 386 | 17 | 0 | 7 | 14 | 35 | 0 | 0.1 | 0 |  | 5114.17 | 2119.1 | 7233.27 | 3797 | 441 | 1739 | 779 | 250 | 74 | 59 | 94 | 0.27 | 0 | 101.18
18:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 347 | 303 |  | 0 | 350 | 0 | 0 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 23 | 17 | 35 | 55 | 22 | 25 | 14 | 28 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 51 | 100 | 97 | 16 | 16 | 5 | 80 | 0 | 0 | 285 | 270 | 190 | 8 | 88 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 122 | 153 | 40 | 0 | 0 | 58 | 0 | 53 | 49 | 100 | 250 | 67 | 76 | 40 | 0 | 18 | 37 | 0 | 275 | 24 | 11 | 0 | 115 | 0 | 0 | 144 | 0 | 30 | 0 | 50 | 47 | 28 | 339 | 0 | 90 | 105 | 0 | 0 | 13 | 0 |  | 778 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 13 | 0 | 40 | 75 | 18 | 16 | 0 | 0 | 60 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 0 | 22 | 0 | 172 | 0 | 373 | 53 | 0 | 73 | 54 | 109 | 0 | 0 | 0 |  | 5877 | 2751 | 8628 | 3980 | 778 | 1831 | 1485 | 250 | 75 | 107 | 122 | 0 | 0 | 101.17
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 344 | 303 |  | 0 | 350 | 0 | 0 | 0 | 15 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 48 | 17 | 35 | 35 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 51 | 100 | 97 | 22 | 16 | 5 | 80 | 0 | 0 | 340 | 270 | 180 | 8 | 81 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 124 | 156 | 16 | 0 | 0 | 58 | 0 | 53 | 49 | 130 | 238 | 68 | 76 | 40 | 0 | 18 | 38 | 0 | 285 | 24 | 11 | 0 | 200 | 0 | 0 | 160 | 0 | 16 | 0 | 50 | 50 | 70 | 341 | 0 | 90 | 105 | 0 | 0 | 17 | 0 |  | 778 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 81 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 251 | 0 | 0 | 197 | 0 | 0 | 0 | 22 | 0 | 188 | 0 | 347 | 17 | 0 | 113 | 48 | 113 | 0 | 0 | 0 |  | 6098 | 2739 | 8837 | 4071 | 778 | 1847 | 1594 | 251 | 78 | 94 | 124 | 0 | 0 | 101.42
19:30 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 348 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 7 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 48 | 17 | 35 | 35 | 19 | 25 | 28 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 17 | 100 | 97 | 0 | 16 | 12 | 80 | 0 | 0 | 340 | 270 | 180 | 8 | 82 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 156 | 0 | 0 | 0 | 58 | 0 | 53 | 49 | 130 | 264 | 68 | 76 | 40 | 0 | 18 | 38 | 0 | 300 | 24 | 11 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 10 | 17 | 30 | 341 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 782 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 270 | 0 | 0 | 198 | 0 | 0 | 0 | 21 | 0 | 188 | 0 | 370 | 17 | 0 | 113 | 17 | 113 | 0 | 0 | 0 |  | 5881 | 2713 | 8594 | 4111 | 782 | 1889 | 1310 | 270 | 78 | 34 | 120 | 0 | 0 | 101.42
20:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 343 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 24 | 0 | 17 | 17 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 11 | 100 | 97 | 0 | 16 | 17 | 80 | 0 | 0 | 340 | 270 | 182 | 8 | 84 | 37 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 156 | 0 | 0 | 0 | 60 | 0 | 53 | 49 | 130 | 294 | 67 | 76 | 40 | 0 | 18 | 38 | 0 | 270 | 24 | 11 | 0 | 110 | 0 | 0 | 160 | 0 | 0 | 0 | 10 | 22 | 0 | 341 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 782 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 90 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 269 | 0 | 0 | 198 | 0 | 0 | 0 | 21 | 0 | 189 | 0 | 383 | 17 | 0 | 113 | 17 | 114 | 0 | 0 | 0 |  | 5708 | 2721 | 8429 | 4151 | 782 | 1881 | 1133 | 269 | 78 | 11 | 124 | 0 | 0 | 101.42
21:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 344 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 24 | 0 | 0 | 17 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 90 | 97 | 0 | 16 | 32 | 80 | 0 | 0 | 340 | 270 | 181 | 8 | 83 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 122 | 156 | 0 | 0 | 0 | 58 | 0 | 53 | 49 | 130 | 290 | 67 | 76 | 40 | 0 | 18 | 36 | 0 | 295 | 24 | 11 | 0 | 95 | 0 | 0 | 160 | 0 | 0 | 0 | 10 | 0 | 0 | 339 | 0 | 70 | 105 | 0 | 0 | 0 | 0 |  | 783 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 90 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 2 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 21 | 0 | 190 | 0 | 384 | 17 | 0 | 74 | 0 | 70 | 0 | 0 | 0 |  | 5682 | 2619 | 8301 | 4183 | 783 | 1906 | 949 | 280 | 78 | 0 | 122 | 0 | 0 | 101.42
22:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 343 | 302 |  | 0 | 350 | 0 | 0 | 0 | 0 | 43 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 39 | 40 | 110 | 0 | 0 | 0 | 0 | 150 | 0 |  | 0 | 0 | 0 | 90 | 65 | 0 | 16 | 36 | 80 | 0 | 0 | 340 | 270 | 181 | 8 | 81 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 158 | 0 | 0 | 0 | 60 | 0 | 53 | 49 | 130 | 282 | 69 | 76 | 40 | 0 | 18 | 36 | 0 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 52 | 105 | 0 | 0 | 0 | 0 |  | 783 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 197 | 0 | 0 | 0 | 21 | 0 | 190 | 0 | 337 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 |  | 5370 | 2414 | 7784 | 4168 | 783 | 1849 | 513 | 280 | 79 | 0 | 112 | 0 | 0 | 0
23:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 344 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 42 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 25 | 30 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 90 | 30 | 0 | 16 | 40 | 80 | 0 | 0 | 315 | 275 | 188 | 8 | 85 | 37 | 56 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 106 | 159 | 0 | 0 | 0 | 60 | 0 | 5 | 49 | 130 | 239 | 56 | 5 | 40 | 0 | 18 | 7 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 783 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 11 | 0 | 0 | 280 | 0 | 0 | 189 | 0 | 0 | 0 | 21 | 0 | 186 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4928 | 2328 | 7256 | 4024 | 783 | 1694 | 291 | 280 | 78 | 0 | 106 | 0 | 0 | 0
24:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 347 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 41 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 25 | 31 | 28 | 33 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 0 | 0 | 150 | 0 |  | 0 | 0 | 0 | 90 | 10 | 0 | 16 | 40 | 80 | 0 | 0 | 260 | 270 | 172 | 8 | 88 | 37 | 55 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 98 | 158 | 0 | 0 | 0 | 58 | 0 | 5 | 5 | 130 | 242 | 40 | 5 | 40 | 0 | 0 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 783 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 21 | 0 | 204 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4687 | 2295 | 6982 | 3873 | 783 | 1676 | 225 | 250 | 77 | 0 | 98 | 0 | 0 | 0
KWH | 840000 | 0 | 1225000 | 0 | 7178855 | 0 | 0 | 8311810 | 8657000 |  | 0 | 8222875 | 0 | 0 | 0 | 59177 | 610337 | 0 | 2024000 | 0 | 0 | 0 | 0 | 0 | 350400 | 0 | 217296 | 44280 | 246474 | 138427 | 249120 | 600000 | 482400 | 677700 | 802500 | 0 | 0 | 779400 | 964000 | 2500000 | 0 | 0 | 0 | 0 | 3272922 | 0 |  | 0 | 0 | 143488 | 1359720 | 1065600 | 84960 | 279312 | 296160 | 1848682 | 0 | 0 | 7017900 | 6470000 | 4313000 | 217454 | 1783520 | 524592 | 791520 | 0 | 525848 | 0 | 0 | 0 | 293364 | 112140 | 404600 | 258350 | 2160000 | 3645120 | 79680 | 122760 | 14200 | 1117000 | 0 | 574200 | 73584 | 2907974 | 4916000 | 1280928 | 899520 | 655200 | 0 | 255000 | 500760 | 0 | 7310000 | 327504 | 134096 | 0 | 740181 | 0 | 0 | 1699200 | 0 | 424800 | 81540 | 272640 | 131520 | 145527 | 6166000 | 0 | 1073076 | 1646792 | 16920 | 0 | 36093 | 0 |  | 12806545 | 0 | 7354080 | 0 | 37440 | 0 | 0 | 0 | 5280 | 0 | 174000 | 676000 | 272300 | 137280 | 0 | 0 | 1305000 | 0 | 0 | 283264 | 642710 | 0 | 0 | 0 | 0 | 290160 | 209700 | 178218 | 0 | 0 | 4787400 | 0 | 0 | 4327091 | 0 | 0 | 0 | 210880 | 0 | 4290009 | 0 | 9037327 | 131040 | 0 | 489216 | 120960 | 498240 | 0 | 29933 | 0 |  | 115651998 | 48294073 | 163946071 | 88174910 | 12806545 | 41652462 | 12046729 | 4787400 | 1743400 | 432032 | 2160000 | 142593 | 0
Fuel Cost | 940800 | 0 | 1310750 | 0 | 5312352.7 | 0 | 0 | 5984503.2 | 6579320 |  | 0 | 6578300 | 0 | 0 | 0 | 607156.02 | 756817.88 | 0 | 2530000 | 0 | 0 | 0 | 0 | 0 | 3188640 | 0 | 2033890.56 | 424645.2 | 2351361.96 | 1378732.92 | 186840 | 450000 | 0 | 0 | 0 | 0 | 0 | 202644 | 250640 | 3825000 | 0 | 0 | 0 | 0 | 4156610.94 | 0 |  | 0 | 0 | 1505189.12 | 13991518.8 | 10133856 | 795225.6 | 256967.04 | 823324.8 | 1941116.1 | 0 | 0 | 5193246 | 5434800 | 3967960 | 213104.92 | 2372081.6 | 430165.44 | 815265.6 | 0 | 751962.64 | 0 | 0 | 0 | 299231.28 | 84105 | 764694 | 193762.5 | 14904000 | 2988998.4 | 757756.8 | 125215.2 | 232880 | 1519120 | 0 | 780912 | 91980 | 3605887.76 | 4522720 | 1908582.72 | 1583155.2 | 727272 | 0 | 405450 | 585889.2 | 0 | 5190100 | 245628 | 101912.96 | 0 | 7749695.07 | 0 | 0 | 16346304 | 0 | 4286232 | 940971.6 | 2541004.8 | 1233657.6 | 1363587.99 | 5796040 | 0 | 9561107.16 | 15562184.4 | 0 | 0 | 0 | 0 |  | 34577671.5 | 0 | 5736182.4 | 0 | 360921.6 | 0 | 0 | 0 | 61248 | 0 | 1720860 | 540800 | 422065 | 1474387.2 | 0 | 0 | 2453400 | 0 | 0 | 2804313.6 | 6664902.7 | 0 | 0 | 0 | 0 | 319176 | 346005 | 134911.026 | 0 | 0 | 19580466 | 0 | 0 | 3807840.08 | 0 | 0 | 0 | 335299.2 | 0 | 3775207.92 | 0 | 6597248.71 | 1239638.4 | 0 | 4491002.88 | 1077753.6 | 4653561.6 | 0 | 0 | 0 |  | 204674826.68 | 103174862.416 | 307849689.096 | 80453812.386 | 34577671.5 | 36346268.03 | 115989584.86 | 19580466 | 453284 | 4370750.72 | 14904000 | 1173851.6 | 0
Yesterday Day Peak | 35 | 0 | 101 | 0 | 340 | 0 | 0 | 344 | 323 |  | 0 | 380 | 0 | 0 | 0 | 5 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 27 | 8 | 33 | 0 | 0 | 35 | 40 | 105 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 90 | 42 | 18 | 16 | 4 | 80 | 0 | 0 | 260 | 265 | 180 | 8 | 87 | 37 | 47 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 4 | 96 | 152 | 0 | 22 | 2.4 | 58 | 0 | 28 | 49 | 100 | 286 | 67 | 68 | 40 | 0 | 17 | 32 | 0 | 280 | 24 | 8 | 0 | 14 | 0 | 0 | 100 | 0 | 68 | 20.9 | 40 | 0 | 0 | 227 | 0 | 70 | 105 | 2.2 | 0 | 0 | 0 |  | 441 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 |  | 7183.2 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 344 | 303 | 0 | 0 | 350 | 0 | 0 | 0 | 15 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 48 | 17 | 35 | 35 | 22 | 25 | 28 | 28 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 51 | 100 | 97 | 22 | 16 | 5 | 80 | 0 | 0 | 340 | 270 | 180 | 8 | 81 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 124 | 156 | 16 | 0 | 0 | 58 | 0 | 53 | 49 | 130 | 238 | 68 | 76 | 40 | 0 | 18 | 38 | 0 | 285 | 24 | 11 | 0 | 200 | 0 | 0 | 160 | 0 | 16 | 0 | 50 | 50 | 70 | 341 | 0 | 90 | 105 | 0 | 0 | 17 | 0 |  | 778 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 81 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 251 | 0 | 0 | 197 | 0 | 0 | 0 | 22 | 0 | 188 | 0 | 347 | 17 | 0 | 113 | 48 | 113 | 0 | 0 | 0 |  | 8837 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 300 | 0 | 200 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 37 | 50 | 110 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 98 | 50 | 19 | 25 | 100 | 0 | 0 | 360 | 360 | 225 | 16 | 90 | 37 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 149 | 200 | 95 | 22 | 0 | 60 | 0 | 51 | 44 | 163 | 300 | 66 | 77 | 40 | 0 | 20 | 36 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 341 | 115 | 90 | 105 | 0 | 300 | 54 | 110 |  | 939 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 92 | 33 | 110 | 30 | 0 | 60 | 50 | 48 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 35 | 0 | 0 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 300 | 0 | 150 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 37 | 50 | 110 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 20 | 19 | 15 | 80 | 0 | 0 | 360 | 360 | 225 | 16 | 80 | 33 | 55 | 0 | 30 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 113 | 170 | 0 | 22 | 1.6 | 60 | 0 | 51 | 44 | 0 | 300 | 66 | 77 | 40 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 310 | 115 | 88 | 105 | 5 | 230 | 54 | 50 |  | 840 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 92 | 33 | 70 | 0 | 0 | 60 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 250 | 0 | 0 | 360 | 303 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 274 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 28 | 33 | 0 | 0 | 34 | 40 | 110 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 80 | 0 | 0 | 270 | 275 | 182 | 8 | 30 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 84 | 160 | 0 | 0 | 0 | 30 | 0 | 5 | 5 | 0 | 270 | 67 | 5 | 5 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 305 | 0 | 52 | 105 | 2 | 0 | 0 | 0 | 0 | 440 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 215 | 0 | 0 | 181 | 0 | 0 | 0 | 12 | 0 | 176 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4949 | 5:00
| Highest Generation |  | 8837 | 19:00
| Day Peak Generation |  | 7183.2 | 12:00
| Evening Peak Generation |  | 8837 | 19:00
| HVDC Max Flow |  | 783 | 21:00
| HVDC EvPeak Flow |  | 778 | 19:00
| Load factor L.F |  | 77.3%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-12
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7183.2 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5848 | MW
Evening Peak Generation : |  | 8837 | MW Hour : | 19:00 | Available Max Generation : |  | 14785 | MW
E.P. Demand (at gen end) : |  | 8837 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9600 | MW
Maximum Generation : |  | 8837 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5185 | MW
Total Gen. (MKWH) : |  | 163.9461 | System Load Factor : | 77.3% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 130 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-12
Actual : | 101.47 | Ft.(MSL) , | Rule curve : | 108 | Ft.( MSL )
Gas Consumed : | Total = | 1074.71 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 116800080.416
: |  | Coal : | 19580466 | Oil : | 120360335.58 | Total : | 256740881.996
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3397.93 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1151.4966 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1030.9923 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 931.3362 |  |  | 0 | 0%
) | 0 | 0:00 | 841.7742 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 679.2719 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 384.9469 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 175.0301 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 523.8637 |  |  | 0 | 0%
Total | 0 |  | 9116.6418 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1&2. | 9) Sirajganj unit-2
|  |  |  | 2) Sylhet-150 MW. | 10) Siddhirganj 335 MW
3) Ghorasal Unit-1,3 & 5
4) Raozan #2
5) Ashuganj unit-4 & 5
6) Chandpur CCPP ST
7)Sylhet 150 MW
8) Fenchuganj # 03 & 04
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi-Uttara 132 kV Ckt close at 08:55.
b) Maniknagar 230/132 kV T-1 auto transformer was under shut down from 09:37 to 17:49 for A/M.
c) Tangail 132/33 kV T-2 transformer was under shut down from 08:19 to 16:10 for A/M.
d) Kabirpur-Kodda 132 kV Ckt-2 was under shut down from 10:43 to 15:37 for A/M.
e) Kaliakoir 132 kV bus-1 was under shut down from 10:06 to 14:02 for A/M.
f) Jamalpur 132/33 kV T-1 transformer was under shut down from 08:14 to 15:33 for A/M.
g) Kishorganj-Mymensingh 132 kV Ckt-2 was under shut down from 09:07 to 17:41 for A/M.
h) Rangpur Confidence-Palashbari 132 kV Ckt-2 was under shut down from 08:47 to 16:50 for A/M.
i) Rangpur-Rangpur Confidence 132 kV Ckt was under shut down from 08:40 to 16:46 for A/M.
j) Barapukuria 230 kV Ckt-1 was under shut down from 08:16 to 16:35 for A/M.
k) Purbosadipur-Thakurgaon 132 kV Ckt-2 was under shut down from 08:35 to 16:35 for A/M.
l) Natore-Rajshahi 132 kV Ckt-1 was under shut down from 08:16 to 16:35 for A/M.
m) Natore-Rajshahi 132 kV Ckt-2 was under shut down from 08:46 to 16:35 for A/M.
n) Goalpara 132/33 kV T-5 transformer was under shut down from 08:03 to 16:05 for A/M.
o) Noapara 132/33 kV T-1 transformer was under shut down from 08:18 to 16:05 for a/M.
p) HVDC station 33 kV Aux transformer O2HO3 was under shut down from 11:09 to 17:31 for A/M.
q) Khulna(s)-HVDC 230 kV Ckt-1 was switched on at 08:46.
r) Barisal(n)-Madaripur 132 kV Ckt-2 was closed on at 09:34.
s) Barisal(n)-Barisal(s) 132 kV Ckt-1 was closed on at 09:57.
t) Barisal(s)-Barisal summit 132 kV Ckt was closed on at 10:00.
u) Barisal 132/33 kV T-2 transformer was closed on at 10:21.
v) Barisal(s)-GT was closed on at 10:12.
w) Bagerhat-Bhandaria 132 kV Ckt was closed on at 10:12.
x) Barisal(s)-Bhandaria 132 kV Ckt was closed on at 10:49.
y) Barisal(n)-Bhola 230 kV Ckt-1 was closed on at 11:07.
z) Barisal(n)-Barisal(s) 132 kV Ckt-2 trialled at 11:47 but failed showing dist. L3N and was close on at 15:03.
aa) Barisal(s)-Patuakhali 132 kV Ckt was closed on at 11:10.
ab) Patuakhali-Payra 132 kV Ckt-2 was closed on at 11:54.
ac) Ghorasal unit-4 was shut down at 12:18 for project work.
ad) Siddhirganj GT-1 & 2 were synchronized at 08:10 & 10:52 respectively.
ae) Madaripur-Faridpur 132 kV Ckt-1 was closed on at 11:16.
af) Khulna(s) 230/132 kV T-3 transformer was shut down at 09:02 for A/M.
ag) Haripur 230 kV CB(855B,mid) was under open from 10:51 to 13:28 for R/H maintenance.
ah) Aminbazar-Meghna 230 kV Ckt-1 was under shut down from 12:56 to 20:23 for flashing at Isolator of Aminbazar
end.
ai) Khulna(c) 132/33 kV T-1 transformer was under shut down from 11:39 to 11:49 for 33 kV Maintenance work |  |  |  |  | About 9 MW power interruption occurred under Khulna(c) S/S area
by WZPDCO. |  |  |  |  | from 11:39 to 11:49.
aj) Bagherhat 132/33 kV T-2 transformer was under shut down from 11:41 to 12:11 for fuse replacement.
ak) Aminbazar-Hasnabad 230 kV Ckt-1 was under shut down from 09:27 to 13:56 for A/M.
al) Bhola 225 MW CCPP GT-1 was synchronized at 14:12 and GT-2 was synchronized at 17:57.
am) Siddhirganj 335 MW GT synchronized at 19:07.
an) Kushiara CCPP was under shut down since at 05:22(12/11/2019) for filter change .
ao) EGCB 335 MW CCPP ST was synchronized at 06:06(12/11/19).
ap) After maintenance Khulna(S)-Satkhira 132 kV Ckt-2 was switched on at 00:20.
aq) Khulna©-Goalpara 132 kV Ckt-1 was under shut down since at 07:24 due to red hot maint wave trap Y
phase at Goalpara end.
ar) Hasnabad-Brammongaon 132 kV Ckt was shut down since at 07:19 for A/M.
as) Dohazari-Cox's bazar 132 kV Ckt-1 was under shut down since at 06:31 for A/M.
at) Tongi-Uttara 132 kV Ckt was under shut down since at 07:52 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 840000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 1225000 | under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 7178855
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8311810 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 303 | 8657000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8222875 | frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 59177 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 249120
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Reserve
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 118 | 2024000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 610337 | Gas shortage.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 217296
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 44280 | Low demand.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 246474 | Low demand.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 138427 | Low demand.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 54 | 350400 | Low demand.
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1082400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 677700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Reserve
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 200 | 740181 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 16 | 424800 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1073076
| Dhaka area Total |  |  |  | 5811 | 2126 | 43175708
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2500000
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 81540
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 84960 | Low demand.
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 78 | 1743400 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 149 | 3272922 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1646792
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 143488 | Low demand.
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1359720
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 272640 | Low demand.
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 279312
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 296160
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1065600
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16920
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 36093 | Low demand.
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 800 | 12799547
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1848682
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4313000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 7017900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6470000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 524592 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 791520
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Low demand
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 525848 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 145527 | Low demand
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 1783520 | Low demand
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 50 | 131520 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 293364
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 112140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2160000
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 404600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 258350
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1411 | 26998017
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3645120
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 122760 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 79680 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 160 | 1699200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 332 | 5560960
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1117000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2907974 | Low demand
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 238 | 4916000 | frequency control.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 574200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 73584
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 134096
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1280928 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 899520 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 40 | 655200 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 255000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 38 | 500760 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 327504
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7310000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 341 | 6166000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Reserve
| Sylhet Area Total |  |  |  | 1949 | 1429 | 27117766
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 778 | 12806545 | Low demand
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 37440 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 5280 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 7354080 | Low demand
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 174000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 131040 | Low demand.
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 48 | 120960 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1209 | 20629345
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 137280 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 18 | 272300 | Low demand
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 81 | 676000 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 210880 | Low demand
| Barisal Area Total |  |  |  | 462 | 121 | 1296460
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1305000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 642710
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 197 | 4327091 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4290009 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 347 | 9037327 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 290160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 209700
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 178218
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 43 | 283264 | low demand.
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 489216
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1045 | 21052695
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 251 | 4787400
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 498240
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29933
| Rangpur Area Total |  |  |  | 605 | 364 | 5315573
| Total |  |  |  | 19018 | 8837 | 163946071
| Eastern Grid Total |  |  |  | 13454 | 6098 | 115651998
| Western Grid Total |  |  |  | 5564 | 2739 | 48294073
| National Grid Total |  |  |  | 19018 | 8837 | 163946071
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-11
(a) ENTIRE EASTERN GRID : |  | 6072 | MW | (b) ENTIRE WESTERN GRID : |  | 2309 | MW
i) Dhaka area |  | 3445 | MW | i) Khulna area |  | 779 | MW
ii) Chittagong area |  | 899 | MW | ii) Rajshahi area |  | 850 | MW
iii) Comilla area |  | 713 | MW | iii) Barisal area |  | 134 | MW
iv) Mymensingh area |  | 674 | MW | iv) Rangpur area |  | 546 | MW
v) Sylhet area |  | 341 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8381 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1500 | Srimongal | 27 | 1800 | Bottail | 96 | 1800
Munsiganj | 88 | 2000 | Shahjibazar | 81 | 1930 | G.K Project | 38 | 1830
Sonargaon | 72 | 2000 | Fenchuganj | 23 | 1800 | Faridpur | 126 | 1800
Shyampur | 172 | 1000 | Kulawara | 31 | 1830 | Madaripur | 30 | 2200
Bhulta | 164 | 1100 | Sylhet | 105 | 1800 | Sariatpur | 20 | 2000
Madanganj | 26 | 1800 | Chatak | 18 | 1830 | Gopalganj | 20 | 2100
Shitalakhya | 85 | 1800 | Sunamganj | 29 | 1830 | Bagerhat | 8 | 2100
Rahim steel | 23 | 900 | Biani Bazar | 37 | 2100 | Mongla | 30 | 1930
Matuail | 88 | 1200 | Comilla (S) | 124 | 1830 | Satkhira | 31 | 2000
Ghorasal | 75 | 1800 | Comilla(N) | 71 | 1900 | Gallamari | 40 | 1300
Narsingdi | 113 | 2000 | Chandpur | 61 | 2100 | Magura | 36 | 1830
Haripur (SBU) | 82 | 1100 | Feni | 96 | 1800 | Norail | 19 | 1800
Ullon | 59 | 1900 | Chowmuhani | 124 | 1800 | Chuadanga | 63 | 1800
Hasnabad | 161 | 1900 | Ashuganj | 39 | 1930 | Barisal(N) | 2 | 1930
Magbazar | 95 | 1600 | Daudkandi | 86 | 2100 | Barisal (S) | 62 | 1900
Maniknagar | 92 | 1300 | B.Baria | 99 | 2100 | Patuakhali | 67 | 2100
Bangabhaban | 20 | 1200 | Ramganj | 40 | 2100 | Bhandaria | 7 | 2100
Narinda | 80 | 1300 | Madunaghat | 49 | 1800 | Borhan Uddin | 17 | 2200
Dhanmondi | 129 | 1300 | Hathazari | 78 | 1930 | Ishurdi | 46 | 1830
Lalbag | 76 | 1300 | Khulshi | 168 | 1300 | Ruppur Paromanobik | 1 | 100
Madartek | 53 | 1900 | Halishahar | 119 | 1100 | Natore | 89 | 1800
Mirpur | 87 | 1800 | Baraulia | 79 | 1830 | Bogra | 144 | 1800
Kalyanpur | 93 | 1830 | Sikalbaha | 21 | 1830 | Noagaon | 78 | 1830
Gulshan | 124 | 1200 | Dohazari | 72 | 1800 | Rajshahi | 99 | 1830
Uttara | 47 | 1800 | Cox'sbazar | 85 | 1800 | Rajshahi New | 9 | 2000
Uttara New | 34 | 1200 | Chandraghona | 24 | 1800 | C.Nawabganj | 51 | 2000
Kamrangirchar | 64 | 1830 | Kaptai | 4 | 1800 | Amnura | 23 | 1800
Savar | 114 | 1500 | A. Khaer Stl. | 0 | 100 | Pabna | 79 | 1800
Bhasantec | 133 | 1800 | Bakulia | 72 | 1830 | Shahjadpur | 73 | 1900
Agargaon | 45 | 1300 | Julda | 18 | 1200 | Serajganj | 72 | 1900
Satmosjid | 79 | 1800 | TK chemical | 13 | 1800 | Niyamatpur | 41 | 2000
Tongi | 129 | 1830 | Modern Steel | 10 | 700 | Joypurhat | 41 | 2000
Kabirpur | 187 | 1800 | Shahmirpur | 24 | 1100 | Sherpur(Bogura) | 36 | 1800
Basundhara | 90 | 1800 | Khagrachhari | 16 | 1800 | Mohastangor | 11 | 1800
Manikganj | 70 | 1800 | Matarbari | 24 | 1900 | Rangpur | 109 | 1830
Joydevpur | 178 | 1900 | Baroiar Hat | 18 | 1800 | Lalmonirhat | 44 | 1800
New Tongi | 92 | 1200 | Rangamati | 10 | 1800 | Saidpur | 83 | 1830
Korda | 208 | 1930 | Abul Khair 230 | 132 | 1300 | Purbasadipur | 77 | 1800
Dhamrai | 50 | 1800 | BSRM | 104 | 1000 | Thakurgaon | 54 | 1900
Valuka | 84 | 1930 | GPH Ispat | 7 | 1600 | Palashbari | 87 | 1800
Tangail | 150 | 1800 | Goalpara | 18 | 200 | Barapukuria | 41 | 1800
Mymensing | 166 | 1800 | Central s/s | 54 | 1830 | Panchagar | 39 | 1800
Kishorganj | 83 | 1900 | Noapara | 31 | 1800 | Joldhaka | 18 | 149
Netrokona | 74 | 1800 | Jessore | 88 | 1830 | Kurigram | 36 | 1830
Jamalpur | 87 | 1800 | Benapol | 28 | 1830
Sherpur | 72 | 1800 | Jhenida | 77 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-11 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 387 | 3:00 | 381 | 16:00 | Kaliakoir | 371 | 4:00 | 357 | 15:00
Bheramara | 404 | 3:00 | 396 | 18:00 | Bhulta | 373 | 2:00 | 366 | 15:00
a f | 380 | 22:00 | 371 | 16:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal | 228 | 1:00 | 228 | 1:00 | Hathazari | 221 | 18:30 | 215 | 5:00
Ishurdi | 239 | 2:00 | 233 | 20:00 | Megnaghat | 222 | 1:00 | 210 | 17:00
Ashuganj | 232 | 18:00 | 226 | 10:00 | Fenchuganj | 234 | 22:00 | 229 | 10:00
Serajganj | 233 | 4:00 | 230 | 8:00 | Siddhirganj | 222 | 6:00 | 215 | 11:00
Baghabari | 238 | 4:00 | 234 | 19:30 | Maniknagar | 221 | 1:00 | 212 | 15:00
Barapukuria | 230 | 4:00 | 225 | 12:00 | Old Airport | 221 | 3:00 | 211 | 15:00
Bogra | 232 | 3:00 | 226 | 13:00 | Barisal | 237 | 10:00 | 0 | 1:00
Khulna South | 240 | 4:00 | 229 | 19:30 | AKSML | 215 | 12:00 | 209 | 23:00
Rampura | 221 | 1:00 | 213 | 16:00 | BSRM | 218 | 14:00 | 211 | 10:00
Haripur | 220 | 1:00 | 213 | 16:00 | Bibiyana | 231 | 3:00 | 227 | 4:00
Hasnabad | 220 | 7:00 | 211 | 15:00 | Bhulta | 223 | 4:00 | 216 | 15:00
Aminbazar | 222 | 1:00 | 211 | 15:00 | Ashuganj (S) | 229 | 3:00 | 225 | 24:00
Tongi | 215 | 19:30 | 207 | 15:00 | Kaliakoir | 223 | 22:00 | 215 | 15:00
Comilla (N) | 227 | 5:00 | 222 | 10:00 | GPH | 216 | 18:00 | 211 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 100 | 129 | 1000 | Halishahar | 132 | 1830 | 125 | 300
Munsiganj | 133 | 400 | 128 | 1000 | Baraulia | 130 | 1830 | 125 | 700
Megnaghat | 132 | 100 | 127 | 700 | Sikalbaha | 129 | 1700 | 126 | 100
Shyampur | 134 | 100 | 129 | 1500 | Dohazari | 130 | 1700 | 124 | 500
Bhulta | 129 | 300 | 124 | 1000 | Cox'sbazar | 125 | 1700 | 112 | 1300
Madanganj | 132 | 1830 | 126 | 1000 | Chandraghona | 131 | 1700 | 127 | 200
Shitalakhya | 136 | 100 | 127 | 1500 | Kaptai | 131 | 1800 | 128 | 100
Rahim steal | 134 | 300 | 130 | 1000 | A. Khaer Stl. | 129 | 1700 | 125 | 400
Matuail | 132 | 100 | 128 | 1200 | Bakulia | 129 | 1800 | 123 | 200
Ghorasal | 135 | 100 | 135 | 200 | Julda | 131 | 1830 | 124 | 200
Narsinghdi | 132 | 600 | 129 | 1830 | TK Chemical | 131 | 1900 | 125 | 100
Haripur (SBU) | 134 | 100 | 130 | 1100 | Modern Steel | 130 | 1830 | 125 | 100
Ullon | 131 | 600 | 127 | 1200 | Shahmirpur | 130 | 1700 | 126 | 100
Hasnabad | 135 | 600 | 128 | 1700 | Khagrachhari | 130 | 1700 | 127 | 200
Magbazar | 134 | 500 | 126 | 1200 | Matarbari | 129 | 1700 | 0 | 800
Maniknagar | 135 | 600 | 125 | 1200 | Baroiar Hat | 129 | 1500 | 126 | 2100
Bangabhaban | 135 | 600 | 125 | 1200 | Rangamati | 130 | 1200 | 127 | 100
Narinda | 135 | 600 | 125 | 1200 | Goalpara | 135 | 300 | 128 | 1300
Dhanmondi | 135 | 600 | 125 | 1200 | Central s/s | 134 | 400 | 127 | 1300
Lalbag | 135 | 600 | 127 | 1300 | Noapara | 134 | 500 | 125 | 1300
Madartek | 132 | 500 | 126 | 1300 | Jessore | 132 | 500 | 124 | 1300
Mirpur | 136 | 600 | 128 | 1200 | Benapol | 135 | 300 | 125 | 1930
Kalyanpur | 137 | 100 | 124 | 1200 | Jhenida | 134 | 200 | 123 | 2000
Gulshan | 131 | 300 | 125 | 1600 | Bottail | 136 | 300 | 129 | 1930
Uttara | 137 | 600 | 128 | 1300 | G.K Project | 140 | 400 | 136 | 1800
Uttara New | 134 | 100 | 127 | 1700 | Faridpur | 133 | 400 | 127 | 1930
Kamrangirchar | 135 | 400 | 126 | 1600 | Madaripur | 134 | 1000 | 125 | 2100
Savar | 134 | 600 | 127 | 1600 | Sariatpur | 133 | 1700 | 125 | 2100
Bhasantec | 134 | 100 | 125 | 1500 | Gopalganj | 140 | 1900 | 130 | 1500
Agargaon | 135 | 400 | 127 | 1500 | Bagerhat | 135 | 400 | 126 | 2200
Satmosjid | 134 | 600 | 127 | 1500 | Mongla | 132 | 400 | 125 | 1300
Tongi | 131 | 400 | 126 | 900 | Satkhira | 134 | 400 | 125 | 2100
Kabirpur | 129 | 1300 | 121 | 800 | Gallamari | 134 | 400 | 128 | 1300
Basundhara | 130 | 200 | 124 | 1500 | Magura | 134 | 500 | 122 | 1930
Manikganj | 135 | 1300 | 128 | 1000 | Norail | 134 | 400 | 121 | 1900
Joydevpur | 135 | 2100 | 133 | 1200 | Chuadanga | 133 | 500 | 119 | 1930
New Tongi | 135 | 900 | 125 | 1500 | Barisal(N) | 136 | 1800 | 129 | 1400
Kodda | 126 | 2000 | 122 | 1600 | Barisal (S) | 136 | 1800 | 128 | 1600
Dhamrai | 131 | 300 | 125 | 1800 | Patuakhali | 135 | 1800 | 127 | 1200
Valuka | 131 | 1700 | 120 | 100 | Bhandaria | 135 | 1800 | 129 | 1400
Tangail | 130 | 500 | 123 | 1800 | Ishurdi | 136 | 600 | 133 | 1800
Mymensing | 131 | 1700 | 121 | 2300 | Ruppur Paromanobik | 135 | 600 | 132 | 1800
Kishorganj | 130 | 1000 | 125 | 2200 | Natore | 135 | 1700 | 130 | 1930
Netrokona | 130 | 1700 | 121 | 100 | Bogra | 136 | 600 | 132 | 1300
Jamalpur | 137 | 1700 | 118 | 100 | Noagaon | 134 | 1800 | 130 | 1900
Sherpur | 135 | 1700 | 118 | 700 | Rajshahi | 133 | 1700 | 127 | 1200
Srimongal | 136 | 1400 | 133 | 2300 | Rajshahi New | 132 | 1800 | 127 | 800
Shahjibazar | 135 | 1200 | 132 | 1000 | C.Nawabganj | 130 | 1700 | 122 | 800
Fenchuganj | 133 | 1400 | 130 | 900 | Amnura | 134 | 1700 | 124 | 700
Khulawara | 132 | 1500 | 130 | 100 | Pabna | 140 | 500 | 133 | 2000
Sylhet | 130 | 1400 | 127 | 1000 | Shahjadpur | 140 | 1700 | 138 | 1900
Chatak | 131 | 2200 | 127 | 1600 | Serajganj | 137 | 500 | 131 | 1300
Sunamganj | 130 | 2200 | 126 | 1800 | Niyamatpur | 133 | 600 | 127 | 1800
Biani Bazar | 130 | 500 | 127 | 1700 | Joypurhat | 135 | 600 | 130 | 2000
Comilla(s) | 131 | 400 | 127 | 1600 | Sherpur(Bogura) | 136 | 600 | 132 | 1830
Comilla(n) | 136 | 700 | 132 | 1000 | Mohastangor | 135 | 1100 | 130 | 1800
Chandpur | 132 | 700 | 130 | 1400 | Rangpur | 129 | 600 | 122 | 1300
Feni | 128 | 1700 | 125 | 2100 | Lalmonirhat | 123 | 500 | 118 | 1200
Chowmuhani | 128 | 200 | 125 | 1700 | Saidpur | 128 | 600 | 120 | 1300
Ashuganj | 135 | 300 | 134 | 1500 | Purbasadipur | 126 | 1700 | 120 | 800
Daudkandi | 131 | 700 | 128 | 1500 | Thakurgaon | 124 | 600 | 114 | 1200
B.Baria | 133 | 1400 | 130 | 2100 | Palashbari | 130 | 600 | 125 | 1800
Ramganj | 129 | 700 | 122 | 2100 | Barapukuria | 130 | 600 | 125 | 1300
Madanhat | 133 | 1900 | 127 | 100 | Panchagar | 123 | 400 | 108 | 1830
Hathazari | 132 | 1830 | 128 | 100 | Joldhaka | 129 | 600 | 120 | 1800
Khulshi | 129 | 1830 | 124 | 100 | Kurigram | 127 | 600 | 120 | 1300
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 440 | 4687 | 2295 | 6982 |  |  |  | QF-LDC-12
0:30 | 296 | 4264.5 | 1919.5 | 6184 | Date: | 2019-11-11
1:00 | 152 | 3842 | 1544 | 5386
1:30 | 183 | 3747 | 1538.5 | 5285.5
2:00 | 214 | 3652 | 1533 | 5185
2:30 | 242 | 3599 | 1531.5 | 5130.5 | [5 empty] | Gen. at Eve. Peak | 8837 | 8837 MW (19:00 )
3:00 | 270 | 3546 | 1530 | 5076 | [6 empty] | 19:00
3:30 | 275 | 3521 | 1527 | 5048 | [5 empty] | Gen. at Day Peak | 7183.2 | 7183.2 MW (12:00 )
4:00 | 280 | 3496 | 1524 | 5020 | [6 empty] | 12:00
4:30 | 288 | 3460 | 1524.5 | 4984.5 | [5 empty] | Highest Generation | 8837
5:00 | 296 | 3424 | 1525 | 4949 | [6 empty] | 19:00
5:30 | 283 | 3447 | 1541 | 4988
6:00 | 270 | 3470 | 1557 | 5027
6:30 | 245 | 3591.65 | 1576.6 | 5168.25
7:00 | 220 | 3713.3 | 1596.2 | 5309.5
7:30 | 225 | 3888.15 | 1656.4 | 5544.55
8:00 | 230 | 4063 | 1716.6 | 5779.6
8:30 | 295 | 4260.1 | 1756.75 | 6016.85
9:00 | 360 | 4457.2 | 1796.9 | 6254.1
9:30 | 380 | 4594.95 | 1805.15 | 6400.1
10:00 | 400 | 4732.7 | 1813.4 | 6546.1
10:30 | 330 | 4916.7 | 1823.9 | 6740.6
11:00 | 260 | 5100.7 | 1834.4 | 6935.1
11:30 | 203 | 5242.1 | 1817.05 | 7059.15
12:00 | 146 | 5383.5 | 1799.7 | 7183.2
12:30 | 138 | 5375.3 | 1845.8 | 7221.1
13:00 | 130 | 5367.1 | 1891.9 | 7259
13:30 | 180 | 5241.833 | 1889.65 | 7131.483
14:00 | 230 | 5116.566 | 1887.4 | 7003.966
14:30 | 295 | 5200.733 | 1918.7 | 7119.433
15:00 | 360 | 5284.9 | 1950 | 7234.9
15:30 | 390 | 5219.1835 | 1971.85 | 7191.0335
16:00 | 420 | 5153.467 | 1993.7 | 7147.167
16:30 | 420 | 5133.8185 | 2056.4 | 7190.2185
17:00 | 420 | 5114.17 | 2119.1 | 7233.27
17:30 | 370 | 5495.585 | 2435.05 | 7930.635
18:00 | 320 | 5877 | 2751 | 8628
18:30 | 308 | 5987.5 | 2745 | 8732.5
19:00 | 296 | 6098 | 2739 | 8837
19:30 | 260 | 5881 | 2713 | 8594
20:00 | 300 | 5708 | 2721 | 8429 |  |  |  | Executive Engineer
20:30 | 300 | 5695 | 2670 | 8365 |  |  |  | Network Operation Division
21:00 | 300 | 5682 | 2619 | 8301
21:30 | 300 | 5526 | 2516.5 | 8042.5
22:00 | 300 | 5370 | 2414 | 7784 |  |  |  |  | Page 6 of 7
22:30 | 355 | 5149 | 2371 | 7520
23:00 | 410 | 4928 | 2328 | 7256
23:30 | 425 | 4807.5 | 2311.5 | 7119
24:00 | 440 | 4687 | 2295 | 6982
8837 MW (19:00 )
7183.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-11 |  | Energy | 163946071
[10 empty] | 2019-11-11 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3873 | 783 | 1676 | 225 | 250 | 77 | 0 | 0 | 98
0:30 | 3589 | 612.5 | 1506.5 | 112.5 | 205 | 74.5 | 0 | 0 | 84 | Date: | 2019-11-11
1:00 | 3305 | 442 | 1337 | 0 | 160 | 72 | 0 | 0 | 70
1:30 | 3233 | 440.5 | 1311 | 0 | 160 | 72 | 0 | 0 | 69 | [7 empty] | Total Energy | 163.9461 | Total Energy Gen 163.946 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 163.946 MKWHr
2:00 | 3161 | 439 | 1285 | 0 | 160 | 72 | 0 | 0 | 68 | [7 empty] | Energy not Served | 0
2:30 | 3099 | 439 | 1292 | 0 | 160 | 72.5 | 0 | 0 | 68 | [7 empty] | Energy Requirement | 163.9461
3:00 | 3037 | 439 | 1299 | 0 | 160 | 73 | 0 | 0 | 68
3:30 | 3016 | 439 | 1293 | 0 | 160 | 73 | 0 | 0 | 67 | [6 empty] | Shortage
4:00 | 2995 | 439 | 1287 | 0 | 160 | 73 | 0 | 0 | 66
4:30 | 2963.5 | 440.5 | 1281 | 0 | 160 | 73.5 | 0 | 0 | 66
5:00 | 2932 | 442 | 1275 | 0 | 160 | 74 | 0 | 0 | 66
5:30 | 2942 | 442 | 1305 | 0 | 160 | 74 | 0 | 0 | 65
6:00 | 2952 | 442 | 1335 | 0 | 160 | 74 | 0 | 0 | 64
6:30 | 3055.5 | 442 | 1372.5 | 0 | 160 | 74 | 0 | 0 | 64 |  |  |  |  | Coal
7:00 | 3159 | 442 | 1410 | 0 | 160 | 74 | 0 | 0 | 64
7:30 | 3340 | 442 | 1438 | 21.5 | 160 | 74 | 0 | 0 | 66 |  |  |  | Oil |  |  |  | ,
8:00 | 3521 | 442 | 1466 | 43 | 160 | 74 | 0 | 0 | 68
8:30 | 3601.5 | 441.5 | 1507 | 145.5 | 160 | 77 | 0 | 0 | 74
9:00 | 3682 | 441 | 1548 | 248 | 160 | 80 | 0 | 0 | 80
9:30 | 3733 | 441 | 1546.5 | 346 | 160 | 77.5 | 0 | 0 | 81
10:00 | 3784 | 441 | 1545 | 444 | 160 | 75 | 0 | 0 | 82
10:30 | 3795.5 | 441 | 1683.5 | 486 | 160 | 75 | 0 | 0 | 84
11:00 | 3807 | 441 | 1822 | 528 | 160 | 75 | 0 | 0 | 86
11:30 | 3844.5 | 441 | 1820.5 | 604.5 | 160 | 75 | 0 | 0 | 91
12:00 | 3882 | 441 | 1819 | 681 | 160 | 75 | 0 | 0 | 96
12:30 | 3856 | 441 | 1836 | 714.5 | 159.5 | 75 | 19.5 | 0 | 92
13:00 | 3830 | 441 | 1853 | 748 | 159 | 75 | 39 | 0 | 88
13:30 | 3830 | 441 | 1853 | 748 | 159 | 75 | 39 | 0 | 88
14:00 | 3830 | 441 | 1853 | 748 | 159 | 75 | 39 | 0 | 88
14:30 | 3832 | 441 | 1881 | 698.5 | 165.5 | 75 | 40.5 | 0 | 91
15:00 | 3834 | 441 | 1909 | 649 | 172 | 75 | 42 | 0 | 94
15:30 | 3801.5 | 441 | 1884 | 640.5 | 202 | 75 | 42 | 0 | 92
16:00 | 3769 | 441 | 1859 | 632 | 232 | 75 | 42 | 0 | 90
16:30 | 3783 | 441 | 1799 | 705.5 | 241 | 74.5 | 50.5 | 0 | 92
17:00 | 3797 | 441 | 1739 | 779 | 250 | 74 | 59 | 0 | 94
17:30 | 3888.5 | 609.5 | 1785 | 1132 | 250 | 74.5 | 83 | 0 | 108
18:00 | 3980 | 778 | 1831 | 1485 | 250 | 75 | 107 | 0 | 122
18:30 | 4025.5 | 778 | 1839 | 1539.5 | 250.5 | 76.5 | 100.5 | 0 | 123
19:00 | 4071 | 778 | 1847 | 1594 | 251 | 78 | 94 | 0 | 124
19:30 | 4111 | 782 | 1889 | 1310 | 270 | 78 | 34 | 0 | 120
20:00 | 4151 | 782 | 1881 | 1133 | 269 | 78 | 11 | 0 | 124
20:30 | 4167 | 782.5 | 1893.5 | 1041 | 274.5 | 78 | 5.5 | 0 | 123
21:00 | 4183 | 783 | 1906 | 949 | 280 | 78 | 0 | 0 | 122
21:30 | 4175.5 | 783 | 1877.5 | 731 | 280 | 78.5 | 0 | 0 | 117
22:00 | 4168 | 783 | 1849 | 513 | 280 | 79 | 0 | 0 | 112
22:30 | 4096 | 783 | 1771.5 | 402 | 280 | 78.5 | 0 | 0 | 109
23:00 | 4024 | 783 | 1694 | 291 | 280 | 78 | 0 | 0 | 106
23:30 | 3948.5 | 783 | 1685 | 258 | 265 | 77.5 | 0 | 0 | 102 | Max Temp. in Dhaka |  | 30.3° C
24:00 | 3873 | 783 | 1676 | 225 | 250 | 77 | 0 | 0 | 98
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 163.946 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 163.946 MKWHr
Note on W13: Author:

## Generation
2019-11-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 32 | 32 | 33 | 33 | 34 | 34 | 34 | 34 | 40 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 |  | 38 | 38 | 38 | 38 | 39 | 38 | 37 | 779400
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [7 empty] | 2.6 | 10.8 | 8.7 | 6.6 | 20.9 | 13.1 | 16.06 | 11.77 | 5.2 | 0.17 | 0 | [8 empty] | 81540
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 103 | 103 | 107 | 105 | 140 | 140 | 50 | 140 | 140 | 145 | 145 | 145 | 146 | 145 |  | 149 | 146 | 147 | 146 | 150 | 146 | 150 | 3272922
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [15 empty] | 0 | 16 | 51 |  | 51 | 17 | 11 | 0 | 0 |  |  | 143488
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 14 | 55 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1646792
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [8 empty] | 100 | 100 | 143 | 161 | 160 | 75 | 120 | 120 | 120 | 120 |  | 118 | 120 | 120 | 120 | 120 | 120 | 120 | 2024000
17 | Siddhirganj 335 MW CCPP | 209 | 95 | 0 | [16 empty] | 0 | 7 | 6 | 45 | 43 | 42 | 41 | 610337
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 3 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 115 |  | 200 | 160 | 110 | 95 | 0 | 0 |  | 740181
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 840000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 101 | 100 | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 100 | 101 | 101 | 0 | [13 empty] | 1225000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 300 | 300 | 300 | 340 | 340 | 330 | 330 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7178855
26
28 | Ashuganj TPP Unit- 3 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1848682
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 27 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 524592
33 | Ashuganj 225 MW CCPP | 155 | 159 | 156 | 156 | 156 | 170 | 180 | 201 | 190 | 193 | 180 | 180 | 187 | 161 | 176 | 163 | 162 | 190 |  | 180 | 180 | 182 | 181 | 181 | 188 | 172 | 4313000
34 | Ashuganj 450 MW CCPP(South) | 225 | 225 | 230 | 230 | 230 | 235 | 250 | 290 | 275 | 275 | 265 | 265 | 260 | 305 | 285 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 275 | 270 | 6470000
| Ashuganj 450 MW CCPP(North) | 240 | 240 | 240 | 240 | 240 | 240 | 290 | 290 | 270 | 265 | 260 | 260 | 270 | 270 | 285 | 270 | 270 | 285 |  | 340 | 340 | 340 | 340 | 340 | 315 | 260 | 7017900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 49 | 47 | 48 | 50 | 48 | 50 | 51 | 51 |  | 52 | 51 | 51 | 55 | 55 | 56 | 55 | 791520
36 | Chandpur 150 MW CCPP | 53 | 51 | 51 | 49 | 50 | 51 | 50 | 90 | 90 | 90 | 80 | 87 | 84 | 90 | 90 | 86 | 80 | 88 |  | 81 | 82 | 84 | 83 | 81 | 85 | 88 | 1783520
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 345 | 353 | 312 | 280 | 280 | 320 | 371 | 365 | 349 | 351 | 344 | 353 | 347 | 369 | 350 | 351 | 347 |  | 344 | 348 | 343 | 344 | 343 | 344 | 347 | 8311810
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 320 | 350 | 350 | 380 | 380 | 380 | 350 | 380 | 380 | 380 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8222875
41 | Haripur 360MW CCPP(HPL) | 269 | 203 | 203 | 203 | 202 | 202 | 240 | 274 | 303 | 303 | 360 | 323 | 323 | 262 | 303 | 303 | 303 | 303 |  | 303 | 303 | 303 | 303 | 302 | 303 | 303 | 8657000
42 | RPCL 210MW CCPP | 158 | 157 | 156 | 157 | 157 | 157 | 158 | 157 | 154 | 154 | 152 | 152 | 149 | 152 | 151 | 152 | 154 | 153 |  | 156 | 156 | 156 | 156 | 158 | 159 | 158 | 3645120
43
44 | Fenchugonj CCPP Phase-1 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 | 60 | 58 | 58 | 59 | 60 | 60 | 60 | 59 | 58 |  | 58 | 58 | 60 | 58 | 60 | 60 | 58 | 1117000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 242 | 250 | 240 | 239 | 238 | 238 | 260 | 302 | 298 | 299 | 285 | 286 | 288 | 239 | 254 | 245 | 244 | 250 |  | 238 | 264 | 294 | 290 | 282 | 239 | 242 | 4916000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 67 | 67 | 66 | 67 | 66 | 67 | 67 | 67 |  | 68 | 68 | 67 | 67 | 69 | 56 | 40 | 1280928
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 60 | 68 | 70 | 70 | 70 | 70 | 20 | 76 |  | 76 | 76 | 76 | 76 | 76 | 5 | 5 | 899520
49 | Shahjibazar 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 655200
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 255000
52 | Sylhet 50MW PP (EPL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 31 | 32 | 34 | 37 | 36 | 11 | 13 | 37 |  | 38 | 38 | 38 | 36 | 36 | 7 | 7 | 500760
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11MW PP Cofidence-E | [9 empty] | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 134096
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 28 | 28 | 28 | 50 | 52 | 53 | 11 | 53 |  | 53 | 53 | 53 | 53 | 53 | 5 | 5 | 574200
56 | Shahjahanulla 25 MW PP | [9 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 |  |  | 327504
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 290 | 290 | 285 | 280 | 305 | 310 | 315 | 315 | 310 | 300 | 280 | 300 | 290 | 320 | 290 | 270 | 275 |  | 285 | 300 | 270 | 295 | 265 | 275 | 300 | 7310000
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 0 | 5 | 55 |  | 35 | 35 | 17 | 17 |  |  |  | 138427
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 279312
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 19 | 19 | 19 | 19 |  |  | 249120
62 | Tangail 22 MW PP (Doreen) | [9 empty] | 22 | 22 | 22 | 22 | 22 | 0 | [11 empty] | 122760
63 | Impoprt (Tripura) | 70 | 68 | 68 | 66 | 66 | 64 | 64 | 68 | 80 | 82 | 86 | 96 | 88 | 90 | 94 | 90 | 94 | 122 |  | 124 | 120 | 124 | 122 | 112 | 106 | 98 | 2160000
64 | Malancha, Ctg. EPZ (United) | 9 | 9 | 6 | 5 | 6 | 9 | 15 | 4 | 2 | 3 | 2 | 4 | 4 | 6 | 4 | 4 | 4 | 5 |  | 5 | 12 | 17 | 32 | 36 | 40 | 40 | 296160
65 | Feni 22MW PP (Doreen) | [8 empty] | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 293364
66 | Feni 11 MW PP (Doreen) | [9 empty] | 5 | 5 | 11 | 11 | 11 | 11 | 0 | 0 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 112140
67 | Jangalia 33MW PP (Summit) | [10 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 404600
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 2 | 2 | 2 | 2 | 6 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 12 | 12 | 15 |  | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 258350
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 16 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 14 |  | 28 | 28 | 30 | 30 | 30 | 30 | 31 | 482400
71 | Maona 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 677700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802500
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [15 empty] | 0 | 12 | 40 |  | 16 | 0 | [5 empty] | 79680
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [7 empty] | 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 90 |  | 90 | 90 | 90 | 70 | 52 | 17 |  | 1073076
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.1 | 0.4 | 0.7 | 1.9 | 3.4 | 2.2 | 5.2 | 4.606 | 2.83 | 0.767 | 0 | [9 empty] | 16920
| Jodiac Power | [15 empty] | 0 | 1 | 13 |  | 17 | 0 | [5 empty] | 36093
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 30 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 1359720
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 28 | 49 | 49 | 46 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 5 | 73584
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 11 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 7 | 7 | 525848
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [10 empty] | 2 | 18 | 18 | 0 |  | 0 | 2 | 16 |  | 22 | 0 | [5 empty] | 84960
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 3 | 42 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 65 | 30 | 10 | 1065600
97 | Katpotti 52 MW PP (Sinha) | [13 empty] | 0 | 1 | 6 | 6 | 23 |  | 48 | 48 | 24 | 24 | 24 | 19 | 13 | 217296
98 | Bosila 108MW PP(CLC) | [10 empty] | 12 | 30 | 30 | 30 | 30 | 30 | 30 | 54 |  | 54 | 56 | 30 | 30 | 8 |  |  | 350400
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 5 | 15 | 0 |  |  | 0 | 15 |  | 15 | 0 | [5 empty] | 59177
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 17 |  |  |  |  | 246474
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2907974
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 1 | 1.7 | 2.1 | 0.7 | 2.4 | 1.8 | 1.9 | 1.3 | 0.5 | 0 | [9 empty] | 14200
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 0 | 14 | 17 |  | 17 | 17 | 0 |  |  |  |  | 44280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 24 | 52 | 80 | 88 | 100 | 100 | 100 | 100 | 100 | 100 | 144 |  | 160 | 160 | 160 | 160 | 80 | 30 | 7 | 1699200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 21 | 68 | 70 | 57 | 48 | 42 | 35 | 30 |  | 16 | 0 | [5 empty] | 424800
115 | Juldah 100 MW PP Unit-3 (Acorn) | [9 empty] | 0 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 50 |  | 50 | 10 | 10 | 10 | 0 | 0 |  | 272640
116 | Chandpur 200MW (Desh energy) | [15 empty] | 0 | 3 | 47 |  | 50 | 17 | 22 | 0 | 0 |  |  | 131520
117 | Ashuganj 150MW PP (Midland) | [15 empty] | 0 | 1 | 28 |  | 70 | 30 | 0 |  |  |  |  | 145527
118 | Bibiyana-III 400 MW CCPP | 228 | 228 | 226 | 227 | 227 | 226 | 226 | 226 | 227 | 227 | 228 | 227 | 227 | 227 | 228 | 229 | 227 | 339 |  | 341 | 341 | 341 | 339 | 340 | 342 | 340 | 6166000
| Jamalpur 115 MW PP (United) | [26 empty] | 0
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 3842 | 3652 | 3546 | 3496 | 3424 | 3470 | 3713.3 | 4063 | 4457.2 | 4732.7 | 5100.7 | 5383.5 | 5367.1 | 5116.566 | 5284.9 | 5153.467 | 5114.17 | 5877 |  | 6098 | 5881 | 5708 | 5682 | 5370 | 4928 | 4687 | 115651998
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [15 empty] | 0 | 9 | 16 |  | 16 | 0 | [5 empty] | 37440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 0 | 13 |  | 0 | [6 empty] | 5280
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [15 empty] | 0 | 17 | 53 |  | 17 | 17 | 17 | 17 | 0 |  |  | 131040
130
131
132
133
| Barisal 110 MW PP (Summit ) | [10 empty] | 16 | 32 | 32 | 16 | 16 | 0 | 16 | 16 |  | 0 | [6 empty] | 137280
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [12 empty] | 5 | 13 | 20 | 21 | 22 | 22 |  | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 210880
| Bhola 225 MW CCPP | [13 empty] | 0 | 15 | 58 | 60 | 75 |  | 81 | 83 | 90 | 90 | 80 | 90 | 80 | 676000
140 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 8 | 8 | 16 | 11 | 12 | 12 | 12 | 13 | 14 | 18 |  | 18 | 17 | 21 | 23 | 20 | 21 | 20 | 272300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 40 |  | 40 | 40 | 40 | 40 | 8 | 0 |  | 174000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [9 empty] | 18 | 0 |  |  |  |  | 0 | 14 | 54 |  | 48 | 17 | 17 | 0 |  |  |  | 120960
146 | Bheramara HVDC | 442 | 439 | 439 | 439 | 442 | 442 | 442 | 442 | 441 | 441 | 441 | 441 | 441 | 441 | 441 | 441 | 441 | 778 |  | 778 | 782 | 782 | 783 | 783 | 783 | 783 | 12806545
147 | Bheramara 360 MW CCPP | 260 | 260 | 240 | 240 | 245 | 245 | 245 | 280 | 325 | 325 | 310 | 310 | 310 | 335 | 330 | 310 | 310 | 320 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7354080
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 172 | 232 | 250 | 250 |  | 251 | 270 | 269 | 280 | 280 | 280 | 250 | 4787400
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 55 | 55 | 55 | 55 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 1305000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 184 | 183 | 176 | 187 | 154 | 163 | 158 | 181 | 170 | 173 | 169 |  | 197 | 198 | 198 | 200 | 197 | 189 | 192 | 4327091
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 133 | 133 | 133 | 133 | 133 | 146 | 188 | 192 | 184 | 182 | 156 | 195 | 173 | 173 | 161 | 171 | 172 |  | 188 | 188 | 189 | 190 | 190 | 186 | 204 | 4290009
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 342 | 342 | 359 | 353 | 346 | 378 | 384 | 391 | 385 | 386 | 383 | 384 | 387 | 387 | 399 | 399 | 386 | 373 |  | 347 | 370 | 383 | 384 | 337 | 363 | 380 | 9037327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 2 | 22 | 0 | 0 | 290160
163 | Bogura 20 MW PP (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 209700
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 178218
165 | Amnura 50 MW PP(Sinha) | 0 | [7 empty] | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 12 | 0 | 0 | 642710
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 0 | 39 | 42 | 42 | 42 | 43 | 43 |  | 43 | 17 | 0 |  |  |  |  | 283264
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [15 empty] | 0 | 7 | 73 |  | 113 | 113 | 113 | 74 | 35 |  |  | 489216
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [15 empty] | 0 | 35 | 109 |  | 113 | 113 | 114 | 70 | 34 | 0 | 0 | 498240
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.2 | 1.6 | 1.9 | 2.4 | 5.4 | 3.7 | 5.9 | 4.4 | 3 | 0.7 | 0.1 | 0 | [8 empty] | 29933
178
178