## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-14 | Thursday
|  | Date (day): | 2019-11-14 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12474.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14915 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-13 | 2019-11-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under S/D
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 35 | 35 | 40 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 14 | 65 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 363 | 320 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 300 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 300 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 252 | 254 | 250 | 250 |  | 85 | Engine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 48 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 50 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 68 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 2 | 180 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 31 | 20 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 71 | 90 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1960 | 2143 | 3760 | 4162 | 660 | 908
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20.1 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 33 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 75 | 75 | 75 | 155 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 149 | 100 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 87 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 10 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 8 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 54 | 63 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.6 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 656.7 | 731 | 1351 | 1518 | 305 | 323
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 175 | 203 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 340 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 360 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 34 | 32 | 34 |  | 11 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 55 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 45 | 45 | 45 | 150 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 25 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 30 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 87 | 86 | 90 |  | 73 | Machine Problem
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 50 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 134 | 113 | 145
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 21 | 21 |  | 4 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1209 | 1530 | 1723 | 2166 | 448 | 104
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 156 | 150 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 36 | 135 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 192.2 | 321 | 388.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 40 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 42 | 54 | 54 | 54
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 275 | 317 | 300 | 320
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 44 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 49 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 74 | 74 | 74 |  | 12 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 6 | 36 | 32 | 36 |  | 14 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 337 | 305 | 350 | 360
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1169 | 1520 | 1600 | 1634 | 0 | 168
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 818 | 915 | 831 | 930
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 335 | 300 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 17 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1153 | 1272 | 1326 | 2156 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 26 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 75 | 141 | 140 | 141
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 60 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 101 | 227 | 331 | 402 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 45 | 60 | 60 | 40 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 24 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 189 | 191 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 185 | 174 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 347 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 17 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 118 | 118 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1025 | 1016 | 1584 | 1848 | 260 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 250 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 235.4 | 363 | 411 | 437 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 7701.3 | 9123 | 12474.6 | 14915 | 1715 | 1688
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7362.7906 | 8722 | 11926.281 | 14259.4136
A. |  | 2019-11-13 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9123 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5992 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9123 | MW
3 | Day peak Generation : |  |  | 7701.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8722 | MW
4 | Evening peak Generation : |  |  | 9123 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 178.7028 | MKWHr | By Solar | 0.21326 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 135.6818 | MKWHr |  | By Oil: | 15.2897 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 5.9389 | MKWHr |  | By Hydro: | 1.7173 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1715 | MW | Dhaka | 3459 | 3459 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1688 | MW | Chittagong | 976 | 976 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3403 | MW | Khulna | 868 | 868 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1090.54 | MMCFD |  |  | Rajshahi | 835 | 835 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 123311124.724 | ii) Oil : | Taka | 120829207.31 | Comilla | 789 | 789 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 24290101 | Total | Taka | 268430433.034 | Mymensingh | 675 | 675 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 376 | 376 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 280 | MW (E to W) at | 19:00 | hrs | Barisal | 186 | 186 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | 150 | MW at | 18:00 | hrs | Rangpur | 558 | 558 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.5° C |  |  | Total | 8722 | 8722 |  | 0
B. |  | 2019-11-14 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 30.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14915 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7800 | MW
4 | Reserve(Generation end) |  |  |  | 5415 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 186.0875 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6170 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2516 | MKWHr. | ii) HVDC Flow at Peak Time |  | 915 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6102 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.57 | 101.57 |  | (b) Today: | 101.57 |  | (c) Rule Curve: |  | 107.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 240 | 14 | 0 | 345 | 243 |  | 0 | 340 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 34 | 40 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 25 | 0 | 19 | 9 | 80 | 0 | 0 | 260 | 325 | 162 | 8 | 88 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 162 | 0 | 0 | 0 | 40 | 44 | 5 | 5 | 100 | 263 | 11 | 5 | 0 | 0 | 0 | 8 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 724 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 280 | 0 | 0 | 172 | 0 | 0 | 0 | 12 | 0 | 166 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4424 | 2271 | 6695 | 3803 | 724 | 1345 | 373 | 280 | 74 | 0 | 96 | 0 | 0 | 101.57
2:00 | 35 | 0 | 0 | 0 | 240 | 14 | 0 | 348 | 243 |  | 0 | 320 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 33 | 40 | 110 | 0 | 0 | 0 | 0 | 110 | 0 |  | 0 | 0 | 0 | 90 | 19 | 0 | 19 | 4 | 80 | 0 | 0 | 260 | 325 | 162 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 90 | 160 | 0 | 0 | 0 | 38 | 44 | 5 | 5 | 100 | 261 | 11 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 432 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 280 | 0 | 0 | 173 | 0 | 0 | 0 | 12 | 0 | 159 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4410 | 1992 | 6402 | 3801 | 432 | 1359 | 367 | 280 | 73 | 0 | 90 | 0 | 0 | 101.57
3:00 | 35 | 0 | 0 | 0 | 240 | 14 | 0 | 344 | 243 |  | 0 | 320 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 33 | 40 | 110 | 0 | 0 | 0 | 0 | 110 | 0 |  | 0 | 0 | 0 | 30 | 0 | 0 | 19 | 4 | 80 | 0 | 0 | 260 | 320 | 161 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 88 | 161 | 0 | 0 | 0 | 40 | 44 | 5 | 5 | 100 | 262 | 11 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 432 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 280 | 0 | 0 | 171 | 0 | 0 | 0 | 12 | 0 | 159 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4224 | 1958 | 6182 | 3713 | 432 | 1337 | 259 | 280 | 73 | 0 | 88 | 0 | 0 | 101.57
4:00 | 35 | 0 | 0 | 0 | 240 | 14 | 0 | 343 | 223 |  | 0 | 280 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 32 | 40 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 4 | 80 | 0 | 0 | 260 | 320 | 162 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 88 | 161 | 0 | 0 | 0 | 39 | 44 | 5 | 5 | 100 | 265 | 11 | 5 | 0 | 0 | 0 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 432 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 280 | 0 | 0 | 168 | 0 | 0 | 0 | 12 | 0 | 158 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4125 | 1958 | 6083 | 3707 | 432 | 1265 | 239 | 280 | 72 | 0 | 88 | 0 | 0 | 101.57
5:00 | 35 | 0 | 0 | 0 | 240 | 14 | 0 | 343 | 223 |  | 0 | 280 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 32 | 40 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 4 | 80 | 0 | 0 | 260 | 325 | 168 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 84 | 129 | 0 | 0 | 0 | 38 | 44 | 5 | 5 | 100 | 274 | 11 | 5 | 0 | 0 | 0 | 8 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 432 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 245 | 0 | 0 | 166 | 0 | 0 | 0 | 12 | 0 | 163 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4091 | 1901 | 5992 | 3704 | 432 | 1216 | 239 | 245 | 72 | 0 | 84 | 0 | 0 | 101.57
6:00 | 35 | 0 | 0 | 0 | 240 | 14 | 0 | 351 | 223 |  | 0 | 280 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 32 | 40 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 9 | 80 | 0 | 0 | 260 | 320 | 163 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 84 | 129 | 0 | 0 | 0 | 38 | 44 | 5 | 5 | 100 | 274 | 11 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 305 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 432 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 176 | 0 | 0 | 0 | 12 | 0 | 168 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4124.02 | 1882 | 6006.02 | 3717 | 432 | 1252 | 239 | 210 | 72 | 0 | 84 | 0.02 | 0 | 101.57
7:00 | 35 | 0 | 0 | 0 | 230 | 14 | 0 | 369 | 271 |  | 0 | 320 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 12 | 80 | 0 | 0 | 295 | 360 | 182 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 82 | 129 | 0 | 0 | 0.2 | 40 | 44 | 5 | 5 | 100 | 283 | 11 | 5 | 0 | 0 | 0 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 305 | 0 | 0 | 105 | 0.565 | 0 | 0 | 0 |  | 431 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 183 | 0 | 0 | 0 | 12 | 0 | 170 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 110 |  | 4341.765 | 1958.2 | 6299.965 | 3878 | 431 | 1381 | 231 | 210 | 75 | 7 | 82 | 4.965 | 0 | 101.57
8:00 | 35 | 0 | 0 | 0 | 260 | 14 | 0 | 356 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 31 | 25 | 16 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 8 | 80 | 0 | 0 | 260 | 325 | 162 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 82 | 161 | 0 | 0 | 0.8 | 39 | 44 | 5 | 5 | 100 | 276 | 11 | 5 | 0 | 0 | 0 | 7 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 10.9 | 0 | 0 | 0 | 352 | 0 | 70 | 105 | 1.4 | 0 | 0 | 0 |  | 432 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 176 | 0 | 0 | 0 | 12 | 0 | 176 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 118 |  | 4488.1 | 2011.7 | 6499.8 | 3826 | 432 | 1433 | 410 | 210 | 75 | 17 | 82 | 14.8 | 0 | 0
9:00 | 35 | 0 | 0 | 0 | 260 | 14 | 0 | 349 | 300 |  | 0 | 350 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 31 | 17 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 4 | 80 | 0 | 0 | 290 | 345 | 176 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92 | 158 | 0 | 0 | 1.5 | 39 | 44 | 5 | 5 | 100 | 280 | 11 | 5 | 0 | 0 | 0 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 17 | 15.4 | 0 | 0 | 0 | 353 | 0 | 70 | 105 | 2 | 0 | 0 | 0 |  | 577 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 175 | 0 | 0 | 0 | 12 | 0 | 187 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 118 |  | 4614.9 | 2096.2 | 6711.1 | 3834 | 577 | 1454 | 430 | 210 | 75 | 17 | 92 | 22.1 | 0 | 0
10:00 | 35 | 0 | 0 | 0 | 260 | 14 | 0 | 362 | 300 |  | 0 | 350 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 82 | 0 | 0 | 16 | 2 | 80 | 0 | 0 | 270 | 320 | 168 | 8 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 102 | 157 | 0 | 0 | 1.9 | 40 | 44 | 5 | 5 | 100 | 279 | 11 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 32 | 18.62 | 0 | 0 | 0 | 338 | 0 | 71 | 105 | 3.2 | 0 | 0 | 0 |  | 771 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 209 | 0 | 0 | 183 | 0 | 0 | 0 | 12 | 0 | 179 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 118 |  | 4715.72 | 2268.2 | 6983.92 | 3803 | 771 | 1461 | 518 | 209 | 75 | 17 | 102 | 27.92 | 0 | 0
11:00 | 35 | 0 | 0 | 0 | 300 | 14 | 0 | 360 | 330 |  | 0 | 350 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 0 | 80 | 22 | 2 | 19 | 2 | 80 | 0 | 0 | 350 | 335 | 173 | 16 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 106 | 156 | 0 | 0 | 2.1 | 40 | 42 | 5 | 5 | 100 | 276 | 11 | 5 | 0 | 0 | 0 | 6 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 33 | 20.3 | 30 | 0 | 0 | 336 | 0 | 70 | 87 | 4.9 | 0 | 0 | 0 |  | 819 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 199 | 0 | 0 | 0 | 13 | 0 | 194 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 118 |  | 4991.3 | 2327.2 | 7318.5 | 4090 | 819 | 1397 | 572 | 210 | 75 | 17 | 106 | 32.5 | 0 | 0
12:00 | 35 | 0 | 0 | 0 | 300 | 14 | 0 | 363 | 330 |  | 0 | 350 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 0 | 80 | 54 | 6 | 19 | 2 | 80 | 0 | 0 | 360 | 345 | 175 | 16 | 88 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 154 | 0 | 0 | 2.2 | 39 | 42 | 5 | 5 | 100 | 275 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 315 | 0 | 0 | 0 | 2 | 0 | 0 | 36 | 0 | 31 | 20.1 | 50 | 0 | 0 | 337 | 0 | 71 | 87 | 4.6 | 0 | 0 | 0 |  | 818 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 14 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 189 | 0 | 0 | 0 | 12 | 0 | 185 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 118 |  | 5186.9 | 2514.4 | 7701.3 | 4175 | 818 | 1584 | 662 | 230 | 75 | 17 | 108 | 32.3 | 0 | 0
13:00 | 35 | 0 | 0 | 0 | 330 | 14 | 0 | 358 | 330 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 0 | 80 | 66 | 6 | 19 | 9 | 80 | 0 | 0 | 345 | 330 | 168 | 16 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 112 | 154 | 0 | 0 | 1 | 40 | 42 | 5 | 5 | 100 | 278 | 53 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 55 | 0 | 0 | 36 | 0 | 32 | 17 | 50 | 0 | 0 | 348 | 0 | 71 | 87 | 4.3 | 0 | 0 | 0 |  | 818 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 14 | 0 | 176 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 118 |  | 5260.3 | 2499.3 | 7759.6 | 4160 | 818 | 1572 | 728 | 250 | 75 | 17 | 112 | 27.6 | 0 | 0
14:00 | 35 | 0 | 0 | 0 | 300 | 14 | 0 | 320 | 300 |  | 0 | 320 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 90 | 66 | 6 | 19 | 5 | 80 | 0 | 0 | 275 | 325 | 162 | 16 | 87 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 116 | 155 | 0 | 0 | 1.5 | 42 | 42 | 5 | 5 | 100 | 266 | 64 | 5 | 0 | 0 | 0 | 7 | 0 | 280 | 0 | 0 | 0 | 60 | 0 | 0 | 36 | 0 | 30 | 16 | 50 | 0 | 0 | 345 | 0 | 71 | 87 | 3 | 0 | 0 | 0 |  | 818 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 250 | 0 | 0 | 169 | 0 | 0 | 0 | 14 | 0 | 166 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 118 |  | 5015.5 | 2495.6 | 7511.1 | 4015 | 818 | 1454 | 741 | 250 | 75 | 17 | 116 | 25.1 | 0 | 0
15:00 | 35 | 0 | 0 | 0 | 300 | 15 | 0 | 300 | 300 |  | 0 | 320 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 66 | 6 | 19 | 2 | 80 | 0 | 0 | 300 | 325 | 189 | 45 | 87 | 23 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 120 | 154 | 0 | 0 | 1 | 40 | 44 | 5 | 5 | 100 | 276 | 63 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 71 | 0 | 0 | 36 | 0 | 30 | 11 | 50 | 0 | 0 | 346 | 0 | 71 | 105 | 2.35 | 0 | 0 | 0 |  | 819 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 13 | 0 | 168 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 118 |  | 5145.35 | 2430.1 | 7575.45 | 4057 | 819 | 1450 | 770 | 250 | 75 | 17 | 120 | 17.45 | 0 | 0
16:00 | 35 | 0 | 0 | 0 | 300 | 15 | 0 | 300 | 270 |  | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 90 | 73 | 6 | 19 | 2 | 80 | 0 | 0 | 300 | 320 | 181 | 45 | 87 | 34 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 110 | 154 | 0 | 0 | 0.3 | 40 | 54 | 5 | 5 | 100 | 265 | 65 | 5 | 0 | 0 | 0 | 8 | 0 | 275 | 0 | 0 | 0 | 95 | 0 | 0 | 36 | 0 | 30 | 5 | 50 | 0 | 0 | 305 | 0 | 71 | 105 | 1.07 | 0 | 0 | 0 |  | 818 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 178 | 0 | 0 | 0 | 14 | 0 | 161 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 118 |  | 4996.37 | 2344.1 | 7340.47 | 3981 | 818 | 1340 | 759 | 250 | 75 | 0 | 110 | 7.47 | 0 | 0
17:00 | 35 | 0 | 0 | 0 | 300 | 15 | 0 | 300 | 270 |  | 0 | 300 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 44 | 90 | 78 | 6 | 19 | 6 | 80 | 0 | 0 | 305 | 330 | 188 | 45 | 87 | 34 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 112 | 154 | 8 | 0 | 0 | 40 | 54 | 5 | 5 | 100 | 272 | 65 | 5 | 0 | 0 | 0 | 7 | 0 | 295 | 0 | 0 | 0 | 94 | 0 | 0 | 36 | 0 | 30 | 0 | 20 | 0 | 0 | 305 | 0 | 71 | 105 | 0 | 0 | 0 | 0 |  | 818 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 14 | 0 | 166 | 0 | 270 | 0 | 0 | 0 | 0 | 65 | 0 | 0.1 | 118 |  | 5097 | 2427.1 | 7524.1 | 4046 | 818 | 1365 | 814 | 250 | 75 | 44 | 112 | 0.1 | 0 | 0
18:00 | 35 | 0 | 0 | 0 | 300 | 40 | 0 | 278 | 270 |  | 0 | 300 | 0 | 0 | 0 | 12 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 38 | 17 | 17 | 55 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 2 | 0 | 0 | 104 | 0 |  | 0 | 0 | 102 | 90 | 93 | 30 | 19 | 3 | 80 | 0 | 0 | 335 | 360 | 180 | 45 | 87 | 34 | 40 | 0 | 11 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 136 | 156 | 45 | 22 | 0 | 40 | 54 | 37 | 47 | 163 | 302 | 65 | 74 | 0 | 0 | 18 | 7 | 0 | 270 | 24 | 11 | 0 | 209 | 0 | 0 | 103 | 0 | 34 | 0 | 20 | 70 | 60 | 306 | 0 | 71 | 105 | 0 | 0 | 21 | 17 |  | 917 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 141 | 20 | 16 | 0 | 30 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 0 | 20 | 0 | 163 | 0 | 271 | 17 | 0 | 0 | 36 | 109 | 0 | 0 | 118 |  | 6167 | 2782 | 8949 | 4244 | 917 | 1654 | 1571 | 250 | 75 | 102 | 136 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 300 | 65 | 0 | 320 | 300 |  | 0 | 300 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 48 | 0 | 0 | 50 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 102 | 100 | 63 | 33 | 19 | 14 | 80 | 0 | 0 | 340 | 360 | 203 | 45 | 87 | 34 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 134 | 156 | 8 | 22 | 0 | 40 | 54 | 44 | 49 | 163 | 317 | 65 | 74 | 0 | 0 | 18 | 36 | 0 | 320 | 24 | 11 | 0 | 180 | 0 | 0 | 135 | 0 | 20 | 0 | 10 | 50 | 30 | 305 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 915 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 141 | 26 | 0 | 0 | 45 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 0 | 60 | 0 | 174 | 0 | 347 | 0 | 0 | 0 | 17 | 113 | 0 | 0 | 118 |  | 6245 | 2878 | 9123 | 4386 | 915 | 1959 | 1302 | 250 | 75 | 102 | 134 | 0 | 0 | 0
19:30 | 35 | 0 | 0 | 0 | 300 | 75 | 50 | 380 | 356 |  | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 32 | 0 | 0 | 17 | 11 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 102 | 100 | 45 | 19 | 19 | 19 | 80 | 0 | 0 | 335 | 360 | 202 | 45 | 88 | 34 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 132 | 157 | 3 | 22 | 0 | 40 | 54 | 47 | 49 | 163 | 304 | 65 | 74 | 0 | 0 | 18 | 36 | 0 | 325 | 24 | 11 | 0 | 60 | 0 | 0 | 135 | 0 | 15 | 0 | 10 | 50 | 10 | 305 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 915 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 141 | 28 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 193 | 0 | 0 | 0 | 65 | 0 | 173 | 0 | 360 | 0 | 0 | 0 | 17 | 85 | 0 | 0 | 118 |  | 6183 | 2906 | 9089 | 4518 | 915 | 2108 | 989 | 250 | 75 | 102 | 132 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 300 | 84 | 60 | 378 | 357 |  | 0 | 300 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 68 | 100 | 15 | 18 | 19 | 25 | 80 | 0 | 0 | 300 | 320 | 190 | 45 | 88 | 34 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 132 | 156 | 0 | 22 | 0 | 58 | 54 | 44 | 49 | 163 | 300 | 65 | 74 | 0 | 0 | 18 | 40 | 0 | 310 | 24 | 11 | 0 | 30 | 0 | 0 | 135 | 0 | 15 | 0 | 10 | 50 | 6 | 305 | 0 | 88 | 105 | 0 | 0 | 0 | 0 |  | 916 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 141 | 26 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 73 | 0 | 175 | 0 | 360 | 0 | 0 | 0 | 17 | 64 | 0 | 0 | 118 |  | 5977 | 2893 | 8870 | 4436 | 916 | 2126 | 867 | 250 | 75 | 68 | 132 | 0 | 0 | 0
21:00 | 35 | 0 | 0 | 0 | 300 | 91 | 77 | 352 | 358 |  | 0 | 300 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 68 | 100 | 12 | 18 | 16 | 30 | 80 | 0 | 0 | 305 | 330 | 190 | 45 | 87 | 34 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 158 | 0 | 22 | 0 | 59 | 54 | 50 | 46 | 163 | 293 | 66 | 74 | 0 | 0 | 18 | 40 | 0 | 310 | 24 | 11 | 0 | 15 | 0 | 0 | 90 | 0 | 0 | 0 | 10 | 34 | 0 | 305 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 915 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 141 | 28 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 84 | 0 | 166 | 0 | 363 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 118 |  | 5882 | 2820 | 8702 | 4394 | 915 | 2175 | 699 | 250 | 75 | 68 | 126 | 0 | 0 | 0
22:00 | 35 | 0 | 0 | 0 | 300 | 94 | 76 | 344 | 361 |  | 0 | 300 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 34 | 90 | 12 | 0 | 16 | 39 | 80 | 0 | 0 | 300 | 320 | 181 | 45 | 88 | 34 | 56 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 120 | 160 | 0 | 22 | 0 | 58 | 54 | 5 | 46 | 130 | 285 | 67 | 5 | 0 | 0 | 18 | 40 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 10 | 0 | 0 | 306 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 916 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 15 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 172 | 0 | 0 | 0 | 88 | 0 | 156 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 5446 | 2666 | 8112 | 4234 | 916 | 1945 | 538 | 250 | 75 | 34 | 120 | 0 | 0 | 101.56
23:00 | 35 | 0 | 0 | 0 | 300 | 94 | 40 | 344 | 361 |  | 0 | 300 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 90 | 0 | 0 | 16 | 40 | 80 | 0 | 0 | 300 | 320 | 181 | 45 | 87 | 33 | 30 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 112 | 160 | 0 | 0 | 0 | 60 | 54 | 5 | 5 | 130 | 285 | 40 | 5 | 0 | 0 | 0 | 9 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 34 | 105 | 0 | 0 | 0 | 0 |  | 915 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 25 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 249 | 0 | 0 | 160 | 0 | 0 | 0 | 33 | 0 | 157 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 5047 | 2596 | 7643 | 4133 | 915 | 1754 | 405 | 249 | 75 | 0 | 112 | 0 | 0 | 101.57
24:00 | 35 | 0 | 0 | 0 | 300 | 14 | 40 | 346 | 364 |  | 0 | 300 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 10 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 0 | 90 | 0 | 0 | 16 | 40 | 80 | 0 | 0 | 300 | 325 | 181 | 8 | 87 | 33 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 106 | 161 | 0 | 0 | 0 | 60 | 54 | 5 | 5 | 130 | 288 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 17 | 105 | 0 | 0 | 0 | 0 |  | 916 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 25 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 158 | 0 | 0 | 0 | 12 | 0 | 167 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4835 | 2562 | 7397 | 4094 | 916 | 1584 | 372 | 250 | 75 | 0 | 106 | 0 | 0 | 101.57
KWH | 820000 | 0 | 0 | 0 | 6663864 | 688954 | 340256 | 8347640 | 7022000 |  | 0 | 7726250 | 0 | 0 | 0 | 18400 | 5326175 | 0 | 0 | 0 | 135360 | 0 | 0 | 0 | 111360 | 0 | 316032 | 510840 | 33816 | 117144 | 120996 | 600000 | 685080 | 610500 | 800500 | 0 | 0 | 745320 | 972000 | 2600000 | 20000 | 4696 | 0 | 0 | 3032816 | 0 |  | 0 | 0 | 421912 | 1600560 | 734400 | 151200 | 423696 | 405120 | 2036516 | 0 | 0 | 7044200 | 8108000 | 4308000 | 568727 | 2078220 | 474480 | 422880 | 0 | 294188 | 0 | 0 | 0 | 90648 | 45360 | 152500 | 429380 | 2610240 | 3628120 | 82560 | 119088 | 11800 | 1031000 | 1135800 | 295800 | 410760 | 2910232 | 6351000 | 902400 | 458880 | 0 | 0 | 93000 | 369300 | 0 | 7365000 | 127160 | 48968 | 0 | 903272 | 0 | 0 | 950400 | 0 | 378720 | 140535 | 383040 | 295680 | 195709 | 7768000 | 0 | 1226988 | 2433818 | 27360 | 0 | 44168 | 22581 |  | 17251636 | 0 | 7771104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141000 | 3107636 | 429800 | 13440 | 0 | 297000 | 1390000 | 0 | 0 | 149872 | 632960 | 0 | 0 | 11040 | 0 | 92640 | 58320 | 190512 | 0 | 0 | 5938900 | 0 | 0 | 4534082 | 0 | 0 | 0 | 601028 | 0 | 4303145 | 0 | 7605054 | 32640 | 0 | 192 | 75456 | 368640 | 0 | 33565 | 2791776 |  | 120881365 | 57821438 | 178702803 | 97616586 | 17251636 | 38065189 | 14717888 | 5938900 | 1717320 | 571784 | 2610240 | 213260 | 0
Fuel Cost | 918400 | 0 | 0 | 0 | 4931259.36 | 668285.38 | 496773.76 | 6010300.8 | 5336720 |  | 0 | 6181000 | 0 | 0 | 0 | 188784 | 6604457 | 0 | 0 | 0 | 1502496 | 0 | 0 | 0 | 1013376 | 0 | 2958059.52 | 4898955.6 | 322604.64 | 1166754.24 | 90747 | 450000 | 0 | 0 | 0 | 0 | 0 | 193783.2 | 252720 | 3978000 | 30600 | 45128.56 | 0 | 0 | 3851676.32 | 0 |  | 0 | 0 | 4425856.88 | 16469762.4 | 6984144 | 1415232 | 389800.32 | 1126233.6 | 2138341.8 | 0 | 0 | 5212708 | 6810720 | 3963360 | 557352.46 | 2764032.6 | 389073.6 | 435566.4 | 0 | 420688.84 | 0 | 0 | 0 | 92460.96 | 34020 | 288225 | 322035 | 18010656 | 2975058.4 | 785145.6 | 121469.76 | 193520 | 1402160 | 1544688 | 402288 | 513450 | 3608687.68 | 5842920 | 1344576 | 807628.8 | 0 | 0 | 147870 | 432081 | 0 | 5229150 | 95370 | 37215.68 | 0 | 9457257.84 | 0 | 0 | 9142848 | 0 | 3821284.8 | 1621773.9 | 3569932.8 | 2773478.4 | 1833793.33 | 7301920 | 0 | 10932463.08 | 22999580.1 | 0 | 0 | 0 | 0 |  | 46579417.2 | 0 | 6061461.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1394490 | 2486108.8 | 666190 | 144345.6 | 0 | 558360 | 2613200 | 0 | 0 | 1483732.8 | 6563795.2 | 0 | 0 | 109958.4 | 0 | 101904 | 96228 | 144217.584 | 0 | 0 | 24290101 | 0 | 0 | 3989992.16 | 0 | 0 | 0 | 955634.52 | 0 | 3786767.6 | 0 | 5551689.42 | 308774.4 | 0 | 1762.56 | 672312.96 | 3443097.6 | 0 | 0 | 0 |  | 223278762.41 | 112003540.924 | 335282303.334 | 89723572.864 | 46579417.2 | 33587551.86 | 114919617.63 | 24290101 | 446503.2 | 5909589.68 | 18010656 | 1815293.9 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 14 | 0 | 363 | 330 |  | 0 | 350 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 149 | 0 |  | 0 | 0 | 0 | 80 | 54 | 6 | 19 | 2 | 80 | 0 | 0 | 360 | 345 | 175 | 16 | 88 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 154 | 0 | 0 | 2.2 | 39 | 42 | 5 | 5 | 100 | 275 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 315 | 0 | 0 | 0 | 2 | 0 | 0 | 36 | 0 | 31 | 20.1 | 50 | 0 | 0 | 337 | 0 | 71 | 87 | 4.6 | 0 | 0 | 0 |  | 818 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 14 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 189 | 0 | 0 | 0 | 12 | 0 | 185 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 118 |  | 7701.3 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 65 | 0 | 320 | 300 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 48 | 0 | 0 | 50 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 35 | 40 | 110 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 102 | 100 | 63 | 33 | 19 | 14 | 80 | 0 | 0 | 340 | 360 | 203 | 45 | 87 | 34 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 134 | 156 | 8 | 22 | 0 | 40 | 54 | 44 | 49 | 163 | 317 | 65 | 74 | 0 | 0 | 18 | 36 | 0 | 320 | 24 | 11 | 0 | 180 | 0 | 0 | 135 | 0 | 20 | 0 | 10 | 50 | 30 | 305 | 0 | 90 | 105 | 0 | 0 | 0 | 0 |  | 915 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 141 | 26 | 0 | 0 | 45 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 0 | 60 | 0 | 174 | 0 | 347 | 0 | 0 | 0 | 17 | 113 | 0 | 0 | 118 |  | 9123 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 100 | 35 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 250 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 35 | 40 | 110 | 100 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 20 | 80 | 0 | 0 | 360 | 360 | 225 | 45 | 90 | 34 | 55 | 0 | 35 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 145 | 160 | 95 | 22 | 0 | 60 | 54 | 51 | 44 | 163 | 320 | 66 | 74 | 0 | 0 | 20 | 36 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 360 | 115 | 90 | 105 | 0 | 300 | 54 | 110 |  | 930 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 141 | 26 | 110 | 30 | 60 | 70 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 35 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 250 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 35 | 40 | 110 | 100 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 8 | 80 | 0 | 0 | 360 | 360 | 225 | 45 | 86 | 32 | 55 | 0 | 30 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 113 | 150 | 0 | 22 | 1.6 | 60 | 54 | 51 | 44 | 163 | 300 | 66 | 74 | 0 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 350 | 115 | 88 | 105 | 5 | 230 | 54 | 50 |  | 831 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 140 | 26 | 70 | 0 | 60 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 250 | 14 | 20 | 369 | 265 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 35 | 40 | 110 | 100 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 80 | 0 | 0 | 305 | 295 | 181 | 8 | 86 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 15 | 86 | 159 | 0 | 22 | 0.8 | 40 | 54 | 5 | 5 | 130 | 290 | 55 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 52 | 28 | 2 | 0 | 0 | 0 | 0 | 432 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 19 | 0 | 0 | 60 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 174 | 0 | 0 | 0 | 12 | 0 | 171 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 118 | 0
199
| Minimum Generation |  | 5992 | 5:00
| Highest Generation |  | 9123 | 19:00
| Day Peak Generation |  | 7701.3 | 12:00
| Evening Peak Generation |  | 9123 | 19:00
| HVDC Max Flow |  | 917 | 18:00
| HVDC EvPeak Flow |  | 915 | 19:00
| Load factor L.F |  | 81.62%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-14
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7701.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6170 | MW
Evening Peak Generation : |  | 9123 | MW Hour : | 19:00 | Available Max Generation : |  | 14915 | MW
E.P. Demand (at gen end) : |  | 9123 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9123 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5415 | MW
Total Gen. (MKWH) : |  | 178.7028 | System Load Factor : | 81.62% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 150 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-14
Actual : | 101.57 | Ft.(MSL) , | Rule curve : | 107.7 | Ft.( MSL )
Gas Consumed : | Total = | 1090.54 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 123311124.724
: |  | Coal : | 24290101 | Oil : | 120829207.31 | Total : | 268430433.034
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3389.0717 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1148.4201 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1028.2244 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 928.8311 |  |  | 0 | 0%
) | 0 | 0:00 | 839.5126 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 677.4467 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 384.0089 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.5623 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 522.4556 |  |  | 0 | 0%
Total | 0 |  | 9092.5334 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1&2.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,3 & 5
4) Ashuganj unit-4 & 5
5) Chandpur CCPP ST
6)Sylhet 150 MW
7) Sirajganj unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari-Baroirhat 132 kV Ckt-2 was under shut down from 08:20 to 14:37 for A/M.
b) Aminbazar-Hasnabad 132 kV Ckt-1 was under shut down from 09:03 to 16:57 for A/M.
c) Mirpur-Uttara 132 kV Ckt was under shut down from 09:35 to 16:50 for A/M.
d) Halisahar-Khulshi 132 kV Ckt-2 was under shut down from 08:50 to 14:49 for A/M.
e) Tangail 132/33 kV T-2 transformer was under shut down from 09:10 to 16:15 for A/M.
f) Kabirpur-Kodda 132 kV Ckt-2 was under shut down from 09:20 to 13:58 for A/M.
g) Cumilla(n)-Meghnaghat 132 kV Ckt-2 was under shut down from 18:28 to 16:38 for A/M.
h) Jamalpur 132/33 kV T-1 transformer was under shut down from 08:20 to 14:12 for A/M.
i) Sherpur 132/33 kV T-2 transformer was under shut down from 08:22 to 16:00 for A/M.
j) Hathazari 230/132/33 kV T-2 transformer was shut down at 10:41 for A/M.
k) Noapara 132/33 kV T-2 transformer was under shut down from 08:58 to 14:30 for A/M.
l) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 12:25 from Ashuganj end showing dist. Z1, 67N relay at
RST-phase of Ashuganj end and was switched on at 12:50.
m) Haripur-Siddhirganj 132 kV Ckt-2 was under shut down from 09:20 to 13:39 for A/M.
n) Rangpur-Confidence 132 kV Ckt-2 was under shut down from 08:50 to 17:20 for A/M.
o) Confidence-Palashbari 132 kV Ckt-2 was under shut down from 08:55 to 16:20 for A/M.
p) Boropukuria-Bogura 230 kV Ckt-1 was under shut down from 08:47 to 16:15 for A/M.
q) Bheramara HVDC-Khulna(s) 132 kV Ckt-1 was under shut down from 08:35 to 16:44 for A/M.
r) Barishal-Madaripur 132 kV Ckt-2 was under shut down from 12:18 to 13:50 for C/M.
s) Chattak 132/33 kV T-3 transformer was under shut down from 13:19 to 15:13 for A/M.
t) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 12:52 to 21:45 for red hot maintenance
at Ashuganj end.
u) Maniknagar-Bangabhaban 132 kV Ckt-2 was switched on at 14:51 from Maniknagar end.
v) Jamalpur 132/33 kV T-2 transformer was under shut down from 14:22 to 16:36 for isolator maintenance |  |  |  |  | About 12 MW power interruption occurred under Jamalpur S/S area
of 33 kV Jamuna feeder(PDB). |  |  |  |  | from 14:22 to 16:36.
w) Norsingdi 132/33 kV T-2 transformer was under shut down from 16:59 to 07:54(14/11/2019) for
R/H maintenance at R-phase 0f 33 kV incomer bus isolator.
x) Baghabari 100 MW was synchronized at 17:32.
y) Raozan unit-2 was synchronized at 23:32 , tripped at 01:25(14/11/2019) and again synchronized
at 02:13(14/11/2019).
z) Sonargaon-Daudkandi 132 kV Ckt-1 was shut down at 07:40(14/11/2019) for A/M.
aa) Dohazari-Cox;s bazar 132 kV Ckt-1 was shut down from 07:15(14/11/2019) for A/M.
ab) Hasnabad 132/33 kV T-1 transformer was shut down at 07:01(14/11/2019) for A/M.
ac) Bagerhat 132/33 kV T-1 & T-2 transformer tripped at 06:18(14/11/2019) for Pirozpur wz feeder |  |  |  |  | About 15 MW power interruption occurred under Bagerhat S/S area
and was switched on at 06:25. |  |  |  |  | from 06:18(14/11/2019) to 06:25.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 820000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6663864 | Frequency control.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 340256 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 65 | 688954
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 320 | 8347640 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 300 | 7022000 | Frequency control.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7726250 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 18400 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 120996 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 135360 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 254 | 5326175 | Frequency control.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 316032
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 510840 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 33816 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 50 | 117144
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 68 | 111360 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1285080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 610500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 800500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 180 | 903272 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 20 | 378720 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1226988 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 2143 | 43504147
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 20000
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 4696 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 140535
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 151200 | Engine problem
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 75 | 1717320 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 3032816 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2433818
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 421912
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1600560
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 383040 | Low demand.
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 423696
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 405120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 63 | 734400 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27360
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 44168 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 22581 | Reserve
| Chattogram area Total |  |  |  | 2166 | 731 | 14163222
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2036516 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4308000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 7044200 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 360 | 8108000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 474480 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 422880
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 568727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 25 | 294188 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 195709 | Low demand
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 2078220
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 50 | 295680 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 90648
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 45360
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 2610240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 152500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 429380 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1530 | 29154728
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3628120 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 119088
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 82560 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 135 | 950400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 321 | 4791968
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 1031000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 54 | 1135800
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 2910232
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 317 | 6351000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 295800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 410760
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 48968
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 902400 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 458880 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Engine problem
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 93000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 36 | 369300 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 127160
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7365000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 305 | 7768000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Reserve
| Sylhet Area Total |  |  |  | 1949 | 1520 | 29267300
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 915 | 17251636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 7771104 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 141000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 32640 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 17 | 75456 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1272 | 25271836
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 13440 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 429800 | Machine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 141 | 3107636 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 60 | 601028 | Low demand
| Barisal Area Total |  |  |  | 462 | 227 | 4151904
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1390000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 45 | 297000
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 24 | 632960 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 191 | 4534082 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 174 | 4303145 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 347 | 7605054 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 92640
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 58320
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 190512
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 11040 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 149872 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 192 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 118 | 2791776 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1016 | 22056593
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5938900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 368640
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33565
| Rangpur Area Total |  |  |  | 605 | 363 | 6341105
| Total |  |  |  | 19018 | 9123 | 178702803
| Eastern Grid Total |  |  |  | 13454 | 6245 | 120881365
| Western Grid Total |  |  |  | 5564 | 2878 | 57821438
| National Grid Total |  |  |  | 19018 | 9123 | 178702803
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-13
(a) ENTIRE EASTERN GRID : |  | 6275 | MW | (b) ENTIRE WESTERN GRID : |  | 2447 | MW
i) Dhaka area |  | 3459 | MW | i) Khulna area |  | 868 | MW
ii) Chittagong area |  | 976 | MW | ii) Rajshahi area |  | 835 | MW
iii) Comilla area |  | 789 | MW | iii) Barisal area |  | 186 | MW
iv) Mymensingh area |  | 675 | MW | iv) Rangpur area |  | 558 | MW
v) Sylhet area |  | 376 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8722 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 1830 | Srimongal | 27 | 1900 | Bottail | 90 | 1800
Munsiganj | 82 | 1500 | Shahjibazar | 87 | 1830 | G.K Project | 37 | 1800
Sonargaon | 72 | 1600 | Fenchuganj | 24 | 1800 | Faridpur | 130 | 1830
Shyampur | 184 | 1000 | Kulawara | 35 | 1900 | Madaripur | 49 | 2100
Bhulta | 179 | 1100 | Sylhet | 112 | 1800 | Sariatpur | 32 | 2000
Madanganj | 44 | 1200 | Chatak | 20 | 1800 | Gopalganj | 40 | 2100
Shitalakhya | 91 | 1800 | Sunamganj | 33 | 1800 | Bagerhat | 30 | 2100
Rahim steel | 19 | 1700 | Biani Bazar | 41 | 1800 | Mongla | 28 | 100
Matuail | 90 | 1000 | Comilla (S) | 136 | 1800 | Satkhira | 50 | 2100
Ghorasal | 76 | 1830 | Comilla(N) | 77 | 1930 | Gallamari | 37 | 1300
Narsingdi | 98 | 1300 | Chandpur | 76 | 1900 | Magura | 36 | 1800
Haripur (SBU) | 80 | 1300 | Feni | 101 | 1800 | Norail | 24 | 1830
Ullon | 60 | 1800 | Chowmuhani | 126 | 1800 | Chuadanga | 60 | 1800
Hasnabad | 164 | 1900 | Ashuganj | 44 | 1800 | Barisal(N) | 13 | 2100
Magbazar | 102 | 1500 | Daudkandi | 94 | 1900 | Barisal (S) | 68 | 1900
Maniknagar | 97 | 1200 | B.Baria | 102 | 1900 | Patuakhali | 76 | 2100
Bangabhaban | 21 | 1200 | Ramganj | 58 | 1830 | Bhandaria | 22 | 2100
Narinda | 88 | 1600 | Madunaghat | 51 | 1800 | Borhan Uddin | 23 | 2100
Dhanmondi | 145 | 1300 | Hathazari | 86 | 1800 | Ishurdi | 48 | 1900
Lalbag | 74 | 1800 | Khulshi | 174 | 1300 | Ruppur Paromanobik | 1 | 100
Madartek | 56 | 1930 | Halishahar | 119 | 1400 | Natore | 85 | 1800
Mirpur | 92 | 1800 | Baraulia | 86 | 900 | Bogra | 149 | 1800
Kalyanpur | 96 | 1800 | Sikalbaha | 23 | 1800 | Noagaon | 80 | 1830
Gulshan | 130 | 1300 | Dohazari | 72 | 1900 | Rajshahi | 96 | 1830
Uttara | 47 | 1800 | Cox'sbazar | 86 | 1800 | Rajshahi New | 10 | 2000
Uttara New | 34 | 1800 | Chandraghona | 26 | 1800 | C.Nawabganj | 54 | 1830
Kamrangirchar | 67 | 1800 | Kaptai | 4 | 1800 | Amnura | 21 | 2000
Savar | 118 | 1800 | A. Khaer Stl. | 0 | 0 | Pabna | 79 | 1800
Bhasantec | 136 | 1830 | Bakulia | 92 | 1830 | Shahjadpur | 78 | 1830
Agargaon | 46 | 1800 | Julda | 22 | 1500 | Serajganj | 73 | 1830
Satmosjid | 81 | 1800 | TK chemical | 12 | 1830 | Niyamatpur | 41 | 1830
Tongi | 137 | 1500 | Modern Steel | 12 | 1930 | Joypurhat | 40 | 1800
Kabirpur | 179 | 1800 | Shahmirpur | 25 | 100 | Sherpur(Bogura) | 36 | 1800
Basundhara | 84 | 1800 | Khagrachhari | 18 | 1800 | Mohastangor | 10 | 1930
Manikganj | 70 | 1800 | Matarbari | 26 | 1800 | Rangpur | 105 | 1830
Joydevpur | 175 | 1800 | Baroiar Hat | 18 | 1800 | Lalmonirhat | 42 | 1800
New Tongi | 90 | 1800 | Rangamati | 10 | 1800 | Saidpur | 85 | 1800
Korda | 220 | 1830 | Abul Khair 230 | 136 | 100 | Purbasadipur | 80 | 1830
Dhamrai | 50 | 1900 | BSRM | 101 | 1000 | Thakurgaon | 52 | 1830
Valuka | 96 | 1200 | GPH Ispat | 8 | 1200 | Palashbari | 85 | 1800
Tangail | 139 | 1800 | Goalpara | 19 | 2100 | Barapukuria | 39 | 1800
Mymensing | 160 | 1830 | Central s/s | 72 | 1900 | Panchagar | 38 | 1800
Kishorganj | 86 | 1900 | Noapara | 33 | 1800 | Joldhaka | 19 | 1900
Netrokona | 73 | 1800 | Jessore | 92 | 1830 | Kurigram | 38 | 1800
Jamalpur | 90 | 2000 | Benapol | 28 | 1800
Sherpur | 66 | 1800 | Jhenida | 74 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-13 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 387 | 8:00 | 377 | 11:00 | Kaliakoir | 367 | 4:00 | 352 | 12:00
Bheramara | 406 | 4:00 | 391 | 18:30 | Bhulta | 375 | 5:00 | 360 | 14:00
Ashuganj(N) | 382 | 6:00 | 366 | 16:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 14:00
Ghorasal | 226 | 1:00 | 220 | 10:00 | Hathazari | 217 | 18:00 | 212 | 15:00
Ishurdi | 241 | 3:00 | 231 | 18:00 | Megnaghat | 220 | 3:00 | 210 | 13:00
Ashuganj | 232 | 7:00 | 225 | 14:00 | Fenchuganj | 232 | 3:00 | 226 | 11:00
Serajganj | 234 | 4:00 | 230 | 1:00 | Siddhirganj | 220 | 5:00 | 211 | 15:00
Baghabari | 240 | 1:00 | 235 | 12:00 | Maniknagar | 219 | 3:00 | 210 | 11:00
Barapukuria | 231 | 4:00 | 226 | 11:00 | Old Airport | 219 | 6:00 | 207 | 12:00
Bogra | 234 | 6:00 | 228 | 12:00 | Barisal | 230 | 4:00 | 220 | 12:00
Khulna South | 243 | 5:00 | 219 | 12:00 | AKSML | 213 | 1:00 | 207 | 13:00
Rampura | 220 | 4:00 | 211 | 15:00 | BSRM | 216 | 8:00 | 209 | 13:00
Haripur | 220 | 1:00 | 211 | 12:00 | Bibiyana | 231 | 4:00 | 223 | 12:00
Hasnabad | 216 | 4:00 | 208 | 12:00 | Bhulta | 221 | 4:00 | 211 | 14:00
Aminbazar | 219 | 5:00 | 209 | 12:00 | Ashuganj (S) | 230 | 8:00 | 221 | 13:00
Tongi | 212 | 7:00 | 203 | 12:00 | Kaliakoir | 221 | 4:00 | 212 | 12:00
Comilla (N) | 226 | 6:00 | 217 | 15:00 | GPH | 214 | 3:00 | 208 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 300 | 126 | 1000 | Halishahar | 131 | 1800 | 124 | 900
Munsiganj | 131 | 900 | 126 | 1200 | Baraulia | 129 | 1830 | 124 | 900
Megnaghat | 130 | 1930 | 126 | 100 | Sikalbaha | 131 | 1800 | 125 | 1000
Shyampur | 132 | 400 | 126 | 1100 | Dohazari | 130 | 1800 | 122 | 900
Bhulta | 126 | 400 | 120 | 1200 | Cox'sbazar | 123 | 800 | 111 | 1200
Madanganj | 134 | 400 | 125 | 1100 | Chandraghona | 130 | 1800 | 124 | 1900
Shitalakhya | 134 | 500 | 124 | 1200 | Kaptai | 130 | 1800 | 126 | 1000
Rahim steal | 132 | 400 | 127 | 1200 | A. Khaer Stl. | 126 | 100 | 125 | 400
Matuail | 131 | 500 | 125 | 1100 | Bakulia | 129 | 1800 | 122 | 900
Ghorasal | 134 | 1800 | 130 | 1000 | Julda | 129 | 1700 | 126 | 700
Narsinghdi | 129 | 400 | 123 | 1000 | TK Chemical | 129 | 1700 | 124 | 1100
Haripur (SBU) | 133 | 500 | 127 | 1300 | Modern Steel | 128 | 100 | 122 | 1700
Ullon | 131 | 600 | 123 | 1200 | Shahmirpur | 130 | 1800 | 123 | 1000
Hasnabad | 132 | 600 | 126 | 1200 | Khagrachhari | 128 | 100 | 125 | 900
Magbazar | 134 | 600 | 123 | 1500 | Matarbari | 125 | 1800 | 120 | 100
Maniknagar | 135 | 600 | 127 | 1200 | Baroiar Hat | 126 | 1800 | 121 | 1300
Bangabhaban | 135 | 600 | 127 | 1200 | Rangamati | 129 | 1800 | 125 | 1100
Narinda | 135 | 600 | 127 | 1200 | Goalpara | 135 | 300 | 122 | 1200
Dhanmondi | 131 | 600 | 123 | 1200 | Central s/s | 135 | 500 | 123 | 1200
Lalbag | 134 | 600 | 124 | 1200 | Noapara | 134 | 400 | 120 | 1200
Madartek | 131 | 600 | 123 | 1200 | Jessore | 131 | 500 | 117 | 1200
Mirpur | 134 | 500 | 127 | 400 | Benapol | 133 | 400 | 119 | 1300
Kalyanpur | 137 | 500 | 129 | 1200 | Jhenida | 131 | 100 | 122 | 1200
Gulshan | 131 | 600 | 123 | 1200 | Bottail | 136 | 100 | 119 | 1200
Uttara | 133 | 500 | 119 | 1200 | G.K Project | 141 | 400 | 135 | 1200
Uttara New | 132 | 300 | 125 | 1200 | Faridpur | 135 | 500 | 125 | 1300
Kamrangirchar | 132 | 200 | 122 | 1200 | Madaripur | 133 | 400 | 124 | 1300
Savar | 133 | 300 | 126 | 1200 | Sariatpur | 134 | 100 | 125 | 1200
Bhasantec | 132 | 300 | 123 | 1200 | Gopalganj | 138 | 600 | 125 | 1300
Agargaon | 133 | 300 | 124 | 1200 | Bagerhat | 136 | 500 | 122 | 1200
Satmosjid | 132 | 400 | 124 | 1200 | Mongla | 131 | 600 | 121 | 1200
Tongi | 130 | 800 | 123 | 1200 | Satkhira | 134 | 100 | 122 | 1200
Kabirpur | 127 | 800 | 119 | 1600 | Gallamari | 135 | 400 | 123 | 1200
Basundhara | 128 | 300 | 120 | 1400 | Magura | 133 | 400 | 121 | 1200
Manikganj | 130 | 1900 | 126 | 1400 | Norail | 132 | 500 | 120 | 1900
Joydevpur | 134 | 300 | 128 | 1500 | Chuadanga | 130 | 400 | 119 | 1200
New Tongi | 129 | 400 | 121 | 1200 | Barisal(N) | 137 | 400 | 130 | 1200
Kodda | 127 | 200 | 120 | 1500 | Barisal (S) | 136 | 500 | 128 | 1200
Dhamrai | 129 | 400 | 122 | 1300 | Patuakhali | 135 | 300 | 125 | 1300
Valuka | 122 | 300 | 117 | 1100 | Bhandaria | 135 | 1700 | 123 | 1400
Tangail | 129 | 600 | 120 | 1200 | Ishurdi | 138 | 200 | 133 | 1800
Mymensing | 124 | 500 | 118 | 1100 | Ruppur Paromanobik | 136 | 500 | 132 | 1800
Kishorganj | 128 | 400 | 122 | 1200 | Natore | 135 | 100 | 130 | 1800
Netrokona | 124 | 400 | 117 | 1300 | Bogra | 139 | 300 | 133 | 1830
Jamalpur | 128 | 1800 | 118 | 700 | Noagaon | 135 | 600 | 130 | 1800
Sherpur | 128 | 1700 | 116 | 1100 | Rajshahi | 132 | 300 | 126 | 1830
Srimongal | 134 | 200 | 130 | 1000 | Rajshahi New | 132 | 400 | 125 | 1900
Shahjibazar | 133 | 700 | 128 | 1200 | C.Nawabganj | 129 | 800 | 121 | 1900
Fenchuganj | 132 | 300 | 128 | 1100 | Amnura | 133 | 800 | 127 | 1830
Khulawara | 132 | 400 | 127 | 1300 | Pabna | 138 | 300 | 132 | 1200
Sylhet | 130 | 100 | 125 | 1100 | Shahjadpur | 142 | 500 | 138 | 1830
Chatak | 130 | 500 | 124 | 1100 | Serajganj | 137 | 600 | 132 | 1830
Sunamganj | 130 | 600 | 123 | 1200 | Niyamatpur | 135 | 400 | 127 | 1800
Biani Bazar | 130 | 600 | 124 | 1200 | Joypurhat | 136 | 200 | 129 | 1830
Comilla(s) | 128 | 100 | 124 | 1300 | Sherpur(Bogura) | 138 | 400 | 132 | 1800
Comilla(n) | 133 | 700 | 129 | 1500 | Mohastangor | 136 | 400 | 130 | 1800
Chandpur | 130 | 1800 | 125 | 1500 | Rangpur | 129 | 600 | 122 | 1200
Feni | 125 | 2100 | 121 | 1400 | Lalmonirhat | 125 | 300 | 118 | 1300
Chowmuhani | 122 | 700 | 120 | 2000 | Saidpur | 128 | 600 | 122 | 1200
Ashuganj | 135 | 700 | 130 | 1300 | Purbasadipur | 128 | 500 | 118 | 1830
Daudkandi | 130 | 700 | 125 | 1100 | Thakurgaon | 124 | 400 | 118 | 1830
B.Baria | 131 | 800 | 127 | 1200 | Palashbari | 132 | 600 | 125 | 1300
Ramganj | 122 | 1800 | 118 | 1200 | Barapukuria | 131 | 400 | 126 | 1100
Madanhat | 132 | 1800 | 125 | 1700 | Panchagar | 125 | 400 | 110 | 1830
Hathazari | 130 | 400 | 126 | 1300 | Joldhaka | 128 | 400 | 120 | 1200
Khulshi | 128 | 1800 | 122 | 900 | Kurigram | 129 | 400 | 121 | 2000
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 610 | 4835 | 2562 | 7397 |  |  |  | QF-LDC-12
0:30 | 540 | 4629.5 | 2416.5 | 7046 | Date: | 2019-11-13
1:00 | 470 | 4424 | 2271 | 6695
1:30 | 425 | 4417 | 2131.5 | 6548.5
2:00 | 380 | 4410 | 1992 | 6402
2:30 | 380 | 4317 | 1975 | 6292 | [5 empty] | Gen. at Eve. Peak | 9123 | 9123 MW (19:00 )
3:00 | 380 | 4224 | 1958 | 6182 | [6 empty] | 19:00
3:30 | 390 | 4174.5 | 1958 | 6132.5 | [5 empty] | Gen. at Day Peak | 7701.3 | 7701.3 MW (12:00 )
4:00 | 400 | 4125 | 1958 | 6083 | [6 empty] | 12:00
4:30 | 375 | 4108 | 1929.5 | 6037.5 | [5 empty] | Highest Generation | 9123
5:00 | 350 | 4091 | 1901 | 5992 | [6 empty] | 19:00
5:30 | 330 | 4107.51 | 1891.5 | 5999.01
6:00 | 310 | 4124.02 | 1882 | 6006.02
6:30 | 235 | 4232.8925 | 1920.1 | 6152.9925
7:00 | 160 | 4341.765 | 1958.2 | 6299.965
7:30 | 190 | 4414.9325 | 1984.95 | 6399.8825
8:00 | 220 | 4488.1 | 2011.7 | 6499.8
8:30 | 350 | 4551.5 | 2053.95 | 6605.45
9:00 | 480 | 4614.9 | 2096.2 | 6711.1
9:30 | 570 | 4665.31 | 2182.2 | 6847.51
10:00 | 660 | 4715.72 | 2268.2 | 6983.92
10:30 | 650 | 4853.51 | 2297.7 | 7151.21
11:00 | 640 | 4991.3 | 2327.2 | 7318.5
11:30 | 640 | 5089.1 | 2420.8 | 7509.9
12:00 | 640 | 5186.9 | 2514.4 | 7701.3
12:30 | 610 | 5223.6 | 2506.85 | 7730.45
13:00 | 580 | 5260.3 | 2499.3 | 7759.6
13:30 | 643 | 5137.9 | 2497.45 | 7635.35
14:00 | 706 | 5015.5 | 2495.6 | 7511.1
14:30 | 693 | 5080.425 | 2462.85 | 7543.275
15:00 | 680 | 5145.35 | 2430.1 | 7575.45
15:30 | 640 | 5070.86 | 2387.1 | 7457.96
16:00 | 600 | 4996.37 | 2344.1 | 7340.47
16:30 | 590 | 5046.685 | 2385.6 | 7432.285
17:00 | 580 | 5097 | 2427.1 | 7524.1
17:30 | 365 | 5632 | 2604.55 | 8236.55
18:00 | 150 | 6167 | 2782 | 8949
18:30 | 215 | 6206 | 2830 | 9036
19:00 | 280 | 6245 | 2878 | 9123
19:30 | 260 | 6183 | 2906 | 9089
20:00 | 280 | 5977 | 2893 | 8870 |  |  |  | Executive Engineer
20:30 | 295 | 5929.5 | 2856.5 | 8786 |  |  |  | Network Operation Division
21:00 | 310 | 5882 | 2820 | 8702
21:30 | 385 | 5664 | 2743 | 8407
22:00 | 460 | 5446 | 2666 | 8112 |  |  |  |  | Page 6 of 7
22:30 | 500 | 5246.5 | 2631 | 7877.5
23:00 | 540 | 5047 | 2596 | 7643
23:30 | 575 | 4941 | 2579 | 7520
24:00 | 610 | 4835 | 2562 | 7397
9123 MW (19:00 )
7701.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-13 |  | Energy | 178702803
[10 empty] | 2019-11-13 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4094 | 916 | 1584 | 372 | 250 | 75 | 0 | 0 | 106
0:30 | 3948.5 | 820 | 1464.5 | 372.5 | 265 | 74.5 | 0 | 0 | 101 | Date: | 2019-11-13
1:00 | 3803 | 724 | 1345 | 373 | 280 | 74 | 0 | 0 | 96
1:30 | 3802 | 578 | 1352 | 370 | 280 | 73.5 | 0 | 0 | 93 | [7 empty] | Total Energy | 178.7028 | Total Energy Gen 178.703 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 178.703 MKWHr
2:00 | 3801 | 432 | 1359 | 367 | 280 | 73 | 0 | 0 | 90 | [7 empty] | Energy not Served | 0
2:30 | 3757 | 432 | 1348 | 313 | 280 | 73 | 0 | 0 | 89 | [7 empty] | Energy Requirement | 178.7028
3:00 | 3713 | 432 | 1337 | 259 | 280 | 73 | 0 | 0 | 88
3:30 | 3710 | 432 | 1301 | 249 | 280 | 72.5 | 0 | 0 | 88 | [6 empty] | Shortage
4:00 | 3707 | 432 | 1265 | 239 | 280 | 72 | 0 | 0 | 88
4:30 | 3705.5 | 432 | 1240.5 | 239 | 262.5 | 72 | 0 | 0 | 86
5:00 | 3704 | 432 | 1216 | 239 | 245 | 72 | 0 | 0 | 84
5:30 | 3710.5 | 432 | 1234 | 239 | 227.5 | 72 | 0 | 0 | 84
6:00 | 3717 | 432 | 1252 | 239 | 210 | 72 | 0 | 0 | 84
6:30 | 3797.5 | 431.5 | 1316.5 | 235 | 210 | 73.5 | 3.5 | 0 | 83 |  |  |  |  | Coal
7:00 | 3878 | 431 | 1381 | 231 | 210 | 75 | 7 | 0 | 82
7:30 | 3852 | 431.5 | 1407 | 320.5 | 210 | 75 | 12 | 0 | 82 |  |  |  | Oil |  |  |  | ,
8:00 | 3826 | 432 | 1433 | 410 | 210 | 75 | 17 | 0 | 82
8:30 | 3830 | 504.5 | 1443.5 | 420 | 210 | 75 | 17 | 0 | 87
9:00 | 3834 | 577 | 1454 | 430 | 210 | 75 | 17 | 0 | 92
9:30 | 3818.5 | 674 | 1457.5 | 474 | 209.5 | 75 | 17 | 0 | 97
10:00 | 3803 | 771 | 1461 | 518 | 209 | 75 | 17 | 0 | 102
10:30 | 3946.5 | 795 | 1429 | 545 | 209.5 | 75 | 17 | 0 | 104
11:00 | 4090 | 819 | 1397 | 572 | 210 | 75 | 17 | 0 | 106
11:30 | 4132.5 | 818.5 | 1490.5 | 617 | 220 | 75 | 17 | 0 | 107
12:00 | 4175 | 818 | 1584 | 662 | 230 | 75 | 17 | 0 | 108
12:30 | 4167.5 | 818 | 1578 | 695 | 240 | 75 | 17 | 0 | 110
13:00 | 4160 | 818 | 1572 | 728 | 250 | 75 | 17 | 0 | 112
13:30 | 4160 | 818 | 1572 | 728 | 250 | 75 | 17 | 0 | 112
14:00 | 4160 | 818 | 1572 | 728 | 250 | 75 | 17 | 0 | 112
14:30 | 4108.5 | 818.5 | 1511 | 749 | 250 | 75 | 17 | 0 | 116
15:00 | 4057 | 819 | 1450 | 770 | 250 | 75 | 17 | 0 | 120
15:30 | 4019 | 818.5 | 1395 | 764.5 | 250 | 75 | 8.5 | 0 | 115
16:00 | 3981 | 818 | 1340 | 759 | 250 | 75 | 0 | 0 | 110
16:30 | 4013.5 | 818 | 1352.5 | 786.5 | 250 | 75 | 22 | 0 | 111
17:00 | 4046 | 818 | 1365 | 814 | 250 | 75 | 44 | 0 | 112
17:30 | 4145 | 867.5 | 1509.5 | 1192.5 | 250 | 75 | 73 | 0 | 124
18:00 | 4244 | 917 | 1654 | 1571 | 250 | 75 | 102 | 0 | 136
18:30 | 4315 | 916 | 1806.5 | 1436.5 | 250 | 75 | 102 | 0 | 135
19:00 | 4386 | 915 | 1959 | 1302 | 250 | 75 | 102 | 0 | 134
19:30 | 4518 | 915 | 2108 | 989 | 250 | 75 | 102 | 0 | 132
20:00 | 4436 | 916 | 2126 | 867 | 250 | 75 | 68 | 0 | 132
20:30 | 4415 | 915.5 | 2150.5 | 783 | 250 | 75 | 68 | 0 | 129
21:00 | 4394 | 915 | 2175 | 699 | 250 | 75 | 68 | 0 | 126
21:30 | 4314 | 915.5 | 2060 | 618.5 | 250 | 75 | 51 | 0 | 123
22:00 | 4234 | 916 | 1945 | 538 | 250 | 75 | 34 | 0 | 120
22:30 | 4183.5 | 915.5 | 1849.5 | 471.5 | 249.5 | 75 | 17 | 0 | 116
23:00 | 4133 | 915 | 1754 | 405 | 249 | 75 | 0 | 0 | 112
23:30 | 4113.5 | 915.5 | 1669 | 388.5 | 249.5 | 75 | 0 | 0 | 109 | Max Temp. in Dhaka |  | 31.5° C
24:00 | 4094 | 916 | 1584 | 372 | 250 | 75 | 0 | 0 | 106
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 178.703 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 178.703 MKWHr
Note on W13: Author:

## Generation
2019-11-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 34 | 33 | 33 | 32 | 32 | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 745320
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2 | [25 empty] | 10 | 20000
5 | Raozan 25 MW PP | [17 empty] | 2 |  | 0 | [6 empty] | 4696
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 0.02 | 4 | 10.9 | 15.4 | 18.62 | 20.3 | 20.1 | 17 | 16 | 11 | 5 | 0 | [9 empty] | 140535
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 110 | 110 | 104 | 104 | 104 | 104 | 104 | 105 | 147 | 149 | 149 | 149 | 144 | 145 | 145 | 145 | 104 |  | 100 | 145 | 145 | 145 | 145 | 148 | 149 | 3032816
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [15 empty] | 0 | 44 | 102 |  | 102 | 102 | 68 | 68 | 34 | 0 |  | 421912
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 87 | 87 | 87 | 87 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2433818
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 200 | 200 | 170 | 170 | 170 | 170 | 200 | 190 | 190 | 190 | 220 | 252 | 250 | 250 | 250 | 250 | 255 | 250 |  | 254 | 250 | 254 | 248 | 229 | 221 | 173 | 5326175
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 2 | 55 | 60 | 71 | 95 | 94 | 209 |  | 180 | 60 | 30 | 15 | 0 | 0 |  | 903272
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 568727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 820000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 240 | 240 | 240 | 240 | 240 | 240 | 230 | 260 | 260 | 260 | 300 | 300 | 330 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6663864
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2036516
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 23 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 474480
33 | Ashuganj 225 MW CCPP | 162 | 162 | 161 | 162 | 168 | 163 | 182 | 162 | 176 | 168 | 173 | 175 | 168 | 162 | 189 | 181 | 188 | 180 |  | 203 | 202 | 190 | 190 | 181 | 181 | 181 | 4308000
34 | Ashuganj 450 MW CCPP(South) | 325 | 325 | 320 | 320 | 325 | 320 | 360 | 325 | 345 | 320 | 335 | 345 | 330 | 325 | 325 | 320 | 330 | 360 |  | 360 | 360 | 320 | 330 | 320 | 320 | 325 | 8108000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 295 | 260 | 290 | 270 | 350 | 360 | 345 | 275 | 300 | 300 | 305 | 335 |  | 340 | 335 | 300 | 305 | 300 | 300 | 300 | 7044200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 |  | 55 | 55 | 55 | 55 | 56 | 30 | 5 | 422880
36 | Chandpur 150 MW CCPP | 88 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 88 | 88 | 87 | 88 | 87 | 87 | 2078220
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 348 | 344 | 343 | 343 | 351 | 369 | 356 | 349 | 362 | 360 | 363 | 358 | 320 | 300 | 300 | 300 | 278 |  | 320 | 380 | 378 | 352 | 344 | 344 | 346 | 8347640
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 320 | 320 | 280 | 280 | 280 | 320 | 350 | 350 | 350 | 350 | 350 | 350 | 320 | 320 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7726250
41 | Haripur 360MW CCPP(HPL) | 243 | 243 | 243 | 223 | 223 | 223 | 271 | 303 | 300 | 300 | 330 | 330 | 330 | 300 | 300 | 270 | 270 | 270 |  | 300 | 356 | 357 | 358 | 361 | 361 | 364 | 7022000
42 | RPCL 210MW CCPP | 162 | 160 | 161 | 161 | 129 | 129 | 129 | 161 | 158 | 157 | 156 | 154 | 154 | 155 | 154 | 154 | 154 | 156 |  | 156 | 157 | 156 | 158 | 160 | 160 | 161 | 3628120
43
44 | Fenchugonj CCPP Phase-1 | 40 | 38 | 40 | 39 | 38 | 38 | 40 | 39 | 39 | 40 | 40 | 39 | 40 | 42 | 40 | 40 | 40 | 40 |  | 40 | 40 | 58 | 59 | 58 | 60 | 60 | 1031000
45 | Fenchugonj CCPP Phase-2 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 42 | 42 | 42 | 44 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1135800
46 | Shajibazar 330 MW CCPP | 263 | 261 | 262 | 265 | 274 | 274 | 283 | 276 | 280 | 279 | 276 | 275 | 278 | 266 | 276 | 265 | 272 | 302 |  | 317 | 304 | 300 | 293 | 285 | 285 | 288 | 6351000
47 | Shahjibazar GTPP Unit- 8 & 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 40 | 53 | 64 | 63 | 65 | 65 | 65 |  | 65 | 65 | 65 | 66 | 67 | 40 | 40 | 902400
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 74 |  | 74 | 74 | 74 | 74 | 5 | 5 | 5 | 458880
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [17 empty] | 18 |  | 18 | 18 | 18 | 18 | 18 | 0 |  | 93000
52 | Sylhet 50MW PP (EPL) | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 8 | 8 | 7 | 7 |  | 36 | 36 | 40 | 40 | 40 | 9 | 8 | 369300
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11MW PP Cofidence-E | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 11 |  | 11 | 11 | 11 | 11 | 0 |  |  | 48968
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 37 |  | 44 | 47 | 44 | 50 | 5 | 5 | 5 | 295800
56 | Shahjahanulla 25 MW PP | [17 empty] | 24 |  | 24 | 24 | 24 | 24 | 16 |  |  | 127160
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 300 | 300 | 285 | 270 | 300 | 310 | 270 | 300 | 310 | 295 | 315 | 300 | 280 | 300 | 275 | 295 | 270 |  | 320 | 325 | 310 | 310 | 280 | 265 | 280 | 7365000
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 55 |  | 50 | 17 | [5 empty] | 117144
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 423696
61 | Narshingdi 22 MW PP (Doreen) | [10 empty] | 22 | 22 | 22 | 0 |  |  | 22 | 0 |  |  | 11 |  |  | 22 | 22 | 0 | 120996
62 | Tangail 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 119088
63 | Impoprt (Tripura) | 96 | 90 | 88 | 88 | 84 | 84 | 82 | 82 | 92 | 102 | 106 | 108 | 112 | 116 | 120 | 110 | 112 | 136 |  | 134 | 132 | 132 | 126 | 120 | 112 | 106 | 2610240
64 | Malancha, Ctg. EPZ (United) | 9 | 4 | 4 | 4 | 4 | 9 | 12 | 8 | 4 | 2 | 2 | 2 | 9 | 5 | 2 | 2 | 6 | 3 |  | 14 | 19 | 25 | 30 | 39 | 40 | 40 | 405120
65 | Feni 22MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 |  |  |  | 90648
66 | Feni 11 MW PP (Doreen) | [17 empty] | 11 |  | 11 | 11 | 11 | 11 |  |  |  | 45360
67 | Jangalia 33MW PP (Summit) | [9 empty] | 0 | 0 | [6 empty] | 33 |  | 33 | 33 | 33 | 33 |  |  |  | 152500
68 | Cumilla 25 MW PP (Summit) | 21 | 14 | 14 | 14 | 14 | 14 | 14 | 11 | 10 | 10 | 15 | 15 | 18 | 18 | 18 | 15 | 15 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 429380
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 0 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 685080
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 610500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 800500
73 | Ghorashal 108MW PP (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 40 |  | 65 | 75 | 84 | 91 | 94 | 94 | 14 | 688954
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 20 | 24 | 24 | 24 | 24 | 0 | [10 empty] | 135360
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 8 | 45 |  | 8 | 3 | 0 | 0 |  |  |  | 82560
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | 17 | 17 | 0 |  |  |  |  | 70 | 70 | 71 | 70 | 71 | 71 | 71 | 71 | 71 | 71 | 71 |  | 90 | 90 | 88 | 90 | 90 | 34 | 17 | 1226988
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.565 | 1.4 | 2 | 3.2 | 4.9 | 4.6 | 4.3 | 3 | 2.35 | 1.07 | 0 | [9 empty] | 27360
| Jodiac Power | [17 empty] | 21 | [8 empty] | 44168
| Karnaphuli Power Ltd. | [17 empty] | 17 | [8 empty] | 22581
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX) | [20 empty] | 50 | 60 | 77 | 76 | 40 | 40 | 340256
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 90 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 82 | 80 | 80 | 80 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 1600560
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 47 |  | 49 | 49 | 49 | 46 | 46 | 5 | 5 | 410760
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 11 |  | 25 | 25 | 25 | 25 | 7 | 7 | 7 | 294188
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [9 empty] | 0 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 30 |  | 33 | 19 | 18 | 18 |  |  |  | 151200
96 | Chattogram 108 MW PP (ECPV) | 25 | 19 | 0 | [7 empty] | 22 | 54 | 66 | 66 | 66 | 73 | 78 | 93 |  | 63 | 45 | 15 | 12 | 12 |  |  | 734400
97 | Katpotti 52 MW PP (Sinha) | 18 | 18 | 6 | 6 | 6 | 6 | 6 | [9 empty] | 0 | 38 |  | 48 | 32 | 32 | 32 | 31 | 18 | 18 | 316032
98 | Bosila 108MW PP(CLC) | [16 empty] | 0 | 68 |  | 68 | 14 | [5 empty] | 111360
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 0 | 12 |  | 0 | 0 | [5 empty] | 18400
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 0 | 17 | [8 empty] | 33816
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 2910232
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 0.8 | 1.5 | 1.9 | 2.1 | 2.2 | 1 | 1.5 | 1 | 0.3 | 0 | [9 empty] | 11800
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 17 | [8 empty] | 510840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 0 | [6 empty] | 4 | 7 | 7 | 7 | 36 | 36 | 36 | 36 | 36 | 36 | 103 |  | 135 | 135 | 135 | 90 | 70 | 40 | 24 | 950400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 0 | 17 | 32 | 33 | 31 | 32 | 30 | 30 | 30 | 30 | 34 |  | 20 | 15 | 15 | 0 | 0 |  |  | 378720
115 | Juldah 100 MW PP Unit-3 (Acorn) | [9 empty] | 0 | 30 | 50 | 50 | 50 | 50 | 50 | 20 | 20 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 383040
116 | Chandpur 200MW (Desh energy) | [17 empty] | 70 |  | 50 | 50 | 50 | 34 | 0 | 0 |  | 295680
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 0 | 60 |  | 30 | 10 | 6 |  |  |  |  | 195709
118 | Bibiyana-III 400 MW CCPP | 347 | 346 | 306 | 307 | 305 | 305 | 305 | 352 | 353 | 338 | 336 | 337 | 348 | 345 | 346 | 305 | 305 | 306 |  | 305 | 305 | 305 | 305 | 306 | 306 | 306 | 7768000
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 4424 | 4410 | 4224 | 4125 | 4091 | 4124.02 | 4341.765 | 4488.1 | 4614.9 | 4715.72 | 4991.3 | 5186.9 | 5260.3 | 5015.5 | 5145.35 | 4996.37 | 5097 | 6167 |  | 6245 | 6183 | 5977 | 5882 | 5446 | 5047 | 4835 | 120881365
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 17 | [8 empty] | 32640
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 | [8 empty] | 13440
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 14 | 14 | 13 | 14 | 14 | 20 |  | 60 | 65 | 73 | 84 | 88 | 33 | 12 | 601028
| Bhola 225 MW CCPP | 110 | 120 | 110 | 111 | 120 | 120 | 120 | 110 | 75 | 75 | 75 | 75 | 75 | 138 | 144 | 142 | 142 | 141 |  | 141 | 141 | 141 | 141 | 120 | 121 | 122 | 3107636
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 19 | 19 | 17 | 17 | 16 | 14 | 12 | 12 | 14 | 14 | 11 | 16 | 16 | 14 | 16 | 20 |  | 26 | 28 | 26 | 28 | 15 | 25 | 25 | 429800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 16 | 0 |  |  | 141000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 36 |  | 17 | 17 | 17 | 0 |  |  |  | 75456
146 | Bheramara HVDC | 724 | 432 | 432 | 432 | 432 | 432 | 431 | 432 | 577 | 771 | 819 | 818 | 818 | 818 | 819 | 818 | 818 | 917 |  | 915 | 915 | 916 | 915 | 916 | 915 | 916 | 17251636
147 | Bheramara 360 MW CCPP | 310 | 310 | 310 | 310 | 310 | 310 | 350 | 310 | 335 | 310 | 325 | 335 | 320 | 310 | 280 | 250 | 250 | 280 |  | 300 | 330 | 330 | 330 | 330 | 330 | 330 | 7771104
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 245 | 210 | 210 | 210 | 210 | 209 | 210 | 230 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 249 | 250 | 5938900
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 50 | 60 | 60 | 60 | 60 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1390000
156 | Baghabari 100 MW GTPP | [17 empty] | 30 |  | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 297000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 172 | 173 | 171 | 168 | 166 | 176 | 183 | 176 | 175 | 183 | 199 | 189 | 180 | 169 | 180 | 178 | 182 | 179 |  | 191 | 193 | 192 | 183 | 172 | 160 | 158 | 4534082
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 159 | 159 | 158 | 163 | 168 | 170 | 176 | 187 | 179 | 194 | 185 | 176 | 166 | 168 | 161 | 166 | 163 |  | 174 | 173 | 175 | 166 | 156 | 157 | 167 | 4303145
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 293 | 303 | 282 | 285 | 253 | 254 | 284 | 320 | 320 | 320 | 230 | 398 | 395 | 355 | 304 | 270 | 270 | 271 |  | 347 | 360 | 360 | 363 | 358 | 360 | 336 | 7605054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 0 |  |  | 92640
163 | Bogura 20 MW PP (Energyprima) | [17 empty] | 14 |  | 14 | 14 | 14 | 14 | 0 |  |  | 58320
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 10 | 10 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 190512
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 24 | 24 | 24 | 24 | 12 | 0 |  | 632960
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 8 |  | 0 | [6 empty] | 11040
170 | Chapainawabganj 100 MW Peaking PP | [5 empty] | 0 | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [10 empty] | 149872
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 192
172 | Confidence Power Bogura Unit-1 113 MW | 118 | 118 | 118 | 118 | 118 | 118 | 110 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 |  | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 2791776
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 65 | 109 |  | 113 | 85 | 64 | 35 | 0 |  |  | 368640
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.2 | 1.7 | 3.2 | 4.2 | 5.2 | 5.4 | 5.3 | 4.6 | 3.1 | 1.1 | 0.1 | 0 | [8 empty] | 33565
178
178