## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-16 | Saturday
|  | Date (day): | 2019-11-16 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12421.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15180 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-15 | 2019-11-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 42 | 110 | 110 |  | 80 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 220 | 260 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 40 | 40
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 306 | 357 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 274 | 357 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 360 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 70 | 70 | 140 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 201 | 220 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 48 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 53 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 22 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 21 | 21 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 52 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1503 | 1849 | 3695 | 4097 | 550 | 1048
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 105 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.6 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 8 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 85 | 82 | 82 | 82 | 148 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 41 | 203 | 150 | 200
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 148 | 144 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 51 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 19 | 26 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.6 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 559.2 | 802 | 1510 | 1725 | 298 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 187 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 280 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 270 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 17 | 33 | 32 | 34 |  | 11 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 50 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 45 | 45 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 35 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 127 | 140 | 140 | 150
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 120 | 114 | 145
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 24 | 10 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1100 | 1294 | 1778 | 2226 | 505 | 31
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 207 | 150 | 200
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.8 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 12 | 80 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 167.8 | 309 | 388.6 | 632 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 40 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 54 | 54 | 54 | 54
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 263 | 285 | 330 | 330
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 21 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 66 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 50 | 74 | 74 |  | 12 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 8 | 39 | 32 | 36 |  | 14 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 291 | 367 | 400 | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 7 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1143 | 1474 | 1680 | 1684 | 0 | 168
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 337 | 823 | 489 | 834
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 320 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 607 | 1183 | 984 | 2060 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 27 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 151 | 161 | 160 | 170
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 52 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 181 | 240 | 351 | 431 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 65 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 100 | 100
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 182 | 202 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 183 | 190 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 382 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 25 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 118 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 911 | 996 | 1624 | 1888 | 220 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 215.5 | 245 | 411 | 437 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 6387.5 | 8392 | 12421.6 | 15180 | 1573 | 1530
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6019.8686 | 7909 | 11706.6771 | 14306.3179
A. |  | 2019-11-15 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8392 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5746.9 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8392 | MW
3 | Day peak Generation : |  |  | 6387.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7909 | MW
4 | Evening peak Generation : |  |  | 8392 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 164.581 | MKWHr | By Solar | 0.17908 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 137.928 | MKWHr |  | By Oil: | 5.8139 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 5.0729 | MKWHr |  | By Hydro: | 1.9582 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1573 | MW | Dhaka | 2913 | 2913 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1530 | MW | Chittagong | 866 | 866 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3103 | MW | Khulna | 868 | 868 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1080.18 | MMCFD |  |  | Rajshahi | 788 | 788 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 128945615.754 | ii) Oil : | Taka | 34634215.31 | Comilla | 770 | 770 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 20748161 | Total | Taka | 184327992.064 | Mymensingh | 644 | 644 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.008 | MKWHr. | Sylhet | 356 | 356 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 164 | MW (E to W) at | 19:00 | hrs | Barisal | 187 | 187 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -46 | MW at | 8:00 | hrs | Rangpur | 517 | 517 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0° C |  |  | Total | 7909 | 7909 |  | 0
B. |  | 2019-11-16 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 29.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15180 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
4 | Reserve(Generation end) |  |  |  | 5780 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 184.3496 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5814 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.1935 | MKWHr. | ii) HVDC Flow at Peak Time |  | 823 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4355 | MKWHr. | iii) Maximum HVDC Flow : |  | 824 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.39 | 101.48 |  | (b) Today: | 101.39 |  | (c) Rule Curve: |  | 107.5
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 346 | 300 |  | 0 | 350 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 48 | 40 | 110 | 120 | 0 | 151 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 260 | 163 | 8 | 133 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 100 | 159 | 0 | 22 | 0 | 58 | 54 | 8 | 5 | 100 | 276 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 |  | 714 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 169 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4753 | 2339 | 7092 | 4216 | 714 | 1537 | 237 | 200 | 88 | 0 | 100 | 0 | 0 | 101.53
2:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 359 | 280 |  | 0 | 350 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 48 | 40 | 110 | 120 | 0 | 151 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 275 | 275 | 176 | 8 | 138 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 98 | 159 | 0 | 22 | 0 | 58 | 54 | 8 | 5 | 100 | 271 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 23 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 0 | 11 | 0 | 181 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4765 | 2070 | 6835 | 4280 | 434 | 1548 | 187 | 200 | 88 | 0 | 98 | 0 | 0 | 101.52
3:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 354 | 260 |  | 0 | 320 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 48 | 40 | 110 | 120 | 0 | 151 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 280 | 285 | 177 | 8 | 137 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 96 | 159 | 0 | 0 | 0 | 58 | 54 | 5 | 5 | 100 | 275 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 |  | 240 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 0 | 11 | 0 | 183 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4709 | 1878 | 6587 | 4276 | 240 | 1506 | 181 | 200 | 88 | 0 | 96 | 0 | 0 | 101.51
4:00 | 35 | 0 | 0 | 0 | 250 | 12 | 20 | 352 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 48 | 40 | 110 | 120 | 0 | 151 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 41 | 80 | 0 | 0 | 270 | 275 | 173 | 8 | 138 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 90 | 159 | 0 | 0 | 0 | 58 | 54 | 5 | 5 | 100 | 277 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 239 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 176 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4626 | 1767 | 6393 | 4204 | 239 | 1415 | 157 | 200 | 88 | 0 | 90 | 0 | 0 | 101.5
5:00 | 35 | 0 | 0 | 0 | 220 | 14 | 20 | 351 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 48 | 40 | 110 | 120 | 0 | 151 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 41 | 80 | 0 | 0 | 260 | 265 | 168 | 8 | 138 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 86 | 159 | 0 | 0 | 0 | 58 | 54 | 5 | 5 | 100 | 273 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 240 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 174 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4520 | 1705 | 6225 | 4088 | 240 | 1366 | 157 | 200 | 88 | 0 | 86 | 0 | 0 | 101.49
6:00 | 35 | 0 | 0 | 0 | 220 | 12 | 20 | 340 | 230 |  | 0 | 300 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 150 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 260 | 265 | 160 | 8 | 127 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 82 | 163 | 0 | 0 | 0 | 60 | 54 | 5 | 5 | 100 | 263 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 240 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 171 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 4407 | 1672 | 6079 | 4009 | 240 | 1306 | 157 | 200 | 85 | 0 | 82 | 0 | 0 | 101.48
7:00 | 35 | 0 | 0 | 0 | 220 | 12 | 20 | 280 | 230 |  | 0 | 300 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 90 | 0 | 110 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 265 | 265 | 167 | 8 | 137 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 78 | 146 | 0 | 0 | 0.1 | 60 | 54 | 5 | 5 | 100 | 277 | 40 | 5 | 0 | 0 | 0 | 7 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 352 | 0 | 4 | 17 | 0.45 | 0 | 0 | 0 | 0 |  | 239 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 118 |  | 4306.55 | 1595.4 | 5901.95 | 3819 | 239 | 1306 | 161 | 210 | 85 | 0 | 78 | 3.95 | 0 | 101.47
8:00 | 35 | 0 | 0 | 0 | 220 | 14 | 20 | 283 | 230 |  | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 24 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 31 | 80 | 0 | 0 | 260 | 260 | 160 | 8 | 126 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 72 | 145 | 0 | 0 | 0.5 | 60 | 54 | 5 | 5 | 100 | 266 | 40 | 5 | 0 | 0 | 0 | 7 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9.1 | 0 | 0 | 0 | 354 | 0 | 17 | 34 | 1.6 | 0 | 0 | 0 | 0 |  | 239 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 205 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 118 |  | 4262.2 | 1580.9 | 5843.1 | 3714 | 239 | 1317 | 198 | 205 | 85 | 0 | 72 | 13.1 | 0 | 101.47
9:00 | 35 | 0 | 0 | 0 | 220 | 0 | 20 | 280 | 240 |  | 0 | 300 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 21 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 24 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 260 | 260 | 161 | 8 | 127 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 76 | 126 | 0 | 0 | 1.6 | 38 | 54 | 5 | 5 | 100 | 265 | 40 | 5 | 0 | 0 | 0 | 5 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 13.3 | 0 | 0 | 0 | 295 | 0 | 52 | 17 | 3.3 | 0 | 0 | 0 | 4 |  | 239 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 130 | 0 | 0 | 0 | 11 | 0 | 130 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 118 |  | 4168.2 | 1578.7 | 5746.9 | 3600 | 239 | 1305 | 210 | 210 | 85 | 0 | 76 | 21.9 | 0 | 101.47
10:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 280 | 239 |  | 0 | 300 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 21 | 0 | 0 | 47 | 40 | 110 | 120 | 0 | 42 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 80 | 0 | 0 | 260 | 260 | 167 | 8 | 130 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 70 | 127 | 0 | 0 | 2 | 40 | 54 | 5 | 5 | 100 | 265 | 40 | 5 | 0 | 0 | 0 | 7 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16.3 | 0 | 0 | 0 | 312 | 0 | 34 | 17 | 4.3 | 0 | 0 | 0 | 8 |  | 239 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 118 |  | 4144.6 | 1598.8 | 5743.4 | 3647 | 239 | 1273 | 190 | 210 | 87 | 0 | 70 | 27.4 | 0 | 101.46
11:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 260 | 237 |  | 0 | 300 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 21 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 40 | 0 | 85 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 80 | 0 | 0 | 275 | 270 | 174 | 8 | 137 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 90 | 126 | 0 | 0 | 2.3 | 40 | 54 | 5 | 5 | 100 | 281 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17.4 | 0 | 0 | 0 | 295 | 0 | 34 | 0 | 4.6 | 0 | 0 | 0 | 19 |  | 337 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 152 | 0 | 0 | 0 | 12 | 0 | 166 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 118 |  | 4169.3 | 1736.8 | 5906.1 | 3733 | 337 | 1237 | 184 | 210 | 85 | 0 | 90 | 30.1 | 0 | 101.46
12:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 306 | 274 |  | 0 | 330 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 45 | 40 | 105 | 120 | 0 | 41 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 80 | 0 | 0 | 275 | 260 | 180 | 8 | 127 | 17 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 154 | 0 | 0 | 1.8 | 41 | 54 | 5 | 5 | 130 | 263 | 51 | 5 | 0 | 0 | 0 | 8 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 17.6 | 0 | 0 | 0 | 291 | 0 | 52 | 0 | 4.6 | 0 | 0 | 0 | 24 |  | 337 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 12 | 0 | 183 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 118 |  | 4473 | 1914.5 | 6387.5 | 3952 | 337 | 1466 | 212 | 210 | 85 | 0 | 96 | 29.5 | 0 | 101.45
13:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 345 | 275 |  | 0 | 330 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 44 | 40 | 105 | 120 | 0 | 52 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 28 | 80 | 0 | 0 | 360 | 285 | 196 | 8 | 138 | 33 | 30 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 104 | 150 | 0 | 0 | 0.5 | 40 | 54 | 8 | 5 | 100 | 279 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 302 | 0 | 52 | 0 | 4.2 | 0 | 0 | 0 | 50 |  | 334 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 191 | 0 | 0 | 0 | 10 | 0 | 200 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 118 |  | 4698.7 | 1951.3 | 6650 | 4164 | 334 | 1469 | 258 | 210 | 84 | 0 | 104 | 27 | 0 | 101.45
14:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 287 | 254 |  | 0 | 330 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 12 | 22 | 21 | 0 | 0 | 42 | 40 | 105 | 120 | 0 | 40 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 80 | 0 | 0 | 300 | 295 | 200 | 8 | 139 | 33 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 151 | 0 | 0 | 0.4 | 38 | 54 | 8 | 5 | 100 | 275 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 13.9 | 0 | 0 | 0 | 320 | 0 | 52 | 17 | 3.4 | 0 | 0 | 0 | 62 |  | 334 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 168 | 0 | 0 | 0 | 11 | 0 | 194 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 118 |  | 4538.7 | 1813.3 | 6352 | 3991 | 334 | 1314 | 293 | 210 | 82 | 0 | 106 | 22 | 0 | 101.45
15:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 312 | 254 |  | 0 | 330 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 12 | 22 | 21 | 0 | 0 | 40 | 40 | 105 | 120 | 0 | 50 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 80 | 0 | 0 | 275 | 265 | 181 | 8 | 140 | 33 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 151 | 0 | 0 | 2.1 | 40 | 54 | 5 | 5 | 100 | 274 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 52 | 51 | 2.3 | 0 | 0 | 0 | 64 |  | 334 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 174 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 76 |  | 4531.4 | 1802.6 | 6334 | 3948 | 334 | 1361 | 287 | 210 | 80 | 0 | 106 | 8 | 0 | 101.45
16:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 321 | 255 |  | 0 | 330 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 12 | 22 | 21 | 0 | 0 | 40 | 40 | 105 | 120 | 0 | 52 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 80 | 0 | 0 | 275 | 265 | 181 | 8 | 126 | 33 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 153 | 0 | 0 | 0.4 | 40 | 54 | 8 | 5 | 100 | 266 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 52 | 51 | 1 | 0 | 0 | 0 | 46 |  | 334 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 209 | 0 | 0 | 167 | 0 | 0 | 0 | 12 | 0 | 187 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 4459.4 | 1680.2 | 6139.6 | 3926 | 334 | 1311 | 177 | 209 | 80 | 0 | 100 | 2.6 | 0 | 101.44
17:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 296 | 253 |  | 0 | 300 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 12 | 22 | 21 | 0 | 0 | 42 | 40 | 105 | 120 | 0 | 101 | 0 | 144 | 0 |  | 0 | 0 | 0 | 5 | 0 | 0 | 19 | 17 | 80 | 0 | 0 | 275 | 265 | 160 | 8 | 126 | 33 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 153 | 0 | 0 | 0 | 40 | 54 | 8 | 5 | 100 | 266 | 40 | 5 | 0 | 0 | 0 | 9 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 52 | 51 | 0 | 0 | 0 | 0 | 27 |  | 334 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 209 | 0 | 0 | 165 | 0 | 0 | 0 | 12 | 0 | 182 | 0 | 253 | 0 | 0 | 4 | 9 | 30 | 0 | 0.1 | 0 |  | 4437 | 1721.1 | 6158.1 | 3922 | 334 | 1293 | 218 | 209 | 82 | 0 | 100 | 0.1 | 0 | 101.44
18:00 | 35 | 0 | 0 | 11 | 260 | 0 | 0 | 333 | 354 |  | 0 | 360 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 0 | 0 | 22 | 25 | 16 | 22 | 21 | 0 | 0 | 42 | 40 | 105 | 120 | 0 | 188 | 0 | 144 | 0 |  | 0 | 0 | 34 | 10 | 0 | 1 | 19 | 23 | 80 | 0 | 0 | 300 | 290 | 201 | 8 | 140 | 33 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 130 | 186 | 0 | 22 | 0 | 40 | 54 | 11 | 21 | 100 | 291 | 51 | 50 | 0 | 0 | 17 | 36 | 7 | 305 | 24 | 3 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 52 | 51 | 0 | 0 | 0 | 0 | 28 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 161 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 178 | 0 | 0 | 0 | 16 | 0 | 186 | 0 | 378 | 17 | 0 | 35 | 17 | 35 | 0 | 0 | 0 |  | 5462 | 2613 | 8075 | 4625 | 823 | 1745 | 400 | 210 | 82 | 60 | 130 | 0 | 0 | 101.44
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 42 | 260 | 0 | 0 | 357 | 357 |  | 0 | 360 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 22 | 25 | 28 | 22 | 21 | 0 | 0 | 42 | 40 | 105 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 34 | 10 | 0 | 8 | 19 | 26 | 80 | 0 | 0 | 280 | 270 | 187 | 8 | 140 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 120 | 207 | 0 | 22 | 0 | 40 | 54 | 53 | 21 | 130 | 285 | 66 | 50 | 0 | 0 | 17 | 39 | 7 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 52 | 51 | 0 | 0 | 0 | 0 | 10 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 161 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 202 | 0 | 0 | 0 | 52 | 0 | 190 | 0 | 382 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 |  | 5728 | 2664 | 8392 | 4736 | 823 | 1943 | 419 | 210 | 82 | 59 | 120 | 0 | 0 | 101.43
19:30 | 35 | 0 | 0 | 40 | 260 | 0 | 0 | 350 | 357 |  | 0 | 360 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 31 | 22 | 21 | 0 | 0 | 42 | 40 | 105 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 17 | 10 | 0 | 12 | 19 | 28 | 80 | 0 | 0 | 285 | 275 | 192 | 8 | 144 | 33 | 49 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 128 | 194 | 0 | 22 | 0 | 40 | 54 | 47 | 21 | 130 | 288 | 67 | 50 | 0 | 0 | 17 | 39 | 7 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 52 | 51 | 0 | 0 | 0 | 0 | 0 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 161 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 209 | 0 | 0 | 200 | 0 | 0 | 0 | 53 | 0 | 189 | 0 | 383 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 |  | 5719 | 2667 | 8386 | 4750 | 823 | 1940 | 412 | 209 | 82 | 42 | 128 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 40 | 260 | 0 | 0 | 351 | 357 |  | 0 | 360 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 22 | 25 | 31 | 22 | 25 | 0 | 0 | 43 | 40 | 105 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 17 | 10 | 0 | 12 | 19 | 26 | 80 | 0 | 0 | 285 | 275 | 192 | 8 | 140 | 33 | 49 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 126 | 191 | 0 | 22 | 0 | 40 | 54 | 44 | 21 | 130 | 290 | 67 | 50 | 0 | 0 | 17 | 39 | 7 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 35 | 51 | 0 | 0 | 0 | 0 | 0 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 161 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 206 | 0 | 0 | 203 | 0 | 0 | 0 | 52 | 0 | 188 | 0 | 382 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5697 | 2604 | 8301 | 4752 | 823 | 1933 | 361 | 206 | 83 | 17 | 126 | 0 | 0 | 101.43
21:00 | 35 | 0 | 0 | 80 | 260 | 0 | 0 | 347 | 358 |  | 0 | 360 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 31 | 22 | 25 | 0 | 0 | 43 | 40 | 105 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 17 | 10 | 0 | 12 | 19 | 42 | 80 | 0 | 0 | 275 | 265 | 179 | 8 | 133 | 33 | 49 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 124 | 181 | 0 | 22 | 0 | 40 | 54 | 53 | 21 | 130 | 287 | 67 | 50 | 0 | 0 | 17 | 40 | 7 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 35 | 51 | 0 | 0 | 0 | 0 | 0 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 156 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 205 | 0 | 0 | 195 | 0 | 0 | 0 | 53 | 0 | 194 | 0 | 368 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5664 | 2533 | 8197 | 4728 | 823 | 1937 | 280 | 205 | 83 | 17 | 124 | 0 | 0 | 101.43
22:00 | 35 | 0 | 0 | 100 | 260 | 0 | 0 | 344 | 310 |  | 0 | 360 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 31 | 22 | 25 | 0 | 0 | 44 | 40 | 110 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 275 | 265 | 179 | 8 | 134 | 33 | 50 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 120 | 181 | 0 | 22 | 0 | 40 | 54 | 7 | 5 | 130 | 274 | 67 | 5 | 0 | 0 | 0 | 6 | 0 | 295 | 0 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 17 | 51 | 0 | 0 | 0 | 0 | 0 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 14 | 11 | 0 | 0 | 205 | 0 | 0 | 188 | 0 | 0 | 0 | 33 | 0 | 185 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5248 | 2406 | 7654 | 4625 | 823 | 1661 | 136 | 205 | 84 | 0 | 120 | 0 | 0 | 101.42
23:00 | 35 | 0 | 0 | 100 | 260 | 0 | 0 | 344 | 310 |  | 0 | 360 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 22 | 25 | 0 | 0 | 44 | 40 | 100 | 100 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 275 | 265 | 180 | 8 | 139 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 112 | 196 | 0 | 0 | 0 | 40 | 54 | 7 | 5 | 130 | 275 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 205 | 0 | 0 | 186 | 0 | 0 | 0 | 13 | 0 | 185 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4945 | 2360 | 7305 | 4413 | 823 | 1584 | 84 | 205 | 84 | 0 | 112 | 0 | 0 | 101.42
24:00 | 35 | 0 | 0 | 100 | 240 | 0 | 0 | 346 | 280 |  | 0 | 360 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 22 | 25 | 0 | 0 | 44 | 40 | 100 | 100 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 275 | 265 | 142 | 8 | 126 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 112 | 198 | 0 | 0 | 0 | 40 | 54 | 7 | 5 | 100 | 250 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 824 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 24 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 205 | 0 | 0 | 130 | 0 | 0 | 0 | 10 | 0 | 130 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4725 | 2209 | 6934 | 4190 | 824 | 1496 | 23 | 205 | 84 | 0 | 112 | 0 | 0 | 101.42
KWH | 825000 | 0 | 0 | 409500 | 5697464 | 153681 | 206976 | 7961440 | 6727000 |  | 0 | 8076250 | 0 | 0 | 0 | 0 | 4098602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470400 | 0 | 0 | 0 | 109476 | 600000 | 554040 | 590000 | 590900 | 0 | 0 | 1002153 | 956000 | 2600000 | 3000000 | 0 | 2797946 | 0 | 3022003 | 0 |  | 0 | 0 | 118756 | 139560 | 3840 | 35520 | 449856 | 730560 | 2006858 | 0 | 0 | 6952000 | 6630500 | 4266000 | 200727 | 3247850 | 497880 | 399840 | 0 | 299076 | 0 | 0 | 0 | 107568 | 54360 | 179000 | 383710 | 2435520 | 3772640 | 0 | 172692 | 11050 | 1112000 | 1296000 | 289200 | 239760 | 2818022 | 6164000 | 1085088 | 330240 | 0 | 0 | 74000 | 304320 | 37080 | 7338000 | 121632 | 47991 | 0 | 0 | 0 | 0 | 643200 | 0 | 0 | 103140 | 0 | 0 | 0 | 8110000 | 0 | 759792 | 783672 | 28800 | 0 | 0 | 0 | 376200 |  | 11193455 | 0 | 7053984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134625 | 3957081 | 486500 | 0 | 0 | 0 | 1640000 | 0 | 0 | 55448 | 214770 | 0 | 0 | 0 | 0 | 86400 | 70992 | 174852 | 0 | 0 | 5072900 | 0 | 0 | 4375227 | 0 | 0 | 0 | 444979 | 0 | 4557391 | 0 | 7341854 | 2592 | 0 | 96864 | 21456 | 171840 | 0 | 36085 | 1785408 |  | 115606331 | 48974703 | 164581034 | 101346531 | 11193455 | 36581457 | 5639739 | 5072900 | 1958153 | 174204 | 2435520 | 179075 | 0
Fuel Cost | 924000 | 0 | 0 | 458640 | 4216123.36 | 149070.57 | 302184.96 | 5732236.8 | 5112520 |  | 0 | 6461000 | 0 | 0 | 0 | 0 | 5082266.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402944 | 0 | 0 | 0 | 82107 | 450000 | 0 | 0 | 0 | 0 | 0 | 260559.78 | 248560 | 3978000 | 4590000 | 0 | 2937843.3 | 0 | 3837943.81 | 0 |  | 0 | 0 | 1245750.44 | 1436072.4 | 36518.4 | 332467.2 | 413867.52 | 2030956.8 | 2107200.9 | 0 | 0 | 5144480 | 5569620 | 3924720 | 196712.46 | 4319640.5 | 408261.6 | 411835.2 | 0 | 427678.68 | 0 | 0 | 0 | 109719.36 | 40770 | 338310 | 287782.5 | 16805088 | 3093564.8 | 0 | 176145.84 | 181220 | 1512320 | 1762560 | 393312 | 299700 | 3494347.28 | 5670880 | 1616781.12 | 581222.4 | 0 | 0 | 117660 | 356054.4 | 87138 | 5209980 | 91224 | 36473.16 | 0 | 0 | 0 | 0 | 6187584 | 0 | 0 | 1190235.6 | 0 | 0 | 0 | 7623400 | 0 | 6769746.72 | 7405700.4 | 0 | 0 | 0 | 0 | 0 |  | 30222328.5 | 0 | 5502107.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1331441.25 | 3165664.8 | 754075 | 0 | 0 | 0 | 3083200 | 0 | 0 | 548935.2 | 2227164.9 | 0 | 0 | 0 | 0 | 95040 | 117136.8 | 132362.964 | 0 | 0 | 20748161 | 0 | 0 | 3850199.76 | 0 | 0 | 0 | 707516.61 | 0 | 4010504.08 | 0 | 5359553.42 | 24520.32 | 0 | 889211.52 | 191172.96 | 1604985.6 | 0 | 0 | 0 |  | 148670701.74 | 84565282.204 | 233235983.944 | 96398581.174 | 30222328.5 | 32547034.58 | 32839529.67 | 20748161 | 509119.78 | 1794685.64 | 16805088 | 1371455.6 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 306 | 274 |  | 0 | 330 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 45 | 40 | 105 | 120 | 0 | 41 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 80 | 0 | 0 | 275 | 260 | 180 | 8 | 127 | 17 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 154 | 0 | 0 | 1.8 | 41 | 54 | 5 | 5 | 130 | 263 | 51 | 5 | 0 | 0 | 0 | 8 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 17.6 | 0 | 0 | 0 | 291 | 0 | 52 | 0 | 4.6 | 0 | 0 | 0 | 24 |  | 337 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 12 | 0 | 183 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 118 |  | 6387.5 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 42 | 260 | 0 | 0 | 357 | 357 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 22 | 25 | 28 | 22 | 21 | 0 | 0 | 42 | 40 | 105 | 120 | 0 | 203 | 0 | 144 | 0 | 0 | 0 | 0 | 34 | 10 | 0 | 8 | 19 | 26 | 80 | 0 | 0 | 280 | 270 | 187 | 8 | 140 | 33 | 50 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 120 | 207 | 0 | 22 | 0 | 40 | 54 | 53 | 21 | 130 | 285 | 66 | 50 | 0 | 0 | 17 | 39 | 7 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 52 | 51 | 0 | 0 | 0 | 0 | 10 |  | 823 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 161 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 202 | 0 | 0 | 0 | 52 | 0 | 190 | 0 | 382 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 |  | 8392 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 110 | 300 | 100 | 40 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 70 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 40 | 110 | 100 | 25 | 200 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 20 | 80 | 0 | 0 | 360 | 360 | 225 | 45 | 150 | 34 | 55 | 0 | 35 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 145 | 200 | 95 | 22 | 0 | 60 | 54 | 51 | 44 | 163 | 330 | 66 | 74 | 0 | 0 | 20 | 36 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 |  |  | 834 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 170 | 26 | 110 | 30 | 100 | 70 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 0 | 110 | 300 | 100 | 40 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 70 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 40 | 110 | 100 | 25 | 150 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 10 | 80 | 0 | 0 | 360 | 360 | 225 | 45 | 140 | 32 | 55 | 0 | 30 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 150 | 0 | 22 | 1.6 | 60 | 54 | 51 | 44 | 163 | 330 | 66 | 74 | 0 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 |  |  | 489 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 26 | 70 | 0 | 100 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 0 | 0 | 100 | 240 | 0 | 0 | 303 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 25 | 31 | 22 | 25 | 0 | 0 | 42 | 40 | 100 | 100 | 0 | 183 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 19 | 9 | 80 | 0 | 0 | 290 | 285 | 178 | 8 | 139 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 84 | 196 | 0 | 0 | 0.3 | 40 | 54 | 53 | 5 | 100 | 258 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9.2 | 0 | 0 | 0 | 323 | 0 | 17 | 10 | 1.1 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 182 | 0 | 0 | 0 | 12 | 0 | 194 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0
199
| Minimum Generation |  | 5746.9 | 9:00
| Highest Generation |  | 8392 | 19:00
| Day Peak Generation |  | 6387.5 | 12:00
| Evening Peak Generation |  | 8392 | 19:00
| HVDC Max Flow |  | 824 | 24:00
| HVDC EvPeak Flow |  | 823 | 19:00
| Load factor L.F |  | 81.72%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-16
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6387.5 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5814 | MW
Evening Peak Generation : |  | 8392 | MW Hour : | 19:00 | Available Max Generation : |  | 15180 | MW
E.P. Demand (at gen end) : |  | 8392 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9400 | MW
Maximum Generation : |  | 8392 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5780 | MW
Total Gen. (MKWH) : |  | 164.581 | System Load Factor : | 81.72% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -46 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-16
Actual : | 101.39 | Ft.(MSL) , | Rule curve : | 107.5 | Ft.( MSL )
Gas Consumed : | Total = | 1080.18 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 128945615.754
: |  | Coal : | 20748161 | Oil : | 34634215.31 | Total : | 184327992.064
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3308.2274 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1120.3425 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1002.9633 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 905.9685 |  |  | 0 | 0%
) | 0 | 0:00 | 818.8724 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 660.7894 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 375.4492 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 170.2934 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 509.605 |  |  | 0 | 0%
Total | 0 |  | 8872.5111 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1&2.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,3 & 5
4) Ashuganj unit-4 & 5
5) Chandpur CCPP ST
6)Sylhet 150 MW
7) Sirajganj unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Halishahar 132/33 kV T3 transformer was under shut down from 08:01 to 12:08 for A/M.
b) Hasnabad 132/33 kV T1 transformer was under shut down from 08:52 to 16:56 for A/M.
c) Kabirpur 132 kV main bus was under shut down from 09:12 to 17:00 for C/M.
d) Haripur-Siddhirganj 230 kV Ckt-1 was under shut down from 10:49 to 13:33 due to R/H at Haripur end
loop T-connector.
e) HVDC Bheramara Filter Bank 20D10B and 20D10C along with Bay was shut down at 09:56 for isolator
and filter maintenance.
f) Shympur 132/33 kV GT-2 transformer(DPDC) was shut down at 09:56 to replace 132 kV breaker. |  |  |  |  | About 11 MW power interruption occurred under Shympur S/S area
from 09:56 to till now(10:59).
g) HVDC pole-2 tripped at 09:28 while switching off filters 20D10B, 20D10C and bay.
h) HVDC pole-2 de-blocked at 11:02 after RMS-voltage came within permissible limit.
i) Feni Lanka Power 114 MW(New PP) started one engine on test basis.
j) Cumilla(N) 132/33 kV T3 transformer was under shut down from 14:04 to 17:53 for C/M.
k) After maintenance Sikalbaha 225 MW CCPP ST was synchronized at 15:01.
l) After maintenance Ghorashal unit-5 was synchronized at 17:41.
m) Hasnabad-Sitalakhya 132 kV Ckt was shut down at 07:15(16/11/2019) for A/M.
n) Ghorashal-Ishwardi 230 kV Ckt-1 was shut down at 07:23(16/11/2019) for A/M and C/M at Tongi,
Maniknagar, Ishwardi, Ghorashal S/S.
o) Sirajganj-Baghabari 132 kV Ckt was shut down at 06:30(16/11/2019) for A/M.
p) Barishal(S) 132/33 kV T-1 transformer was shut down at 07:13(16/11/2019) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 825000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 42 | 409500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 5697464 | Transformer over load
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 206976 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 153681 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 357 | 7961440 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 357 | 6727000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8076250 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 109476
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 220 | 4098602 | Frequency control.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 470400
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1154040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 590000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 590900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 759792 | Low demand
| Dhaka area Total |  |  |  | 5811 | 1849 | 37830521
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 105 | 2600000
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 103140
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 8 | 35520 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1958153 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 2797946
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 144 | 3022003 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 51 | 783672 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 118756 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 139560 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 449856
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 730560
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 3840 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28800
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 802 | 15771806
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2006858 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 187 | 4266000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6952000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6630500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 497880 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 399840
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 299076 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3247850
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 107568
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 54360 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2435520
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 179000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 383710 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 10 | 376200
| Cumilla Area Total |  |  |  | 3005 | 1294 | 28037089
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 207 | 3772640
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 172692
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11050
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 80 | 643200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 309 | 4599582
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 1112000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 54 | 1296000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2818022 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 285 | 6164000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 289200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 21 | 239760
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 47991
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1085088 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 330240 | Low demand
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 74000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 39 | 304320 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 121632
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7338000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8110000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 37080 | Engine problem
| Sylhet Area Total |  |  |  | 1949 | 1474 | 29367333
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 823 | 11193455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 7053984 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 134625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 2592 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 21456 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1183 | 18406112
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 27 | 486500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 161 | 3957081 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 52 | 444979 | Low demand
| Barisal Area Total |  |  |  | 462 | 240 | 4888560
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 65 | 1640000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 214770
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 202 | 4375227 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4557391 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 382 | 7341854 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 86400
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 70992
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 174852
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 25 | 55448 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 96864 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 1785408 | On test
| Rajshahi Area Total |  |  |  | 2183 | 996 | 20399206
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5072900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 171840 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36085
| Rangpur Area Total |  |  |  | 605 | 245 | 5280825
| Total |  |  |  | 19132 | 8392 | 164581034
| Eastern Grid Total |  |  |  | 13568 | 5728 | 115606331
| Western Grid Total |  |  |  | 5564 | 2664 | 48974703
| National Grid Total |  |  |  | 19132 | 8392 | 164581034
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-15
(a) ENTIRE EASTERN GRID : |  | 5549 | MW | (b) ENTIRE WESTERN GRID : |  | 2360 | MW
i) Dhaka area |  | 2913 | MW | i) Khulna area |  | 868 | MW
ii) Chittagong area |  | 866 | MW | ii) Rajshahi area |  | 788 | MW
iii) Comilla area |  | 770 | MW | iii) Barisal area |  | 187 | MW
iv) Mymensingh area |  | 644 | MW | iv) Rangpur area |  | 517 | MW
v) Sylhet area |  | 356 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7909 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 100 | Srimongal | 29 | 1800 | Bottail | 92 | 1800
Munsiganj | 80 | 1800 | Shahjibazar | 88 | 1800 | G.K Project | 24 | 1800
Sonargaon | 61 | 100 | Fenchuganj | 28 | 1800 | Faridpur | 114 | 1830
Shyampur | 180 | 100 | Kulawara | 36 | 1800 | Madaripur | 49 | 2100
Bhulta | 150 | 100 | Sylhet | 100 | 1830 | Sariatpur | 36 | 1830
Madanganj | 47 | 100 | Chatak | 19 | 1830 | Gopalganj | 46 | 1830
Shitalakhya | 87 | 100 | Sunamganj | 30 | 2000 | Bagerhat | 39 | 2200
Rahim steel | 20 | 1830 | Biani Bazar | 36 | 1800 | Mongla | 24 | 100
Matuail | 72 | 100 | Comilla (S) | 128 | 1930 | Satkhira | 56 | 2000
Ghorasal | 60 | 100 | Comilla(N) | 85 | 1830 | Gallamari | 31 | 1300
Narsingdi | 107 | 1930 | Chandpur | 70 | 1900 | Magura | 34 | 1800
Haripur (SBU) | 88 | 100 | Feni | 97 | 1800 | Norail | 26 | 1800
Ullon | 62 | 2000 | Chowmuhani | 132 | 2000 | Chuadanga | 60 | 1800
Hasnabad | 132 | 2000 | Ashuganj | 42 | 1800 | Barisal(N) | 14 | 1800
Magbazar | 75 | 1900 | Daudkandi | 90 | 1930 | Barisal (S) | 62 | 1830
Maniknagar | 74 | 2000 | B.Baria | 100 | 1930 | Patuakhali | 73 | 2100
Bangabhaban | 12 | 2000 | Ramganj | 48 | 1800 | Bhandaria | 30 | 2100
Narinda | 68 | 1900 | Madunaghat | 45 | 1800 | Borhan Uddin | 25 | 2100
Dhanmondi | 98 | 1800 | Hathazari | 75 | 1800 | Ishurdi | 41 | 1900
Lalbag | 52 | 1830 | Khulshi | 15 | 1400 | Ruppur Paromanobik | 1 | 100
Madartek | 56 | 2000 | Halishahar | 112 | 1900 | Natore | 76 | 1800
Mirpur | 84 | 1900 | Baraulia | 95 | 100 | Bogra | 128 | 1800
Kalyanpur | 87 | 1830 | Sikalbaha | 24 | 1500 | Noagaon | 77 | 1830
Gulshan | 102 | 1800 | Dohazari | 75 | 2000 | Rajshahi | 96 | 1830
Uttara | 45 | 1800 | Cox'sbazar | 81 | 1800 | Rajshahi New | 8 | 1900
Uttara New | 28 | 1800 | Chandraghona | 24 | 1800 | C.Nawabganj | 52 | 1930
Kamrangirchar | 50 | 1930 | Kaptai | 3 | 1300 | Amnura | 23 | 1830
Savar | 96 | 1500 | A. Khaer Stl. | 0 | 0 | Pabna | 68 | 1800
Bhasantec | 122 | 1800 | Bakulia | 82 | 2200 | Shahjadpur | 62 | 1800
Agargaon | 41 | 1800 | Julda | 18 | 100 | Serajganj | 54 | 1800
Satmosjid | 78 | 1830 | TK chemical | 14 | 1500 | Niyamatpur | 41 | 1800
Tongi | 102 | 1800 | Modern Steel | 11 | 2400 | Joypurhat | 39 | 1800
Kabirpur | 114 | 1200 | Shahmirpur | 24 | 100 | Sherpur(Bogura) | 35 | 1800
Basundhara | 81 | 1800 | Khagrachhari | 16 | 1800 | Mohastangor | 10 | 1800
Manikganj | 57 | 1800 | Matarbari | 26 | 1800 | Rangpur | 96 | 1900
Joydevpur | 132 | 1830 | Baroiar Hat | 20 | 1800 | Lalmonirhat | 42 | 1800
New Tongi | 67 | 1200 | Rangamati | 8 | 1100 | Saidpur | 67 | 1800
Korda | 163 | 100 | Abul Khair 230 | 146 | 1400 | Purbasadipur | 75 | 1800
Dhamrai | 44 | 1900 | BSRM | 109 | 200 | Thakurgaon | 54 | 1800
Valuka | 72 | 1900 | GPH Ispat | 11 | 100 | Palashbari | 78 | 1800
Tangail | 136 | 1800 | Goalpara | 24 | 1900 | Barapukuria | 34 | 1930
Mymensing | 151 | 1800 | Central s/s | 57 | 1900 | Panchagar | 36 | 1900
Kishorganj | 82 | 1930 | Noapara | 41 | 1800 | Joldhaka | 18 | 1800
Netrokona | 69 | 1800 | Jessore | 78 | 1830 | Kurigram | 34 | 1800
Jamalpur | 86 | 1900 | Benapol | 26 | 1800 | 0 | 0 | 0
Sherpur | 64 | 1800 | Jhenida | 74 | 1830 | 0 | 0 | 0
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-15 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 388 | 17:00 | 381 | 1:00 | Kaliakoir | 368 | 7:00 | 361 | 12:00
Bheramara | 407 | 3:00 | 394 | 18:00 | Bhulta | 377 | 7:00 | 370 | 1:00
Ashuganj(N) | 383 | 8:00 | 374 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 1:00
Ghorasal | 228 | 8:00 | 220 | 1:00 | Hathazari | 219 | 18:30 | 215 | 1:00
Ishurdi | 242 | 5:00 | 235 | 18:00 | Megnaghat | 221 | 10:00 | 218 | 18:30
Ashuganj | 237 | 21:00 | 228 | 1:00 | Fenchuganj | 233 | 17:00 | 229 | 1:00
Serajganj | 232 | 9:00 | 230 | 8:00 | Siddhirganj | 222 | 8:00 | 217 | 1:00
Baghabari | 241 | 5:00 | 237 | 18:00 | Maniknagar | 220 | 6:00 | 216 | 1:00
Barapukuria | 233 | 6:00 | 224 | 18:00 | Old Airport | 219 | 6:00 | 215 | 1:00
Bogra | 237 | 6:00 | 225 | 18:00 | Barisal | 233 | 2:00 | 224 | 19:30
Khulna South | 244 | 5:00 | 231 | 20:00 | AKSML | 215 | 17:00 | 209 | 2:00
Rampura | 220 | 4:00 | 218 | 23:00 | BSRM | 217 | 17:00 | 211 | 2:00
Haripur | 228 | 21:00 | 216 | 1:00 | Bibiyana | 231 | 9:00 | 225 | 1:00
Hasnabad | 218 | 12:00 | 213 | 1:00 | Bhulta | 223 | 8:00 | 218 | 1:00
Aminbazar | 220 | 6:00 | 215 | 1:00 | Ashuganj (S) | 231 | 8:00 | 227 | 4:00
Tongi | 216 | 7:00 | 209 | 1:00 | Kaliakoir | 224 | 7:00 | 219 | 1:00
Comilla (N) | 228 | 8:00 | 221 | 1:00 | GPH | 215 | 17:00 | 210 | 2:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 900 | 130 | 100 | Halishahar | 129 | 600 | 125 | 1200
Munsiganj | 132 | 600 | 128 | 100 | Baraulia | 128 | 700 | 124 | 1200
Megnaghat | 130 | 1000 | 126 | 100 | Sikalbaha | 129 | 1500 | 124 | 1200
Shyampur | 134 | 1300 | 132 | 100 | Dohazari | 128 | 800 | 123 | 100
Bhulta | 128 | 500 | 124 | 100 | Cox'sbazar | 120 | 1700 | 100 | 1300
Madanganj | 132 | 500 | 127 | 100 | Chandraghona | 130 | 100 | 125 | 1300
Shitalakhya | 134 | 700 | 130 | 100 | Kaptai | 130 | 700 | 125 | 1300
Rahim steal | 133 | 500 | 130 | 100 | A. Khaer Stl. | 127 | 700 | 125 | 100
Matuail | 131 | 400 | 128 | 100 | Bakulia | 126 | 100 | 123 | 1200
Ghorasal | 135 | 1300 | 130 | 100 | Julda | 127 | 500 | 124 | 1200
Narsinghdi | 131 | 700 | 127 | 100 | TK Chemical | 127 | 700 | 125 | 1400
Haripur (SBU) | 134 | 900 | 130 | 100 | Modern Steel | 126 | 400 | 124 | 100
Ullon | 132 | 900 | 130 | 1700 | Shahmirpur | 128 | 800 | 124 | 1200
Hasnabad | 135 | 800 | 132 | 1300 | Khagrachhari | 129 | 800 | 125 | 1200
Magbazar | 132 | 600 | 129 | 1300 | Matarbari | 123 | 600 | 118 | 100
Maniknagar | 135 | 700 | 132 | 600 | Baroiar Hat | 129 | 700 | 124 | 1900
Bangabhaban | 135 | 700 | 132 | 600 | Rangamati | 129 | 800 | 125 | 1400
Narinda | 135 | 700 | 132 | 600 | Goalpara | 138 | 300 | 131 | 2000
Dhanmondi | 132 | 900 | 130 | 1700 | Central s/s | 138 | 600 | 131 | 1930
Lalbag | 134 | 600 | 131 | 1200 | Noapara | 137 | 200 | 129 | 1800
Madartek | 132 | 600 | 129 | 1200 | Jessore | 134 | 400 | 124 | 1300
Mirpur | 134 | 500 | 131 | 1200 | Benapol | 138 | 400 | 127 | 1300
Kalyanpur | 137 | 600 | 133 | 1830 | Jhenida | 134 | 100 | 124 | 1800
Gulshan | 131 | 500 | 128 | 1800 | Bottail | 137 | 400 | 130 | 1800
Uttara | 134 | 500 | 129 | 1500 | G.K Project | 141 | 600 | 137 | 1800
Uttara New | 133 | 500 | 130 | 1400 | Faridpur | 136 | 500 | 127 | 2100
Kamrangirchar | 133 | 500 | 131 | 1100 | Madaripur | 137 | 300 | 126 | 2200
Savar | 134 | 600 | 129 | 1700 | Sariatpur | 136 | 100 | 125 | 1930
Bhasantec | 132 | 600 | 129 | 1100 | Gopalganj | 140 | 200 | 129 | 1930
Agargaon | 133 | 600 | 129 | 1800 | Bagerhat | 137 | 500 | 129 | 2000
Satmosjid | 132 | 500 | 129 | 1200 | Mongla | 135 | 400 | 128 | 1930
Tongi | 134 | 800 | 128 | 100 | Satkhira | 138 | 400 | 130 | 2000
Kabirpur | 131 | 800 | 123 | 100 | Gallamari | 140 | 500 | 132 | 1800
Basundhara | 133 | 800 | 126 | 100 | Magura | 137 | 500 | 123 | 1800
Manikganj | 136 | 800 | 130 | 100 | Norail | 135 | 400 | 118 | 1930
Joydevpur | 135 | 600 | 130 | 1200 | Chuadanga | 132 | 300 | 121 | 1800
New Tongi | 133 | 800 | 128 | 1800 | Barisal(N) | 139 | 200 | 132 | 2100
Kodda | 130 | 800 | 124 | 100 | Barisal (S) | 138 | 900 | 131 | 1800
Dhamrai | 130 | 600 | 127 | 1800 | Patuakhali | 137 | 700 | 129 | 2100
Valuka | 127 | 700 | 121 | 1100 | Bhandaria | 136 | 500 | 130 | 1400
Tangail | 130 | 600 | 125 | 1100 | Ishurdi | 138 | 200 | 133 | 1930
Mymensing | 128 | 600 | 122 | 1800 | Ruppur Paromanobik | 137 | 600 | 134 | 1830
Kishorganj | 130 | 500 | 125 | 1930 | Natore | 136 | 500 | 130 | 1800
Netrokona | 127 | 600 | 121 | 1800 | Bogra | 140 | 600 | 132 | 1800
Jamalpur | 128 | 1900 | 122 | 100 | Noagaon | 135 | 600 | 128 | 1800
Sherpur | 125 | 1500 | 121 | 100 | Rajshahi | 132 | 500 | 128 | 1200
Srimongal | 134 | 1930 | 131 | 100 | Rajshahi New | 133 | 400 | 127 | 1200
Shahjibazar | 134 | 2100 | 129 | 100 | C.Nawabganj | 130 | 600 | 123 | 1200
Fenchuganj | 133 | 600 | 130 | 100 | Amnura | 130 | 500 | 125 | 1200
Khulawara | 132 | 700 | 129 | 100 | Pabna | 138 | 300 | 134 | 1300
Sylhet | 132 | 2100 | 127 | 100 | Shahjadpur | 142 | 900 | 140 | 1500
Chatak | 131 | 2100 | 127 | 100 | Serajganj | 138 | 500 | 132 | 1830
Sunamganj | 130 | 900 | 125 | 100 | Niyamatpur | 135 | 400 | 125 | 1800
Biani Bazar | 131 | 2100 | 127 | 100 | Joypurhat | 136 | 500 | 126 | 1800
Comilla(s) | 129 | 2400 | 124 | 1200 | Sherpur(Bogura) | 139 | 600 | 132 | 1800
Comilla(n) | 133 | 1000 | 131 | 1500 | Mohastangor | 137 | 600 | 128 | 1800
Chandpur | 130 | 900 | 126 | 2300 | Rangpur | 130 | 600 | 121 | 1800
Feni | 129 | 900 | 123 | 2000 | Lalmonirhat | 125 | 400 | 119 | 1900
Chowmuhani | 126 | 700 | 119 | 1100 | Saidpur | 130 | 500 | 120 | 1800
Ashuganj | 135 | 700 | 132 | 2400 | Purbasadipur | 130 | 500 | 114 | 1800
Daudkandi | 132 | 800 | 127 | 1800 | Thakurgaon | 126 | 600 | 112 | 1800
B.Baria | 132 | 700 | 129 | 2000 | Palashbari | 134 | 500 | 124 | 1830
Ramganj | 122 | 700 | 120 | 1800 | Barapukuria | 133 | 600 | 124 | 1800
Madanhat | 130 | 400 | 128 | 100 | Panchagar | 125 | 600 | 107 | 1800
Hathazari | 130 | 1000 | 126 | 100 | Joldhaka | 130 | 500 | 120 | 1800
Khulshi | 126 | 700 | 123 | 1200 | Kurigram | 129 | 600 | 117 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 360 | 4725 | 2209 | 6934 |  |  |  | QF-LDC-12
0:30 | 380 | 4739 | 2274 | 7013 | Date: | 2019-11-15
1:00 | 400 | 4753 | 2339 | 7092
1:30 | 380 | 4759 | 2204.5 | 6963.5
2:00 | 360 | 4765 | 2070 | 6835
2:30 | 295 | 4737 | 1974 | 6711 | [5 empty] | Gen. at Eve. Peak | 8392 | 8392 MW (19:00 )
3:00 | 230 | 4709 | 1878 | 6587 | [6 empty] | 19:00
3:30 | 227 | 4667.5 | 1822.5 | 6490 | [5 empty] | Gen. at Day Peak | 6387.5 | 6387.5 MW (12:00 )
4:00 | 224 | 4626 | 1767 | 6393 | [6 empty] | 12:00
4:30 | 212 | 4573 | 1736 | 6309 | [5 empty] | Highest Generation | 8392
5:00 | 200 | 4520 | 1705 | 6225 | [6 empty] | 19:00
5:30 | 162 | 4463.5 | 1688.5 | 6152
6:00 | 124 | 4407 | 1672 | 6079
6:30 | 64 | 4356.775 | 1633.7 | 5990.475
7:00 | 4 | 4306.55 | 1595.4 | 5901.95
7:30 | 25 | 4284.375 | 1588.15 | 5872.525
8:00 | 46 | 4262.2 | 1580.9 | 5843.1
8:30 | 51 | 4215.2 | 1579.8 | 5795
9:00 | 56 | 4168.2 | 1578.7 | 5746.9
9:30 | 101 | 4156.4 | 1588.75 | 5745.15
10:00 | 146 | 4144.6 | 1598.8 | 5743.4
10:30 | 208 | 4156.95 | 1667.8 | 5824.75
11:00 | 270 | 4169.3 | 1736.8 | 5906.1
11:30 | 282 | 4321.15 | 1825.65 | 6146.8
12:00 | 294 | 4473 | 1914.5 | 6387.5
12:30 | 240 | 4585.85 | 1932.9 | 6518.75
13:00 | 186 | 4698.7 | 1951.3 | 6650
13:30 | 221 | 4618.7 | 1882.3 | 6501
14:00 | 256 | 4538.7 | 1813.3 | 6352
14:30 | 260 | 4535.05 | 1807.95 | 6343
15:00 | 264 | 4531.4 | 1802.6 | 6334
15:30 | 228 | 4495.4 | 1741.4 | 6236.8
16:00 | 192 | 4459.4 | 1680.2 | 6139.6
16:30 | 199 | 4448.2 | 1700.65 | 6148.85
17:00 | 206 | 4437 | 1721.1 | 6158.1
17:30 | 185 | 4949.5 | 2167.05 | 7116.55
18:00 | 164 | 5462 | 2613 | 8075
18:30 | 164 | 5595 | 2638.5 | 8233.5
19:00 | 164 | 5728 | 2664 | 8392
19:30 | 124 | 5719 | 2667 | 8386
20:00 | 104 | 5697 | 2604 | 8301 |  |  |  | Executive Engineer
20:30 | 109 | 5680.5 | 2568.5 | 8249 |  |  |  | Network Operation Division
21:00 | 114 | 5664 | 2533 | 8197
21:30 | 172 | 5456 | 2469.5 | 7925.5
22:00 | 230 | 5248 | 2406 | 7654 |  |  |  |  | Page 6 of 7
22:30 | 295 | 5096.5 | 2383 | 7479.5
23:00 | 360 | 4945 | 2360 | 7305
23:30 | 360 | 4835 | 2284.5 | 7119.5
24:00 | 360 | 4725 | 2209 | 6934
8392 MW (19:00 )
6387.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-15 |  | Energy | 164581034
[10 empty] | 2019-11-15 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4190 | 824 | 1496 | 23 | 205 | 84 | 0 | 0 | 112
0:30 | 4203 | 769 | 1516.5 | 130 | 202.5 | 86 | 0 | 0 | 106 | Date: | 2019-11-15
1:00 | 4216 | 714 | 1537 | 237 | 200 | 88 | 0 | 0 | 100
1:30 | 4248 | 574 | 1542.5 | 212 | 200 | 88 | 0 | 0 | 99 | [7 empty] | Total Energy | 164.581 | Total Energy Gen 164.581 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 164.581 MKWHr
2:00 | 4280 | 434 | 1548 | 187 | 200 | 88 | 0 | 0 | 98 | [7 empty] | Energy not Served | 0
2:30 | 4278 | 337 | 1527 | 184 | 200 | 88 | 0 | 0 | 97 | [7 empty] | Energy Requirement | 164.581
3:00 | 4276 | 240 | 1506 | 181 | 200 | 88 | 0 | 0 | 96
3:30 | 4240 | 239.5 | 1460.5 | 169 | 200 | 88 | 0 | 0 | 93 | [6 empty] | Shortage
4:00 | 4204 | 239 | 1415 | 157 | 200 | 88 | 0 | 0 | 90
4:30 | 4146 | 239.5 | 1390.5 | 157 | 200 | 88 | 0 | 0 | 88
5:00 | 4088 | 240 | 1366 | 157 | 200 | 88 | 0 | 0 | 86
5:30 | 4048.5 | 240 | 1336 | 157 | 200 | 86.5 | 0 | 0 | 84
6:00 | 4009 | 240 | 1306 | 157 | 200 | 85 | 0 | 0 | 82
6:30 | 3914 | 239.5 | 1306 | 159 | 205 | 85 | 0 | 0 | 80 |  |  |  |  | Coal
7:00 | 3819 | 239 | 1306 | 161 | 210 | 85 | 0 | 0 | 78
7:30 | 3766.5 | 239 | 1311.5 | 179.5 | 207.5 | 85 | 0 | 0 | 75 |  |  |  | Oil |  |  |  | ,
8:00 | 3714 | 239 | 1317 | 198 | 205 | 85 | 0 | 0 | 72
8:30 | 3657 | 239 | 1311 | 204 | 207.5 | 85 | 0 | 0 | 74
9:00 | 3600 | 239 | 1305 | 210 | 210 | 85 | 0 | 0 | 76
9:30 | 3623.5 | 239 | 1289 | 200 | 210 | 86 | 0 | 0 | 73
10:00 | 3647 | 239 | 1273 | 190 | 210 | 87 | 0 | 0 | 70
10:30 | 3690 | 288 | 1255 | 187 | 210 | 86 | 0 | 0 | 80
11:00 | 3733 | 337 | 1237 | 184 | 210 | 85 | 0 | 0 | 90
11:30 | 3842.5 | 337 | 1351.5 | 198 | 210 | 85 | 0 | 0 | 93
12:00 | 3952 | 337 | 1466 | 212 | 210 | 85 | 0 | 0 | 96
12:30 | 4058 | 335.5 | 1467.5 | 235 | 210 | 84.5 | 0 | 0 | 100
13:00 | 4164 | 334 | 1469 | 258 | 210 | 84 | 0 | 0 | 104
13:30 | 4164 | 334 | 1469 | 258 | 210 | 84 | 0 | 0 | 104
14:00 | 4164 | 334 | 1469 | 258 | 210 | 84 | 0 | 0 | 104
14:30 | 4056 | 334 | 1415 | 272.5 | 210 | 82 | 0 | 0 | 105
15:00 | 3948 | 334 | 1361 | 287 | 210 | 80 | 0 | 0 | 106
15:30 | 3937 | 334 | 1336 | 232 | 209.5 | 80 | 0 | 0 | 103
16:00 | 3926 | 334 | 1311 | 177 | 209 | 80 | 0 | 0 | 100
16:30 | 3924 | 334 | 1302 | 197.5 | 209 | 81 | 0 | 0 | 100
17:00 | 3922 | 334 | 1293 | 218 | 209 | 82 | 0 | 0 | 100
17:30 | 4273.5 | 578.5 | 1519 | 309 | 209.5 | 82 | 30 | 0 | 115
18:00 | 4625 | 823 | 1745 | 400 | 210 | 82 | 60 | 0 | 130
18:30 | 4680.5 | 823 | 1844 | 409.5 | 210 | 82 | 59.5 | 0 | 125
19:00 | 4736 | 823 | 1943 | 419 | 210 | 82 | 59 | 0 | 120
19:30 | 4750 | 823 | 1940 | 412 | 209 | 82 | 42 | 0 | 128
20:00 | 4752 | 823 | 1933 | 361 | 206 | 83 | 17 | 0 | 126
20:30 | 4740 | 823 | 1935 | 320.5 | 205.5 | 83 | 17 | 0 | 125
21:00 | 4728 | 823 | 1937 | 280 | 205 | 83 | 17 | 0 | 124
21:30 | 4676.5 | 823 | 1799 | 208 | 205 | 83.5 | 8.5 | 0 | 122
22:00 | 4625 | 823 | 1661 | 136 | 205 | 84 | 0 | 0 | 120
22:30 | 4519 | 823 | 1622.5 | 110 | 205 | 84 | 0 | 0 | 116
23:00 | 4413 | 823 | 1584 | 84 | 205 | 84 | 0 | 0 | 112
23:30 | 4301.5 | 823.5 | 1540 | 53.5 | 205 | 84 | 0 | 0 | 112 | Max Temp. in Dhaka |  | 32.0° C
24:00 | 4190 | 824 | 1496 | 23 | 205 | 84 | 0 | 0 | 112
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 164.581 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 164.581 MKWHr
Note on W13: Author:

## Generation
2019-11-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 48 | 48 | 48 | 48 | 48 | 45 | 45 | 45 | 45 | 47 | 45 | 45 | 44 | 42 | 40 | 40 | 42 | 42 |  | 42 | 42 | 43 | 43 | 44 | 44 | 44 | 1002153
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 956000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 110 | 100 | 100 | 2600000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 3000000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9.1 | 13.3 | 16.3 | 17.4 | 17.6 | 17 | 13.9 | [12 empty] | 103140
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 151 | 151 | 151 | 150 | 90 | 24 | 24 | 42 | 40 | 41 | 52 | 40 | 50 | 52 | 101 | 188 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 2797946
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 100 | 100 | 110 | 120 | 120 | 105 | 85 | 148 | 147 | 144 | 145 | 145 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 120 | 120 | 3022003
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 34 |  | 34 | 17 | 17 | 17 | 0 | 0 |  | 118756
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 17 | 17 | 0 |  |  | 17 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 34 | 17 | 783672
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 173 | 165 | 165 | 150 | 145 | 135 | 123 | 120 | 123 | 122 | 162 | 201 | 170 | 150 | 170 | 170 | 170 | 220 |  | 220 | 220 | 220 | 225 | 171 | 160 | 184 | 4098602
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 825000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | [17 empty] | 11 |  | 42 | 40 | 40 | 80 | 100 | 100 | 100 | 409500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 240 | 5697464
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2006858
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 17 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 10 | 10 | 497880
33 | Ashuganj 225 MW CCPP | 163 | 176 | 177 | 173 | 168 | 160 | 167 | 160 | 161 | 167 | 174 | 180 | 196 | 200 | 181 | 181 | 160 | 201 |  | 187 | 192 | 192 | 179 | 179 | 180 | 142 | 4266000
34 | Ashuganj 450 MW CCPP(South) | 260 | 275 | 285 | 275 | 265 | 265 | 265 | 260 | 260 | 260 | 270 | 260 | 285 | 295 | 265 | 265 | 265 | 290 |  | 270 | 275 | 275 | 265 | 265 | 265 | 265 | 6630500
| Ashuganj 450 MW CCPP(North) | 260 | 275 | 280 | 270 | 260 | 260 | 265 | 260 | 260 | 260 | 275 | 275 | 360 | 300 | 275 | 275 | 275 | 300 |  | 280 | 285 | 285 | 275 | 275 | 275 | 275 | 6952000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 5 | 5 | 5 | 5 | 5 |  | 50 | 49 | 49 | 49 | 50 | 5 | 5 | 399840
36 | Chandpur 150 MW CCPP | 133 | 138 | 137 | 138 | 138 | 127 | 137 | 126 | 127 | 130 | 137 | 127 | 138 | 139 | 140 | 126 | 126 | 140 |  | 140 | 144 | 140 | 133 | 134 | 139 | 126 | 3247850
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 346 | 359 | 354 | 352 | 351 | 340 | 280 | 283 | 280 | 280 | 260 | 306 | 345 | 287 | 312 | 321 | 296 | 333 |  | 357 | 350 | 351 | 347 | 344 | 344 | 346 | 7961440
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 330 | 300 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8076250
41 | Haripur 360MW CCPP(HPL) | 300 | 280 | 260 | 260 | 260 | 230 | 230 | 230 | 240 | 239 | 237 | 274 | 275 | 254 | 254 | 255 | 253 | 354 |  | 357 | 357 | 357 | 358 | 310 | 310 | 280 | 6727000
42 | RPCL 210MW CCPP | 159 | 159 | 159 | 159 | 159 | 163 | 146 | 145 | 126 | 127 | 126 | 154 | 150 | 151 | 151 | 153 | 153 | 186 |  | 207 | 194 | 191 | 181 | 181 | 196 | 198 | 3772640
43
44 | Fenchugonj CCPP Phase-1 | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 38 | 40 | 40 | 41 | 40 | 38 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1112000
45 | Fenchugonj CCPP Phase-2 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1296000
46 | Shajibazar 330 MW CCPP | 276 | 271 | 275 | 277 | 273 | 263 | 277 | 266 | 265 | 265 | 281 | 263 | 279 | 275 | 274 | 266 | 266 | 291 |  | 285 | 288 | 290 | 287 | 274 | 275 | 250 | 6164000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 51 | 40 | 40 | 40 | 40 | 40 | 51 |  | 66 | 67 | 67 | 67 | 67 | 40 | 40 | 1085088
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 |  | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 330240
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 0 | 0 |  | 74000
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 5 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 36 |  | 39 | 39 | 39 | 40 | 6 | 10 | 10 | 304320
53 | Sylhet 10MW PP (Desh) | [17 empty] | 7 |  | 7 | 7 | 7 | 7 | 0 | 0 |  | 37080
54 | Hobiganj 11MW PP Cofidence-E | [16 empty] | 11 | 3 |  | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 47991
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 5 | 8 | 8 | 11 |  | 53 | 47 | 44 | 53 | 7 | 7 | 7 | 289200
56 | Shahjahanulla 25 MW PP | [17 empty] | 24 |  | 24 | 24 | 24 | 24 |  |  | 0 | 121632
57 | Bibiana-II 341 MW CCPP (Summit) | 265 | 290 | 300 | 310 | 300 | 270 | 270 | 290 | 280 | 290 | 265 | 290 | 275 | 285 | 310 | 285 | 290 | 305 |  | 310 | 310 | 310 | 300 | 295 | 290 | 260 | 7338000
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 449856
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 109476
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | [15 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 0 | 172692
63 | Impoprt (Tripura) | 100 | 98 | 96 | 90 | 86 | 82 | 78 | 72 | 76 | 70 | 90 | 96 | 104 | 106 | 106 | 100 | 100 | 130 |  | 120 | 128 | 126 | 124 | 120 | 112 | 112 | 2435520
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 41 | 41 | 42 | 42 | 31 | 36 | 12 | 12 | 19 | 28 | 18 | 11 | 12 | 17 | 23 |  | 26 | 28 | 26 | 42 | 40 | 42 | 42 | 730560
65 | Feni 22MW PP (Doreen) | [17 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 |  | 0 | 107568
66 | Feni 11 MW PP (Doreen) | [17 empty] | 8 |  | 8 | 11 | 11 | 11 | 11 |  | 0 | 54360
67 | Jangalia 33MW PP (Summit) | [17 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 179000
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 21 | 21 | 21 | [6 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 383710
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 28 | 28 | 28 | 28 | 24 | 22 | 22 | 8 | 8 | 12 | 12 | 12 | 12 | 16 |  | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 554040
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 590000
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 25 | 25 | 25 | 25 | 25 | 590900
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 14 | 12 | 12 | 14 | 0 | [16 empty] | 0 | 153681
| Feni Lanka Power | [8 empty] | 4 | 8 | 19 | 24 | 50 | 62 | 64 | 46 | 27 | 28 |  | 10 | [5 empty] | 0 | 376200
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | 35 | 17 | 17 |  |  |  | 4 | 17 | 52 | 34 | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 35 | 35 | 17 |  | 0 | 759792
| Kaptai 7 MW Solar PP | [6 empty] | 0.45 | 1.6 | 3.3 | 4.3 | 4.6 | 4.6 | 4.2 | 3.4 | 2.3 | 1 | 0 | [9 empty] | 28800
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [17 empty] | 206976
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | [6 empty] | 5 | 10 |  | 10 | 10 | 10 | 10 | 0 | 0 |  | 139560
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 21 |  | 21 | 21 | 21 | 21 | 5 | 5 | 5 | 239760
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 |  | 35 | 35 | 35 | 35 | 7 | 7 | 7 | 299076
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [17 empty] | 1 |  | 8 | 12 | 12 | 12 |  |  | 0 | 35520
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 3840
97 | Katpotti 52 MW PP (Sinha) | 24 | 18 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 6 | 6 | 6 | 12 | 12 | 12 | 12 | 19 |  | 48 | 47 | 48 | 47 | 24 | 18 | 6 | 470400
98 | Bosila 108MW PP(CLC) | [17 empty] | 8 | [7 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 2818022
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.5 | 1.6 | 2 | 2.3 | 1.8 | 0.5 | 0.4 | 2.1 | 0.4 | 0 | [9 empty] | 11050
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 | 7 | 7 |  |  |  |  | 7 | 7 | 7 | 7 | 12 | 32 | 32 | 32 | 16 | 16 | 53 |  | 80 | 80 | 80 | 50 | 32 | 32 | 0 | 643200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn)
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 352 | 363 | 366 | 360 | 354 | 354 | 352 | 354 | 295 | 312 | 295 | 291 | 302 | 320 | 293 | 293 | 292 | 371 |  | 367 | 372 | 372 | 367 | 367 | 367 | 366 | 8110000
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4753 | 4765 | 4709 | 4626 | 4520 | 4407 | 4306.55 | 4262.2 | 4165.1 | 4144.6 | 4169.3 | 4473 | 4698.7 | 4538.7 | 4531.4 | 4459.4 | 4437 | 5462 | 0 | 5728 | 5719 | 5697 | 5664 | 5248 | 4945 | 4725 | 115606331
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 0 | 17 |  | 0 | [6 empty] | 2592
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 11 | 12 | 12 | 12 | 10 | 11 | 11 | 12 | 12 | 16 |  | 52 | 53 | 52 | 53 | 33 | 13 | 10 | 444979
| Bhola 225 MW CCPP | 172 | 172 | 172 | 173 | 173 | 162 | 173 | 162 | 151 | 169 | 160 | 151 | 160 | 161 | 161 | 156 | 150 | 161 |  | 161 | 161 | 161 | 156 | 154 | 161 | 158 | 3957081
140 | Bhola 33 MW PP (Venture) | 22 | 23 | 22 | 20 | 19 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 18 | 19 | 25 |  | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 486500
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 24 |  | 40 | 40 | 40 | 16 | 0 |  |  | 134625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 9 | 17 |  | 0 | [6 empty] | 21456
146 | Bheramara HVDC | 714 | 434 | 240 | 239 | 240 | 240 | 239 | 239 | 239 | 239 | 337 | 337 | 334 | 334 | 334 | 334 | 334 | 823 |  | 823 | 823 | 823 | 823 | 823 | 823 | 824 | 11193455
147 | Bheramara 360 MW CCPP | 300 | 300 | 300 | 270 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 270 | 270 | 270 | 270 | 270 | 270 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 280 | 7053984
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 210 | 205 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 209 | 209 | 210 |  | 210 | 209 | 206 | 205 | 205 | 205 | 205 | 5072900
153 | Baghabari 71 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 70 | 70 | 70 | 70 | 70 | 70 | 1640000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 169 | 178 | 177 | 176 | 174 | 171 | 130 | 130 | 130 | 130 | 152 | 182 | 191 | 168 | 174 | 167 | 165 | 178 |  | 202 | 200 | 203 | 195 | 188 | 186 | 130 | 4375227
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 181 | 183 | 185 | 185 | 185 | 130 | 130 | 130 | 130 | 166 | 183 | 200 | 194 | 188 | 187 | 182 | 186 |  | 190 | 189 | 188 | 194 | 185 | 185 | 130 | 4557391
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 373 | 378 | 380 | 300 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 350 | 360 | 250 | 282 | 253 | 253 | 378 |  | 382 | 383 | 382 | 368 | 359 | 368 | 373 | 7341854
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 5 | 0 | 0 | 86400
163 | Bogura 20 MW PP (Energyprima) | [16 empty] | 2 | 14 |  | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 70992
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 174852
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 12 | 50 |  | 50 | 50 | 50 | 24 | 12 | 0 | 0 | 214770
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 26 |  | 25 | 25 | 0 | 0 |  |  |  | 55448
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 4 | 35 |  | 35 | 35 |  |  |  |  | 0 | 96864
172 | Confidence Power Bogura Unit-1 113 MW | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 76 | 0 | [10 empty] | 1785408
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 30 | 35 |  | 35 | 35 | 35 | 35 | 0 | 0 |  | 171840
177 | Sympa Solar Power 8MW | [6 empty] | 0.4 | 1.9 | 3.7 | 4.8 | 5.8 | 5.5 | 5.3 | 4.3 | 3.6 | 1.2 | 0.1 | 0 | [8 empty] | 36085
178
178