## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-18 | Monday
|  | Date (day): | 2019-11-18 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12355.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15116 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-17 | 2019-11-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 100 | 110 | 110 | 80 |  | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 350 | 350 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas Shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 350 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 356 | 323 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 3 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 47 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 79 | 80 | 210 | 210
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 28 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 65 | 32 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 70 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 50 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 90 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 8 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 17 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2037 | 2258 | 3695 | 4097 | 676 | 968
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 6 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 34 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 82 | 83 | 85 | 85 | 145 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 203 | 200 | 200
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 104 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 63 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 86 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 30 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 0 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 8 | 7 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.45 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 15 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 14 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 16 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 700.45 | 988 | 1580 | 1748 | 275 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 180 | 0 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 275 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 275 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 50 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 35 | 8 | 45 | 45 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 12 | 30 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 93 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 138 | 140 | 150
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 120 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 132 | 115 | 147
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 5 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 21 | 21 |  | 4 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 50 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1418 | 1491 | 1559 | 2231 | 505 | 28
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 146 | 165 | 200
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 0 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 19 | 86 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 7 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 166 | 261 | 403.6 | 632 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 52 | 52 | 54 | 54
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 305 | 296 | 330 | 330
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 48 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 15 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 79 | 77 | 77 |  | 9 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 8 | 33 | 32 | 36 |  | 14 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 275 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 393 | 355 | 400 | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1315 | 1430 | 1683 | 1687 | 0 | 165
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 639 | 826 | 644 | 839
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 310 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 36 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 989 | 1247 | 1139 | 2065 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 26 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 172 | 160 | 170 | 170
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 44 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 201 | 230 | 361 | 431 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 167 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 204 | 190 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 261 | 231 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 8 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 26 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 96 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 748 | 889 | 1524 | 1788 | 220 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 92 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 215.2 | 302 | 411 | 437 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 7789.65 | 9096 | 12355.6 | 15116 | 1676 | 1444
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7675.7512 | 8963 | 12174.9387 | 14894.9767
A. |  | 2019-11-17 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 9096 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6200 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9096 | MW
3 | Day peak Generation : |  |  | 7789.65 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8963 | MW
4 | Evening peak Generation : |  |  | 9096 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 183.2126 | MKWHr | By Solar | 0.62377 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 152.0336 | MKWHr |  | By Oil: | 6.8444 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 5.1483 | MKWHr |  | By Hydro: | 2.0009 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1676 | MW | Dhaka | 3566 | 3566 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1444 | MW | Chittagong | 1047 | 1047 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3120 | MW | Khulna | 986 | 986 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1196.19 | MMCFD |  |  | Rajshahi | 845 | 845 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 142145275.386 | ii) Oil : | Taka | 62641763.92 | Comilla | 750 | 750 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 21056547 | Total | Taka | 225843586.306 | Mymensingh | 687 | 687 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.0635 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 10 | MW (E to W) at | 18:00 | hrs | Barisal | 203 | 203 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -44 | MW at | 18:30 | hrs | Rangpur | 563 | 563 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.6° C |  |  | Total | 8963 | 8963 |  | 0
B. |  | 2019-11-18 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 29.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15116 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7900 | MW
4 | Reserve(Generation end) |  |  |  | 5616 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 191.35 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6120 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.0109 | MKWHr. | ii) HVDC Flow at Peak Time |  | 826 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5507 | MKWHr. | iii) Maximum HVDC Flow : |  | 827 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 101.21 | 101.31 |  | (b) Today: | 101.21 |  | (c) Rule Curve: |  | 107.3
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 343 | 303 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 45 | 40 | 100 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 100 | 0 | 0 | 260 | 265 | 179 | 8 | 135 | 37 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 98 | 167 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 257 | 69 | 5 | 0 | 0 | 0 | 7 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 675 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 225 | 0 | 0 | 156 | 0 | 0 | 0 | 13 | 0 | 168 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4789 | 2150 | 6939 | 4335 | 675 | 1452 | 69 | 225 | 85 | 0 | 98 | 0 | 0 | 101.32
2:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 344 | 303 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 45 | 40 | 100 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 100 | 0 | 0 | 260 | 265 | 184 | 8 | 123 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 183 | 0 | 0 | 0 | 59 | 52 | 5 | 5 | 100 | 258 | 68 | 5 | 0 | 0 | 0 | 7 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 431 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 22 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 160 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4754 | 1931 | 6685 | 4337 | 431 | 1509 | 17 | 210 | 85 | 0 | 96 | 0 | 0 | 101.32
3:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 344 | 303 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 45 | 40 | 100 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 100 | 0 | 0 | 260 | 265 | 179 | 8 | 126 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 94 | 184 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 250 | 69 | 5 | 0 | 0 | 0 | 7 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 285 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 162 | 0 | 0 | 0 | 11 | 0 | 175 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4729 | 1753 | 6482 | 4318 | 285 | 1473 | 17 | 210 | 85 | 0 | 94 | 0 | 0 | 101.32
4:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 343 | 279 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 44 | 40 | 100 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 265 | 158 | 8 | 132 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 90 | 184 | 0 | 0 | 0 | 30 | 52 | 5 | 5 | 100 | 252 | 68 | 5 | 0 | 0 | 0 | 7 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 285 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 160 | 0 | 0 | 0 | 11 | 0 | 164 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4564 | 1732 | 6296 | 4196 | 285 | 1414 | 17 | 210 | 84 | 0 | 90 | 0 | 0 | 101.31
5:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 343 | 274 |  | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 43 | 40 | 100 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 265 | 159 | 8 | 138 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 90 | 164 | 0 | 0 | 0 | 29 | 52 | 5 | 5 | 100 | 248 | 69 | 5 | 0 | 0 | 0 | 7 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 159 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4491 | 1709 | 6200 | 4132 | 284 | 1401 | 0 | 210 | 83 | 0 | 90 | 0 | 0 | 101.31
6:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 347 | 274 |  | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 43 | 40 | 100 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 265 | 161 | 8 | 138 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 88 | 166 | 0 | 0 | 0 | 28 | 52 | 5 | 5 | 100 | 254 | 68 | 5 | 0 | 0 | 0 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 285 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 166 | 0 | 0 | 0 | 12 | 0 | 175 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4524.01 | 1726 | 6250.01 | 4155 | 285 | 1429 | 0 | 210 | 83 | 0 | 88 | 0.01 | 0 | 101.31
7:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 362 | 305 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 25 | 0 | 0 | 43 | 40 | 100 | 120 | 0 | 217 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 260 | 305 | 180 | 8 | 139 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 167 | 0 | 0 | 0.2 | 28 | 52 | 5 | 5 | 100 | 269 | 68 | 5 | 0 | 0 | 0 | 7 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0.589 | 0 | 0 | 0 | 0 |  | 285 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 176 | 0 | 0 | 0 | 12 | 0 | 193 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 |  | 4708.509 | 1860.4 | 6568.909 | 4424 | 285 | 1482 | 0 | 210 | 83 | 0 | 80 | 4.909 | 0 | 101.3
8:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 359 | 304 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 30 | 25 | 27 | 0 | 43 | 40 | 100 | 120 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 2 | 80 | 0 | 0 | 275 | 275 | 193 | 8 | 138 | 37 | 41 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 86 | 165 | 0 | 0 | 0.6 | 30 | 52 | 5 | 5 | 100 | 262 | 67 | 5 | 0 | 0 | 0 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 345 | 0 | 50 | 0 | 1.97 | 0 | 0 | 0 | 0 |  | 294 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 174 | 0 | 0 | 0 | 12 | 0 | 197 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 4881.57 | 1857.4 | 6738.97 | 4427 | 294 | 1533 | 78 | 210 | 83 | 16 | 86 | 11.97 | 0 | 0
9:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 356 | 302 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 25 | 20 | 0 | 45 | 40 | 110 | 120 | 0 | 214 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 10 | 19 | 3 | 80 | 0 | 0 | 270 | 275 | 198 | 8 | 139 | 33 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 94 | 165 | 0 | 0 | 1 | 30 | 52 | 5 | 5 | 100 | 271 | 65 | 5 | 0 | 0 | 0 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 375 | 0 | 52 | 0 | 3.04 | 0 | 0 | 0 | 0 |  | 394 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 175 | 0 | 0 | 0 | 12 | 0 | 213 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4966.04 | 1980.8 | 6946.84 | 4503 | 394 | 1543 | 82 | 210 | 85 | 16 | 94 | 19.84 | 0 | 0
10:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 358 | 304 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 42 | 0 | 45 | 40 | 110 | 120 | 0 | 216 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 2 | 80 | 0 | 0 | 295 | 295 | 199 | 8 | 140 | 33 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 96 | 164 | 0 | 0 | 1.6 | 29 | 52 | 5 | 5 | 100 | 267 | 65 | 5 | 0 | 0 | 0 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16 | 0 | 0 | 0 | 394 | 0 | 52 | 0 | 3.92 | 0 | 0 | 0 | 0 |  | 589 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 173 | 0 | 0 | 0 | 11 | 0 | 191 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 |  | 5103.52 | 2159.7 | 7263.22 | 4547 | 589 | 1533 | 113 | 210 | 85 | 65 | 96 | 25.22 | 0 | 0
11:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 375 | 351 |  | 0 | 420 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 51 | 0 | 42 | 40 | 110 | 120 | 0 | 210 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 2 | 80 | 0 | 0 | 290 | 360 | 180 | 8 | 139 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 92 | 157 | 0 | 0 | 1.9 | 30 | 30 | 5 | 5 | 130 | 268 | 64 | 5 | 0 | 0 | 0 | 8 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 18 | 0 | 0 | 0 | 397 | 0 | 52 | 3 | 4.41 | 0 | 0 | 0 | 30 |  | 639 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 202 | 0 | 0 | 0 | 11 | 0 | 186 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 5313.31 | 2245.8 | 7559.11 | 4575 | 639 | 1711 | 156 | 210 | 82 | 65 | 92 | 29.11 | 0 | 0
12:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 371 | 356 |  | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 0 | 79 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 51 | 0 | 42 | 40 | 110 | 120 | 0 | 217 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 2 | 80 | 0 | 0 | 355 | 360 | 180 | 35 | 140 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 145 | 0 | 0 | 2 | 30 | 52 | 8 | 5 | 130 | 305 | 64 | 5 | 0 | 0 | 0 | 8 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 17 | 0 | 0 | 0 | 393 | 0 | 52 | 17 | 4.45 | 0 | 0 | 0 | 50 |  | 639 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 205 | 0 | 0 | 0 | 11 | 0 | 204 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 5636.45 | 2153.2 | 7789.65 | 4779 | 639 | 1662 | 216 | 210 | 82 | 65 | 108 | 28.65 | 0 | 0
13:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 377 | 354 |  | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 45 | 0 | 42 | 40 | 110 | 120 | 0 | 209 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 6 | 80 | 0 | 0 | 320 | 320 | 200 | 8 | 126 | 37 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 104 | 145 | 0 | 0 | 1.8 | 30 | 52 | 8 | 5 | 130 | 276 | 65 | 5 | 0 | 0 | 0 | 9 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 16 | 0 | 0 | 0 | 354 | 0 | 52 | 17 | 4.16 | 0 | 0 | 0 | 55 |  | 639 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 209 | 0 | 0 | 204 | 0 | 0 | 0 | 13 | 0 | 208 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 5530.96 | 2271.1 | 7802.06 | 4645 | 639 | 1789 | 243 | 209 | 82 | 65 | 104 | 26.06 | 0 | 0
14:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 349 | 332 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 78 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 43 | 0 | 42 | 40 | 110 | 120 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 4 | 80 | 0 | 0 | 270 | 285 | 180 | 8 | 136 | 33 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 112 | 144 | 0 | 0 | 1.6 | 30 | 52 | 8 | 5 | 100 | 292 | 65 | 5 | 0 | 0 | 0 | 9 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 14.2 | 0 | 0 | 0 | 356 | 0 | 52 | 17 | 3.2 | 0 | 0 | 0 | 55 |  | 639 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 191 | 0 | 0 | 0 | 12 | 0 | 175 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 |  | 5268 | 2198.8 | 7466.8 | 4452 | 639 | 1628 | 256 | 210 | 82 | 65 | 112 | 22.8 | 0 | 101.36
15:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 370 | 323 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 44 | 0 | 40 | 40 | 110 | 120 | 0 | 210 | 0 | 100 | 0 |  | 0 | 0 | 0 | 8 | 0 | 12 | 19 | 2 | 80 | 0 | 0 | 290 | 300 | 180 | 8 | 140 | 37 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 110 | 140 | 0 | 0 | 0.9 | 60 | 52 | 8 | 5 | 100 | 297 | 64 | 5 | 0 | 0 | 0 | 10 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 10.6 | 0 | 0 | 0 | 369 | 0 | 52 | 17 | 2 | 0 | 0 | 0 | 42 |  | 639 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 187 | 0 | 0 | 0 | 12 | 0 | 184 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 5332.5 | 2249.8 | 7582.3 | 4579 | 639 | 1664 | 252 | 210 | 80 | 32 | 110 | 16.3 | 0 | 101.36
16:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 356 | 324 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 80 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 43 | 0 | 42 | 40 | 110 | 120 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 12 | 19 | 2 | 80 | 0 | 0 | 280 | 285 | 180 | 8 | 140 | 37 | 48 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 106 | 144 | 0 | 0 | 0.3 | 59 | 52 | 8 | 5 | 100 | 299 | 65 | 5 | 0 | 0 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 5.6 | 0 | 0 | 0 | 361 | 0 | 52 | 17 | 0.9 | 0 | 0 | 0 | 37 |  | 639 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 12 | 0 | 184 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 5243.8 | 2218.7 | 7462.5 | 4507 | 639 | 1647 | 248 | 210 | 82 | 16 | 106 | 7.5 | 0 | 101.36
17:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 365 | 324 |  | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 80 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 10 | 0 | 13 | 0 | 25 | 30 | 33 | 25 | 47 | 0 | 42 | 40 | 110 | 120 | 0 | 218 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 2 | 12 | 19 | 5 | 80 | 0 | 0 | 300 | 305 | 180 | 8 | 140 | 33 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 116 | 142 | 0 | 0 | 0 | 59 | 52 | 8 | 5 | 100 | 305 | 65 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 0 | 2 | 381 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 25 |  | 639 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 178 | 0 | 0 | 0 | 20 | 0 | 185 | 0 | 348 | 0 | 0 | 1 | 0 | 70 | 0 | 0 | 0 |  | 5378 | 2256 | 7634 | 4608 | 639 | 1606 | 348 | 210 | 82 | 25 | 116 | 0 | 0 | 101.35
18:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 350 | 323 |  | 0 | 400 | 0 | 3 | 0 | 47 | 0 | 0 | 80 | 0 | 7 | 0 | 32 | 10 | 70 | 0 | 28 | 17 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 51 | 0 | 43 | 40 | 110 | 120 | 6 | 203 | 0 | 104 | 0 |  | 0 | 0 | 51 | 86 | 45 | 34 | 0 | 8 | 80 | 0 | 0 | 275 | 275 | 180 | 8 | 138 | 37 | 50 | 0 | 12 | 0 | 0 | 5 | 22 | 11 | 33 | 20 | 132 | 146 | 0 | 22 | 0 | 60 | 52 | 48 | 15 | 100 | 296 | 67 | 79 | 0 | 0 | 17 | 33 | 9 | 275 | 24 | 0 | 0 | 90 | 0 | 0 | 86 | 0 | 8 | 0 | 30 | 120 | 93 | 355 | 7 | 17 | 63 | 0 | 15 | 14 | 16 | 0 |  | 826 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 26 | 50 | 8 | 0 | 8 | 0 | 18 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 167 | 0 | 0 | 0 | 44 | 0 | 190 | 0 | 231 | 35 | 0 | 96 | 36 | 92 | 0 | 0 | 0 |  | 6428 | 2668 | 9096 | 4600 | 826 | 1693 | 1443 | 210 | 83 | 109 | 132 | 0 | 0 | 101.35
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 365 | 359 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 30 | 0 | 17 | 0 | 22 | 25 | 30 | 33 | 25 | 51 | 0 | 43 | 40 | 110 | 120 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 51 | 90 | 11 | 34 | 19 | 3 | 80 | 0 | 0 | 300 | 275 | 180 | 8 | 140 | 37 | 50 | 0 | 19 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 134 | 146 | 0 | 22 | 0 | 60 | 52 | 53 | 21 | 100 | 301 | 67 | 79 | 0 | 0 | 17 | 35 | 10 | 300 | 24 | 11 | 0 | 75 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 50 | 120 | 355 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 |  | 826 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 171 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 18 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 171 | 0 | 0 | 0 | 96 | 0 | 185 | 0 | 382 | 0 | 0 | 110 | 17 | 50 | 0 | 0 | 0 |  | 6361 | 2733 | 9094 | 4780 | 826 | 2024 | 986 | 210 | 83 | 51 | 134 | 0 | 0 | 101.34
19:30 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 350 | 359 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 30 | 0 | 17 | 0 | 22 | 25 | 30 | 33 | 25 | 34 | 0 | 43 | 40 | 110 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 51 | 70 | 11 | 18 | 19 | 17 | 80 | 0 | 0 | 345 | 285 | 190 | 8 | 140 | 37 | 50 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 132 | 146 | 0 | 22 | 0 | 60 | 52 | 53 | 21 | 163 | 301 | 67 | 79 | 0 | 0 | 17 | 39 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 6 | 357 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 826 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 168 | 0 | 0 | 0 | 96 | 0 | 186 | 0 | 381 | 0 | 0 | 70 | 5 | 85 | 0 | 0 | 0 |  | 6223 | 2679 | 8902 | 4819 | 826 | 2114 | 667 | 210 | 83 | 51 | 132 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 350 | 360 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 25 | 34 | 0 | 43 | 40 | 110 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 47 | 70 | 11 | 11 | 19 | 21 | 80 | 0 | 0 | 340 | 275 | 185 | 8 | 140 | 37 | 51 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 130 | 144 | 0 | 22 | 0 | 60 | 52 | 53 | 21 | 163 | 300 | 67 | 79 | 0 | 0 | 17 | 38 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 826 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 21 | 14 | 11 | 0 | 0 | 210 | 0 | 17 | 171 | 0 | 0 | 0 | 95 | 0 | 182 | 0 | 381 | 0 | 0 | 70 | 0 | 112 | 0 | 0 | 0 |  | 6148 | 2707 | 8855 | 4786 | 826 | 2127 | 629 | 210 | 83 | 64 | 130 | 0 | 0 | 101.34
21:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 351 | 360 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 25 | 34 | 0 | 44 | 40 | 110 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 34 | 70 | 11 | 0 | 19 | 27 | 80 | 0 | 0 | 340 | 275 | 182 | 8 | 140 | 37 | 51 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 126 | 144 | 0 | 22 | 0 | 60 | 52 | 53 | 21 | 163 | 288 | 67 | 79 | 0 | 0 | 17 | 37 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 826 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 28 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 190 | 0 | 0 | 0 | 96 | 0 | 191 | 0 | 380 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 |  | 5990 | 2646 | 8636 | 4797 | 826 | 2124 | 435 | 210 | 84 | 34 | 126 | 0 | 0 | 101.34
22:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 343 | 361 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 8 | 0 | 44 | 40 | 110 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 20 | 7 | 0 | 19 | 36 | 80 | 0 | 0 | 340 | 275 | 179 | 8 | 126 | 37 | 52 | 0 | 25 | 0 | 0 | 0 | 22 | 0 | 33 | 20 | 118 | 160 | 0 | 22 | 0 | 58 | 52 | 53 | 21 | 130 | 290 | 68 | 79 | 0 | 0 | 17 | 39 | 10 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 827 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 187 | 0 | 0 | 0 | 96 | 0 | 181 | 0 | 349 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 |  | 5752 | 2500 | 8252 | 4716 | 827 | 2062 | 235 | 210 | 84 | 0 | 118 | 0 | 0 | 101.25
23:00 | 35 | 0 | 0 | 100 | 300 | 0 | 0 | 347 | 362 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 39 | 80 | 0 | 0 | 260 | 270 | 180 | 8 | 139 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 112 | 158 | 0 | 22 | 0 | 59 | 52 | 47 | 21 | 130 | 275 | 68 | 5 | 0 | 0 | 17 | 39 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 826 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 210 | 0 | 0 | 184 | 0 | 0 | 0 | 40 | 0 | 165 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5343 | 2361 | 7704 | 4448 | 826 | 1878 | 145 | 210 | 85 | 0 | 112 | 0 | 0 | 101.25
24:00 | 35 | 0 | 0 | 100 | 300 | 0 | 0 | 350 | 362 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 45 | 40 | 110 | 120 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 260 | 270 | 187 | 8 | 130 | 37 | 30 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 106 | 158 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 130 | 263 | 40 | 5 | 0 | 0 | 0 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 827 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 23 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 163 | 0 | 0 | 0 | 12 | 0 | 164 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5006 | 2322 | 7328 | 4322 | 827 | 1715 | 63 | 210 | 85 | 0 | 106 | 0 | 0 | 101.24
KWH | 807000 | 0 | 0 | 2488500 | 7499782 | 0 | 0 | 8657920 | 7678000 |  | 0 | 9055750 | 0 | 5760 | 0 | 154452 | 0 | 0 | 2530000 | 0 | 5760 | 8784 | 482400 | 11868 | 170880 | 0 | 318048 | 28440 | 78803 | 81916 | 88128 | 600000 | 683100 | 802700 | 626100 | 618708 | 0 | 1032873 | 968000 | 2600000 | 3000000 | 9563 | 4914025 | 0 | 2751275 | 0 |  | 0 | 0 | 157374 | 356400 | 113280 | 193440 | 419328 | 482889 | 2076060 | 0 | 0 | 7281000 | 7018500 | 4428000 | 217454 | 3243100 | 688032 | 913440 | 0 | 307100 | 0 | 0 | 6422 | 114912 | 42120 | 1666000 | 423620 | 2550720 | 3682400 | 0 | 126936 | 11800 | 1113000 | 1213080 | 398400 | 270000 | 2986445 | 6480000 | 1577472 | 540480 | 0 | 0 | 110000 | 372700 | 55800 | 7360000 | 121632 | 44304 | 0 | 245891 | 0 | 0 | 847200 | 0 | 14400 | 122850 | 51840 | 223680 | 225818 | 8516000 | 9600 | 548532 | 903273 | 28320 | 17564 | 19081 | 21745 | 290700 |  | 14010909 | 0 | 7752384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74250 | 4143934 | 494900 | 0 | 0 | 0 | 1600000 | 0 | 0 | 28564 | 124790 | 3607 | 0 | 6240 | 0 | 96000 | 80748 | 184788 | 0 | 0 | 5148300 | 0 | 5000 | 4542064 | 0 | 0 | 0 | 701230 | 0 | 4660218 | 0 | 8704873 | 30240 | 0 | 301152 | 42912 | 6000 | 0 | 460800 | 0 |  | 130008669 | 53203903 | 183212572 | 111317414 | 14010909 | 40716209 | 6171039 | 5148300 | 2000873 | 673338 | 2550720 | 623770 | 0
Fuel Cost | 903840 | 0 | 0 | 2787120 | 5549838.68 | 0 | 0 | 6233702.4 | 5835280 |  | 0 | 7244600 | 0 | 58752 | 0 | 1584677.52 | 0 | 0 | 3162500 | 0 | 63936 | 89245.44 | 4780584 | 124376.64 | 1555008 | 0 | 2976929.28 | 272739.6 | 751780.62 | 815883.36 | 66096 | 450000 | 0 | 0 | 0 | 5927222.64 | 0 | 268546.98 | 251680 | 3978000 | 4590000 | 91900.43 | 5159726.25 | 0 | 3494119.25 | 0 |  | 0 | 0 | 1650853.26 | 3667356 | 1077292.8 | 1810598.4 | 385781.76 | 1342431.42 | 2179863 | 0 | 0 | 5387940 | 5895540 | 4073760 | 213104.92 | 4313323 | 564186.24 | 940843.2 | 0 | 439153 | 0 | 0 | 60366.8 | 117210.24 | 31590 | 3148740 | 317715 | 17599968 | 3019568 | 0 | 129474.72 | 193520 | 1513680 | 1649788.8 | 541824 | 337500 | 3703191.8 | 5961600 | 2350433.28 | 951244.8 | 0 | 0 | 174900 | 436059 | 131130 | 5225600 | 91224 | 33671.04 | 0 | 2574478.77 | 0 | 0 | 8150064 | 0 | 145296 | 1417689 | 483148.8 | 2098118.4 | 2115914.66 | 8005040 | 84192 | 4887420.12 | 8535929.85 | 0 | 161940.08 | 0 | 0 | 0 |  | 37829454.3 | 0 | 6046859.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734332.5 | 3315147.2 | 767095 | 0 | 0 | 0 | 3008000 | 0 | 0 | 282783.6 | 1294072.3 | 42237.97 | 0 | 62150.4 | 0 | 105600 | 133234.2 | 139884.516 | 0 | 0 | 21056547 | 0 | 141150 | 3997016.32 | 0 | 0 | 0 | 1114955.7 | 0 | 4100991.84 | 0 | 6354557.29 | 286070.4 | 0 | 2764575.36 | 382345.92 | 56040 | 0 | 0 | 0 |  | 189389343.25 | 94015101.336 | 283404444.586 | 106327871.056 | 37829454.3 | 35817404.33 | 55786393.06 | 21056547 | 520226.98 | 6855370.86 | 17599968 | 1611209 | 0
Yesterday Day Peak | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 371 | 356 |  | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 0 | 79 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 51 | 0 | 42 | 40 | 110 | 120 | 0 | 217 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 2 | 80 | 0 | 0 | 355 | 360 | 180 | 35 | 140 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 145 | 0 | 0 | 2 | 30 | 52 | 8 | 5 | 130 | 305 | 64 | 5 | 0 | 0 | 0 | 8 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 17 | 0 | 0 | 0 | 393 | 0 | 52 | 17 | 4.45 | 0 | 0 | 0 | 50 |  | 639 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 205 | 0 | 0 | 0 | 11 | 0 | 204 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 7789.65 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 350 | 323 | 0 | 0 | 400 | 0 | 3 | 0 | 47 | 0 | 0 | 80 | 0 | 7 | 0 | 32 | 10 | 70 | 0 | 28 | 17 | 55 | 55 | 22 | 25 | 25 | 33 | 25 | 51 | 0 | 43 | 40 | 110 | 120 | 6 | 203 | 0 | 104 | 0 | 0 | 0 | 0 | 51 | 86 | 45 | 34 | 0 | 8 | 80 | 0 | 0 | 275 | 275 | 180 | 8 | 138 | 37 | 50 | 0 | 12 | 0 | 0 | 5 | 22 | 11 | 33 | 20 | 132 | 146 | 0 | 22 | 0 | 60 | 52 | 48 | 15 | 100 | 296 | 67 | 79 | 0 | 0 | 17 | 33 | 9 | 275 | 24 | 0 | 0 | 90 | 0 | 0 | 86 | 0 | 8 | 0 | 30 | 120 | 93 | 355 | 7 | 17 | 63 | 0 | 15 | 14 | 16 | 0 |  | 826 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 160 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 26 | 50 | 8 | 0 | 8 | 0 | 18 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 167 | 0 | 0 | 0 | 44 | 0 | 190 | 0 | 231 | 35 | 0 | 96 | 36 | 92 | 0 | 0 | 0 |  | 9096 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 110 | 300 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 210 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 40 | 110 | 120 | 25 | 200 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 20 | 80 | 0 | 0 | 360 | 360 | 225 | 45 | 150 | 37 | 55 | 0 | 35 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 147 | 200 | 95 | 22 | 0 | 60 | 54 | 51 | 44 | 163 | 330 | 66 | 77 | 0 | 0 | 20 | 36 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 |  |  | 839 | 46 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 170 | 26 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 0 | 110 | 300 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 210 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 40 | 110 | 120 | 25 | 200 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 7 | 80 | 0 | 0 | 360 | 360 | 0 | 45 | 140 | 37 | 55 | 0 | 30 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 115 | 165 | 0 | 22 | 1.6 | 60 | 54 | 51 | 44 | 163 | 330 | 66 | 77 | 0 | 0 | 20 | 32 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 |  |  | 644 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 170 | 26 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 0 | 0 | 100 | 230 | 0 | 0 | 369 | 284 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 33 | 4 | 0 | 45 | 40 | 110 | 120 | 0 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 80 | 0 | 0 | 270 | 275 | 0 | 8 | 140 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 19 | 0 | 33 | 15 | 88 | 160 | 0 | 22 | 0.3 | 60 | 52 | 53 | 21 | 100 | 289 | 67 | 77 | 0 | 0 | 17 | 36 | 9 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 9.1 | 0 | 0 | 0 | 272 | 0 | 0 | 1 | 1.7 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 5 | 0 | 0 | 209 | 0 | 0 | 179 | 0 | 0 | 0 | 12 | 0 | 180 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0
199
| Minimum Generation |  | 6200 | 5:00
| Highest Generation |  | 9096 | 18:00
| Day Peak Generation |  | 7789.65 | 12:00
| Evening Peak Generation |  | 9096 | 18:00
| HVDC Max Flow |  | 827 | 22:00
| HVDC EvPeak Flow |  | 826 | 18:00
| Load factor L.F |  | 83.93%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7789.65 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6120 | MW
Evening Peak Generation : |  | 9096 | MW Hour : | 18:00 | Available Max Generation : |  | 15116 | MW
E.P. Demand (at gen end) : |  | 9096 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9096 | MW Hour : | 18:00 | Reserve(Generation end) |  | 5616 | MW
Total Gen. (MKWH) : |  | 183.2126 | System Load Factor : | 83.93% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -44 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-18
Actual : | 101.21 | Ft.(MSL) , | Rule curve : | 107.3 | Ft.( MSL )
Gas Consumed : | Total = | 1196.19 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142145275.386
: |  | Coal : | 21056547 | Oil : | 62641763.92 | Total : | 225843586.306
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3488.7585 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1183.0419 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1059.3731 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 957.0223 |  |  | 0 | 0%
) | 0 | 0:00 | 864.9634 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 697.9864 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 394.5637 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 179.8261 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 538.3013 |  |  | 0 | 0%
Total | 0 |  | 9363.8368 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1&2.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,3
4) Ashuganj unit-4 & 5
5) Chandpur CCPP ST
6)Sylhet 150 MW
7) Sirajganj unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Daudkandi 132/33 kV T1 transformer was under shut down from 08:17 to 16:18 for A/M.
b) Kishoreganj 132 bus-A was under shut down from 10:18 to 14:10 for A/M.
c) UMPL P/S-Sherpur S/S 132 kV Ckt-2 was under shut down from 08:21 to 15:43 for A/M.
d) Mirpur 132 kV bus coupler was under shut down from 10:05 to 16:30 for A/M.
e) Aminbazar-Hasnabad 230 kV Ckt-2 was under shut down from 09:02 to 20:30 for A/M.
f) Sonargaon-Daudkandi 132 kV Ckt-1 was under shut down from 08:41 to 14:47 for A/M.
g) Netrokona 132/33 kV T1 transformer was under shut down from 07:58 to 16:31 for A/M.
h) Jamalpur S/S-UMPL P/S 132 kV Ckt-2 was under shut down from 08:13 to 15:48 for A/M.
i) Kishoreganj-Mymensingh 132 kV Ckt-2 was under shut down from 09:05 to 17:02 for A/M.
j) Sunamganj 132/33 kV T1 transformer was under shut down from 08:57 to 16:05 for A/M.
k) Rangpur-Barapukuria 132 kV Ckt-1 was under shut down from 08:36 to 16:08 for A/M.
l) Barapukuria-Bogura 230 kV Ckt-2 was under shut down from 08:23 to 15:43 for A/M.
m) Rajshahi(N)-Rajshahi(O) 132 kV Ckt-1 was under shut down from 09:10 to 15:24 for A/M.
n) Rajshahi-Amnura 132 kV Ckt-1 was under shut down from 08:08 to 16:52 for A/M.
o) Khulna(S)-Bheramara HVDC 230 kV Ckt-2 was under shut down from 08:22 to 17:04 for A/M.
p) Noapara 132/33 kV T4 transformer was under shut down from 09:17 to 15:06 for A/M.
q) Barisal(N) 132/33 kV T4 transformer was under shut down from 08:22 to 15:38 for A/M.
r) Khulna(C)-Noapara 132 kV Ckt-2 was under shut down from 08:49 to 12:21 for C/M.
s) Rampura-Bashundhara 132 Ckt-2 tripped at 12:27 from Rampura end showing Dist. B-phase Z1 relay
and was switched on at 20:29.
t) Barapukuria 230/132 kV T2 & T6 transformers tripped at 18:54 showing master relay, 50 BF trip and
was switched on at 19:50.
u) Saidpur-Rangpur 132 kV Ckt 1 & 2 tripped at 18:54 from Rangpur end showing O/C relay and were
switched on at 19:15, 19:08 respectively.
v) Barapukuria 132/33 kV T3 & T5 transformers tripped at 18:54 showing lock out relay and was |  |  |  |  | About 309 MW power interruption occurred under Rangpur Zone area
switched on at 20:05. |  |  |  |  | from 18:54 to 20:05.
w) Ashuganj 225 MW CCPP tripped at 00:11(18/11/2019) due to problem in flame monitoring system.
x) Hasnabad 132/33 kV T2 transformer was shut down at 07:22(18/11/2019) for A/M.
y) Ghorasal-Ishurdi 230 kV Ckt-1 was shut down at 07:40(18/11/2019) for A/M
z) Barisal(S) 132/33 kV T1 transformer was shut down at 07:14(18/11/2019) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 807000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 100 | 2488500 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 7499782
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8657920 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 7678000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9055750 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 3 | 5760 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 47 | 154452
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 10 | 11868 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 88128
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 80 | 2530000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 5760 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 8784 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 28 | 318048 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 28440 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 482400 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 78803
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 81916
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 70 | 170880
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1283100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 626100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 618708
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 90 | 245891 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 8 | 14400 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 548532 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2258 | 44291622
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 6 | 9563 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122850
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 34 | 193440 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 83 | 2000873 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4914025
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2751275 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 63 | 903273 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 157374 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 86 | 356400
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 30 | 51840 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 419328 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 482889
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 113280 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28320
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 15 | 17564 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 14 | 19081 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 16 | 21745 | Low demand
| Chattogram area Total |  |  |  | 2166 | 988 | 18163120
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2076060 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4428000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7281000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7018500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 688032 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 913440
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 12 | 307100 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 93 | 225818 | Low demand
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3243100
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 223680 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 114912
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 42120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 2550720
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 1666000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 5 | 6422 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 423620 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 290700
| Cumilla Area Total |  |  |  | 3005 | 1491 | 31716678
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 146 | 3682400
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 126936
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 86 | 847200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 7 | 9600 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 261 | 4677936
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1113000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1213080
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 2986445 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 296 | 6480000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 398400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 15 | 270000
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 44304
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1577472 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 540480
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 110000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 33 | 372700 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 121632
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7360000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 355 | 8516000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 55800 | Engine problem
| Sylhet Area Total |  |  |  | 1949 | 1430 | 31159313
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 826 | 14010909
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 7752384 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 74250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 30240 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 36 | 42912 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1247 | 21910695
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 494900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 160 | 4143934 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 44 | 701230 | Low demand
| Barisal Area Total |  |  |  | 462 | 230 | 5340064
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1600000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 124790
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 3607 | Low demand
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 4542064 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4660218 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 231 | 8704873 | GBC test
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 96000
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 80748
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 184788
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 6240 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 26 | 28564 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 96 | 301152
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 889 | 20333044
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5148300
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 5000 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 92 | 6000
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 460800
| Rangpur Area Total |  |  |  | 605 | 302 | 5620100
| Total |  |  |  | 19132 | 9096 | 183212572
| Eastern Grid Total |  |  |  | 13568 | 6428 | 130008669
| Western Grid Total |  |  |  | 5564 | 2668 | 53203903
| National Grid Total |  |  |  | 19132 | 9096 | 183212572
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-17
(a) ENTIRE EASTERN GRID : |  | 6366 | MW | (b) ENTIRE WESTERN GRID : |  | 2597 | MW
i) Dhaka area |  | 3566 | MW | i) Khulna area |  | 986 | MW
ii) Chittagong area |  | 1047 | MW | ii) Rajshahi area |  | 845 | MW
iii) Comilla area |  | 750 | MW | iii) Barisal area |  | 203 | MW
iv) Mymensingh area |  | 687 | MW | iv) Rangpur area |  | 563 | MW
v) Sylhet area |  | 316 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8963 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 1800 | Srimongal | 27 | 1800 | Bottail | 96 | 1800
Munsiganj | 82 | 2100 | Shahjibazar | 80 | 1930 | G.K Project | 35 | 1800
Sonargaon | 72 | 2000 | Fenchuganj | 26 | 1830 | Faridpur | 126 | 1800
Shyampur | 184 | 2400 | Kulawara | 28 | 2100 | Madaripur | 49 | 2000
Bhulta | 166 | 1200 | Sylhet | 110 | 1830 | Sariatpur | 38 | 2000
Madanganj | 41 | 2400 | Chatak | 18 | 1800 | Gopalganj | 54 | 1830
Shitalakhya | 104 | 1800 | Sunamganj | 28 | 1800 | Bagerhat | 43 | 1930
Rahim steel | 24 | 1000 | Biani Bazar | 34 | 1800 | Mongla | 36 | 1200
Matuail | 92 | 1000 | Comilla (S) | 138 | 1830 | Satkhira | 59 | 1930
Ghorasal | 61 | 1900 | Comilla(N) | 79 | 1930 | Gallamari | 39 | 1300
Narsingdi | 114 | 1830 | Chandpur | 72 | 1930 | Magura | 36 | 1800
Haripur (SBU) | 86 | 900 | Feni | 101 | 1800 | Norail | 26 | 1900
Ullon | 63 | 1800 | Chowmuhani | 128 | 2100 | Chuadanga | 61 | 1800
Hasnabad | 165 | 1900 | Ashuganj | 43 | 2300 | Barisal(N) | 24 | 1930
Magbazar | 97 | 1300 | Daudkandi | 92 | 1930 | Barisal (S) | 72 | 1800
Maniknagar | 94 | 1200 | B.Baria | 97 | 1900 | Patuakhali | 76 | 2100
Bangabhaban | 28 | 1200 | Ramganj | 46 | 1830 | Bhandaria | 32 | 2100
Narinda | 82 | 1200 | Madunaghat | 48 | 1700 | Borhan Uddin | 27 | 2100
Dhanmondi | 130 | 1300 | Hathazari | 80 | 1800 | Ishurdi | 45 | 1830
Lalbag | 66 | 1800 | Khulshi | 176 | 1800 | Ruppur Paromanobik | 1 | 100
Madartek | 56 | 1830 | Halishahar | 125 | 1800 | Natore | 90 | 1800
Mirpur | 90 | 1800 | Baraulia | 134 | 1200 | Bogra | 136 | 1830
Kalyanpur | 96 | 1800 | Sikalbaha | 23 | 1800 | Noagaon | 81 | 1830
Gulshan | 128 | 1100 | Dohazari | 66 | 1800 | Rajshahi | 94 | 1800
Uttara | 58 | 1200 | Cox'sbazar | 81 | 1800 | Rajshahi New | 9 | 1900
Uttara New | 37 | 1200 | Chandraghona | 24 | 1800 | C.Nawabganj | 52 | 1900
Kamrangirchar | 68 | 1800 | Kaptai | 4 | 1800 | Amnura | 22 | 1800
Savar | 118 | 1800 | A. Khaer Stl. | 0 | 0 | Pabna | 76 | 1800
Bhasantec | 132 | 1800 | Bakulia | 95 | 1800 | Shahjadpur | 76 | 1900
Agargaon | 56 | 1300 | Julda | 18 | 100 | Serajganj | 69 | 1900
Satmosjid | 81 | 1800 | TK chemical | 12 | 1830 | Niyamatpur | 40 | 1800
Tongi | 127 | 1800 | Modern Steel | 13 | 1000 | Joypurhat | 41 | 1800
Kabirpur | 164 | 1200 | Shahmirpur | 25 | 1800 | Sherpur(Bogura) | 36 | 1800
Basundhara | 93 | 1800 | Khagrachhari | 14 | 1830 | Mohastangor | 11 | 1800
Manikganj | 58 | 1830 | Matarbari | 25 | 1800 | Rangpur | 100 | 1800
Joydevpur | 183 | 1700 | Baroiar Hat | 18 | 1400 | Lalmonirhat | 43 | 1830
New Tongi | 91 | 1200 | Rangamati | 10 | 1800 | Saidpur | 82 | 1830
Korda | 215 | 1800 | Abul Khair 230 | 134 | 1100 | Purbasadipur | 76 | 1800
Dhamrai | 50 | 1800 | BSRM | 112 | 200 | Thakurgaon | 57 | 1830
Valuka | 86 | 1800 | GPH Ispat | 5 | 1500 | Palashbari | 81 | 1800
Tangail | 140 | 1830 | Goalpara | 20 | 1900 | Barapukuria | 41 | 1800
Mymensing | 164 | 1800 | Central s/s | 72 | 1800 | Panchagar | 39 | 1800
Kishorganj | 80 | 1900 | Noapara | 46 | 1800 | Joldhaka | 19 | 1800
Netrokona | 71 | 1800 | Jessore | 84 | 1800 | Kurigram | 35 | 1800
Jamalpur | 86 | 1800 | Benapol | 28 | 1800 | 0 | 0 | 0
Sherpur | 66 | 1800 | Jhenida | 78 | 1800 | 0 | 0 | 0
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-17 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 387 | 6:00 | 378 | 12:00 | Kaliakoir | 369 | 5:00 | 351 | 12:00
Bheramara | 404 | 3:00 | 395 | 18:00 | Bhulta | 376 | 4:00 | 360 | 15:00
Ashuganj(N) | 383 | 7:00 | 363 | 10:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal | 226 | 24:00 | 224 | 1:00 | Hathazari | 220 | 18:00 | 214 | 4:00
Ishurdi | 241 | 3:00 | 229 | 12:00 | Megnaghat | 220 | 4:00 | 210 | 10:00
Ashuganj | 232 | 6:00 | 225 | 11:00 | Fenchuganj | 233 | 5:00 | 227 | 17:00
Serajganj | 233 | 3:00 | 229 | 12:00 | Siddhirganj | 221 | 3:00 | 210 | 10:00
Baghabari | 240 | 5:00 | 231 | 13:00 | Maniknagar | 220 | 4:00 | 208 | 12:00
Barapukuria | 231 | 2:00 | 225 | 12:00 | Old Airport | 219 | 4:00 | 206 | 12:00
Bogra | 232 | 6:00 | 223 | 13:00 | Barisal | 233 | 6:00 | 223 | 12:00
Khulna South | 243 | 4:00 | 216 | 13:00 | AKSML | 214 | 6:00 | 207 | 11:00
Rampura | 227 | 18:00 | 211 | 13:00 | BSRM | 217 | 6:00 | 210 | 12:00
Haripur | 220 | 3:00 | 210 | 16:00 | Bibiyana | 231 | 5:00 | 225 | 11:00
Hasnabad | 218 | 4:00 | 206 | 11:00 | Bhulta | 222 | 3:00 | 211 | 12:00
Aminbazar | 220 | 3:00 | 208 | 12:00 | Ashuganj (S) | 231 | 6:00 | 222 | 15:00
Tongi | 216 | 6:00 | 205 | 12:00 | Kaliakoir | 222 | 5:00 | 212 | 11:00
Comilla (N) | 227 | 5:00 | 217 | 16:00 | GPH | 214 | 6:00 | 208 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 100 | 126 | 1100 | Halishahar | 130 | 1800 | 124 | 1000
Munsiganj | 135 | 700 | 124 | 1100 | Baraulia | 127 | 600 | 124 | 1100
Megnaghat | 129 | 100 | 126 | 1800 | Sikalbaha | 130 | 1800 | 125 | 1000
Shyampur | 133 | 300 | 124 | 1200 | Dohazari | 128 | 1800 | 123 | 1100
Bhulta | 126 | 500 | 119 | 1200 | Cox'sbazar | 122 | 700 | 116 | 1200
Madanganj | 134 | 1800 | 124 | 1200 | Chandraghona | 130 | 1800 | 125 | 1600
Shitalakhya | 134 | 400 | 123 | 1200 | Kaptai | 130 | 400 | 125 | 1100
Rahim steal | 133 | 300 | 126 | 1100 | A. Khaer Stl. | 126 | 600 | 125 | 100
Matuail | 132 | 500 | 124 | 1200 | Bakulia | 128 | 1800 | 122 | 1200
Ghorasal | 133 | 100 | 132 | 1800 | Julda | 128 | 1800 | 123 | 1200
Narsinghdi | 131 | 800 | 127 | 1500 | TK Chemical | 130 | 1800 | 124 | 1100
Haripur (SBU) | 131 | 100 | 126 | 1200 | Modern Steel | 128 | 1800 | 123 | 1000
Ullon | 131 | 600 | 123 | 1600 | Shahmirpur | 129 | 1800 | 123 | 1200
Hasnabad | 133 | 600 | 124 | 1200 | Khagrachhari | 129 | 1800 | 125 | 1100
Magbazar | 133 | 600 | 124 | 1200 | Matarbari | 125 | 700 | 120 | 100
Maniknagar | 135 | 600 | 125 | 1200 | Baroiar Hat | 128 | 1800 | 122 | 1100
Bangabhaban | 135 | 600 | 125 | 1200 | Rangamati | 129 | 1800 | 125 | 1200
Narinda | 135 | 600 | 125 | 1200 | Goalpara | 140 | 400 | 123 | 1300
Dhanmondi | 131 | 600 | 123 | 1600 | Central s/s | 138 | 600 | 123 | 1300
Lalbag | 135 | 400 | 122 | 1200 | Noapara | 137 | 500 | 120 | 1200
Madartek | 132 | 600 | 123 | 1200 | Jessore | 134 | 300 | 118 | 1200
Mirpur | 133 | 300 | 126 | 1600 | Benapol | 132 | 600 | 120 | 1200
Kalyanpur | 133 | 200 | 127 | 1200 | Jhenida | 135 | 600 | 121 | 1200
Gulshan | 134 | 300 | 123 | 1100 | Bottail | 137 | 600 | 128 | 1200
Uttara | 133 | 300 | 123 | 1200 | G.K Project | 141 | 600 | 134 | 1200
Uttara New | 134 | 400 | 122 | 1200 | Faridpur | 135 | 600 | 127 | 1300
Kamrangirchar | 133 | 300 | 122 | 1200 | Madaripur | 135 | 600 | 127 | 1300
Savar | 133 | 400 | 122 | 1200 | Sariatpur | 135 | 600 | 126 | 1300
Bhasantec | 132 | 500 | 122 | 1200 | Gopalganj | 139 | 600 | 128 | 1300
Agargaon | 133 | 600 | 123 | 1200 | Bagerhat | 136 | 600 | 122 | 1300
Satmosjid | 132 | 300 | 124 | 1100 | Mongla | 135 | 400 | 120 | 1200
Tongi | 133 | 400 | 125 | 1500 | Satkhira | 138 | 500 | 122 | 1300
Kabirpur | 130 | 600 | 121 | 1200 | Gallamari | 140 | 600 | 123 | 1300
Basundhara | 131 | 500 | 123 | 1500 | Magura | 135 | 600 | 120 | 1930
Manikganj | 134 | 600 | 128 | 1830 | Norail | 135 | 300 | 129 | 1930
Joydevpur | 134 | 600 | 128 | 900 | Chuadanga | 134 | 400 | 118 | 1930
New Tongi | 131 | 400 | 124 | 1500 | Barisal(N) | 139 | 600 | 132 | 1600
Kodda | 130 | 800 | 122 | 1900 | Barisal (S) | 139 | 400 | 129 | 1300
Dhamrai | 131 | 400 | 122 | 1100 | Patuakhali | 138 | 600 | 128 | 2100
Valuka | 129 | 500 | 120 | 1100 | Bhandaria | 137 | 400 | 125 | 1200
Tangail | 129 | 300 | 120 | 1200 | Ishurdi | 138 | 500 | 131 | 2000
Mymensing | 130 | 400 | 120 | 1100 | Ruppur Paromanobik | 137 | 600 | 131 | 1200
Kishorganj | 130 | 500 | 125 | 1200 | Natore | 134 | 600 | 126 | 1200
Netrokona | 127 | 600 | 120 | 1100 | Bogra | 137 | 400 | 128 | 1200
Jamalpur | 130 | 300 | 119 | 1100 | Noagaon | 134 | 500 | 125 | 1300
Sherpur | 129 | 1800 | 117 | 1100 | Rajshahi | 131 | 600 | 123 | 1200
Srimongal | 135 | 300 | 131 | 1100 | Rajshahi New | 132 | 500 | 120 | 1200
Shahjibazar | 134 | 1800 | 130 | 1100 | C.Nawabganj | 130 | 600 | 125 | 1700
Fenchuganj | 133 | 600 | 128 | 1600 | Amnura | 130 | 1800 | 117 | 1200
Khulawara | 134 | 2300 | 128 | 1100 | Pabna | 137 | 400 | 132 | 2000
Sylhet | 132 | 2300 | 125 | 1200 | Shahjadpur | 144 | 400 | 137 | 1200
Chatak | 132 | 2200 | 124 | 1200 | Serajganj | 137 | 500 | 130 | 1200
Sunamganj | 132 | 2300 | 123 | 1200 | Niyamatpur | 132 | 600 | 124 | 1300
Biani Bazar | 132 | 100 | 125 | 1700 | Joypurhat | 135 | 600 | 125 | 1200
Comilla(s) | 129 | 2000 | 124 | 1800 | Sherpur(Bogura) | 137 | 500 | 128 | 1200
Comilla(n) | 134 | 700 | 129 | 1500 | Mohastangor | 134 | 500 | 126 | 1200
Chandpur | 135 | 1830 | 125 | 1600 | Rangpur | 128 | 1700 | 121 | 1200
Feni | 126 | 700 | 122 | 1600 | Lalmonirhat | 125 | 600 | 116 | 1200
Chowmuhani | 125 | 700 | 120 | 1700 | Saidpur | 130 | 500 | 117 | 1930
Ashuganj | 135 | 900 | 131 | 1600 | Purbasadipur | 132 | 600 | 117 | 2000
Daudkandi | 130 | 700 | 123 | 1200 | Thakurgaon | 126 | 600 | 113 | 1300
B.Baria | 132 | 1830 | 129 | 1500 | Palashbari | 133 | 600 | 123 | 1300
Ramganj | 124 | 2000 | 120 | 1700 | Barapukuria | 131 | 600 | 125 | 1200
Madanhat | 130 | 100 | 127 | 1000 | Panchagar | 123 | 400 | 110 | 1300
Hathazari | 130 | 1800 | 126 | 1000 | Joldhaka | 128 | 600 | 117 | 2000
Khulshi | 128 | 1800 | 122 | 1000 | Kurigram | 128 | 500 | 118 | 1300
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 364 | 5006 | 2322 | 7328 |  |  |  | QF-LDC-12
0:30 | 347 | 4897.5 | 2236 | 7133.5 | Date: | 2019-11-17
1:00 | 330 | 4789 | 2150 | 6939
1:30 | 240 | 4771.5 | 2040.5 | 6812
2:00 | 150 | 4754 | 1931 | 6685
2:30 | 145 | 4741.5 | 1842 | 6583.5 | [5 empty] | Gen. at Eve. Peak | 9096 | 9096 MW (18:00 )
3:00 | 140 | 4729 | 1753 | 6482 | [6 empty] | 18:00
3:30 | 143 | 4646.5 | 1742.5 | 6389 | [5 empty] | Gen. at Day Peak | 7789.65 | 7789.65 MW (12:00 )
4:00 | 146 | 4564 | 1732 | 6296 | [6 empty] | 12:00
4:30 | 138 | 4527.5 | 1720.5 | 6248 | [5 empty] | Highest Generation | 9096
5:00 | 130 | 4491 | 1709 | 6200 | [6 empty] | 18:00
5:30 | 100 | 4507.505 | 1717.5 | 6225.005
6:00 | 70 | 4524.01 | 1726 | 6250.01
6:30 | 90 | 4616.2595 | 1793.2 | 6409.4595
7:00 | 110 | 4708.509 | 1860.4 | 6568.909
7:30 | 105 | 4795.0395 | 1858.9 | 6653.9395
8:00 | 100 | 4881.57 | 1857.4 | 6738.97
8:30 | 215 | 4923.805 | 1919.1 | 6842.905
9:00 | 330 | 4966.04 | 1980.8 | 6946.84
9:30 | 415 | 5034.78 | 2070.25 | 7105.03
10:00 | 500 | 5103.52 | 2159.7 | 7263.22
10:30 | 495 | 5208.415 | 2202.75 | 7411.165
11:00 | 490 | 5313.31 | 2245.8 | 7559.11
11:30 | 375 | 5474.88 | 2199.5 | 7674.38
12:00 | 260 | 5636.45 | 2153.2 | 7789.65
12:30 | 280 | 5583.705 | 2212.15 | 7795.855
13:00 | 300 | 5530.96 | 2271.1 | 7802.06
13:30 | 345 | 5399.48 | 2234.95 | 7634.43
14:00 | 390 | 5268 | 2198.8 | 7466.8
14:30 | 440 | 5300.25 | 2224.3 | 7524.55
15:00 | 490 | 5332.5 | 2249.8 | 7582.3
15:30 | 485 | 5288.15 | 2234.25 | 7522.4
16:00 | 480 | 5243.8 | 2218.7 | 7462.5
16:30 | 480 | 5310.9 | 2237.35 | 7548.25
17:00 | 480 | 5378 | 2256 | 7634
17:30 | 245 | 5903 | 2462 | 8365
18:00 | 10 | 6428 | 2668 | 9096
18:30 | 75 | 6394.5 | 2700.5 | 9095
19:00 | 140 | 6361 | 2733 | 9094
19:30 | 190 | 6223 | 2679 | 8902
20:00 | 100 | 6148 | 2707 | 8855 |  |  |  | Executive Engineer
20:30 | 75 | 6069 | 2676.5 | 8745.5 |  |  |  | Network Operation Division
21:00 | 50 | 5990 | 2646 | 8636
21:30 | 100 | 5871 | 2573 | 8444
22:00 | 150 | 5752 | 2500 | 8252 |  |  |  |  | Page 6 of 7
22:30 | 205 | 5547.5 | 2430.5 | 7978
23:00 | 260 | 5343 | 2361 | 7704
23:30 | 312 | 5174.5 | 2341.5 | 7516
24:00 | 364 | 5006 | 2322 | 7328
9096 MW (18:00 )
7789.65 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-17 |  | Energy | 183212572
[10 empty] | 2019-11-17 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4322 | 827 | 1715 | 63 | 210 | 85 | 0 | 0 | 106
0:30 | 4328.5 | 751 | 1583.5 | 66 | 217.5 | 85 | 0 | 0 | 102 | Date: | 2019-11-17
1:00 | 4335 | 675 | 1452 | 69 | 225 | 85 | 0 | 0 | 98
1:30 | 4336 | 553 | 1480.5 | 43 | 217.5 | 85 | 0 | 0 | 97 | [7 empty] | Total Energy | 183.2126 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 4337 | 431 | 1509 | 17 | 210 | 85 | 0 | 0 | 96 | [7 empty] | Energy not Served | 0
2:30 | 4327.5 | 358 | 1491 | 17 | 210 | 85 | 0 | 0 | 95 | [7 empty] | Energy Requirement | 183.2126
3:00 | 4318 | 285 | 1473 | 17 | 210 | 85 | 0 | 0 | 94
3:30 | 4257 | 285 | 1443.5 | 17 | 210 | 84.5 | 0 | 0 | 92 | [6 empty] | Shortage
4:00 | 4196 | 285 | 1414 | 17 | 210 | 84 | 0 | 0 | 90
4:30 | 4164 | 284.5 | 1407.5 | 8.5 | 210 | 83.5 | 0 | 0 | 90
5:00 | 4132 | 284 | 1401 | 0 | 210 | 83 | 0 | 0 | 90
5:30 | 4143.5 | 284.5 | 1415 | 0 | 210 | 83 | 0 | 0 | 89
6:00 | 4155 | 285 | 1429 | 0 | 210 | 83 | 0 | 0 | 88
6:30 | 4289.5 | 285 | 1455.5 | 0 | 210 | 83 | 0 | 0 | 84 |  |  |  |  | Coal
7:00 | 4424 | 285 | 1482 | 0 | 210 | 83 | 0 | 0 | 80
7:30 | 4425.5 | 289.5 | 1507.5 | 39 | 210 | 83 | 8 | 0 | 83 |  |  |  | Oil |  |  |  | ,
8:00 | 4427 | 294 | 1533 | 78 | 210 | 83 | 16 | 0 | 86
8:30 | 4465 | 344 | 1538 | 80 | 210 | 84 | 16 | 0 | 90
9:00 | 4503 | 394 | 1543 | 82 | 210 | 85 | 16 | 0 | 94
9:30 | 4525 | 491.5 | 1538 | 97.5 | 210 | 85 | 40.5 | 0 | 95
10:00 | 4547 | 589 | 1533 | 113 | 210 | 85 | 65 | 0 | 96
10:30 | 4561 | 614 | 1622 | 134.5 | 210 | 83.5 | 65 | 0 | 94
11:00 | 4575 | 639 | 1711 | 156 | 210 | 82 | 65 | 0 | 92
11:30 | 4677 | 639 | 1686.5 | 186 | 210 | 82 | 65 | 0 | 100
12:00 | 4779 | 639 | 1662 | 216 | 210 | 82 | 65 | 0 | 108
12:30 | 4712 | 639 | 1725.5 | 229.5 | 209.5 | 82 | 65 | 0 | 106
13:00 | 4645 | 639 | 1789 | 243 | 209 | 82 | 65 | 0 | 104
13:30 | 4645 | 639 | 1789 | 243 | 209 | 82 | 65 | 0 | 104
14:00 | 4645 | 639 | 1789 | 243 | 209 | 82 | 65 | 0 | 104
14:30 | 4612 | 639 | 1726.5 | 247.5 | 209.5 | 81 | 48.5 | 0 | 107
15:00 | 4579 | 639 | 1664 | 252 | 210 | 80 | 32 | 0 | 110
15:30 | 4543 | 639 | 1655.5 | 250 | 210 | 81 | 24 | 0 | 108
16:00 | 4507 | 639 | 1647 | 248 | 210 | 82 | 16 | 0 | 106
16:30 | 4557.5 | 639 | 1626.5 | 298 | 210 | 82 | 20.5 | 0 | 111
17:00 | 4608 | 639 | 1606 | 348 | 210 | 82 | 25 | 0 | 116
17:30 | 4604 | 732.5 | 1649.5 | 895.5 | 210 | 82.5 | 67 | 0 | 124
18:00 | 4600 | 826 | 1693 | 1443 | 210 | 83 | 109 | 0 | 132
18:30 | 4690 | 826 | 1858.5 | 1214.5 | 210 | 83 | 80 | 0 | 133
19:00 | 4780 | 826 | 2024 | 986 | 210 | 83 | 51 | 0 | 134
19:30 | 4819 | 826 | 2114 | 667 | 210 | 83 | 51 | 0 | 132
20:00 | 4786 | 826 | 2127 | 629 | 210 | 83 | 64 | 0 | 130
20:30 | 4791.5 | 826 | 2125.5 | 532 | 210 | 83.5 | 49 | 0 | 128
21:00 | 4797 | 826 | 2124 | 435 | 210 | 84 | 34 | 0 | 126
21:30 | 4756.5 | 826.5 | 2093 | 335 | 210 | 84 | 17 | 0 | 122
22:00 | 4716 | 827 | 2062 | 235 | 210 | 84 | 0 | 0 | 118
22:30 | 4582 | 826.5 | 1970 | 190 | 210 | 84.5 | 0 | 0 | 115
23:00 | 4448 | 826 | 1878 | 145 | 210 | 85 | 0 | 0 | 112
23:30 | 4385 | 826.5 | 1796.5 | 104 | 210 | 85 | 0 | 0 | 109 | Max Temp. in Dhaka |  | 30.6° C
24:00 | 4322 | 827 | 1715 | 63 | 210 | 85 | 0 | 0 | 106
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-11-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 45 | 44 | 43 | 43 | 43 | 43 | 45 | 45 | 42 | 42 | 42 | 42 | 40 | 42 | 42 | 43 |  | 43 | 43 | 43 | 44 | 44 | 45 | 45 | 1032873
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | [17 empty] | 6 | [8 empty] | 9563
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.01 | 3.72 | 8 | 13 | 16 | 18 | 17 | 16 | 14.2 | 10.6 | 5.6 | 0 | [9 empty] | 122850
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 217 | 204 | 214 | 216 | 210 | 217 | 209 | 204 | 210 | 205 | 218 | 203 |  | 206 | 204 | 203 | 204 | 203 | 204 | 202 | 4914025
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 145 | 145 | 140 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2751275
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 51 |  | 51 | 51 | 47 | 34 | 0 |  |  | 157374
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 17 | 17 | 17 | 0 | [5 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 63 |  | 91 | 105 | 105 | 105 | 105 | 105 | 51 | 903273
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 80 | 80 | 80 | 80 | 80 | 76 | 80 | 80 | 80 | 80 | 80 | 79 | 120 | 78 | 80 | 80 | 80 | 80 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2530000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 90 |  | 75 | 0 | 0 |  |  |  |  | 245891
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 35 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 807000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2488500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 7499782
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2076060
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 33 | 33 | 37 | 37 | 37 | 33 | 37 | 37 | 33 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 688032
33 | Ashuganj 225 MW CCPP | 179 | 184 | 179 | 158 | 159 | 161 | 180 | 193 | 198 | 199 | 180 | 180 | 200 | 180 | 180 | 180 | 180 | 180 |  | 180 | 190 | 185 | 182 | 179 | 180 | 187 | 4428000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 305 | 275 | 275 | 295 | 360 | 360 | 320 | 285 | 300 | 285 | 305 | 275 |  | 275 | 285 | 275 | 275 | 275 | 270 | 270 | 7018500
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 270 | 295 | 290 | 355 | 320 | 270 | 290 | 280 | 300 | 275 |  | 300 | 345 | 340 | 340 | 340 | 260 | 260 | 7281000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 41 | 50 | 52 | 51 | 51 | 50 | 50 | 49 | 48 | 50 | 50 |  | 50 | 50 | 51 | 51 | 52 | 52 | 30 | 913440
36 | Chandpur 150 MW CCPP | 135 | 123 | 126 | 132 | 138 | 138 | 139 | 138 | 139 | 140 | 139 | 140 | 126 | 136 | 140 | 140 | 140 | 138 |  | 140 | 140 | 140 | 140 | 126 | 139 | 130 | 3243100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 344 | 344 | 343 | 343 | 347 | 362 | 359 | 356 | 358 | 375 | 371 | 377 | 349 | 370 | 356 | 365 | 350 |  | 365 | 350 | 350 | 351 | 343 | 347 | 350 | 8657920
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 290 | 290 | 300 | 330 | 330 | 330 | 420 | 450 | 450 | 400 | 400 | 400 | 400 | 400 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 9055750
41 | Haripur 360MW CCPP(HPL) | 303 | 303 | 303 | 279 | 274 | 274 | 305 | 304 | 302 | 304 | 351 | 356 | 354 | 332 | 323 | 324 | 324 | 323 |  | 359 | 359 | 360 | 360 | 361 | 362 | 362 | 7678000
42 | RPCL 210MW CCPP | 167 | 183 | 184 | 184 | 164 | 166 | 167 | 165 | 165 | 164 | 157 | 145 | 145 | 144 | 140 | 144 | 142 | 146 |  | 146 | 146 | 144 | 144 | 160 | 158 | 158 | 3682400
43
44 | Fenchugonj CCPP Phase-1 | 60 | 59 | 60 | 30 | 29 | 28 | 28 | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 60 | 59 | 59 | 60 |  | 60 | 60 | 60 | 60 | 58 | 59 | 60 | 1113000
45 | Fenchugonj CCPP Phase-2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 30 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1213080
46 | Shajibazar 330 MW CCPP | 257 | 258 | 250 | 252 | 248 | 254 | 269 | 262 | 271 | 267 | 268 | 305 | 276 | 292 | 297 | 299 | 305 | 296 |  | 301 | 301 | 300 | 288 | 290 | 275 | 263 | 6480000
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 68 | 69 | 68 | 69 | 68 | 68 | 67 | 65 | 65 | 64 | 64 | 65 | 65 | 64 | 65 | 65 | 67 |  | 67 | 67 | 67 | 67 | 68 | 68 | 40 | 1577472
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 79 |  | 79 | 79 | 79 | 79 | 79 | 5 | 5 | 540480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 110000
52 | Sylhet 50MW PP (EPL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 9 | 10 | 6 | 6 | 33 |  | 35 | 39 | 38 | 37 | 39 | 39 | 7 | 372700
53 | Sylhet 10MW PP (Desh) | [17 empty] | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 55800
54 | Hobiganj 11MW PP Cofidence-E | [19 empty] | 11 | 11 | 11 | 11 | 11 | 0 |  | 44304
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 48 |  | 53 | 53 | 53 | 53 | 53 | 47 | 5 | 398400
56 | Shahjahanulla 25 MW PP | [17 empty] | 24 |  | 24 | 24 | 24 | 24 | 0 |  |  | 121632
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 295 | 285 | 260 | 270 | 300 | 290 | 310 | 310 | 300 | 310 | 315 | 310 | 290 | 300 | 290 | 300 | 275 |  | 300 | 305 | 310 | 300 | 290 | 300 | 300 | 7360000
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 13 | 55 | [8 empty] | 81916
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 419328
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 0 |  |  | 88128
62 | Tangail 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 126936
63 | Impoprt (Tripura) | 98 | 96 | 94 | 90 | 90 | 88 | 80 | 86 | 94 | 96 | 92 | 108 | 104 | 112 | 110 | 106 | 116 | 132 |  | 134 | 132 | 130 | 126 | 118 | 112 | 106 | 2550720
64 | Malancha, Ctg. EPZ (United) | 38 | 40 | 40 | 40 | 40 | 40 | 36 | 2 | 3 | 2 | 2 | 2 | 6 | 4 | 2 | 2 | 5 | 8 |  | 3 | 17 | 21 | 27 | 36 | 39 | 40 | 482889
65 | Feni 22MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 114912
66 | Feni 11 MW PP (Doreen) | [17 empty] | 11 |  | 11 | 11 | 11 | 11 | 0 |  |  | 42120
67 | Jangalia 33MW PP (Summit) | [17 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 | 0 |  | 1666000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 15 | 15 | 15 | 15 | 12 | 12 | 14 | 14 | 18 | 15 | 15 | 15 | 12 | 12 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 423620
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 683100
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802700
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 626100
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [10 empty] | 30 | 50 | 55 | 55 | 42 | 37 | 25 | [9 empty] | 290700
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 0 | 7 | [8 empty] | 5760
78 | Gazipur 52 MW PP | [6 empty] | 0 | 27 | 20 | 42 | 51 | 51 | 45 | 43 | 44 | 43 | 47 | 51 |  | 51 | 34 | 34 | 34 | 8 | 0 |  | 618708
79 | Kodda 150MW PP | [7 empty] | 16 | 16 | 65 | 65 | 65 | 65 | 65 | 32 | 16 | 16 | 32 | [8 empty] | 482400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 0 | 5 |  | 0 | 0 | [5 empty] | 6422
| Gazipur 100 MW PP | [7 empty] | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 17 | [8 empty] | 548532
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.589 | 1.97 | 3.04 | 3.92 | 4.41 | 4.45 | 4.16 | 3.2 | 2 | 0.9 | 0 | 0 | [8 empty] | 28320
| Jodiac Power | [17 empty] | 14 | [8 empty] | 19081
| Karnaphuli Power Ltd. | [17 empty] | 16 | [8 empty] | 21745
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 10 | [8 empty] | 11868
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 3 | [8 empty] | 5760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [14 empty] | 8 | 10 | 10 | 86 |  | 90 | 70 | 70 | 70 | 20 | 0 |  | 356400
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 |  | 21 | 21 | 21 | 21 | 21 | 21 | 5 | 270000
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 |  | 19 | 25 | 25 | 25 | 25 | 35 | 7 | 307100
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 0 |  | 0 | [6 empty] | 8784
95 | Patenga 50MW PP (Baraka) | [7 empty] | 1 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 34 |  | 34 | 18 | 11 | 0 |  |  |  | 193440
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 2 | 45 |  | 11 | 11 | 11 | 11 | 7 | 0 |  | 113280
97 | Katpotti 52 MW PP (Sinha) | 18 | 0 | [10 empty] | 6 | 12 | 12 | 12 | 12 | 28 |  | 30 | 30 | 30 | 24 | 24 | 24 | 12 | 318048
98 | Bosila 108MW PP(CLC) | [17 empty] | 70 |  | 70 | 70 | 48 | 0 |  |  |  | 170880
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 47 |  | 0 | 0 | [5 empty] | 154452
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 55 |  | 17 | 17 | [5 empty] | 78803
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 |  | 100 | 163 | 163 | 163 | 130 | 130 | 130 | 2986445
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 0.6 | 1 | 1.6 | 1.9 | 2 | 1.8 | 1.6 | 0.9 | 0.3 | 0 | 0 | [8 empty] | 11800
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 10 | 17 | [8 empty] | 28440
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [9 empty] | 7 | 7 | 19 | 41 | 50 | 50 | 50 | 50 | 86 |  | 120 | 120 | 120 | 60 | 40 | 16 | 0 | 847200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 14400
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 30 |  | 0 | 0 | [5 empty] | 51840
116 | Chandpur 200MW (Desh energy) | [17 empty] | 120 |  | 50 | 0 | 0 |  |  |  |  | 223680
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 2 | 93 |  | 120 | 6 | [5 empty] | 225818
118 | Bibiyana-III 400 MW CCPP | 366 | 366 | 366 | 320 | 307 | 304 | 329 | 345 | 375 | 394 | 397 | 393 | 354 | 356 | 369 | 361 | 381 | 355 |  | 355 | 357 | 354 | 355 | 355 | 292 | 292 | 8516000
| Jamalpur 115 MW PP (United) | [17 empty] | 7 | [8 empty] | 9600
| Anwara 300 MW PP (United) | [17 empty] | 15 | [8 empty] | 17564
120 | Eastern Zone Total | 4789 | 4754 | 4729 | 4564 | 4491 | 4524.01 | 4708.509 | 4881.57 | 4966.04 | 5103.52 | 5313.31 | 5636.45 | 5530.96 | 5268 | 5332.5 | 5243.8 | 5378 | 6428 |  | 6361 | 6223 | 6148 | 5990 | 5752 | 5343 | 5006 | 130008669
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 35 |  | 0 | [6 empty] | 30240
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 13 | 12 | 12 | 12 | 20 | 44 |  | 96 | 96 | 95 | 96 | 96 | 40 | 12 | 701230
| Bhola 225 MW CCPP | 162 | 171 | 163 | 160 | 163 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 173 | 160 |  | 171 | 172 | 172 | 172 | 170 | 163 | 172 | 4143934
140 | Bhola 33 MW PP (Venture) | 23 | 22 | 20 | 17 | 18 | 19 | 17 | 17 | 18 | 19 | 18 | 18 | 19 | 18 | 20 | 19 | 20 | 26 |  | 27 | 26 | 27 | 28 | 27 | 25 | 23 | 494900
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 24 | 8 | 0 |  |  |  |  | 74250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 36 |  | 17 | 5 | 0 |  |  |  |  | 42912
146 | Bheramara HVDC | 675 | 431 | 285 | 285 | 284 | 285 | 285 | 294 | 394 | 589 | 639 | 639 | 639 | 639 | 639 | 639 | 639 | 826 |  | 826 | 826 | 826 | 826 | 827 | 826 | 827 | 14010909
147 | Bheramara 360 MW CCPP | 310 | 310 | 310 | 315 | 270 | 270 | 350 | 325 | 325 | 335 | 345 | 350 | 310 | 320 | 330 | 310 | 325 | 310 |  | 325 | 315 | 310 | 305 | 305 | 305 | 300 | 7752384
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 225 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 209 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 5148300
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1600000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 156 | 160 | 162 | 160 | 159 | 166 | 176 | 174 | 175 | 173 | 202 | 205 | 204 | 191 | 187 | 181 | 178 | 167 |  | 171 | 168 | 171 | 190 | 187 | 184 | 163 | 4542064
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 168 | 175 | 175 | 164 | 173 | 175 | 193 | 197 | 213 | 191 | 186 | 204 | 208 | 175 | 184 | 184 | 185 | 190 |  | 185 | 186 | 182 | 191 | 181 | 165 | 164 | 4660218
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 353 | 376 | 352 | 345 | 356 | 352 | 380 | 380 | 381 | 378 | 380 | 261 | 415 | 380 | 415 | 413 | 348 | 231 |  | 382 | 381 | 381 | 380 | 349 | 351 | 381 | 8704873
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [17 empty] | 18 |  | 18 | 18 | 21 | 22 | 22 | 0 |  | 96000
163 | Bogura 20 MW PP (Energyprima) | [17 empty] | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 80748
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 |  | 184788
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 26 | 18 | 18 | 18 | 6 | 0 |  | 124790
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 0 | [6 empty] | 3607
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 0 | [6 empty] | 6240
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 9 | 26 |  | 0 | [6 empty] | 28564
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 1 | 96 |  | 110 | 70 | 70 |  |  |  |  | 301152
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [21 empty] | 17 | 0 |  |  |  | 5000
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 70 | 92 |  | 50 | 85 | 112 | 113 | 25 | 0 |  | 6000
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.4 | 1.4 | 2.8 | 3.7 | 4.8 | 5.2 | 4.1 | 3.8 | 2.8 | 0.7 | 0 | 0 | [8 empty] | 460800
178
178