## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:October' 2019
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | October 2019 |  | September 2019 |  | October 2018
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11952 | 17/10/19 | 12717 | 01/09/19 | 11485 | 02/10/18 | 12893 | 29/05/19
|  |  | 19:00 |  | 21:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 5208 | 26/10/19 | 6957 | 27/09/19 | 5397.7 | 13/10/18 | - | -
|  |  | 5:00 |  | 8:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11952 | 17/10/19 | 12717 | 01/09/19 | 11485 | 02/10/18 | 12893 | 29/05/19
|  |  | 19:00 |  | 21:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9531.4 | 07/10/19 | 10636.2 | 01/09/19 | 9591.9 | 04/10/18 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11952 | 17/10/19 | 12717 | 01/09/19 | 11485 | 02/10/18 | 12893 | 29/05/19
|  |  | 19:00 |  | 21:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 10692.2903 |  | 11679.07 |  | 9999.13 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 8531.2581 |  | 9378.19 |  | 8021.34 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 942 | 20/10/19 | 930 | 22/09/19 | 772 | 05/10/18 | 956 | 27/3/2019
|  |  | 12:00 |  | 17:00 |  | 14:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 184 | 21/10/19 | 194 | 19/09/19 | 178 | 06/10/18 | 194 | 12/06/19
|  |  | 19:30 |  | 20:00 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3525.1883 |  | 3805.72 |  | 3330.01 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 133.5169 |  | 124.66 |  | 116.21
22 | Net Generation of BPDB (MKWH) | 3391.6713 |  | 3681.05 |  | 3213.81
23 | Net Generation of IPP & RPCL (MKWH) | 1792.18 |  | 2209.5 |  | 1451.65
24 | Net Generation of REB (MKWH) | 144.8634 |  | 154.88 |  | 142.92
24 | Net Generation of Rental Power Plant (MKWH) | 371.5133 |  | 508.3 |  | 556.87
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5700.2281 |  | 6553.73 |  | 5365.25 |  | 6553.86 | Sep-19
26 | Energy Generation by Gas (MKWH) | 4520.3065 |  | 4756.96 |  | 4224.64 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 141.1366 |  | 171.52 |  | 233.56 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 848.4787 |  | 1362.45 |  | 834.1 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 84.059 |  | 139.79 |  | 69.33 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 6.7654 |  | 22.56 |  | 3.14 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 235.097 |  | 243.72 |  | 116.7 |  | 243.72 | Sept-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 711.459 |  | 762.62 |  | 602.91 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 73.629 |  | 81.47 |  | 71.21 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:October' 2019
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11952 | 17/10/19 | 19:00
Generation Period
| Dhaka | MW | 4192
| Chattogram | MW | 1142
| Cumilla | MW | 1064
| Mymensingh | MW | 901
| Sylhet | MW | 472
a) | Total supply in East zone | MW | 7771
| Khulna | MW | 1394
| Barisal | MW | 315
| Rajshahi | MW | 1137
| Rangpur | MW | 651
b) | Total supply in West zone | MW | 3497
c) | Total supply in both zone ( a+b) | MW | 11268
Ref: | 27.21.0000.603.16.086.18.206 | Date: 14/11/2019
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October' 2019
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 960 | 18/10/19 | 16:00
| b) Ishurdi end | MW | 380 | 27/10/19 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 960 | 27/10/19 | 17:00
| b) Ishurdi end | MW | 180 | 18/10/19 | 16:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 1.7815
| b) Ishurdi end | MKWH | 114.5935
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 111.1557
| b) Ishurdi end | MKWH | 1.7296
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 130 | 01/10/19 | 19:00
| b)Serajganj end | MW | 480 | 28/10/19 | 11:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 440 | 28/10/19 | 11:00
| b)Sirajganj end | MW | 110 | 01/10/19 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | - | -
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 3.068
| b)Sirajganj end | MKWH | 147.688
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 143.92
| b)Sirajganj end | MKWH | 3.042
30 | Transmission loss of EWI /NO-2 | % | 2.483
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV Transformer-T2 | 2019-10-01 07:52 | 2019-10-01 09:20 | 1:28 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T3 | 2019-10-02 05:32 | 2019-10-02 08:06 | 2:34 | T | Tripped showing OLTC oil serge trip | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T3 | 2019-10-06 07:17 | 2019-10-06 09:20 | 2:03 | T | Tripped showing 33 kV feeder fault | 30 | 61.5 | Power interruption
Kabirpur | 132/33 kV Transformer-T2 | 2019-10-06 11:23 | 2019-10-06 12:32 | 1:09 | E/O | Due to red hot maintenance at 33 kV side | 70 | 80.5 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2019-10-07 05:50 | 2019-10-07 06:37 | 0:47 | T | Tripped showing dist.REF 87N relay | 8 | 6.2667 | Power interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-10-09 22:10 | 2019-10-09 23:43 | 1:33 | E/O | Due to red hot maintenance at 33 kV side | 5 | 7.75 | Power interruption
|  |  | Total : | 9:34 |  | Unserved Energy: |  | 156.0167
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformer-T5 | 2019-10-01 11:12 | 2019-10-01 11:45 | 0:33 | E/O | Due to heavy flashing observe on 132 kV reserve bus | 60 | 33 | Power interruption
| 33 kV reserve Bus | 2019-10-03 07:55 | 2019-10-03 09:25 | 1:30 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
Maniknagar | 230/132 kV Transformer-T2 | 2019-10-17 11:08 | 2019-10-17 11:51 | 0:43 | T | Tripped showing E/F relay | 0 | 0 | No interruption
|  |  | Total : | 2:46 |  | Unserved Energy: |  | 33
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformer-T1 | 2019-10-03 11:52 | 2019-10-03 12:53 | 1:01 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-10-05 14:04 | 2019-10-05 14:55 | 0:51 | E/O | Due to red hot maintenance at 33 kV side | 25 | 21.25 | Power interruption
Bakulia | 132/33 kV Transformer-T3 | 2019-10-06 12:55 | 2019-10-06 16:15 | 3:20 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2019-10-14 08:46 | 2019-10-14 09:18 | 0:32 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformers-T1& T2 | 2019-10-16 12:39 | 2019-10-16 18:28 | 5:49 | E/O | Due to bursting of PT at 33 kV side | 30 | 174.5 | Power interruption
Sikalbaha | 132/33 kV Transformers-T1 | 2019-10-18 19:43 | 2019-10-18 20:48 | 1:05 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-10-18 19:43 | 2019-10-18 23:44 | 4:01 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-10-23 07:45 | 2019-10-23 08:10 | 0:25 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T3 | 2019-10-27 20:11 | 2019-10-27 23:12 | 3:01 | T | Tripped showing PRD relay | 6 | 18.1 | Power interruption
|  |  | Total : | 20:05 |  | Unserved Energy: |  | 213.85
Cumilla Grid Circle :
Cumilla (S) | 132/33 kV Transformer-T1 | 2019-10-03 06:55 | 2019-10-03 08:03 | 1:08 | E/O | Due to red hot maintenance at 33 kV side | 30 | 34 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-10-03 06:08 | 2019-10-03 09:22 | 3:14 | E/O | Due to winding temperature high | 0 | 0 | No interruption
Feni | 132/33 kV Transformers-T1 | 2019-10-10 00:12 | 2019-10-10 00:54 | 0:42 | T | Tripped showing O/C relay at 33 kV CT burst | 25 | 17.5 | Power interruption
| 132/33 kV Transformers-T2 | 2019-10-10 00:12 | 2019-10-10 01:54 | 1:42 | T
B.Baria | 132/33 kV Transformers-T2 & T3 | 2019-10-17 09:50 | 2019-10-17 10:31 | 0:41 | E/O | Due to red hot maintenance at 33 kV side | 24 | 16.4 | Power interruption
Chatek | 132/33 kV Transformer-T2 | 2019-10-22 18:01 | 2019-10-22 18:15 | 0:14 | T | Tripped showing E/F relay | 6 | 1.4 | Power interruption
|  |  | Total : | 7:41 |  | Unserved Energy: |  | 69.3
Khulna Grid Circle :
Barisal | 132/33 kV Transformer-T1 | 2019-10-01 00:18 | 2019-10-01 00:23 | 7:35 | T | Tripped showing E/F & O/C relay | 15 | 113.75 | Power interruption
Bagerhat | 132/33 kV Transformer-T2 | 2019-10-02 05:09 | 2019-10-02 05:29 | 0:20 | T | Tripped showing E/F relay at 33 kV side | 8 | 2.6667 | Power interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2019-10-03 16:51 | 2019-10-03 17:12 | 0:21 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2019-10-04 04:32 | 2019-10-04 04:45 | 0:13 | T | Tripped showing 33 kV feeder fault | 12 | 2.6 | Power interruption
Patuakhali | 132/33 kV Transformer-T3 | 2019-10-05 17:10 | 2019-10-05 17:14 | 0:04 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-10-06 07:12 | 2019-10-06 09:12 | 2:00 | T | Tripped showing 33 kV feeder fault | 40 | 80 | Power interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2019-10-08 11:36 | 2019-10-08 11:44 | 0:08 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Mongla | 132/33 kV Transformers-T1 & T2 & 33 kV Bus | 2019-10-25 09:13 | 2019-10-25 09:37 | 0:24 | T | Tripped showing 33 kV feeder fault | 14 | 5.6 | Power interruption
|  |  | Total : | 11:50 |  | Unserved Energy: |  | 204.6167
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Jhenidah | 132/33 kV Transformer-T5 & 33 kV Bus | 2019-10-01 08:14 | 2019-10-01 09:20 | 1:06 | E/O | Due to red hot maintenance at 33 kV side | 29 | 31.9 | Power interruption
Bottail | 132/33 kV Transformer-T1 | 2019-10-05 06:12 | 2019-10-05 07:34 | 1:22 | E/O | Due to red hot maintenance at 33 kV side | 20 | 27.3333 | Power interruption
Magura | 132/33 kV Transformer-T2 | 2019-10-26 11:21 | 2019-10-26 12:10 | 0:49 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 2:28 |  |  |  | 59.2333
Bogura Grid Circle:
Barapukuria | 230/132 kV Transformer-T01 | 2019-10-01 14:01 | 2019-10-01 17:29 | 3:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformers-T3 & T4 | 2019-10-02 15:14 | 2019-10-02 17:17 | 2:03 | E/O | Due to red hot maintenance at 33 kV side | 15 | 30.75 | Power interruption
Bogura(O) | 132/33 kV Transformer-T4 | 2019-10-13 07:25 | 2019-10-13 08:15 | 0:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T6 | 2019-10-18 18:40 | 2019-10-18 18:52 | 0:12 | T | Tripped showing O/C relay | 478 | 868.3667 | Power interruption 11:50 to 13:39
Bogura(O) | 132 kV main Bus | 2019-10-21 10:15 | 2019-10-21 10:56 | 0:41 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T3 | 2019-10-26 21:19 | 2019-10-26 22:50 | 1:31 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 8:45 |  | Unserved Energy: |  | 899.1167
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 63:09 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2019-10-02 10:58 | 2019-10-02 11:17 | 0:19 | T | Tripped showing dist.(Z1) PT fail | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2019-10-02 10:58 | 2019-10-02 11:17 | 0:19 | T | Tripped showing (Z1) PT fail | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-10-03 10:43 | 2019-10-03 10:49 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2019-10-08 03:10 | 2019-10-08 13:06 | 9:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2019-10-11 10:53 | 2019-10-11 11:01 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-10-11 09:10 | 2019-10-11 12:10 | 3:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Uttara 3rd phase | Uttara 3rd phase-Mirpur 132 kV line | 2019-10-20 10:50 | 2019-10-20 14:22 | 3:32 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 17:20 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Lalbagh | Lalbagh-Kallyanpur 132 kV line-1 | 2019-10-01 19:30 | 2019-10-01 19:40 | 0:10 | T | Tripped showing dist.86B,67N relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2019-10-05 19:59 | 2019-10-05 20:10 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-B.baria 132 kV line-2 | 2019-10-05 17:02 | 2019-10-05 17:17 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Narsinghdi-B.baria 132 kV line-2 | 2019-10-06 12:13 | 2019-10-07 16:01 | 27:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2019-10-07 09:17 | 2019-10-07 15:05 | 5:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Meghnagaht | Meghnagaht-Cumilla(N) 230 kV line-2 | 2019-10-10 12:15 | 2019-10-10 14:19 | 2:04 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2019-10-13 10:55 | 2019-10-15 21:21 | 58:26 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 94:42 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-10-04 10:19 | 2019-10-04 10:42 | 0:23 | T | Tripped showing dist. relay | 11 | 4.2167 | Power interruption
Rangamati | Rangamati-Kagrachari 132 kV line | 2019-10-05 17:50 | 2019-10-05 18:08 | 0:18 | T | Tripped showing dist. relay | 15 | 4.5 | Power interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line | 2019-10-17 11:38 | 2019-10-17 13:38 | 2:00 | T | Tripped showing dist. relay | 15 | 30 | Power interruption
Juldah | Juldah-Sikalbaha 132 kV line | 2019-10-19 22:17 | 2019-10-19 22:44 | 0:27 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 3:08 |  | Unserved Energy: |  | 38.7167
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-1 | 2019-09-01 13:08 | 2019-09-01 13:25 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-2 | 2019-10-05 17:18 | 2019-10-05 17:41 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2019-10-09 15:50 | 2019-10-09 16:20 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chatak | Chatak-Sunamganj 132 kV line | 2019-10-11 13:20 | 2019-10-11 13:38 | 0:18 | T | Tripped showing dist. relay | 21 | 6.3 | Power interruption
| Chatak-Sunamganj 132 kV line | 2019-10-28 10:34 | 2019-10-28 10:54 | 0:20 | T | Tripped showing dist. relay | 14 | 4.6667 | Power interruption
|  |  | Total : | 1:31 |  | Unserved Energy: |  | 10.9667
Khulna Grid Circle :
Barishal | Barishal-Bhola 230 kV line-1 | 2019-10-03 11:33 | 2019-10-03 12:30 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madaripur 132 kV line | 2019-10-11 06:37 | 2019-10-11 07:37 | 1:00 | E/O | Due to red hot maintenance | 40 | 40 | Power interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-10-17 13:01 | 2019-10-17 13:16 | 0:15 | T | Tripped showing dist.E/F relay | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-2 | 2019-10-18 13:15 | 2019-10-18 14:00 | 0:45 | T | Tripped showing dist.E/F relay | 0 | 0 | No interruption
Madaripur | Madaripur-Sariatpur 132 kV line-2 | 2019-10-22 12:44 | 2019-10-22 14:04 | 1:20 | T | Tripped showing over voltage | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-1 | 2019-10-24 10:38 | 2019-10-24 11:09 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
khulna© | khulna©-Goalpara 132 kV line-1 | 2019-10-24 18:05 | 2019-10-24 22:49 | 4:44 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line | 2019-10-31 07:04 | 2019-10-31 08:17 | 1:13 | E/O | Due to red hot maintenance | 30 | 36.5 | Power interruption
|  |  | Total : | 10:45 |  | Unserved Energy: |  | 76.5
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2019
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Natore | Natore-Rajshahi 132 kV line-1 | 2019-10-03 15:13 | 2019-10-03 15:30 | 0:17 | E/O | Due to bursting of R-phase CT | 137 | 38.8167 | Power interruption
| Natore-Rajshahi 132 kV line-2 | 2019-10-03 15:30 | 2019-10-03 20:56 | 5:26 | E/O
Naogaon | Naogaon-Joypurhat 132 kV line | 2019-10-08 05:30 | 2019-10-08 05:48 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line-1 | 2019-10-10 15:34 | 2019-10-10 16:56 | 1:22 | E/O | Due to bursting of lightning arrester | 0 | 0 | No interruption
Bogura | Bogura -Sherpur 132 kV line-1 & 2 | 2019-10-11 02:26 | 2019-10-11 03:38 | 1:12 | T | Tripped showing E/F relay | 20 | 24 | Power interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-1 & 2 | 2019-10-11 02:26 | 2019-10-11 03:23 | 0:57 | T | Due to bursting of lightning arrester | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-1 | 2019-10-11 12:40 | 2019-10-11 12:47 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Natore-Bogura 132 kV line-2 | 2019-10-11 12:40 | 2019-10-11 12:47 | 0:07 | T |  | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-1 | 2019-10-17 11:45 | 2019-10-17 13:07 | 1:22 | E/O | Due to SF6 gas filling | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV line | 2019-10-18 18:40 | 2019-10-18 18:58 | 0:18 | T | Tripped showing O/C & E/F.relay | 0 | 0 | No interruption
Bogura | Bogura -Mohastangarh 132 kV line-2 | 2019-10-18 18:40 | 2019-10-18 19:01 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur confidence 132 kV line-1 & 2 | 2019-10-21 17:50 | 2019-10-21 17:58 | 0:08 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 11:55 |  | Unserved Energy: |  | 62.8167
Others :
Ullon | Ullon-Dhanmondi 132 kV line-2 | 2019-10-05 20:04 | 2019-10-05 20:18 | 0:14 | T | Tripped showing gen trip relay | 100 | 23.3333 | Power interruption
| Maniknagar-Bangabhaban 132 kV line-1 & 2 | 2019-10-17 11:08 | 2019-10-17 15:09 | 4:01 | T | Tripped showing pilot wire& main protection. relay | 0 | 0 | No interruption
|  |  | Total : | 4:15 |  | Unserved Energy: |  | 23.3333
Total outage period of Sub-station Equipment : |  |  |  | 142:05 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kadda | 33 kV Bus | 2019-10-03 06:58 | 2019-10-03 09:45 | 2:47 | S/O | Due to PBS work | 177 | 492.65 | Power interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2019-10-05 07:11 | 2019-10-05 10:02 | 2:51 | S/O | Due to C/M work | 45 | 128.25 | Power interruption
| 132/33 kV Transformer-T1 | 2019-10-05 10:42 | 2019-10-05 14:58 | 4:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-10-06 10:31 | 2019-10-06 12:10 | 1:39 | S/O | Due to CT probltm | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2019-10-10 19:03 | 2019-10-10 19:08 | 0:05 | S/O | Due to shifed at 132/33 kV Transformer T3 | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-10-13 10:34 | 2019-10-13 15:14 | 4:40 | S/O |  | 13 | 60.6667 | Power interruption
Netrakona | 132/33 kV Transformer-T3 | 2019-10-15 08:50 | 2019-10-15 09:43 | 0:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2019-10-18 07:22 | 2019-10-18 10:10 | 2:48 | S/O | Due to maintenance at 33 kV side | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2019-10-19 09:10 | 2019-10-19 15:15 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Uttara 3rd phase | 132/33 kV Transformer-T1 | 2019-10-20 10:01 | 2019-10-20 11:00 | 0:59 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2019-10-21 07:17 | 2019-10-21 08:20 | 1:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Uttara 3rd phase | 132/33 kV Transformer-T2 | 2019-10-21 14:41 | 2019-10-21 15:45 | 1:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2019-10-23 07:30 | 2019-10-23 09:49 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2019-10-25 07:08 | 2019-10-25 10:35 | 3:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T2 | 2019-10-26 08:43 | 2019-10-26 14:56 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 & 33 kV Bus | 2019-10-28 07:05 | 2019-10-28 08:15 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2019-10-28 07:34 | 2019-10-28 14:24 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | 400 kV Bus-1 |  | 2019-10-28 12:57 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-10-29 08:28 | 2019-10-29 12:57 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T2 | 2019-10-29 13:31 | 2019-10-29 14:12 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 & 33 kV Bus | 2019-10-30 07:42 | 2019-10-30 10:20 | 2:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2019-10-30 12:15 | 2019-10-30 17:13 | 4:58 | S/O | Due to tan delta test | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2019-10-30 09:42 | 2019-10-30 12:49 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 65:02 |  | Unserved Energy: |  | 681.5667
Dhaka (South) Grid Circle :
Hasnabad | 132 kV reserve Bus | 2019-10-11 07:36 | 2019-10-11 18:50 | 11:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer-T5 | 2019-10-11 07:26 | 2019-10-11 12:33 | 5:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T1 | 2019-10-11 06:12 | 2019-10-11 12:43 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-10-11 07:18 | 2019-10-11 12:43 | 5:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 230/132 kV Transformer-T03 | 2019-10-11 08:58 | 2019-10-11 12:43 | 3:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2019-10-22 09:02 | 2019-10-22 10:07 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2019-10-24 12:42 | 2019-10-24 12:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 33:07 |  | Unserved Energy: |  | 0
Page: 2/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Khulshi | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-10-03 11:20 | 2019-10-03 12:40 | 1:20 | S/O | Due to replacement work at 33 kV side | 40 | 53.3333 | Power interruption
Sikalbaha | 132/33 kV Transformer-T1 & 132 kV Bus-B | 2019-10-13 07:05 | 2019-10-13 17:16 | 10:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132 kV Bus-B | 2019-10-16 07:40 | 2019-10-16 13:02 | 5:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main bus-A | 2019-10-17 07:53 | 2019-10-17 12:57 | 5:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-B | 2019-10-18 07:23 | 2019-10-18 13:15 | 5:52 | S/O | Due to D/W work | 0 | 0 | No interruption
T.K chemical | 132/33 kV Transformer-T2 | 2019-10-18 08:15 | 2019-10-18 16:55 | 8:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2019-10-19 06:57 | 2019-10-19 16:18 | 9:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-B | 2019-10-20 08:25 | 2019-10-20 09:24 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 33 kV Bus-2 | 2019-10-21 22:30 | 2019-10-21 22:57 | 0:27 | S/O | Due to C/M work | 52 | 23.4 | Power interruption
Juldah | 132 kV main Bus | 2019-10-22 08:15 | 2019-10-22 12:15 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haishahar | 132 kV main Bus | 2019-10-25 07:29 | 2019-10-25 11:24 | 3:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(O) | 132 kV Bus-A | 2019-10-27 07:42 | 2019-10-27 13:07 | 5:25 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 60:36 |  | Unserved Energy : |  | 76.7333
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformers-T1 & T2 | 2019-10-04 07:07 | 2019-10-04 09:27 | 26:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 | 2019-10-05 12:12 | 2019-10-05 13:13 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-10-05 13:24 | 2019-10-05 14:18 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2019-10-11 05:02 | 2019-10-11 08:11 | 3:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T4 | 2019-10-11 21:20 | 2019-10-11 23:02 | 1:42 | S/O | Due to C/M work | 61 | 103.7 | Power interruption
Shahjibazar | 132/33 kV Transformers-T4 & T6 | 2019-10-15 09:20 | 2019-10-15 13:28 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2019-10-16 10:17 | 2019-10-16 12:34 | 2:17 | S/O | Due to maintenance work at 33 kV side | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2019-10-18 06:59 | 2019-10-18 10:33 | 3:34 | S/O |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 & Bus section-4 | 2019-10-19 06:41 | 2019-10-19 10:25 | 3:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2019-10-21 10:25 | 2019-10-21 15:16 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV Transformer-AT-2 | 2019-10-22 13:54 | 2019-10-22 17:15 | 3:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2019-10-23 12:24 | 2019-10-23 13:04 | 0:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2019-10-24 09:23 | 2019-10-24 17:34 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2019-10-27 09:50 | 2019-10-27 14:25 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2019-10-28 08:30 | 2019-10-28 13:52 | 5:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer-TR-1 | 2019-10-29 10:05 | 2019-10-29 13:49 | 3:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 & T4 | 2019-10-29 08:32 | 2019-10-29 09:04 | 0:32 | S/O | Due to PDB feeder fault | 46 | 24.5333 | Power interruption
| 132/33 kV Transformer-T4 | 2019-10-31 08:32 | 2019-10-31 14:24 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformers-T2 & T2 | 2019-10-31 09:54 | 2019-10-31 10:46 | 0:52 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 85:01 |  | Unserved Energy : |  | 128.2333
Page: 3/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Thakurgaon | 132/33 kV Transformer-T2 | 2019-10-05 08:40 | 2019-10-05 16:15 | 7:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-10-05 08:40 | 2019-10-05 16:15 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2019-10-05 08:03 | 2019-10-05 09:10 | 1:07 | S/O | Due to S/D of 33 kV Bus | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 & 33 KV Bus | 2019-10-05 08:08 | 2019-10-05 09:09 | 1:01 | S/O | Due to S/D of 33 kV Bus | 20 | 20.3333 | Power interruption
Patuakhali | 132/33 kV Transformer-T1 | 2019-10-06 09:53 | 2019-10-06 17:02 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-10-06 14:30 | 2019-10-06 15:02 | 0:32 | S/O | Due to S/D of 33 kV side | 21 | 11.2 | Power interruption
| 132/33 kV Transformer-T1 | 2019-10-07 07:01 | 2019-10-07 17:38 | 10:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2019-10-09 07:04 | 2019-10-09 17:23 | 10:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 & 33 KV Bus | 2019-10-10 09:08 | 2019-10-10 17:02 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2019-10-13 07:08 | 2019-10-13 17:08 | 10:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | 132 kV Bus-A | 2019-10-14 07:03 | 2019-10-14 13:32 | 6:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2019-10-14 11:50 | 2019-10-14 13:39 | 1:49 | S/O | Due to replacemnet work | 50 | 90.8333 | Power interruption
Bakulia | 132/33 kV Transformer-T2 | 2019-10-19 06:57 | 2019-10-19 16:18 | 9:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2019-10-21 08:05 | 2019-10-21 16:34 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 & 33 kV Bus | 2019-10-26 09:42 | 2019-10-26 17:07 | 7:25 | S/O | Due to A/M work | 30 | 222.5 | Power interruption
Khulna(S) | 230/132 kV Transformer-T02 | 2019-10-26 10:55 | 2019-10-26 11:28 | 0:33 | S/O | Due to Oil refile | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2019-10-27 08:29 | 2019-10-27 15:53 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2019-10-28 08:38 | 2019-10-28 15:44 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | 230/132 kV Transformer-T1 | 2019-10-28 08:09 | 2019-10-28 16:08 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2019-10-29 08:34 | 2019-10-29 14:38 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | 230/132 kV Transformer-T1 | 2019-10-29 08:09 | 2019-10-29 18:00 | 9:51 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 136:19 |  | Unserved Energy : |  | 344.8667
HVDC Grid Circle :
Ishurdi | 132 kV Bus-2 | 2019-10-03 07:16 | 2019-10-03 14:05 | 6:49 | S/O | Due to C/M work | 30 | 204.5 | No interruption
Bottail | 33 kV Bus-1 | 2019-10-13 07:07 | 2019-10-13 08:40 | 1:33 | S/O | Due to PBS work | 23 | 35.65 | Power interruption
Bheramara | Bheramara HVDC 20DF-11 | 2019-10-21 09:41 | 2019-10-21 16:26 | 6:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC 20DF-11 | 2019-10-23 09:45 | 2019-10-23 16:15 | 6:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/ kV Transformer-T1 | 2019-10-26 10:20 | 2019-10-26 11:33 | 1:13 | S/O | Due to NGR problem | 0 | 0 | No interruption
|  |  | Total : | 22:50 |  | Unserved Energy : |  | 240.15
Bogura Grid Circle:
Bogura | 230/132 kV Transformer-T2 | 2019-10-02 09:10 | 2019-10-02 16:20 | 7:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Ruppur | 132/ kV Transformer-T2 | 2019-10-02 10:43 | 2019-10-02 20:20 | 9:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T01 | 2019-10-03 09:13 | 2019-10-03 13:19 | 4:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Thaurgaon | 132/ kV Transformer-T1 | 2019-10-03 08:40 | 2019-10-03 16:10 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/ kV Transformer-T2 | 2019-10-03 15:59 | 2019-10-03 21:13 | 5:14 | S/O | Due to SAS work | 0 | 0 | No interruption
Saidpur | 132/ kV Transformer-T3 | 2019-10-04 08:05 | 2019-10-04 17:17 | 9:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 4/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Bogura | 230/132 kV Transformer-T02 | 2019-10-05 08:42 | 2019-10-05 19:07 | 10:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T1 & 33 kV Bus | 2019-10-05 12:43 | 2019-10-05 13:22 | 0:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T03 | 2019-10-06 09:14 | 2019-10-06 13:41 | 4:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformers-T1 | 2019-10-07 13:30 | 2019-10-07 16:58 | 3:28 | S/O | Due to SAS work | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2019-10-07 17:01 | 2019-10-07 17:45 | 0:44 | S/O |  | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T1 | 2019-10-08 14:44 | 2019-10-08 17:14 | 2:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Saidpur | 132/ kV Transformer-T4 | 2019-10-09 08:40 | 2019-10-09 11:45 | 3:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T3 | 2019-10-10 10:10 | 2019-10-10 15:45 | 5:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2019-10-10 16:18 | 2019-10-10 17:07 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T5 | 2019-10-12 10:10 | 2019-10-12 14:05 | 3:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 | 2019-10-12 08:03 | 2019-10-12 15:12 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132 kV Bus | 2019-10-12 11:10 | 2019-10-12 17:00 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-10-13 07:13 | 2019-10-13 08:30 | 1:17 | S/O | Due to A/M work | 20 | 25.6667 | Power interruption
Bogura(O) | 132 kV main Bus | 2019-10-13 07:20 | 2019-10-13 09:38 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T3 | 2019-10-13 11:40 | 2019-10-13 21:13 | 9:33 | S/O | Due to project work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T1 | 2019-10-13 09:05 | 2019-10-13 15:15 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 | 2019-10-13 08:05 | 2019-10-13 15:15 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T1 | 2019-10-14 07:40 | 2019-10-14 14:33 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2019-10-14 08:02 | 2019-10-14 15:15 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T1 | 2019-10-14 09:33 | 2019-10-14 16:45 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T1 | 2019-10-14 10:06 | 2019-10-14 16:00 | 5:54 | S/O | Due to SAS work | 0 | 0 | No interruption
Baghabari | 132 kV Bus-2 | 2019-10-14 08:40 | 2019-10-14 17:25 | 8:45 | S/O | Due to PT connection | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T2 | 2019-10-15 09:00 | 2019-10-15 15:40 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2019-10-15 08:05 | 2019-10-15 15:40 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2019-10-15 08:10 | 2019-10-15 15:08 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2019-10-16 08:10 | 2019-10-16 15:40 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(O) | 132/33 kV Transformer-T2 | 2019-10-16 09:08 | 2019-10-16 16:45 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T2 | 2019-10-16 07:48 | 2019-10-16 15:11 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T3 | 2019-10-16 08:06 | 2019-10-16 15:20 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-10-17 06:16 | 2019-10-17 18:20 | 12:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T2 | 2019-10-17 09:05 | 2019-10-17 15:20 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T3 | 2019-10-17 08:10 | 2019-10-17 15:20 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2019-10-17 08:10 | 2019-10-17 15:20 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T2 | 2019-10-17 08:07 | 2019-10-17 15:55 | 7:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T2 | 2019-10-18 05:45 | 2019-10-18 06:45 | 1:00 | S/O | Due to D/W work | 8 | 8 | No interruption
Palashbari | 132/33 kV Transformer-T4 | 2019-10-19 08:10 | 2019-10-19 15:08 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T2 | 2019-10-19 08:55 | 2019-10-19 15:03 | 6:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T2 | 2019-10-19 08:15 | 2019-10-19 15:15 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-TR2 | 2019-10-19 11:13 | 2019-10-19 15:43 | 4:30 | S/O | Due to D/W work | 8 | 36 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-10-20 07:20 | 2019-10-20 16:08 | 8:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 5/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Palashbari | 132/33 kV Transformer-T4 | 2019-10-20 08:10 | 2019-10-20 15:05 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 |  | 2019-10-24 20:50 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T1 | 2019-10-21 07:17 | 2019-10-21 16:36 |  | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV Transformer-T2 | 2019-10-21 07:20 | 2019-10-21 16:37 | 9:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2019-10-21 08:54 | 2019-10-21 15:30 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2019-10-21 08:10 | 2019-10-21 15:15 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2019-10-21 13:05 | 2019-10-21 16:58 | 3:53 | S/O | Due to SAS work | 0 | 0 | No interruption
| 132 kV Bus-B | 2019-10-21 16:10 | 2019-10-21 16:10 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T4 | 2019-10-22 08:43 | 2019-10-22 16:11 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2019-10-22 08:51 | 2019-10-22 19:18 | 10:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132 kV Bus-A | 2019-10-23 08:30 | 2019-10-23 15:35 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T1 | 2019-10-23 07:56 | 2019-10-23 15:02 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Mohastangarth | 132/33 kV Transformer-T1 | 2019-10-23 09:10 | 2019-10-23 15:20 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T1 | 2019-10-23 08:58 | 2019-10-23 15:37 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2019-10-24 06:50 | 2019-10-24 18:55 | 12:05 | S/O | Due to D/W work | 5 | 60.4167 | Power interruption
| 132/33 kV Transformer-T1 & 132 kV main Bus | 2019-10-25 10:20 | 2019-10-25 13:30 | 3:10 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nawabganj | 132 kV main Bus | 2019-10-26 06:06 | 2019-10-26 07:09 | 1:03 | S/O | Due to D/W work | 30 | 31.5 | Power interruption
Rangpur | 132/33 kV Transformer-T1 | 2019-10-26 08:25 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Mohastangarth | 132/33 kV Transformer-T2 | 2019-10-26 10:05 | 2019-10-26 16:26 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T3 | 2019-10-27 08:41 | 2019-10-27 15:44 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2019-10-28 06:15 | 2019-10-28 08:30 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T3 | 2019-10-28 10:16 | 2019-10-28 16:53 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T3 | 2019-10-28 08:02 | 2019-10-28 13:52 | 5:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 |  | 2019-10-28 17:01 |  |  | Due to new connection | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T3 | 2019-10-29 09:32 | 2019-10-29 11:30 | 1:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T2 | 2019-10-29 09:10 | 2019-10-29 12:43 | 3:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T4 | 2019-10-30 08:37 | 2019-10-30 17:15 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T03 | 2019-10-31 08:31 | 2019-10-31 12:35 | 4:04 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 375:52 |  | Unserved Energy : |  | 161.5833
Others :
Bashundhara | 132/ kV Transformer-T1 | 2019-10-02 10:45 | 2019-10-05 15:10 | 76:25 | S/O | Due to new connection of Trnasformer GT1 | 0 | 0 | No interruption
|  |  | Total | 76:25 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance:
|  |  |  | 855:12 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2019-10-02 11:10 | 2019-10-02 11:42 | 0:32 | S/O | Due to SAS work | 0 | 0 | No interruption
Kailakoir | Kailakoir-Tangail 132 kV line-1 | 2019-10-04 10:18 | 2019-10-04 11:15 | 0:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Uttara | Uttara-Mirpur 132 kV line | 2019-10-06 07:04 | 2019-10-20 15:20 | 344:16 | S/O | Due to SAS work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 132 kV line-2 | 2019-10-09 09:55 | 2019-10-09 13:53 | 3:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Summit P/P 132 kV line | 2019-10-12 09:35 | 2019-10-12 14:06 | 4:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 & 2 | 2019-10-14 08:07 | 2019-10-14 18:20 | 10:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line | 2019-10-15 08:41 | 2019-10-15 14:17 | 5:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Kadda 132 kV line-1 & 2 | 2019-10-15 08:07 | 2019-10-15 12:29 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2019-10-16 09:07 | 2019-10-16 16:12 | 7:05 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-2 | 2019-10-17 09:25 | 2019-10-17 16:37 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-2 | 2019-10-19 09:10 | 2019-10-19 15:45 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2019-10-20 09:13 | 2019-10-20 13:50 | 4:37 | S/O | Due to A/M work | 20 | 92.3333 | Power interruption
Tongi | Tongi-Bashundhara 132 kV line-1 & 2 |  | 2019-10-20 10:12 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 | 2019-10-21 09:09 | 2019-10-21 15:30 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2019-10-22 09:20 | 2019-10-22 16:36 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Sherpur 132 kV line-1 | 2019-10-22 08:52 | 2019-10-22 12:44 | 3:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jamalpur-Sherpur 132 kV line-2 | 2019-10-22 12:45 | 2019-10-22 16:23 | 3:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2019-10-22 13:31 | 2019-10-22 14:28 | 0:57 | S/O | Due to tree trimming | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2019-10-23 09:02 | 2019-10-23 16:14 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2019-10-23 08:07 | 2019-10-23 11:30 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2019-10-24 09:19 | 2019-10-24 14:33 | 5:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-1 | 2019-10-24 09:55 | 2019-10-24 21:37 | 11:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2019-10-26 09:03 | 2019-10-26 12:28 | 3:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2019-10-26 09:17 | 2019-10-26 20:16 | 10:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2019-10-27 10:01 | 2019-10-27 14:30 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2019-10-27 08:51 | 2019-10-27 16:43 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2019-10-27 10:10 | 2019-10-27 19:20 | 9:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-2 | 2019-10-28 09:46 | 2019-10-28 15:43 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Hasnabad 230 kV line-1 | 2019-10-28 09:05 | 2019-10-28 16:23 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2019-10-28 08:39 | 2019-10-28 17:40 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2019-10-28 08:04 | 2019-10-28 17:23 | 9:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-2 | 2019-10-29 08:08 | 2019-10-29 14:58 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-2 | 2019-10-30 08:33 | 2019-10-30 15:33 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-10-30 08:30 | 2019-10-30 20:58 | 12:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mirpur-Aminbazar 132 kV line-1 | 2019-10-30 09:27 | 2019-10-30 17:34 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2019-10-31 09:53 | 2019-10-31 15:50 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2019-10-31 08:53 | 2019-10-31 16:40 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 565:08 |  | Unserved Energy: |  | 92.3333
Dhaka (South) Grid Circle :
Shyampur | Shyampur-Haripur-Brahongaon 132 kV line | 2019-09-02 10:22 | 2019-09-02 11:13 | 0:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-2 |  | 2019-10-02 08:57 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-2 | 2019-10-05 09:01 | 2019-10-05 13:50 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 |  | 2019-10-05 13:00 |  | S/O | Due to S/D of 33 kV Bus | 0 | 0 | No interruption
| Bashundhara-Tongi 132 kV line-1 & 2 | 2019-10-08 08:27 | 2019-10-20 10:00 | 289:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati-Kamrangirchar kV line | 2019-10-11 06:25 | 2019-10-11 19:49 | 13:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Lalbagh 132 kV line | 2019-10-11 06:19 | 2019-10-11 19:55 | 13:36 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Aminbazar 230 kV line-1 | 2019-10-11 07:15 | 2019-10-11 15:12 | 7:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Bramongaon -Shyampur 132 kV line | 2019-10-11 07:05 | 2019-10-11 17:21 | 10:16 | S/O | Due to C/M work | 0 | 0
Shyampur | Shyampur-Bramongaon 132 kV line | 2019-10-11 07:53 |  |  | S/O | Due to DPDC work | 0 | 0 | No interruption
Page: 2/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Bashundhara | Bashundhara-Rampura 132 kV line-2 | 2019-10-11 09:05 | 2019-10-11 16:07 | 7:02 | S/O | Due to safety to carryout GIS work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aggreko 132 kV line-Lalbagh | 2019-10-12 06:40 | 2019-10-12 15:31 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line-1 | 2019-10-12 06:59 | 2019-10-12 14:49 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV line-1 | 2019-10-18 08:51 | 2019-10-18 18:27 | 9:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Manknagar 230 kV line-1 | 2019-10-19 08:49 | 2019-10-19 17:17 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-shyampur 230 kV line-2 | 2019-10-21 09:04 | 2019-10-21 18:06 | 9:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2019-10-22 08:26 | 2019-10-22 17:35 | 9:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line | 2019-10-22 09:23 | 2019-10-22 16:47 | 7:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2019-10-23 07:16 | 2019-10-23 17:35 | 10:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2019-10-29 06:45 | 2019-10-29 08:17 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 410:48 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-10-03 08:42 | 2019-10-03 13:28 | 4:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line | 2019-10-04 06:37 | 2019-10-04 17:47 | 11:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-10-04 09:30 | 2019-10-04 13:00 | 3:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
BSRM | BSRM-Hathazari 230 kV line | 2019-10-05 06:10 | 2019-10-05 22:58 | 16:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-10-05 09:16 | 2019-10-05 13:50 | 4:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-BSRM 230 kV line | 2019-10-05 20:44 | 2019-10-05 22:58 | 2:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-10-06 06:26 | 2019-10-06 13:20 | 6:54 | S/O | Due to D/W work | 20 | 138 | Power interruption
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-10-06 09:28 | 2019-10-06 14:33 | 5:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-10-07 10:31 | 2019-10-07 15:23 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-1 | 2019-10-08 08:16 | 2019-10-08 15:45 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV line-1 | 2019-10-09 08:17 | 2019-10-09 17:03 | 8:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rangamati-Kagrachari 132 kV line-2 | 2019-10-10 08:28 | 2019-10-10 15:37 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-10-12 07:23 | 2019-10-12 17:20 | 9:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2019-10-12 06:07 | 2019-10-12 06:27 | 0:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV line-1 | 2019-10-12 16:10 | 2019-10-12 18:50 | 2:40 | S/O | Due to shift of tower conductor | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-10-13 07:05 | 2019-10-13 17:28 | 10:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha(New) | Sikalbaha(New)-Sikalbaha(Old) 132 kV line-1 | 2019-10-13 09:31 | 2019-10-13 12:33 | 3:02 | S/O | Due to tightning loops connection of loop at Sikalbaha (New) | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-2 | 2019-10-13 08:13 | 2019-10-13 14:30 | 6:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line | 2019-10-13 14:40 | 2019-10-13 16:22 | 1:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-10-14 06:52 | 2019-10-14 13:33 | 6:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-2 | 2019-10-14 08:24 | 2019-10-14 14:08 | 5:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 | 2019-10-14 08:04 | 2019-10-14 16:02 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2019-10-15 07:31 | 2019-10-15 18:57 | 11:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-2 | 2019-10-15 08:24 | 2019-10-15 14:08 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2019-10-16 05:33 | 2019-10-16 08:14 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Kagrachari 132 kV line-2 | 2019-10-16 08:44 | 2019-10-16 14:45 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-2 | 2019-10-16 08:08 | 2019-10-16 15:42 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line | 2019-10-17 07:53 | 2019-10-17 16:26 | 8:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line | 2019-10-17 08:10 | 2019-10-17 15:42 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2019-10-18 07:04 | 2019-10-18 13:19 | 6:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalabha(O) | Sikalabha(O)-Sikalbaha (N) 132 kV line-2 | 2019-10-18 07:55 | 2019-10-18 09:50 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-1 | 2019-10-19 07:36 | 2019-10-19 16:07 | 8:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV line-1 | 2019-10-19 08:44 | 2019-10-19 13:01 | 4:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Madunaghat 132 kV line-1 | 2019-10-20 07:25 | 2019-10-20 15:34 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV line-1 | 2019-10-20 08:40 | 2019-10-20 12:52 | 4:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Madunaghat 132 kV line-1 | 2019-10-21 07:14 | 2019-10-21 15:32 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV line-1 | 2019-10-21 08:43 | 2019-10-21 15:12 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Madunaghat 132 kV line-1 | 2019-10-22 07:20 | 2019-10-22 15:28 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chandraghona-Rangamati 132 kV line-1 | 2019-10-22 08:30 | 2019-10-22 14:48 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line | 2019-10-22 08:04 | 2019-10-22 14:07 | 6:03 | S/O | Due to D/W work | 0 | 0 | No interruption
| Juldah-Halishahar 132 kV line | 2019-10-23 08:42 | 2019-10-23 13:43 | 5:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| Juldah-Halishahar 132 kV line | 2019-10-24 08:14 | 2019-10-24 14:24 | 6:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2019-10-24 08:19 | 2019-10-24 14:17 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Abul khair | Abul khair-Hathazari 230 kV line | 2019-10-25 08:27 | 2019-10-25 16:34 | 8:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2019-10-26 07:02 | 2019-10-26 12:59 | 5:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2019-10-27 07:18 | 2019-10-27 14:15 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha(New)-Sikalbaha( O) 132 kV line-1 | 2019-10-27 07:42 | 2019-10-27 13:26 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2019-10-28 07:14 | 2019-10-28 14:30 | 7:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2019-10-29 07:27 | 2019-10-29 16:14 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-1 | 2019-10-29 08:36 | 2019-10-29 14:56 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikabaha | Sikabaha-Madunagaht 132 kV line-2 | 2019-10-30 07:40 | 2019-10-30 14:58 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2019-10-31 08:23 | 2019-10-31 13:31 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 334:50 |  | Unserved Energy: |  | 138
Cumilla Grid Circle :
Ramganj | Ramganj-Desh Energy 132 kV line-2 | 2019-10-05 09:13 | 2019-10-05 10:48 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ramganj-Chowmuhani 132 kV line-1 | 2019-10-05 10:55 | 2019-10-05 11:56 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Baroairhat 132 kV line-1 | 2019-10-11 07:44 | 2019-10-11 18:25 | 10:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Feni-Baroairhat 132 kV line-2 | 2019-10-12 07:37 | 2019-10-12 17:42 | 10:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj -Kishoreganj 132 kV line-1 | 2019-10-21 05:47 | 2019-10-21 19:11 | 13:24 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 36:46 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Faridpur | Faridpur-Madaripur 132 kV line | 2019-10-01 06:31 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur -Shariatpur 132 kV line-1 | 2019-10-02 12:55 | 2019-10-02 17:00 | 4:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madaripur -Shariatpur 132 kV line-2 | 2019-10-02 17:00 | 2019-10-02 21:24 | 4:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV line-2 | 2019-10-15 16:57 | 2019-10-15 16:57 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
Faridpur | Faridpur-Madaripur 132 kV line-2 | 2019-10-16 06:47 | 2019-10-27 15:08 | 272:21 | S/O | Due to reconductoring | 0 | 0 | No interruption
Khulna© | Khulna©-Satkhira 132 kV line-2 | 2019-10-17 12:10 | 2019-10-17 12:02 |  | S/O | Due to D/W work | 0 | 0 | No interruption
| Khulna©-Satkhira 132 kV line-1 | 2019-10-17 12:20 | 2019-10-17 15:08 | 2:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Khulna©-KPCL-2 132 kV line | 2019-10-18 07:29 | 2019-10-18 14:02 | 6:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-Khulna(S) 132 kV line-1 | 2019-10-18 08:23 | 2019-10-18 14:01 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna©-Khulna(S) 132 kV line-2 | 2019-10-21 09:22 | 2019-10-21 15:06 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2019-10-21 11:47 | 2019-10-21 13:09 | 1:22 | S/O | Due to tree trimmimg | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Bheramara 230 kV line-1 | 2019-10-24 08:26 | 2019-10-24 14:14 | 5:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola -Burhanuddin 230 kV line-2 | 2019-10-24 13:37 | 2019-10-24 15:52 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur -Faridpur 132 kV line-1 | 2019-10-28 09:52 | 2019-10-28 09:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 310:58 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ruppur 132 kV line-1 | 2019-10-07 08:11 | 2019-10-07 13:25 | 5:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Bhamrampur 400 kV line-1 | 2019-10-18 10:09 | 2019-10-18 17:35 | 7:26 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Bhamrampur 400 kV line-2 | 2019-10-18 10:11 | 2019-10-18 17:41 | 7:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Jessore | Jessore-Benapole 132 kV line-1 | 2019-10-19 11:33 | 2019-10-19 15:07 | 3:34 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jessore-Benapole 132 kV line-2 | 2019-10-19 15:11 | 2019-10-19 16:16 | 1:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV line | 2019-10-27 08:04 | 2019-10-27 16:31 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Pabna-Ishurdi 132 kV line | 2019-10-28 08:23 | 2019-10-28 17:46 | 9:23 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 42:39 |  | Unserved Energy: |  | 0
Page: 4/4 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: October 2019
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Saidpur | Saidpur-Barapukuria 132 kV line-1 | 2019-10-10 10:19 | 2019-10-10 15:49 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2019-10-11 09:23 | 2019-10-11 16:30 | 5:10 | S/O | Due to maintenance work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-2 |  | 2019-10-13 17:20 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line-1 | 2019-10-14 12:40 | 2019-10-14 17:50 | 5:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria P/S -Barapukuria S/S 132 kV line-1 | 2019-10-17 06:15 | 2019-10-21 16:36 | 106:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-2 |  | 2019-10-17 11:09 | 0:02 | S/O | Due to maintenance work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV line-1 & 2 | 2019-10-17 06:14 | 2019-10-17 06:16 | 0:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura -Mohastangarth 132 kV line-1 | 2019-10-18 10:55 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | Barapukuria S/S-Barapukuria P/S 230 kv line-1 |  | 2019-10-21 20:32 |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura(N) 132 kV line-2 | 2019-10-23 07:06 | 2019-10-23 17:03 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2019-10-23 09:18 | 2019-10-23 17:03 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV line-1 | 2019-10-23 08:15 | 2019-10-23 15:18 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2019-10-24 09:50 | 2019-10-24 17:04 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bogura-Sherpur 132 kV line-2 | 2019-10-27 09:30 | 2019-10-27 15:44 | 6:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-2 | 2019-10-27 08:34 | 2019-10-27 14:58 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-2 | 2019-10-28 08:22 | 2019-10-28 12:07 | 3:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-1 | 2019-10-29 07:44 | 2019-10-29 10:52 | 5:32 | S/O | Due to maintenance work | 15 | 83 | Power interruption
Bogura | Bogura-Sherpur 132 kV line-2 | 2019-10-29 10:42 | 2019-10-29 16:14 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 171:44 |  | Unserved Energy: |  | 83
Others :
Ullon | Ullon-Haripur 132 kV line-2 | 2019-10-04 07:56 | 2019-10-04 19:37 | 11:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ullon-Haripur 132 kV line-2 | 2019-10-05 06:28 | 2019-10-05 09:52 | 3:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2019-10-11 09:37 |  |  | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ullon-Haripur 132 kV line-2 | 2019-10-18 07:01 | 2019-10-18 20:46 | 13:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ullon-Haripur 132 kV line-2 | 2019-10-19 06:44 | 2019-10-19 10:24 | 3:40 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 32:30 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 1905:23 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October' 2019
| Area | Previous Month (September 2019) |  |  |  | Current Month (October 2019)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 15 | 7 | 48 | 70 | 9 | 4 | 60 | 73
2 | Dhaka (South) Grid Circle. | 16 | 9 | 32 | 57 | 5 | 5 | 27 | 37
3 | Chattogram Grid Circle. | 11 | 10 | 20 | 41 | 9 | 4 | 64 | 77
4 | Cumilla Grid Circle. | 13 | 8 | 25 | 46 | 8 | 3 | 24 | 35
5 | Khulna Grid Circle. | 13 | 3 | 23 | 39 | 14 | 2 | 35 | 51
6 | Bheramara HVDC Grid Circle | 8 | 6 | 13 | 27 | 1 | 2 | 12 | 15
7 | Bogura Grid Circle. | 12 | 13 | 53 | 78 | 8 | 10 | 91 | 109
8 | Others | 2 |  |  | 2 | 2 |  | 6 | 8
9 | Total | 90 | 56 | 214 | 360 | 56 | 30 | 319 | 405
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October' 2019
| Area | Previous Month (September 2019) |  |  |  | Current Month (October 2019)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 661.25 | 304.41 | 498.67 | 1464.33 | 67.77 | 88.25 | 773.9 | 929.92
2 | Dhaka (South) Grid Circle. | 137.41 | 73.33 | 99 | 309.74 | - | 33 | - | 33
3 | Chattogram Grid Circle. | 76.8 | 147.58 | 380.8 | 605.18 | 56.82 | 195.75 | 214.73 | 467.3
4 | Cumilla Grid Circle. | 7.9333 | 119.05 | - | 126.9833 | 29.87 | 50.4 | 128.2367 | 208.5067
5 | Khulna Grid Circle. | 245.38 | 7.4 | 118.67 | 371.45 | 204.62 | 76.5 | 344.87 | 625.99
6 | Bheramara HVDC Grid Circle | 355.5 | 17.03 | 84.8 | 457.33 |  | 59.23 | 240.15 | 299.38
7 | Bogura Grid Circle. | 300.29 | 516.42 | 294.5 | 1111.21 | 892.37 | 69.57 | 244.58 | 1206.52
8 | Others | 6.5 | - | - | 6.5 | 23.33 | - | - | 23.33
9 | Total | 1791.0633 | 1185.22 | 1476.44 | 4452.7233 | 1274.78 | 572.7 | 1946.4667 | 3793.9467
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October' 2019
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 4 | 3 | 7 |  | 1 | 3 | 837.59
2 | Dhaka (South) | 5031.6 | 1 |  | 1 |  | 1 |  | 33
3 | Chattogram | 2042 | 3 | 2 | 5 | 1 | 1 | 3 | 290.58
4 | Khulna | 2434 | 5 | 4 | 9 | 3 | 1 | 5 | 549.49
5 | Bheramara (HVDC) | 2423.3 | 2 | 2 | 4 |  |  | 4 | 299.38
6 | Bogura | 3145.6 | 2 | 5 | 7 | 1 | 1 | 5 | 1060.7
7 | Cumilla | 2981 | 4 | 2 | 6 | 1 | 3 | 2 | 197.5367
8 | Others | -
| Total | 23365.5 | [6 empty] | 3268.2767
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.89%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October' 2019
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) |  | 1 | 1 |  |  | 1 | 92.33
2 | Dhaka (South) | 990.29
3 | Chattogram | 917 | 20+9(Partial) | 3 | 1 | 4 | 2 | - | 2 | 176.72
4 | Khulna | 1238.4 | 21 | 2 |  | 2 |  | 1 | 1 | 76.5
5 | Bheramara (HVDC) | 598.7 |  | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | 38 | 2 | 1 | 3 | 1 |  | 2 | 145.82
7 | Cumilla | 1648.16 | 17 | 2 | - | 2 | 2 | - | - | 10.97
7 | Others | - |  | 1 |  | 1 | 1 |  |  | 23.33
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 525.67
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.63%
3 | Chattogram | 99.96%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.99% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October' 2019
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2019-10-18 | 12 |  | 1 | 33min | 3 | 2hr30min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:October' 2019
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kadda | 1 | 2:03 | 30 | 61.5 | Due to tripping of 132/33 kV Transformer T3
Kabirpur | 1 | 1:09 | 70 | 80.5 | Due to red-hot maintenance of 132/33 kV Transformer T2
Mymensingh | 1 | 0:47 | 8 | 6.2667 | Due to tripping of 132/33 kV Transformer T3
Jamalpur | 1 | 1:33 | 5 | 7.75 | Due to red-hot maintenance of 132/33 kV Transformer T4
Kadda | 1 | 2:47 | 177 | 492.65 | Due to S/D of 33 kV Bus
Kishoreganj | 1 | 2:51 | 45 | 128.25 | Due to tripping of 132/33 kV Transformer T2
Valuka | 1 | 4:40 | 13 | 60.6667 | Due to S/D of 132/33 kV Transformer T2 & 33 kV Bus
Kaliakoir | 1 | 4:37 | 20 | 92.3333 | Due to S/D of Kaliakoir-Kabirpur 132 kv line-1
Hasnabad | 1 | 0:33 | 60 | 33 | Due to flashing of 132 kV reserve Bus
Madunaghat | 1 | 0:51 | 25 | 21.25 | Due to red-hot maintenance of 132/33 kV Transformer T1
Khulshi | 1 | 5:49 | 30 | 174.5 | Due to bursting of PT
Hathazari | 1 | 3:01 | 6 | 18.1 | Due to tripping of 230/132 kV Transformer MT3
Dohazari | 1 | 0:23 | 11 | 4.2167 | Due to tripping of Dohazari-Cox'sbazar 132 kV line
Rangamati | 1 | 0:18 | 15 | 4.5 | Due to tripping of Rangamati-Kagrachari 132 kV line
Dohazari | 1 | 2:00 | 15 | 30 | Due to tripping of Dohazari-Cox'sbazar 132 kV line
Khulshi | 1 | 1:20 | 40 | 53.3333 | Due to S/D of 132/33 kV Transformers T2
Dohazari | 2 | 0:27 | 52 | 23.4 | Due to S/D of 33 Kv Bus
|  | 6:54 | 20 | 138 | Due to S/D of Dohazari-Cox'sbazar 132 kV line
Cumilla (S) | 1 | 1:08 | 30 | 34 | Due to red-hot maintenance of 132/33 kV Transformer T1
Feni |  | 0:42 | 25 | 17.5 | Due to tripping of 132/33 kV Transformers T1 & T2
B.Baria | 1 | 0:41 | 24 | 16.4 | Due to tripping of 132/33 kV Transformers T2 ,&,T3
Chatek | 3 | 0:14 | 6 | 1.4 | Due to tripping of 132/33 kV Transformer T2
|  | 0:18 | 21 | 6.3 | Due to tripping of Chatak-Sunamganj 132 kV line
|  | 0:20 | 14 | 4.6667
Sylhet | 1 | 1:42 | 61 | 103.7 | Due to S/D of 132/33 kV Transformer T4
Cumilla(N) | 1 | 0:32 | 46 | 24.5333 | Due to S/D of 132/33 kV Transformers T3 & T4
Barisal | 1 | 7:35 | 15 | 113.75 | Due to tripping of 132/33 kV Transformer T1
Bagerhat | 2 | 0:20 | 8 | 2.6667 | Due to tripping of 132/33 kV Transformer T2
|  | 0:13 | 12 | 2.6 | Due to tripping of 132/33 kV Transformer T1
Faridpur | 1 | 2:00 | 40 | 80 | Due to tripping of 132/33 kV Transformer T2 & 33 kV Bus
Mongla | 2 | 0:24 | 14 | 5.6 | Due to tripping of 132/33 kV Transformer T2
Gopalganj | 1 | 1:00 | 40 | 40 | Due to tripping of Gopalganj -Madaripur 132 kV line
Barishal | 1 | 1:13 | 30 | 36.5 | Due to red-hot maintenance of Barishal -Patuakhali 132 kV line
Madaripur | 1 | 1:01 | 20 | 20.3333 | Due to S/D of 132/33 kV Transformer T2 & 33 kV Bus
Patuakhali |  | 0:32 | 21 | 11.2 | Due to S/D of 132/33 kV Transformer T2
Khulna© | 1 | 1:49 | 50 | 90.8333 | Due to S/D of 132/33 kV Transformer T1
Barishal(N) | 1 | 7:25 | 30 | 222.5 | Due to S/D of 132/33 kV Transformer T4
Jhenidah | 1 | 1:06 | 29 | 31.9 | Due to red hot maintenance of 132/33 kV Transformer T5
Bottail | 1 | 1:22 | 20 | 27.3333 | Due to red-hot maintenance of 132/33 kV Transformer T1
Ishurdi | 1 | 6:49 | 30 | 204.5 | Due to S/D of 132 kV Bus-2
Bottail |  | 1:33 | 23 | 35.65 | Due to S/D of 33 kV Bus-1
Palashbari | 1 | 2:03 | 15 | 30.75 | Due to red-hot maintenance of 13233 kV Transformers T3 & T4
Barapukuria | 1 | 0:12 | 478 | 868.3667 | Due to tripping of 230/132 kV Transformer T6
Natore | 1 | 0:17 | 137 | 38.8167 | Due to bursting of R-phase CT
Bogura | 1 | 1:12 | 20 | 24 | Due to tripping of Bogura -Sherpur 132 kV line-1 & 2
Naogaon | 1 | 1:17 | 20 | 25.6667 | Due to S/D of 132/33 kV Transformer T3
Barapukuria | 2 | 4:30 | 8 | 36 | Due to S/D of 230/132 kV Transformer TR2
|  | 1:00 | 8 | 8
Rangpur | 1 | 12:05 | 5 | 60.4167 | Due to S/D of 132/33 kV Transformer T2
C.nawabganj | 1 | 1:03 | 30 | 31.5 | Due to S/D of 132 kV mian Bus
Saidpur | 1 | 5:32 | 15 | 83 | Due to S/D of Saidpur-Purbasadipur 132 kV line
Ullon |  | 0:14 | 100 | 23.3333 | Due to tripping of Ullon-Dhanmondi 132 kV line
| Total Unserved energy : |  |  | 3793.9333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 134 | 15 | 2019-10-03 | 1900
2 | Munsiganj | 118 | 17 | 2019-10-03 | 2000
3 | Sonargaon | 90 | 17 | 2019-10-03 | 1900
4 | Shyampur | 200 | 3 | 2019-10-03 | 4:00
5 | Bhulta | 189 | 19 | 2019-10-03 | 1930
6 | Madanganj | 64 | 18 | 2019-10-03 | 2300
7 | Shitalakhya | 120 | 21 | 2019-10-03 | 1200
8 | Rahim steel | 27 | 15 | 2019-10-03 | 1000
9 | Matuail | 98 | 23 | 2019-10-03 | 900
10 | Ghorasal | 85 | 15 | 2019-10-03 | 1830
11 | Narsingdi | 147 | 7 | 2019-10-03 | 1930
12 | Haripur (SBU) | 105 | 21 | 2019-10-03 | 1800
13 | Ullon | 89 | 21 | 2019-10-03 | 1700
14 | Hasnabad | 211 | 22 | 2019-10-03 | 2000
15 | Magbazar | 129 | 23 | 2019-10-03 | 1100
16 | Maniknagar | 125 | 14 | 2019-10-03 | 1300
17 | Bangabhaban | 36 | 3 | 2019-10-03 | 1000
18 | Narinda | 104 | 20 | 2019-10-03 | 1800
19 | Dhanmondi | 179 | 21 | 2019-10-03 | 1300
20 | Lalbag | 88 | 7 | 2019-10-03 | 1300
21 | Madartek | 67 | 5 | 2019-10-03 | 1900
22 | Mirpur | 112 | 20 | 2019-10-03 | 1830
23 | Kalyanpur | 120 | 5 | 2019-10-03 | 1800
24 | Gulshan | 164 | 15 | 2019-10-03 | 1300
25 | Uttara | 82 | 3 | 2019-10-03 | 1830
26 | Uttara(new) | 45 | 15 | 2019-10-03 | 1400
27 | Kamrangirchar | 84 | 2 | 2019-10-03 | 1830
28 | Savar | 157 | 20 | 2019-10-03 | 1800
29 | Bhasantec | 164 | 3 | 2019-10-03 | 1800
30 | Agargaon | 62 | 21 | 2019-10-03 | 1300
31 | Satmosjid | 117 | 19 | 2019-10-03 | 1800
32 | Tongi | 158 | 19 | 2019-10-03 | 1500
33 | Kabirpur | 237 | 21 | 2019-10-03 | 1830
34 | Basundhara | 142 | 21 | 2019-10-03 | 1800
35 | Manikganj | 96 | 4 | 2019-10-03 | 1930
36 | Joydevpur | 241 | 22 | 2019-10-03 | 1900
37 | New Tongi | 271 | 15 | 2019-10-03 | 1830
38 | Kodda | 271 | 15 | 2019-10-03 | 1830
39 | Dhamrai | 70 | 20 | 2019-10-03 | 1900
40 | Valuka | 126 | 19 | 2019-10-03 | 1800
41 | Tangail | 196 | 5 | 2019-10-03 | 1930
42 | Mymensing | 232 | 3 | 2019-10-03 | 1830
43 | Kishorganj | 128 | 19 | 2019-10-03 | 19:30
44 | Netrokona | 99 | 19 | 2019-10-03 | 1900
45 | Jamalpur | 126 | 4 | 2019-10-03 | 1900
46 | Sherpur | 96 | 3 | 2019-10-03 | 2100
47 | Srimongal | 39 | 17 | 2019-10-03 | 1830
48 | Shahjibazar | 120 | 20 | 2019-10-03 | 1930
49 | Fenchuganj | 42 | 21 | 2019-10-03 | 1800
50 | Kulawara | 48 | 17 | 2019-10-03 | 1830
51 | Sylhet | 143 | 19 | 2019-10-03 | 1900
52 | Chatak | 34 | 19 | 2019-10-03 | 1800
53 | Sunamganj | 41 | 18 | 2019-10-03 | 1900
54 | Bianibazar | 64 | 15 | 2019-10-03 | 1830
55 | Cumilla (S) | 184 | 21 | 2019-10-03 | 1930
56 | Cumilla(N) | 157 | 8 | 2019-10-03 | 1830
57 | Chandpur | 142 | 20 | 2019-10-03 | 1800
58 | Feni | 142 | 20 | 2019-10-03 | 2000
59 | Chowmuhani | 172 | 21 | 2019-10-03 | 1830
60 | Ashuganj | 128 | 15 | 2019-10-03 | 2000
61 | Daudkandi | 142 | 4 | 2019-10-03 | 1930
62 | B.Baria | 135 | 22 | 2019-10-03 | 1930
63 | Ramganj | 90 | 21 | 2019-10-03 | 1930
64 | Madanhat | 102 | 19 | 2019-10-03 | 1930
65 | Hathazari | 102 | 19 | 2019-10-03 | 1930
66 | Khulshi | 200 | 26 | 2019-10-03 | 1800
67 | Halishahar | 153 | 20 | 2019-10-03 | 1500
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:October'2019
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
68 | Baraulia | 121 | 11 | 2019-10-03 | 1300
69 | Sikalbaha | 38 | 19 | 2019-10-03 | 1830
70 | Dohazari | 96 | 22 | 2019-10-03 | 1830
71 | Cox'sbazar | 97 | 19 | 2019-10-03 | 1830
72 | Chandraghona | 36 | 9 | 2019-10-03 | 1930
73 | Kaptai | 5 | 16 | 2019-10-03 | 1800
74 | A. Khaer Stl. | 8 | 18 | 2019-10-03 | 1830
75 | Bakulia | 115 | 16 | 2019-10-03 | 1830
76 | Julda | 24 | 23 | 2019-10-03 | 1100
77 | TK chemical | 18 | 5 | 2019-10-03 | 1900
78 | Modern Steel | 29 | 18 | 2019-10-03 | 100
79 | Shahmirpur | 32 | 7 | 2019-10-03 | 1830
80 | Khagrachhari | 29 | 18 | 2019-10-03 | 1830
81 | Matarbari | 31 | 4 | 2019-10-03 | 1900
82 | Baroiar Hat | 34 | 3 | 2019-10-03 | 1830
83 | Rangamati | 18 | 7 | 2019-10-03 | 1830
84 | Abul Khair 230 | 152 | 5 | 2019-10-03 | 800
85 | BSRM | 111 | 2 | 2019-10-03 | 1600
86 | GPH Ispat | 14 | 31 | 2019-10-03 | 2600
87 | Goalpara | 38 | 5 | 2019-10-03 | 1930
88 | Central s/s | 105 | 17 | 2019-10-03 | 1900
89 | Noapara | 87 | 26 | 2019-10-03 | 1830
90 | Jashore | 124 | 15 | 2019-10-03 | 1900
91 | Benapol | 40 | 1 | 2019-10-03 | 1830
92 | Jhenidah | 106 | 20 | 2019-10-03 | 1800
93 | Bottail | 128 | 2 | 2019-10-03 | 1830
94 | G.K Project | 59 | 15 | 2019-10-03 | 1900
95 | Faridpur | 174 | 20 | 2019-10-03 | 1900
96 | Madaripur | 89 | 4 | 2019-10-03 | 1900
97 | Sariatpur | 60 | 19 | 2019-10-03 | 2000
98 | Gopalganj | 89 | 19 | 2019-10-03 | 2200
99 | Bagerhat | 89 | 19 | 2019-10-03 | 1830
100 | Mongla | 83 | 9 | 2019-10-03 | 1400
101 | Satkhira | 100 | 5 | 2019-10-03 | 1930
102 | Gallamari | 49 | 3 | 2019-10-03 | 1300
103 | Magura | 51 | 2 | 2019-10-03 | 1830
104 | Norail | 28 | 3 | 2019-10-03 | 800
105 | Chuadanga | 86 | 20 | 2019-10-03 | 1830
106 | Barsal(N) | 45 | 17 | 2019-10-03 | 2100
107 | Barsal(S) | 106 | 20 | 2019-10-03 | 1830
108 | Patuakhali | 110 | 20 | 2019-10-03 | 2100
109 | Bhandaria | 54 | 20 | 2019-10-03 | 1900
110 | Borhan Uddin | 38 | 5 | 2019-10-03 | 2100
111 | Ishurdi | 62 | 20 | 2019-10-03 | 1900
112 | Ruppur Paromanobik | 2 | 1 | 2019-10-03 | 700
113 | Natore | 119 | 5 | 2019-10-03 | 2000
114 | Bogura | 188 | 16 | 2019-10-03 | 1930
115 | Naogaon | 108 | 7 | 2019-10-03 | 2000
116 | Rajshahi | 132 | 2 | 2019-10-03 | 1930
117 | Rajshahi New | 12 | 15 | 2019-10-03 | 1930
118 | C.Nawabganj | 79 | 22 | 2019-10-03 | 2000
119 | Amnura | 33 | 4 | 2019-10-03 | 1930
120 | Pabna | 116 | 5 | 2019-10-03 | 1930
121 | Shahjadpur | 106 | 15 | 2019-10-03 | 1900
122 | Serajganj | 95 | 15 | 2019-10-03 | 1900
123 | Niyamatpur | 59 | 3 | 2019-10-03 | 1830
124 | Joypurhat | 54 | 16 | 2019-10-03 | 1900
125 | Sherpur(Bogura) | 43 | 5 | 2019-10-03 | 1900
126 | Mohastangar | 16 | 5 | 2019-10-03 | 1900
127 | Rangpur | 138 | 16 | 2019-10-03 | 1830
128 | Lalmonirhat | 66 | 3 | 2019-10-03 | 2000
129 | Saidpur | 104 | 16 | 2019-10-03 | 2000
130 | Purbasadipur | 93 | 15 | 2019-10-03 | 100
131 | Thakurgaon | 71 | 4 | 2019-10-03 | 2000
132 | Palshbari | 114 | 5 | 2019-10-03 | 1800
133 | Barapukuria | 50 | 15 | 2019-10-03 | 2000
134 | Panchugar | 46 | 22 | 2019-10-03 | 1800
135 | Joldhaka | 24 | 3 | 2019-10-03 | 2000
136 | Kurigram | 41 | 22 | 2019-10-03 | 1830
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:October' 2019
Area | MW | Date | Hour | Remarks
Dhaka | 4259 | 21.10.19 | 18:30
Chattogram | 1255 | 01.10.19 | 19:00
Khulna | 1427 | 20.10.19 | 18:30
Rajshahi | 1190 | 02.10.19 | 20:00
Cumilla | 1112 | 21.10.19 | 19:30
Mymensingh | 934 | 20.10.19 | 19:00
Sylhet | 494 | 14.10.19 | 19:00
Barisal | 341 | 20.10.19 | 21:00
Rangpur | 714 | 16.10.19 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2019
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 383 | 400 | 20 | 2019-10-03 | 7:00 | 373 | 3 | 2019-10-03 | 11:00
2 | Bheramara | 388 | 409 | 1 | 2019-10-03 | 9:00 | 211 | 20 | 2019-10-03 | 12:00
3 | Ashuganj(N) | 376 | 382 | 22 | 2019-10-03 | 18:30 | 359 | 8 | 2019-10-03 | 12:00
4 | Kaliakoir | 400 | 378 | 20 | 2019-10-03 | 20:00 | 347 | 1 | 2019-10-03 | 11:00
5 | Bhulta | 400 | 384 | 20 | 2019-10-03 | 1:00 | 354 | 15 | 2019-10-03 | 15:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 5 | 2019-10-03 | 21:00 | 220 | 3 | 2019-10-03 | 8:00
2 | Ishurdi | 230 | 237 | 14 | 2019-10-03 | 6:00 | 225 | 2 | 2019-10-03 | 11:00
3 | Ashuganj | 230 | 232 | 5 | 2019-10-03 | 21:00 | 220 | 3 | 2019-10-03 | 12:00
4 | Serajganj | 230 | 233 | 28 | 2019-10-03 | 3:00 | 222 | 2 | 2019-10-03 | 15:00
5 | Baghabari | 230 | 238 | 29 | 2019-10-03 | 2:00 | 228 | 2 | 2019-10-03 | 10:00
6 | Barapukuria | 230 | 238 | 1 | 2019-10-03 | 3:00 | 219 | 17 | 2019-10-03 | 18:00
7 | Bogra | 230 | 234 | 29 | 2019-10-03 | 5:00 | 216 | 2 | 2019-10-03 | 19:00
8 | Khulna South | 230 | 238 | 26 | 2019-10-03 | 2:00 | 206 | 24 | 2019-10-03 | 11:00
9 | Rampura | 230 | 222 | 26 | 2019-10-03 | 4:00 | 205 | 15 | 2019-10-03 | 15:00
10 | Haripur | 230 | 221 | 25 | 2019-10-03 | 13:00 | 207 | 15 | 2019-10-03 | 15:00
11 | Hasnabad | 230 | 222 | 26 | 2019-10-03 | 3:00 | 203 | 15 | 2019-10-03 | 13:00
12 | Aminbazar | 230 | 226 | 22 | 2019-10-03 | 2:00 | 205 | 3 | 2019-10-03 | 11:00
13 | Tongi | 230 | 222 | 26 | 2019-10-03 | 6:00 | 203 | 1 | 2019-10-03 | 12:00
14 | Comilla (N) | 230 | 228 | 26 | 2019-10-03 | 7:00 | 217 | 9 | 2019-10-03 | 11:00
15 | Hathazari | 230 | 221 | 10 | 2019-10-03 | 19:00 | 209 | 9 | 2019-10-03 | 9:00
16 | Megnaghat | 230 | 223 | 26 | 2019-10-03 | 3:00 | 208 | 15 | 2019-10-03 | 11:00
17 | Fenchuganj | 230 | 237 | 26 | 2019-10-03 | 3:00 | 227 | 1 | 2019-10-03 | 12:00
18 | Siddhirganj | 230 | 224 | 26 | 2019-10-03 | 4:00 | 206 | 15 | 2019-10-03 | 15:00
19 | Maniknagar | 230 | 222 | 26 | 2019-10-03 | 4:00 | 205 | 15 | 2019-10-03 | 11:00
20 | Old Airport | 230 | 223 | 26 | 2019-10-03 | 4:00 | 203 | 3 | 2019-10-03 | 11:00
21 | Barisal | 230 | 236 | 20 | 2019-10-03 | 16:00 | 217 | 3 | 2019-10-03 | 12:00
22 | AKSML | 230 | 218 | 24 | 2019-10-03 | 17:00 | 204 | 9 | 2019-10-03 | 9:00
23 | BSRM | 230 | 219 | 24 | 2019-10-03 | 18:00 | 207 | 15 | 2019-10-03 | 5:00
24 | Bibiyana | 230 | 234 | 26 | 2019-10-03 | 6:00 | 211 | 20 | 2019-10-03 | 11:00
25 | Bhulta | 230 | 229 | 20 | 2019-10-03 | 1:00 | 207 | 15 | 2019-10-03 | 15:00
26 | Ashuganj (S) | 230 | 232 | 5 | 2019-10-03 | 19:30 | 210 | 20 | 2019-10-03 | 12:00
27 | Kaliakoir | 230 | 229 | 20 | 2019-10-03 | 20:00 | 208 | 5 | 2019-10-03 | 16:00
28 | GPH | 230 | 216 | 21 | 2019-10-03 | 20:00 | 207 | 26 | 2019-10-03 | 12:00
132 kV Substation
1 | Siddhirganj | 132 | 134 | 25 | 2019-10-03 | 1500 | 123 | 15 | 2019-10-03 | 1000
2 | Munsiganj | 132 | 135 | 16 | 2019-10-03 | 2000 | 122 | 15 | 2019-10-03 | 1000
3 | Megnaghat | 132 | 131 | 25 | 2019-10-03 | 1300 | 122 | 5 | 2019-10-03 | 1100
4 | Shyampur | 132 | 136 | 25 | 2019-10-03 | 19:00 | 124 | 1 | 2019-10-03 | 1100
5 | Bhulta | 132 | 128 | 25 | 2019-10-03 | 1300 | 113 | 13 | 2019-10-03 | 1100
6 | Madanganj | 132 | 136 | 8 | 2019-10-03 | 1900 | 121 | 1 | 2019-10-03 | 1100
7 | Shitalakhya | 132 | 138 | 22 | 2019-10-03 | 1900 | 122 | 15 | 2019-10-03 | 900
8 | Rahim Steal | 132 | 134 | 25 | 2019-10-03 | 1300 | 124 | 15 | 2019-10-03 | 1000
9 | Matuail | 132 | 133 | 25 | 2019-10-03 | 1300 | 121 | 23 | 2019-10-03 | 1200
10 | Ghorasal | 132 | 138 | 14 | 2019-10-03 | 100 | 130 | 2 | 2019-10-03 | 1200
11 | Narsinghdi | 132 | 134 | 25 | 2019-10-03 | 1500 | 122 | 13 | 2019-10-03 | 1100
12 | Haripur (SBU) | 132 | 135 | 25 | 2019-10-03 | 1930 | 125 | 1 | 2019-10-03 | 1000
13 | Ullon | 132 | 137 | 24 | 2019-10-03 | 600 | 122 | 15 | 2019-10-03 | 1500
14 | Hasnabad | 132 | 136 | 11 | 2019-10-03 | 800 | 124 | 1 | 2019-10-03 | 1100
15 | Magbazar | 132 | 137 | 24 | 2019-10-03 | 600 | 123 | 15 | 2019-10-03 | 1100
16 | Maniknagar | 132 | 138 | 25 | 2019-10-03 | 800 | 121 | 19 | 2019-10-03 | 1100
17 | Bangabhaban | 132 | 138 | 25 | 2019-10-03 | 800 | 121 | 19 | 2019-10-03 | 1100
18 | Narinda | 132 | 138 | 25 | 2019-10-03 | 800 | 121 | 19 | 2019-10-03 | 1100
19 | Dhanmondi | 132 | 137 | 24 | 2019-10-03 | 600 | 122 | 15 | 2019-10-03 | 1500
20 | Lalbag | 132 | 136 | 25 | 2019-10-03 | 1800 | 120 | 23 | 2019-10-03 | 1200
21 | Madartek | 132 | 137 | 25 | 2019-10-03 | 700 | 121 | 15 | 2019-10-03 | 1300
22 | Mirpur | 132 | 135 | 24 | 2019-10-03 | 700 | 123 | 17 | 2019-10-03 | 1600
23 | Kalyanpur | 132 | 138 | 25 | 2019-10-03 | 300 | 125 | 1 | 2019-10-03 | 1100
24 | Gulshan | 132 | 137 | 24 | 2019-10-03 | 500 | 121 | 9 | 2019-10-03 | 1100
25 | Uttara | 132 | 135 | 25 | 2019-10-03 | 500 | 120 | 6 | 2019-10-03 | 1000
26 | Uttara(New) | 132 | 136 | 8 | 2019-10-03 | 1830 | 121 | 30 | 2019-10-03 | 1000
27 | Kamrangirchar | 132 | 135 | 25 | 2019-10-03 | 500 | 120 | 1 | 2019-10-03 | 1200
28 | Savar | 132 | 136 | 25 | 2019-10-03 | 500 | 122 | 19 | 2019-10-03 | 1200
29 | Bhasantec | 132 | 137 | 24 | 2019-10-03 | 500 | 124 | 9 | 2019-10-03 | 1100
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
30 | Agargaon | 132 | 140 | 24 | 2019-10-03 | 1800 | 126 | 9 | 2019-10-03 | 1200
31 | Satmosjid | 132 | 138 | 24 | 2019-10-03 | 600 | 123 | 16 | 2019-10-03 | 1700
32 | Tongi | 132 | 135 | 10 | 2019-10-03 | 1800 | 123 | 1 | 2019-10-03 | 800
33 | Kabirpur | 132 | 137 | 25 | 2019-10-03 | 1900 | 118 | 29 | 2019-10-03 | 1100
34 | Basundhara | 132 | 135 | 11 | 2019-10-03 | 800 | 120 | 29 | 2019-10-03 | 1100
35 | Manikganj | 132 | 139 | 10 | 2019-10-03 | 1830 | 124 | 1 | 2019-10-03 | 200
36 | Joydevpur | 132 | 140 | 29 | 2019-10-03 | 1830 | 125 | 20 | 2019-10-03 | 1200
37 | New Tongi | 132 | 134 | 16 | 2019-10-03 | 1830 | 122 | 1 | 2019-10-03 | 800
38 | Kodda | 132 | 140 | 10 | 2019-10-03 | 1900 | 117 | 1 | 2019-10-03 | 800
39 | Dhamrai | 132 | 135 | 24 | 2019-10-03 | 1800 | 120 | 6 | 2019-10-03 | 400
40 | Valuka | 133 | 133 | 25 | 2019-10-03 | 1900 | 112 | 21 | 2019-10-03 | 1800
41 | Tangail | 132 | 135 | 9 | 2019-10-03 | 1400 | 120 | 6 | 2019-10-03 | 1100
42 | Mymensing | 132 | 137 | 25 | 2019-10-03 | 1900 | 117 | 21 | 2019-10-03 | 1100
43 | Kishorganj | 132 | 135 | 25 | 2019-10-03 | 1930 | 116 | 21 | 2019-10-03 | 1800
44 | Netrokona | 132 | 136 | 25 | 2019-10-03 | 1900 | 114 | 8 | 2019-10-03 | 1800
45 | Jamalpur | 132 | 140 | 5 | 2019-10-03 | 1800 | 114 | 14 | 2019-10-03 | 1100
46 | Sherpur | 132 | 139 | 14 | 2019-10-03 | 1830 | 114 | 12 | 2019-10-03 | 1200
47 | Srimongal | 132 | 140 | 25 | 2019-10-03 | 1900 | 130 | 27 | 2019-10-03 | 1700
48 | Shahjibazar | 132 | 139 | 25 | 2019-10-03 | 1900 | 130 | 1 | 2019-10-03 | 1200
49 | Fenchuganj | 132 | 136 | 25 | 2019-10-03 | 1900 | 124 | 30 | 2019-10-03 | 2400
50 | Khulawara | 132 | 136 | 25 | 2019-10-03 | 1830 | 126 | 16 | 2019-10-03 | 1800
51 | Sylhet | 132 | 135 | 16 | 2019-10-03 | 800 | 122 | 29 | 2019-10-03 | 900
52 | Chattak | 132 | 135 | 28 | 2019-10-03 | 100 | 122 | 16 | 2019-10-03 | 1800
53 | Sunamganj | 132 | 134 | 5 | 2019-10-03 | 1400 | 120 | 16 | 2019-10-03 | 1800
54 | Biani Bazar | 132 | 134 | 18 | 2019-10-03 | 1000 | 121 | 16 | 2019-10-03 | 1800
55 | Comilla(South) | 132 | 128 | 1 | 2019-10-03 | 700 | 117 | 20 | 2019-10-03 | 1800
56 | Comilla (North) | 132 | 135 | 2 | 2019-10-03 | 2100 | 127 | 4 | 2019-10-03 | 1930
57 | Chandpur | 132 | 135 | 10 | 2019-10-03 | 1900 | 124 | 4 | 2019-10-03 | 1900
58 | Feni | 132 | 128 | 4 | 2019-10-03 | 700 | 118 | 4 | 2019-10-03 | 2000
59 | Chowmuhani | 132 | 126 | 4 | 2019-10-03 | 800 | 112 | 4 | 2019-10-03 | 1830
60 | Ashuganj | 132 | 140 | 25 | 2019-10-03 | 1900 | 131 | 15 | 2019-10-03 | 1800
61 | Daudkandi | 132 | 132 | 25 | 2019-10-03 | 900 | 121 | 8 | 2019-10-03 | 2300
62 | Brahminbaria | 132 | 135 | 24 | 2019-10-03 | 1800 | 126 | 4 | 2019-10-03 | 2100
63 | Ramganj | 132 | 127 | 24 | 2019-10-03 | 1800 | 110 | 11 | 2019-10-03 | 1800
64 | Madanhat | 132 | 133 | 6 | 2019-10-03 | 700 | 126 | 9 | 2019-10-03 | 900
65 | Hathazari | 132 | 132 | 10 | 2019-10-03 | 1900 | 125 | 9 | 2019-10-03 | 900
66 | Khulshi | 132 | 130 | 2 | 2019-10-03 | 2000 | 121 | 9 | 2019-10-03 | 1500
67 | Halishahar | 132 | 134 | 10 | 2019-10-03 | 1900 | 113 | 8 | 2019-10-03 | 1900
68 | Baraulia | 132 | 130 | 1 | 2019-10-03 | 1930 | 121 | 9 | 2019-10-03 | 1000
69 | Sikalbaha | 132 | 134 | 2 | 2019-10-03 | 2200 | 124 | 29 | 2019-10-03 | 900
70 | Dohazari | 132 | 132 | 9 | 2019-10-03 | 1830 | 122 | 25 | 2019-10-03 | 2100
71 | Cox'sbazar | 132 | 129 | 11 | 2019-10-03 | 900 | 110 | 19 | 2019-10-03 | 1000
72 | Chandraghona | 132 | 132 | 2 | 2019-10-03 | 1930 | 124 | 30 | 2019-10-03 | 1500
73 | Kaptai | 132 | 132 | 1 | 2019-10-03 | 1930 | 125 | 9 | 2019-10-03 | 1100
74 | A. Khaer Stl. | 132 | 130 | 2 | 2019-10-03 | 1930 | 123 | 17 | 2019-10-03 | 1000
75 | Bakulia | 132 | 132 | 3 | 2019-10-03 | 300 | 122 | 29 | 2019-10-03 | 900
76 | Julda | 132 | 132 | 2 | 2019-10-03 | 1930 | 124 | 25 | 2019-10-03 | 1400
77 | TK Chemical | 132 | 133 | 16 | 2019-10-03 | 1900 | 124 | 29 | 2019-10-03 | 700
78 | Modern Steel | 132 | 133 | 10 | 2019-10-03 | 1900 | 122 | 30 | 2019-10-03 | 300
79 | Shahmirpur | 132 | 132 | 2 | 2019-10-03 | 1930 | 124 | 25 | 2019-10-03 | 1600
80 | Khagrachhari | 132 | 136 | 2 | 2019-10-03 | 700 | 123 | 30 | 2019-10-03 | 400
81 | Matarbari | 132 | 133 | 3 | 2019-10-03 | 200 | 112 | 30 | 2019-10-03 | 300
82 | Baroiar Hat | 132 | 130 | 18 | 2019-10-03 | 600 | 120 | 4 | 2019-10-03 | 1800
83 | Rangamati | 133 | 132 | 7 | 2019-10-03 | 1400 | 119 | 11 | 2019-10-03 | 1400
84 | Goalpara | 132 | 140 | 18 | 2019-10-03 | 900 | 123 | 3 | 2019-10-03 | 1200
85 | Khulna Central | 132 | 139 | 18 | 2019-10-03 | 800 | 122 | 19 | 2019-10-03 | 1100
86 | Noapara | 132 | 138 | 18 | 2019-10-03 | 900 | 121 | 3 | 2019-10-03 | 1100
87 | Jessore | 132 | 136 | 19 | 2019-10-03 | 1700 | 117 | 1 | 2019-10-03 | 1830
88 | Benapol | 132 | 136 | 24 | 2019-10-03 | 1600 | 119 | 10 | 2019-10-03 | 2000
89 | Jhenida | 132 | 138 | 14 | 2019-10-03 | 600 | 114 | 10 | 2019-10-03 | 1930
90 | Bottail | 132 | 138 | 25 | 2019-10-03 | 500 | 125 | 12 | 2019-10-03 | 1830
91 | G.K Project | 132 | 145 | 7 | 2019-10-03 | 2000 | 128 | 30 | 2019-10-03 | 900
92 | Faridpur | 132 | 135 | 18 | 2019-10-03 | 800 | 120 | 5 | 2019-10-03 | 1900
93 | Madaripur | 132 | 138 | 23 | 2019-10-03 | 1800 | 120 | 12 | 2019-10-03 | 1100
94 | Sariatpur | 132 | 136 | 18 | 2019-10-03 | 800 | 114 | 9 | 2019-10-03 | 2100
95 | Gopalganj | 132 | 143 | 23 | 2019-10-03 | 1800 | 122 | 11 | 2019-10-03 | 1200
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October '2019
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
96 | Bagerhat | 132 | 140 | 18 | 2019-10-03 | 800 | 120 | 24 | 2019-10-03 | 1100
97 | Mongla | 132 | 135 | 1 | 2019-10-03 | 1900 | 118 | 19 | 2019-10-03 | 1200
98 | Satkhira | 132 | 138 | 9 | 2019-10-03 | 1800 | 122 | 3 | 2019-10-03 | 1100
99 | Gallamari | 132 | 141 | 18 | 2019-10-03 | 800 | 124 | 3 | 2019-10-03 | 1100
100 | Magura | 132 | 135 | 14 | 2019-10-03 | 600 | 114 | 12 | 2019-10-03 | 1830
101 | Norail | 132 | 137 | 21 | 2019-10-03 | 900 | 112 | 2 | 2019-10-03 | 2000
102 | Chuadanga | 132 | 133 | 25 | 2019-10-03 | 300 | 108 | 2 | 2019-10-03 | 1930
103 | Barisal(N) | 132 | 141 | 23 | 2019-10-03 | 1800 | 127 | 29 | 2019-10-03 | 1100
104 | Barisal(S) | 132 | 139 | 16 | 2019-10-03 | 1500 | 126 | 19 | 2019-10-03 | 1500
105 | Patuakhali | 132 | 138 | 18 | 2019-10-03 | 700 | 122 | 12 | 2019-10-03 | 1500
106 | Bhandaria | 132 | 137 | 23 | 2019-10-03 | 1800 | 124 | 31 | 2019-10-03 | 1200
107 | Ishurdi | 132 | 140 | 2 | 2019-10-03 | 600 | 131 | 3 | 2019-10-03 | 1200
108 | Ruppur paromanobik | 132 | 141 | 24 | 2019-10-03 | 1800 | 133 | 12 | 2019-10-03 | 1830
109 | Natore | 132 | 140 | 24 | 2019-10-03 | 1800 | 127 | 18 | 2019-10-03 | 200
110 | Bogra | 132 | 140 | 24 | 2019-10-03 | 1800 | 129 | 2 | 2019-10-03 | 1100
111 | Noagaon | 132 | 136 | 24 | 2019-10-03 | 1800 | 123 | 2 | 2019-10-03 | 1900
112 | Rajshahi | 132 | 137 | 4 | 2019-10-03 | 1700 | 121 | 3 | 2019-10-03 | 1100
113 | C.Nawabganj | 132 | 135 | 1 | 2019-10-03 | 1830 | 116 | 1 | 2019-10-03 | 1200
114 | Amnura | 132 | 139 | 9 | 2019-10-03 | 1800 | 120 | 1 | 2019-10-03 | 1300
115 | Pabna | 132 | 140 | 18 | 2019-10-03 | 600 | 126 | 29 | 2019-10-03 | 1200
116 | Shahjadpur | 132 | 144 | 28 | 2019-10-03 | 400 | 134 | 15 | 2019-10-03 | 1200
117 | Serajganj | 132 | 140 | 24 | 2019-10-03 | 1800 | 128 | 2 | 2019-10-03 | 1900
118 | Niyamatpur | 132 | 136 | 25 | 2019-10-03 | 700 | 118 | 2 | 2019-10-03 | 1900
119 | Joypurhat | 132 | 139 | 25 | 2019-10-03 | 600 | 121 | 2 | 2019-10-03 | 1900
120 | Mohastangor | 132 | 139 | 25 | 2019-10-03 | 500 | 125 | 2 | 2019-10-03 | 1500
121 | Rangpur | 132 | 134 | 1 | 2019-10-03 | 600 | 110 | 19 | 2019-10-03 | 1830
122 | Lalmonirhat | 132 | 132 | 11 | 2019-10-03 | 600 | 109 | 17 | 2019-10-03 | 1830
123 | Saidpur | 132 | 136 | 21 | 2019-10-03 | 1700 | 107 | 2 | 2019-10-03 | 1900
124 | Purbasadipur | 132 | 135 | 1 | 2019-10-03 | 400 | 104 | 19 | 2019-10-03 | 1800
125 | Thakurgaon | 132 | 130 | 1 | 2019-10-03 | 600 | 102 | 2 | 2019-10-03 | 1830
126 | Palashbari | 132 | 138 | 20 | 2019-10-03 | 600 | 120 | 2 | 2019-10-03 | 1200
127 | Barapukuria | 132 | 138 | 1 | 2019-10-03 | 300 | 117 | 19 | 2019-10-03 | 1800
128 | Panchagar | 132 | 129 | 18 | 2019-10-03 | 500 | 94 | 2 | 2019-10-03 | 1900
129 | Joldhaka | 132 | 134 | 1 | 2019-10-03 | 500 | 107 | 2 | 2019-10-03 | 1900
130 | Kurigram | 133 | 135 | 18 | 2019-10-03 | 1900 | 108 | 3 | 2019-10-03 | 1900
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:October' 2019
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 110 | 350
Hasnabad | TR2 | 225 | 97 | 350 | 17.10.19 | 09:00
| TR3 | 225 | 95 | 320
| TR1 | 225 | 180 | 550
Tongi | TR2 | 225 | 180 | 550 | 31.10.19 | 10:00
| TR3 | 225 | 180 | 550
| TR1 | 225 | 136 | 440
Haripur | TR2 | 225 |  |  | 26.10.19 | 12:00 | S/D
| TR3 | 225 | 136 | 440
| TR1 | 225 | 196 | 540
Rampura | TR2 | 225 | 196 | 540 | 19.10.19 | 11:00
| TR3 | 225 | 196 | 540
| TR1 | 225 | 127 | 377
Aminbazar | TR2 | 225 | 127 | 377 | 11.10.19 | 12:00
| TR3 | 225 | 133 | 383
Maniknagar | TR1 | 300 | 120 | 390 | 06.10.19 | 13:00
| TR2 | 300 | 120 | 390
Cumilla (N) | TR1 | 225 | 170 | 540 | 11.10.19 | 18:00
| TR2 | 225 | 167 | 516
Fenchuganj | TR1 | 300 | 179 | 476 | 16.10.19 | 8:00
| MT1 | 150 | 85 | 240
Hathazari | MT2 | 150 | 85 | 240 | 19.10.19 | 9:00
| MT3 | 150 | 85 | 240
| MT4 | 150 | 85 | 240
| TR1 | 225 | 120 | 320
Ishurdi | TR2 | 225 | 120 | 320 | 21.10.19 | 20:00
| TR3 | 225 | 120 | 320
Khulna(S) | TR1 | 225 | 121 | 355
| TR2 | 225 | 121 | 355 | 03.10.19 | 13:00
| TR3 | 300 | 158 | 457
Bogra | TR1 | 225 | 128 | 347 | 18.10.19 | 19:00
| TR2 | 225 | 128 | 347
| TR3 | 225 | 202 | 540
Baghabari | TR1 | 225 | 160 | 470 | 15.10.19 | 20:00
Barapukuria | TR1 | 225 | 150 | 700 | 06.10.19 | 18:30 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 131 | 660 |  |  | 132 kV current is being provided
| TR6 | 300 | 172 | 868
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:October' 2019
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 180 | 334 | 01.10.19 | 8:30
| TR2(400/230 kV) | 520 | 183 | 334
| TR1(400/132 kV) | 325 | 246 | 430 | 17.10.19 | 18:15
| TR2(400/132 kV) | 325 | 246 | 430
Bibiyana | ICT1(400/230 kV) | 520 | 92 | 161 | 03.10.19 | 2:00
| ICT2(400/230kV) | 520 | 93 | 162
Bhulta | ATR1(400/230 kV) | 520 | 222 | 423 | 05.10.19 | 16:15
| ATR2(400/230kV) | 520 | 220 | 423
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:October' 2019 | [6 empty] | (For Evening Peak) | [7 empty] | Month:October' 2019 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-10-19 | 10478 | 10478 | - | - | - | - | - | - | - | - | - | - | - | - | 01-10-19 | 8380.3 | 8380.3 | - | - | - | - | - | - | - | - | - | - | - | -
02-10-19 | 11257 | 11257 | - | - | - | - | - | - | - | - | - | - | - | - | 02-10-19 | 8800.6 | 8800.6 | - | - | - | - | - | - | - | - | - | - | - | -
03-10-19 | 11122 | 11122 | - | - | - | - | - | - | - | - | - | - | - | - | 03-10-19 | 9006.9 | 9006.9 | - | - | - | - | - | - | - | - | - | - | - | -
04-10-19 | 10722 | 10722 | - | - | - | - | - | - | - | - | - | - | - | - | 04-10-19 | 8103.2 | 8103.2 | - | - | - | - | - | - | - | - | - | - | - | -
05-10-19 | 11556 | 11556 | - | - | - | - | - | - | - | - | - | - | - | - | 05-10-19 | 9216.9 | 9216.9 | - | - | - | - | - | - | - | - | - | - | - | -
06-10-19 | 11301 | 11301 | - | - | - | - | - | - | - | - | - | - | - | - | 06-10-19 | 9351.7 | 9351.7 | - | - | - | - | - | - | - | - | - | - | - | -
07-10-19 | 10945 | 10945 | - | - | - | - | - | - | - | - | - | - | - | - | 07-10-19 | 9531.4 | 9531.4 | - | - | - | - | - | - | - | - | - | - | - | -
08-10-19 | 10450 | 10450 | - | - | - | - | - | - | - | - | - | - | - | - | 08-10-19 | 8408.6 | 8408.6 | - | - | - | - | - | - | - | - | - | - | - | -
09-10-19 | 10284 | 10284 | - | - | - | - | - | - | - | - | - | - | - | - | 09-10-19 | 8864.7 | 8864.7 | - | - | - | - | - | - | - | - | - | - | - | -
10-10-19 | 9992 | 9992 | - | - | - | - | - | - | - | - | - | - | - | - | 10-10-19 | 8376 | 8376 | - | - | - | - | - | - | - | - | - | - | - | -
11-10-19 | 9945 | 9945 | - | - | - | - | - | - | - | - | - | - | - | - | 11-10-19 | 7333 | 7333 | - | - | - | - | - | - | - | - | - | - | - | -
12-10-19 | 11327 | 11327 | - | - | - | - | - | - | - | - | - | - | - | - | 12-10-19 | 8685.5 | 8685.5 | - | - | - | - | - | - | - | - | - | - | - | -
13-10-19 | 11219 | 11219 | - | - | - | - | - | - | - | - | - | - | - | - | 13-10-19 | 8904 | 8904 | - | - | - | - | - | - | - | - | - | - | - | -
14-10-19 | 11326 | 11326 | - | - | - | - | - | - | - | - | - | - | - | - | 14-10-19 | 9026.7 | 9026.7 | - | - | - | - | - | - | - | - | - | - | - | -
15-10-19 | 11666 | 11666 | - | - | - | - | - | - | - | - | - | - | - | - | 15-10-19 | 9248.9 | 9248.9 | - | - | - | - | - | - | - | - | - | - | - | -
16-10-19 | 11284 | 11284 | - | - | - | - | - | - | - | - | - | - | - | - | 16-10-19 | 8967.3 | 8967.3 | - | - | - | - | - | - | - | - | - | - | - | -
17-10-19 | 11952 | 11952 | - | - | - | - | - | - | - | - | - | - | - | - | 17-10-19 | 9341.3 | 9341.3 | - | - | - | - | - | - | - | - | - | - | - | -
18-10-19 | 10691 | 10691 | - | - | - | - | - | - | - | - | - | - | - | - | 18-10-19 | 8083 | 8083 | - | - | - | - | - | - | - | - | - | - | - | -
19-10-19 | 11791 | 11791 | - | - | - | - | - | - | - | - | - | - | - | - | 19-10-19 | 8721 | 8721 | - | - | - | - | - | - | - | - | - | - | - | -
20-10-19 | 11829 | 11829 | - | - | - | - | - | - | - | - | - | - | - | - | 20-10-19 | 9495 | 9495 | - | - | - | - | - | - | - | - | - | - | - | -
21-10-19 | 11707 | 11707 | - | - | - | - | - | - | - | - | - | - | - | - | 21-10-19 | 9272 | 9272 | - | - | - | - | - | - | - | - | - | - | - | -
22-10-19 | 11586 | 11586 | - | - | - | - | - | - | - | - | - | - | - | - | 22-10-19 | 9187.9 | 9187.9 | - | - | - | - | - | - | - | - | - | - | - | -
23-10-19 | 11063 | 11063 | - | - | - | - | - | - | - | - | - | - | - | - | 23-10-19 | 9229.4 | 9229.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-10-19 | 9023 | 9023 | - | - | - | - | - | - | - | - | - | - | - | - | 24-10-19 | 7842.5 | 7842.5 | - | - | - | - | - | - | - | - | - | - | - | -
25-10-19 | 7696 | 7696 | - | - | - | - | - | - | - | - | - | - | - | - | 25-10-19 | 5991.3 | 5991.3 | - | - | - | - | - | - | - | - | - | - | - | -
26-10-19 | 9282 | 9282 | - | - | - | - | - | - | - | - | - | - | - | - | 26-10-19 | 7227.4 | 7227.4 | - | - | - | - | - | - | - | - | - | - | - | -
27-10-19 | 9660 | 9660 | - | - | - | - | - | - | - | - | - | - | - | - | 27-10-19 | 7607.3 | 7607.3 | - | - | - | - | - | - | - | - | - | - | - | -
28-10-19 | 9849 | 9849 | - | - | - | - | - | - | - | - | - | - | - | - | 28-10-19 | 7689.6 | 7689.6 | - | - | - | - | - | - | - | - | - | - | - | -
29-10-20 | 10099 | 10099 | - | - | - | - | - | - | - | - | - | - | - | - | 29-10-20 | 8095.9 | 8095.9 | - | - | - | - | - | - | - | - | - | - | - | -
30-10-19 | 10244 | 10244 | - | - | - | - | - | - | - | - | - | - | - | - | 30-10-19 | 8198.7 | 8198.7 | - | - | - | - | - | - | - | - | - | - | - | -
31-10-20 | 10115 | 10115 | - | - | - | - | - | - | - | - | - | - | - | - | 31-10-20 | 8281 | 8281 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:October' 2019
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11952 | 17/10/19 | 19:00
2 | Maximum Day Peak Genaration | MW | 9531.4 | 07/10/19 | 12:00
3 | Maximum Evening Peak Demand | MW | 11952 | 17/10/19 | 19:00
4 | Minimum Generation | MW | 5208 | 26/10/19 | 5:00
5 | Average of the daily evening peak Genaration | MW | 10711.5333
6 | Average of the daily day peak Genaration | MW | 8531.2581
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6545.2041
12 | Total Generation by IPP | MKWH | 1651.6762 | % of total Gen. | 25.23%
13 | Total Generation by BPDB | MKWH | 3525.1883 | " | 53.86%
14 | A) Total Generation by RPCL | MKWH | 140.5038 | '' | 2.147%
| B) Total Generation by REB | MKWH | 144.8634 | " | 2.213%
| C) Total Generation by RENTAL | MKWH | 371.5133 | " | 5.676%
| D) Total Imported from India (HVDC) | MKWH | 614.5537 | " | 9.389%
| E) Total Imported from Tripura, India (A.C) | MKWH | 96.9053 | " | 1.481%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4520.3065 | % of total Gen. | 69.06%
| B) Oil | MKWH | 989.6153 | '' | 15.12%
| C) Hydro | MKWH | 84.059 | '' | 1.284%
| D) Solar | MKWH | 4.6673 | '' | 0.07131%
| E) Coal | MKWH | 235.097 | '' | 3.592%
| F) HVDC (Import from India) | MKWH | 614.5537 | '' | 9.389%
| G) A.C (Import from Tripura, India) | MKWH | 96.9053 | '' | 1.481%
16 | Maximun of the daily total Generation . | MKWH | 237.7538 | 20/10/19
17 | Monthly Load factor | % | 73.629
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 13898.6479
| A) Gas | M.Taka | 4206.3171
| B) Liquid fuel | M.Taka | 8665.553
| C) Coal | M.Taka | 1026.7778
| D) HVDC (Import from India) | M.Taka | 3134.224
| E) Tripura(Import from India) | M.Taka | 726.7894
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 631.661 | 05/10/19
| A) Gas | M.Taka | 150.9235 | 17/10/19
| B) Liquid fuel | M.Taka | 458.4702 | 05/10/19
| C) Coal | M.Taka | 40.5063 | 06/10/19
| D) HVDC (Import from India) | M.Taka | 114.3105 | 20-10-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.1368
| B) Excluding Hydro & Solar | Taka/KWHR | 3.1799
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 102.1 | 31/10/19 | 06:00
b) | Actual | FT (MSL) | 108.9 | 31/10/19 | 06:00
22 | Peak Genaration of October 2018 | MW | 11485 | 02/10/18 | 19:00
23 | Peak Demand of October 2018 | MW | 11485 | 02/10/18 | 19:00
24 | Maximum peak Generation recorded upto 31/10/19 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/10/19 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/10/19 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.