## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-24 | Sunday
|  | Date (day): | 2019-11-24 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12227.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14774 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-23 | 2019-11-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 100 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 360 | 320 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas Shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 346 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 353 | 363 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 120 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 35 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 24 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 28 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 32 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 45 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 52 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1784 | 2199 | 3545 | 3992 | 656 | 1158
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 150 | 130 | 150 | 30 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.1 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 15 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 45 | 85 | 85 | 145 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 230 | 229 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 80 | 145 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 5 | 8 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 30 | 30 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 589.5 | 760 | 1498 | 1678 | 355 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 60 | 80 | 80 | 80 | 55 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 198 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 330 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 294 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 4 | 52 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 44 | 36 | 36 | 151 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 35 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 96 | 120 | 130
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 17 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 124 | 116 | 144
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 115 | 0 | 119 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1283 | 1394 | 1855 | 2174 | 469 | 24
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 124 | 159 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 24 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 80 | 150 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 204 | 355 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 52 | 52
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 70 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 268 | 311 | 330 | 330
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 2 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 2 | 49 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 35 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 1 | 80 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 2 | 39 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 278 | 357 | 400 | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 868 | 1356 | 1691 | 1691 | 0 | 159
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 444 | 784 | 442 | 787
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 12 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 315 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 17 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 741 | 1221 | 937 | 2007 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 25 | 25 | 25 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 153 | 174 | 153 | 175
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 10 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 183 | 241 | 343 | 435 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 50 | 0 | 50 | 50 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 202 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 194 | 210 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 424 | 433 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 15 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 874 | 992 | 1454 | 1768 | 341 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 109 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 205.2 | 309 | 411 | 437 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 6731.7 | 8827 | 12227.6 | 14774 | 1863 | 1624
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6380.892 | 8367 | 11590.3851 | 14004.085
A. |  | 2019-11-23 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8827 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5200 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8827 | MW
3 | Day peak Generation : |  |  | 6731.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8367 | MW
4 | Evening peak Generation : |  |  | 8827 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 162.2691 | MKWHr | By Solar | 0.17033 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 132.4253 | MKWHr |  | By Oil: | 11.01 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.8889 | MKWHr |  | By Hydro: | 1.002 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1863 | MW | Dhaka | 3223 | 3223 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1624 | MW | Chittagong | 897 | 897 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3487 | MW | Khulna | 974 | 974 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1064.57 | MMCFD |  |  | Rajshahi | 814 | 814 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 116444815.624 | ii) Oil : | Taka | 63444903.02 | Comilla | 729 | 729 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19995601 | Total | Taka | 199885319.644 | Mymensingh | 652 | 652 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.6145 | MKWHr. | Sylhet | 328 | 328 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 50 | MW (E to W) at | 19:00 | hrs | Barisal | 210 | 210 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -100 | MW at | 8:00 | hrs | Rangpur | 540 | 540 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.8° C |  |  | Total | 8367 | 8367 |  | 0
B. |  | 2019-11-24 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 28° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14774 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
4 | Reserve(Generation end) |  |  |  | 7574 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 132.3595 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5470 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.648 | MKWHr. | ii) HVDC Flow at Peak Time |  | 784 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1245 | MKWHr. | iii) Maximum HVDC Flow : |  | 785 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 100.64 | 100.7 |  | (b) Today: | 100.64 |  | (c) Rule Curve: |  | 106.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 343 | 310 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 250 | 148 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 82 | 110 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 100 | 248 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 |  | 243 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 344 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4140 | 1584 | 5724 | 3490 | 243 | 1404 | 262 | 200 | 43 | 0 | 82 | 0 | 0 | 100.7
2:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 344 | 250 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 203 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 250 | 148 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 78 | 110 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 100 | 240 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 |  | 244 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3951 | 1538 | 5489 | 3347 | 244 | 1339 | 239 | 200 | 42 | 0 | 78 | 0 | 0 | 100.7
3:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 344 | 210 |  | 0 | 260 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 229 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 220 | 250 | 148 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 110 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 100 | 238 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 |  | 244 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3815 | 1515 | 5330 | 3271 | 244 | 1260 | 239 | 200 | 42 | 0 | 74 | 0 | 0 | 100.7
4:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 348 | 185 |  | 0 | 260 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 44 | 0 | 0 | 120 | 0 | 203 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 220 | 235 | 148 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 110 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 100 | 248 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 |  | 243 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3744 | 1476 | 5220 | 3209 | 243 | 1211 | 239 | 200 | 44 | 0 | 74 | 0 | 0 | 100.7
5:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 347 | 185 |  | 0 | 260 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 44 | 0 | 0 | 120 | 0 | 180 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 220 | 235 | 148 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 72 | 110 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 100 | 252 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 |  | 244 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3725 | 1475 | 5200 | 3195 | 244 | 1206 | 239 | 200 | 44 | 0 | 72 | 0 | 0 | 100.7
6:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 373 | 240 |  | 0 | 290 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 189 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 60 | 0 | 0 | 220 | 235 | 148 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 72 | 111 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 263 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 |  | 244 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 200 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3793 | 1576 | 5369 | 3336 | 244 | 1233 | 239 | 200 | 45 | 0 | 72 | 0 | 0 | 100.7
7:00 | 35 | 0 | 0 | 100 | 200 | 0 | 0 | 373 | 270 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 30 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 187 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 60 | 0 | 0 | 285 | 290 | 148 | 8 | 88 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 70 | 110 | 0 | 0 | 0.1 | 0 | 0 | 2 | 2 | 0 | 267 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0.241 | 0 | 0 | 0 | 119 |  | 243 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 3985.971 | 1624.2 | 5610.171 | 3511 | 243 | 1299 | 239 | 200 | 45 | 0 | 70 | 3.171 | 0 | 100.7
8:00 | 35 | 0 | 0 | 100 | 220 | 0 | 0 | 366 | 300 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 0 | 30 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 215 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 60 | 0 | 0 | 285 | 290 | 180 | 8 | 86 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 78 | 160 | 0 | 0 | 0.6 | 0 | 0 | 2 | 2 | 0 | 253 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.46 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 | 119 |  | 243 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4283.46 | 1648.1 | 5931.56 | 3748 | 243 | 1367 | 239 | 200 | 45 | 0 | 78 | 11.56 | 0 | 0
9:00 | 35 | 0 | 0 | 100 | 250 | 0 | 0 | 359 | 309 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25 | 21 | 0 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 202 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 260 | 260 | 204 | 8 | 87 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 160 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 238 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 12.6 | 0 | 0 | 0 | 355 | 0 | 35 | 0 | 1.7 | 0 | 0 | 0 | 119 |  | 388 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 7 | 0 | 0 | 200 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 309 | 17 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 |  | 4276.3 | 1790.9 | 6067.2 | 3676 | 388 | 1332 | 336 | 200 | 42 | 0 | 76 | 17.2 | 0 | 0
10:00 | 35 | 0 | 0 | 100 | 230 | 0 | 0 | 357 | 258 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 21 | 0 | 33 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 181 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 275 | 275 | 183 | 8 | 50 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 74 | 125 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 252 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 15.8 | 0 | 0 | 0 | 301 | 0 | 35 | 0 | 4 | 0 | 0 | 0 | 119 |  | 438 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 344 | 17 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4076.8 | 1841.2 | 5918 | 3491 | 438 | 1250 | 396 | 200 | 45 | 0 | 74 | 24 | 0 | 0
11:00 | 35 | 0 | 0 | 100 | 280 | 0 | 0 | 381 | 259 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 305 | 360 | 182 | 8 | 50 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 124 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 255 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 16.9 | 0 | 0 | 0 | 328 | 0 | 35 | 0 | 4.4 | 0 | 0 | 0 | 119 |  | 446 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 402 | 17 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 4371.3 | 1933.8 | 6305.1 | 3700 | 446 | 1393 | 415 | 200 | 45 | 0 | 80 | 26.1 | 0 | 0
12:00 | 35 | 0 | 0 | 100 | 320 | 0 | 0 | 378 | 353 |  | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 230 | 0 | 80 | 0 |  | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 355 | 345 | 200 | 8 | 95 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 84 | 124 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 268 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 17.1 | 10 | 0 | 0 | 278 | 0 | 17 | 51 | 4.4 | 0 | 0 | 0 | 115 |  | 444 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 424 | 17 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 4728.5 | 2003.2 | 6731.7 | 3929 | 444 | 1534 | 469 | 200 | 40 | 5 | 84 | 26.7 | 0 | 0
13:00 | 35 | 0 | 0 | 100 | 350 | 0 | 0 | 384 | 358 |  | 0 | 420 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 230 | 0 | 120 | 0 |  | 0 | 8 | 0 | 30 | 6 | 0 | 19 | 3 | 60 | 0 | 0 | 320 | 305 | 200 | 8 | 95 | 37 | 4 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 82 | 125 | 0 | 22 | 0 | 0 | 0 | 2 | 12 | 0 | 252 | 0 | 1 | 0 | 0 | 0 | 29 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 15.64 | 10 | 0 | 0 | 235 | 0 | 35 | 51 | 4 | 0 | 0 | 0 | 0 |  | 445 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 427 | 17 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 |  | 4794.64 | 2026.9 | 6821.54 | 3986 | 445 | 1638 | 398 | 200 | 40 | 8 | 82 | 24.54 | 0 | 0
14:00 | 35 | 0 | 0 | 100 | 320 | 0 | 0 | 347 | 359 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 231 | 0 | 80 | 0 |  | 0 | 8 | 0 | 10 | 11 | 0 | 19 | 3 | 60 | 0 | 0 | 285 | 275 | 181 | 8 | 91 | 37 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 88 | 125 | 0 | 20 | 0 | 0 | 0 | 53 | 43 | 0 | 258 | 0 | 1 | 0 | 0 | 17 | 39 | 10 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 13 | 0 | 0 | 0 | 113 | 0 | 17 | 17 | 3.29 | 0 | 0 | 0 | 0 |  | 445 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 423 | 17 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 |  | 4553.29 | 1989.1 | 6542.39 | 3660 | 445 | 1728 | 354 | 200 | 40 | 8 | 88 | 19.39 | 0 | 0
15:00 | 35 | 0 | 0 | 100 | 320 | 0 | 0 | 361 | 324 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 229 | 0 | 80 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 19 | 2 | 60 | 0 | 0 | 265 | 275 | 181 | 8 | 95 | 37 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 86 | 124 | 0 | 20 | 0 | 0 | 0 | 53 | 46 | 0 | 256 | 0 | 1 | 0 | 0 | 17 | 34 | 10 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 9 | 0 | 0 | 0 | 208 | 0 | 0 | 17 | 2.17 | 0 | 0 | 0 | 0 |  | 445 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 427 | 17 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 |  | 4640.17 | 1968.3 | 6608.47 | 3729 | 445 | 1732 | 358 | 200 | 37 | 8 | 86 | 13.47 | 0 | 0
16:00 | 35 | 0 | 0 | 100 | 320 | 0 | 0 | 349 | 324 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 230 | 0 | 80 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 19 | 6 | 60 | 0 | 0 | 260 | 275 | 181 | 8 | 95 | 37 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 86 | 125 | 0 | 20 | 0 | 0 | 0 | 53 | 43 | 0 | 260 | 0 | 1 | 0 | 0 | 17 | 36 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 4 | 0 | 0 | 0 | 270 | 0 | 0 | 17 | 0.95 | 0 | 0 | 0 | 0 |  | 445 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 410 | 17 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 4683.95 | 1943.7 | 6627.65 | 3773 | 445 | 1715 | 358 | 200 | 37 | 8 | 86 | 5.65 | 0 | 0
17:00 | 35 | 0 | 0 | 100 | 320 | 0 | 0 | 375 | 322 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 17 | 0 | 25 | 21 | 0 | 33 | 14 | 0 | 37 | 0 | 0 | 120 | 0 | 231 | 0 | 80 | 0 |  | 0 | 8 | 1 | 30 | 0 | 2 | 19 | 6 | 80 | 0 | 0 | 265 | 275 | 201 | 8 | 95 | 37 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10 | 18 | 92 | 125 | 0 | 22 | 0 | 0 | 0 | 11 | 10 | 70 | 305 | 0 | 50 | 0 | 0 | 17 | 11 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 |  | 445 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 16 | 0 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 6 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 431 | 17 | 0 | 0 | 0 | 51 | 0 | 0.1 | 0 |  | 4967 | 2094.1 | 7061.1 | 3984 | 445 | 1772 | 522 | 200 | 37 | 9 | 92 | 0.1 | 0 | 0
18:00 | 35 | 0 | 0 | 100 | 340 | 0 | 0 | 362 | 361 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 14 | 0 | 13 | 0 | 17 | 17 | 19 | 25 | 22 | 14 | 33 | 52 | 0 | 38 | 0 | 0 | 120 | 0 | 230 | 0 | 144 | 0 |  | 0 | 8 | 34 | 80 | 0 | 18 | 19 | 2 | 80 | 0 | 0 | 350 | 320 | 200 | 44 | 96 | 37 | 51 | 0 | 21 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 130 | 157 | 14 | 22 | 0 | 0 | 0 | 53 | 33 | 70 | 313 | 5 | 80 | 0 | 0 | 17 | 37 | 10 | 305 | 24 | 11 | 0 | 36 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 22 | 0 | 373 | 0 | 88 | 75 | 0 | 0 | 0 | 0 | 0 |  | 785 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 40 | 177 | 21 | 16 | 0 | 40 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 11 | 0 | 209 | 0 | 430 | 53 | 0 | 0 | 13 | 64 | 0 | 0 | 0 |  | 6056 | 2727 | 8783 | 4539 | 785 | 1985 | 1035 | 200 | 38 | 71 | 130 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 100 | 360 | 0 | 0 | 346 | 363 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 24 | 0 | 35 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 32 | 0 | 45 | 0 | 0 | 150 | 0 | 229 | 0 | 145 | 0 |  | 0 | 8 | 0 | 30 | 0 | 15 | 19 | 14 | 80 | 0 | 0 | 330 | 294 | 198 | 44 | 96 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 159 | 24 | 22 | 0 | 0 | 0 | 53 | 49 | 70 | 311 | 35 | 80 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 357 | 0 | 52 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 174 | 25 | 32 | 0 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 202 | 0 | 0 | 0 | 10 | 0 | 210 | 0 | 433 | 53 | 0 | 0 | 17 | 109 | 0 | 0 | 0 |  | 6064 | 2763 | 8827 | 4539 | 784 | 2033 | 1082 | 200 | 45 | 20 | 124 | 0 | 0 | 100.83
19:30 | 35 | 0 | 0 | 100 | 380 | 0 | 0 | 344 | 363 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 24 | 0 | 47 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 32 | 0 | 45 | 0 | 0 | 150 | 0 | 229 | 0 | 145 | 0 |  | 0 | 8 | 0 | 10 | 0 | 3 | 19 | 18 | 80 | 0 | 0 | 330 | 300 | 198 | 44 | 93 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 160 | 24 | 22 | 0 | 0 | 0 | 53 | 49 | 70 | 310 | 35 | 80 | 0 | 0 | 17 | 40 | 10 | 305 | 24 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 356 | 0 | 52 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 170 | 25 | 32 | 0 | 50 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 202 | 0 | 0 | 0 | 10 | 0 | 205 | 0 | 432 | 53 | 0 | 0 | 17 | 113 | 0 | 0 | 0 |  | 6070 | 2726 | 8796 | 4545 | 784 | 2042 | 1041 | 199 | 45 | 20 | 120 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 100 | 380 | 0 | 0 | 344 | 363 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 32 | 0 | 45 | 0 | 0 | 150 | 0 | 229 | 0 | 144 | 0 |  | 0 | 7 | 0 | 10 | 0 | 0 | 19 | 25 | 80 | 0 | 0 | 330 | 300 | 198 | 44 | 92 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 122 | 159 | 24 | 22 | 0 | 0 | 0 | 53 | 50 | 70 | 307 | 36 | 80 | 0 | 0 | 17 | 41 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 785 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 158 | 25 | 32 | 0 | 50 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 201 | 0 | 0 | 0 | 10 | 0 | 206 | 0 | 426 | 53 | 0 | 0 | 17 | 71 | 0 | 0 | 0 |  | 5958 | 2643 | 8601 | 4527 | 785 | 2040 | 875 | 200 | 45 | 7 | 122 | 0 | 0 | 100.82
21:00 | 35 | 0 | 0 | 100 | 380 | 0 | 0 | 343 | 363 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 16 | 0 | 45 | 0 | 0 | 150 | 0 | 229 | 0 | 144 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 31 | 80 | 0 | 0 | 330 | 300 | 198 | 44 | 90 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 160 | 0 | 22 | 0 | 0 | 0 | 53 | 50 | 70 | 307 | 36 | 40 | 0 | 0 | 17 | 40 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 785 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 32 | 0 | 50 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 198 | 0 | 0 | 0 | 10 | 0 | 203 | 0 | 408 | 53 | 0 | 0 | 17 | 40 | 0 | 0 | 0 |  | 5743 | 2583 | 8326 | 4514 | 785 | 1982 | 673 | 200 | 45 | 7 | 120 | 0 | 0 | 100.82
22:00 | 35 | 0 | 0 | 100 | 380 | 0 | 0 | 343 | 363 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 45 | 0 | 0 | 150 | 0 | 229 | 0 | 144 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 260 | 260 | 200 | 44 | 95 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 160 | 0 | 22 | 0 | 0 | 0 | 53 | 50 | 70 | 262 | 36 | 40 | 0 | 0 | 17 | 40 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 |  | 785 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 154 | 24 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 0 | 10 | 0 | 187 | 0 | 343 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5352 | 2398 | 7750 | 4350 | 785 | 1886 | 363 | 200 | 45 | 7 | 114 | 0 | 0 | 100.71
23:00 | 35 | 0 | 0 | 100 | 340 | 0 | 0 | 344 | 363 |  | 0 | 390 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 203 | 0 | 147 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 265 | 265 | 205 | 36 | 95 | 37 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 102 | 160 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 70 | 263 | 36 | 0 | 0 | 0 | 0 | 40 | 10 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 592 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 23 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 10 | 0 | 184 | 0 | 381 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4846 | 2182 | 7028 | 4158 | 592 | 1736 | 189 | 200 | 44 | 7 | 102 | 0 | 0 | 0
24:00 | 35 | 0 | 0 | 100 | 340 | 0 | 0 | 367 | 363 |  | 0 | 390 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 205 | 0 | 148 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 39 | 80 | 0 | 0 | 265 | 260 | 205 | 8 | 95 | 37 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 265 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 22 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 2 | 0 | 179 | 0 | 380 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4746 | 1826 | 6572 | 4187 | 251 | 1599 | 189 | 200 | 43 | 7 | 96 | 0 | 0 | 0
KWH | 822000 | 0 | 0 | 2520000 | 6830536 | 0 | 0 | 8684420 | 7288000 |  | 0 | 8515875 | 3362851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 851040 | 18240 | 0 | 58560 | 0 | 237888 | 0 | 43479 | 40009 | 92304 | 600000 | 522180 | 473900 | 628200 | 180792 | 0 | 1001978 | 0 | 0 | 3000000 | 10364 | 5060267 | 0 | 2385173 | 0 |  | 0 | 98788 | 49698 | 234240 | 25920 | 41280 | 217200 | 339840 | 1650962 | 0 | 0 | 7086700 | 6850500 | 4327000 | 401454 | 2059590 | 440280 | 630720 | 0 | 190348 | 0 | 0 | 0 | 218988 | 51840 | 193800 | 410120 | 2124480 | 3133840 | 83520 | 218304 | 600 | 0 | 0 | 473400 | 530064 | 1081480 | 6985000 | 207648 | 433920 | 0 | 0 | 182000 | 402800 | 110700 | 7300500 | 135855 | 56296 | 0 | 148036 | 0 | 0 | 1360800 | 0 | 0 | 112455 | 28800 | 74880 | 0 | 7494000 | 0 | 388272 | 623088 | 27360 | 0 | 0 | 0 | 1442100 |  | 10648000 | 0 | 7030080 | 0 | 0 | 0 | 0 | 0 | 31680 | 0 | 201000 | 3934387 | 442024 | 320640 | 0 | 353000 | 0 | 0 | 0 | 0 | 136680 | 0 | 0 | 12480 | 0 | 407040 | 303624 | 162162 | 0 | 0 | 4888900 | 0 | 0 | 4632982 | 0 | 0 | 0 | 65077 | 0 | 4682055 | 0 | 9174909 | 478080 | 0 | 0 | 63936 | 362880 | 0 | 29915 | 0 |  | 113907522 | 48361531 | 162269053 | 94333569 | 10648000 | 38091775 | 10811615 | 4888900 | 1001978 | 198406 | 2124480 | 170330 | 0
Fuel Cost | 920640 | 0 | 0 | 2822400 | 5054596.64 | 0 | 0 | 6252782.4 | 5538880 |  | 0 | 6812700 | 3026565.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8646566.4 | 180758.4 | 0 | 532896 | 0 | 2226631.68 | 0 | 414789.66 | 398489.64 | 69228 | 450000 | 0 | 0 | 0 | 1731987.36 | 0 | 260514.28 | 0 | 0 | 4590000 | 99598.04 | 5313280.35 | 0 | 3029169.71 | 0 |  | 0 | 1046164.92 | 521332.02 | 2410329.6 | 246499.2 | 386380.8 | 199824 | 944755.2 | 1733510.1 | 0 | 0 | 5244158 | 5754420 | 3980840 | 393424.92 | 2739254.7 | 361029.6 | 649641.6 | 0 | 272197.64 | 0 | 0 | 0 | 223367.76 | 38880 | 366282 | 307590 | 14658912 | 2569748.8 | 794275.2 | 222670.08 | 9840 | 0 | 0 | 643824 | 662580 | 1341035.2 | 6426200 | 309395.52 | 763699.2 | 0 | 0 | 289380 | 471276 | 260145 | 5183355 | 101891.25 | 42784.96 | 0 | 1549936.92 | 0 | 0 | 13090896 | 0 | 0 | 1297730.7 | 268416 | 702374.4 | 0 | 7044360 | 0 | 3459503.52 | 5888181.6 | 0 | 0 | 0 | 0 | 0 |  | 28749600 | 0 | 5483462.4 | 0 | 0 | 0 | 0 | 0 | 367488 | 0 | 1987890 | 3147509.6 | 685137.2 | 3443673.6 | 0 | 663640 | 0 | 0 | 0 | 0 | 1417371.6 | 0 | 0 | 124300.8 | 0 | 447744 | 500979.6 | 122756.634 | 0 | 0 | 19995601 | 0 | 0 | 4077024.16 | 0 | 0 | 0 | 103472.43 | 0 | 4120208.4 | 0 | 6697683.57 | 4522636.8 | 0 | 0 | 569669.76 | 3389299.2 | 0 | 0 | 0 |  | 154244767.87 | 90617148.754 | 244861916.624 | 84072285.064 | 28749600 | 32372530.56 | 61329159.68 | 19995601 | 260514.28 | 2115743.34 | 14658912 | 1307570.7 | 0
Yesterday Day Peak | 35 | 0 | 0 | 100 | 320 | 0 | 0 | 378 | 353 |  | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 230 | 0 | 80 | 0 |  | 0 | 5 | 0 | 30 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 355 | 345 | 200 | 8 | 95 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 84 | 124 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 268 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 17.1 | 10 | 0 | 0 | 278 | 0 | 17 | 51 | 4.4 | 0 | 0 | 0 | 115 |  | 444 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 5 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 424 | 17 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 6731.7 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 100 | 360 | 0 | 0 | 346 | 363 | 0 | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 24 | 0 | 35 | 0 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 32 | 0 | 45 | 0 | 0 | 150 | 0 | 229 | 0 | 145 | 0 | 0 | 0 | 8 | 0 | 30 | 0 | 15 | 19 | 14 | 80 | 0 | 0 | 330 | 294 | 198 | 44 | 96 | 37 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 159 | 24 | 22 | 0 | 0 | 0 | 53 | 49 | 70 | 311 | 35 | 80 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 357 | 0 | 52 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 174 | 25 | 32 | 0 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 202 | 0 | 0 | 0 | 10 | 0 | 210 | 0 | 433 | 53 | 0 | 0 | 17 | 109 | 0 | 0 | 0 |  | 8827 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 40 | 0 | 150 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 15 | 80 | 0 | 0 | 360 | 360 | 200 | 36 | 130 | 37 | 55 | 0 | 35 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 144 | 160 | 95 | 22 | 0 | 60 | 52 | 51 | 44 | 163 | 330 | 66 | 79 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 787 | 40 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 175 | 25 | 110 | 30 | 50 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 45 | 40 | 0 | 130 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 10 | 80 | 0 | 0 | 360 | 360 | 200 | 36 | 120 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 160 | 95 | 22 | 1.6 | 60 | 52 | 51 | 44 | 163 | 330 | 66 | 79 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 119 |  | 442 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 368 | 360 | 0 | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 16 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 203 | 0 | 144 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 4 | 80 | 0 | 0 | 290 | 320 | 205 | 8 | 90 | 34 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 72 | 168 | 0 | 22 | 0.5 | 0 | 0 | 0 | 9 | 130 | 264 | 36 | 0 | 0 | 0 | 0 | 20 | 10 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 159 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0
199
| Minimum Generation |  | 5200 | 5:00
| Highest Generation |  | 8827 | 19:00
| Day Peak Generation |  | 6731.7 | 12:00
| Evening Peak Generation |  | 8827 | 19:00
| HVDC Max Flow |  | 785 | 18:00
| HVDC EvPeak Flow |  | 784 | 19:00
| Load factor L.F |  | 76.6%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6731.7 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5470 | MW
Evening Peak Generation : |  | 8827 | MW Hour : | 19:00 | Available Max Generation : |  | 14774 | MW
E.P. Demand (at gen end) : |  | 8827 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 7200 | MW
Maximum Generation : |  | 8827 | MW Hour : | 19:00 | Reserve(Generation end) |  | 7574 | MW
Total Gen. (MKWH) : |  | 162.2691 | System Load Factor : | 76.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -100 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-24
Actual : | 100.64 | Ft.(MSL) , | Rule curve : | 106.8 | Ft.( MSL )
Gas Consumed : | Total = | 1064.57 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 116444815.624
: |  | Coal : | 19995601 | Oil : | 63444903.02 | Total : | 199885319.644
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2560.3635 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 860.6053 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 769.2813 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 694.4741 |  |  | 0 | 0%
) | 0 | 0:00 | 627.9371 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 506.6977 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 296.266 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 130.8036 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 390.7284 |  |  | 0 | 0%
Total | 0 |  | 6837.157 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,3,4,5
4) Ashuganj unit-4 & 5
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Barapukuria ST: unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ghorasal-Ashuganj 132 kV Ckt-1 was under shut down from 09:11 to 20:16 for A/M.
b) Mymensing S/S-RPCL P/S 132 kV Ckt-1 was under shut down from 09:22 to 17:02 for A/M.
c) Bheramara HVDC-Ishurdi 230 kV Ckt-2 was under shut down from 08:18 to 16:07 for A/M.
d) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 08:27 to 13:41 for A/M.
e) Sikalbaha-Dohazari 132 kV Ckt-1 was under shut down from 09:18 to 15:09 for A/M.
f) Maniknagar-Kabirpur 132 kV Ckt-1 was under shut down from 08:13 to 17:04 for A/M.
g) Bibiyana ICT1 was under shut down from 09:02 to 15:08 for A/M.
h) Haripur-Megnaghat 132 kV Ckt-2 was under shut down from 08:36 to 16:44 for A/M.
i) Rangpur-Saidpur 132 kV Ckt-1 was under shut down from 09:03 to 15:28 for A/M.
j) Sikalbaha-150 MW GT tripped at 10:48 showing E/F relay and was synchronized at 11:10.
k) Bagerhat 132/33 kV T-3 transformer was under shut down from 08:02 to 16:22 for A/M.
l) Mirpur 132/33 kV T-1 transformer was under shut down from 08:41 to 15:58 for A/M.
m) Rampura 132 kV Bus-1 was under shut down from 08:12 to 15:22 for A/M.
n) Jamalpur 132/33 kV T-1 transformer was under shut down from 08:17 to 11:38 for A/M.
o) Bianibazar 132/33 kV T-1 transformer was under shut down from 08:42 to 17:09 for A/M.
p) B.Baria 132/33 kV T-1 transformer was under shut down from 09:05 to 16:18 for A/M.
q) Feni-Baroiarhat 132 kV Ckt-1 & 2 were under shut down from 10:20 to 21:22 for A/M.
r) Jhenida-Magura 132 kV Ckt-1 was under shut down from 08:06 to 16:34 for A/M.
s) Bagura-Sirajganj 230 kV Ckt-2 was under shut down from 08:17 to 15:55 for A/M.
t) Goalpara 132 kV Bus-B was under shut down from 08:05 to 16:57 for A/M.
u) Gallamari 132/33 kV T-1 transformer was under shut down from 09:40 to 14:24 for A/M.
v) Chandpur 132/33 kV T-1 transformer was under shut down from 07:13 to 09:14 for A/M.
w) Cumilla(N) 132/33 kV T-4 transformer was under shut down from 10:25 to 12:02 for C/M.
x) Chandpur-150 MW CCPP ST tripped at 09:16 showing E/F relay.
y) Bibiyana #3 CCPP ST tripped at 11:36 and synchronized at 14:14.
z) Cumilla(N)-Chandpur 132 kV Ckt-2 tripped at 09:46 showing dist.Z1,A-phase and was switched on at 09:57.
aa) Rajshahi(N)-Rajshahi(O) 132 kV Ckt-2 was shut down at 14:50 due to abnormal sound was generating from
B-phase CT of Rajshahi(N) end and was switched on at 16:04.
ab) After maintenance Kushiara-163 MW CCPP GT & ST were synchronized at 16:13 & 22:40 respectively.
ac) After restoration of gas Baghabari-100 MW synchronized at 16:56.
ad) Aminbazar 230/132 kV TR-3 transformer was under shut down from 09:12 to 17:08 for A/M.
ae) Ghorasal #5 was forced shut down at 02:20(24/11/19) due to controller problem.
af) Dhamrai-Kaliakoir 132 kV Ckt-2 tripped from 07:05 to 07:21(24/11/19) showing E/F relay.
ag) Sylhet-Chatak 132 kV Ckt-2 tripped from 07:21 to 07:42(24/11/19) showing dist.B-phase.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 822000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 100 | 2520000 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 360 | 6830536
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8684420 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 363 | 7288000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8515875 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3362851 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 92304
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 851040
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 35 | 237888 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 18240 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 43479 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 40009 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 24 | 58560 | Low demand
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1122180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 473900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 628200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 32 | 180792 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 148036 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 388272 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2199 | 42306582
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 150 | 3000000
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 10364 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 112455
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 15 | 41280 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 1001978 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 229 | 5060267
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 2385173 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 623088
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 98788 | Low demand
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 49698 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 234240 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 28800 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 217200
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 339840
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 25920 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27360
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 760 | 13256451
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1650962 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4327000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7086700 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 294 | 6850500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 440280 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 630720
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 44 | 401454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 190348 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2059590
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 74880 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 218988
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 51840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2124480
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 193800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 410120 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 1442100
| Cumilla Area Total |  |  |  | 3005 | 1394 | 28153762
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 159 | 3133840 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 218304
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 83520 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 600
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 1360800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 355 | 4797064
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Reserve
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Reserve
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 70 | 1081480 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 311 | 6985000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 473400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 530064
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 56296
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 35 | 207648 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 433920
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 182000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 39 | 402800 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 135855
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7300500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 357 | 7494000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 110700
| Sylhet Area Total |  |  |  | 1949 | 1356 | 25393663
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 784 | 10648000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 12 | 31680 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 315 | 7030080 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 201000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 478080 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 17 | 63936 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1221 | 18452776
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 320640 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 442024 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 174 | 3934387
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 10 | 65077 | Low demand
| Barisal Area Total |  |  |  | 462 | 241 | 4762128
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 353000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 136680
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 202 | 4632982 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 4682055 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 433 | 9174909 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 407040
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 303624
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 162162
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 12480 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 992 | 19864932
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4888900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 109 | 362880
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29915
| Rangpur Area Total |  |  |  | 605 | 309 | 5281695
| Total |  |  |  | 19132 | 8827 | 162269053
| Eastern Grid Total |  |  |  | 13568 | 6064 | 113907522
| Western Grid Total |  |  |  | 5564 | 2763 | 48361531
| National Grid Total |  |  |  | 19132 | 8827 | 162269053
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-23
(a) ENTIRE EASTERN GRID : |  | 5829 | MW | (b) ENTIRE WESTERN GRID : |  | 2538 | MW
i) Dhaka area |  | 3223 | MW | i) Khulna area |  | 974 | MW
ii) Chittagong area |  | 897 | MW | ii) Rajshahi area |  | 814 | MW
iii) Comilla area |  | 729 | MW | iii) Barisal area |  | 210 | MW
iv) Mymensingh area |  | 652 | MW | iv) Rangpur area |  | 540 | MW
v) Sylhet area |  | 328 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8367 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1600 | Srimongal | 26 | 1800 | Bottail | 100 | 1800
Munsiganj | 88 | 2000 | Shahjibazar | 80 | 1800 | G.K Project | 26 | 1800
Sonargaon | 56 | 1800 | Fenchuganj | 24 | 1800 | Faridpur | 120 | 1800
Shyampur | 160 | 1000 | Kulawara | 33 | 1800 | Madaripur | 56 | 1930
Bhulta | 153 | 1930 | Sylhet | 96 | 1800 | Sariatpur | 38 | 1900
Madanganj | 39 | 900 | Chatak | 17 | 1800 | Gopalganj | 55 | 1900
Shitalakhya | 103 | 1700 | Sunamganj | 28 | 1930 | Bagerhat | 55 | 1800
Rahim steel | 13 | 1830 | Biani Bazar | 33 | 1830 | Mongla | 34 | 1000
Matuail | 88 | 1200 | Comilla (S) | 130 | 1800 | Satkhira | 62 | 1900
Ghorasal | 65 | 1800 | Comilla(N) | 69 | 1900 | Gallamari | 34 | 2000
Narsingdi | 108 | 2000 | Chandpur | 68 | 1830 | Magura | 36 | 1800
Haripur (SBU) | 76 | 1830 | Feni | 93 | 1900 | Norail | 26 | 1830
Ullon | 56 | 1800 | Chowmuhani | 120 | 1930 | Chuadanga | 58 | 1800
Hasnabad | 152 | 1830 | Ashuganj | 40 | 2200 | Barisal(N) | 24 | 1930
Magbazar | 82 | 1300 | Daudkandi | 84 | 1830 | Barisal (S) | 68 | 1800
Maniknagar | 90 | 1300 | B.Baria | 92 | 1900 | Patuakhali | 75 | 2000
Bangabhaban | 12 | 1830 | Ramganj | 46 | 1830 | Bhandaria | 34 | 2000
Narinda | 78 | 1100 | Madunaghat | 43 | 1830 | Borhan Uddin | 27 | 2000
Dhanmondi | 106 | 1300 | Hathazari | 67 | 1900 | Ishurdi | 43 | 1800
Lalbag | 61 | 1300 | Khulshi | 166 | 1500 | Ruppur Paromanobik | 1 | 100
Madartek | 52 | 1830 | Halishahar | 94 | 1500 | Natore | 82 | 1800
Mirpur | 84 | 1800 | Baraulia | 158 | 1200 | Bogra | 138 | 1830
Kalyanpur | 81 | 1800 | Sikalbaha | 20 | 1900 | Noagaon | 76 | 1830
Gulshan | 88 | 1300 | Dohazari | 64 | 1830 | Rajshahi | 89 | 1830
Uttara | 43 | 1800 | Cox'sbazar | 70 | 1800 | Rajshahi New | 9 | 1830
Uttara New | 31 | 1800 | Chandraghona | 22 | 1800 | C.Nawabganj | 48 | 1930
Kamrangirchar | 65 | 1800 | Kaptai | 4 | 1800 | Amnura | 22 | 1830
Savar | 106 | 1800 | A. Khaer Stl. | 0 | 0 | Pabna | 73 | 1900
Bhasantec | 131 | 1830 | Bakulia | 78 | 1800 | Shahjadpur | 68 | 1800
Agargaon | 40 | 1830 | Julda | 16 | 100 | Serajganj | 63 | 1900
Satmosjid | 81 | 1830 | TK chemical | 11 | 1830 | Niyamatpur | 40 | 1830
Tongi | 121 | 1100 | Modern Steel | 13 | 700 | Joypurhat | 40 | 1800
Kabirpur | 163 | 1830 | Shahmirpur | 22 | 1800 | Sherpur(Bogura) | 30 | 1800
Basundhara | 88 | 1800 | Khagrachhari | 14 | 1800 | Mohastangor | 10 | 1800
Manikganj | 56 | 1830 | Matarbari | 21 | 1800 | Rangpur | 97 | 1900
Joydevpur | 163 | 1830 | Baroiar Hat | 16 | 1800 | Lalmonirhat | 42 | 1800
New Tongi | 87 | 1800 | Rangamati | 10 | 1800 | Saidpur | 81 | 1800
Korda | 206 | 1800 | Abul Khair 230 | 48 | 1400 | Purbasadipur | 72 | 1800
Dhamrai | 56 | 1830 | BSRM | 111 | 1830 | Thakurgaon | 57 | 1830
Valuka | 78 | 1800 | GPH Ispat | 2 | 1200 | Palashbari | 78 | 1800
Tangail | 135 | 1830 | Goalpara | 19 | 1830 | Barapukuria | 39 | 2000
Mymensing | 153 | 1800 | Central s/s | 66 | 1800 | Panchagar | 38 | 1830
Kishorganj | 80 | 1900 | Noapara | 42 | 1830 | Joldhaka | 19 | 1830
Netrokona | 72 | 1900 | Jessore | 86 | 1800 | Kurigram | 33 | 1800
Jamalpur | 87 | 1830 | Benapol | 28 | 1800 | 0 | 0 | 0
Sherpur | 70 | 1830 | Jhenida | 72 | 1900 | 0 | 0 | 0
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-23 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 389 | 2:00 | 377 | 11:00 | Kaliakoir | 375 | 3:00 | 358 | 12:00
Bheramara | 406 | 3:00 | 396 | 18:00 | Bhulta | 385 | 2:00 | 371 | 12:00
Ashuganj(N) | 388 | 8:00 | 376 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
Ghorasal | 232 | 1:00 | 226 | 11:00 | Hathazari | 222 | 1:00 | 210 | 11:00
Ishurdi | 242 | 3:00 | 228 | 18:00 | Megnaghat | 226 | 1:00 | 218 | 10:00
Ashuganj | 236 | 7:00 | 230 | 11:00 | Fenchuganj | 233 | 20:00 | 225 | 12:00
Serajganj | 233 | 1:00 | 229 | 18:00 | Siddhirganj | 227 | 2:00 | 218 | 12:00
Baghabari | 240 | 1:00 | 232 | 18:00 | Maniknagar | 225 | 2:00 | 216 | 12:00
Barapukuria | 231 | 3:00 | 222 | 18:00 | Old Airport | 224 | 2:00 | 213 | 12:00
Bogra | 234 | 5:00 | 222 | 18:00 | Barisal | 231 | 4:00 | 222 | 18:30
Khulna South | 239 | 3:00 | 221 | 18:30 | AKSML | 219 | 2:00 | 207 | 11:00
Rampura | 224 | 1:00 | 218 | 12:00 | BSRM | 221 | 1:00 | 210 | 11:00
Haripur | 222 | 1:00 | 218 | 15:00 | Bibiyana | 233 | 3:00 | 224 | 12:00
Hasnabad | 225 | 2:00 | 215 | 10:00 | Bhulta | 227 | 2:00 | 218 | 12:00
Aminbazar | 224 | 1:00 | 214 | 11:00 | Ashuganj (S) | 234 | 2:00 | 227 | 12:00
Tongi | 222 | 4:00 | 210 | 11:00 | Kaliakoir | 228 | 1:00 | 217 | 12:00
Comilla (N) | 233 | 2:00 | 224 | 12:00 | GPH | 219 | 7:00 | 207 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 130 | 1200 | Halishahar | 131 | 200 | 124 | 1100
Munsiganj | 134 | 100 | 129 | 1200 | Baraulia | 130 | 700 | 123 | 1100
Megnaghat | 133 | 300 | 130 | 1000 | Sikalbaha | 130 | 300 | 125 | 1100
Shyampur | 137 | 200 | 130 | 1200 | Dohazari | 130 | 100 | 123 | 1100
Bhulta | 130 | 300 | 125 | 1600 | Cox'sbazar | 126 | 200 | 120 | 2000
Madanganj | 136 | 1830 | 128 | 1100 | Chandraghona | 132 | 600 | 124 | 1100
Shitalakhya | 138 | 400 | 129 | 1200 | Kaptai | 132 | 100 | 128 | 900
Rahim steal | 136 | 100 | 132 | 1000 | A. Khaer Stl. | 130 | 100 | 124 | 1100
Matuail | 135 | 100 | 129 | 1300 | Bakulia | 130 | 600 | 121 | 1100
Ghorasal | 138 | 100 | 132 | 1200 | Julda | 130 | 100 | 123 | 1100
Narsinghdi | 135 | 300 | 129 | 1200 | TK Chemical | 130 | 500 | 127 | 1000
Haripur (SBU) | 137 | 300 | 131 | 1200 | Modern Steel | 130 | 100 | 125 | 1300
Ullon | 135 | 500 | 127 | 1200 | Shahmirpur | 130 | 400 | 122 | 1100
Hasnabad | 138 | 600 | 130 | 1200 | Khagrachhari | 131 | 100 | 126 | 1200
Magbazar | 135 | 600 | 127 | 1300 | Matarbari | 128 | 700 | 121 | 1100
Maniknagar | 138 | 600 | 134 | 1200 | Baroiar Hat | 134 | 100 | 124 | 1100
Bangabhaban | 138 | 600 | 134 | 1200 | Rangamati | 131 | 100 | 123 | 1100
Narinda | 138 | 600 | 134 | 1200 | Goalpara | 137 | 500 | 126 | 1800
Dhanmondi | 135 | 500 | 127 | 1200 | Central s/s | 135 | 100 | 124 | 1800
Lalbag | 139 | 500 | 129 | 1200 | Noapara | 134 | 100 | 125 | 1200
Madartek | 135 | 600 | 128 | 1200 | Jessore | 131 | 100 | 122 | 1800
Mirpur | 136 | 100 | 131 | 1300 | Benapol | 133 | 600 | 123 | 1830
Kalyanpur | 139 | 200 | 130 | 1000 | Jhenida | 134 | 100 | 121 | 1800
Gulshan | 134 | 100 | 127 | 1200 | Bottail | 136 | 100 | 127 | 1800
Uttara | 134 | 300 | 124 | 1200 | G.K Project | 141 | 200 | 135 | 1800
Uttara New | 135 | 100 | 126 | 1200 | Faridpur | 136 | 300 | 125 | 1800
Kamrangirchar | 137 | 100 | 128 | 1200 | Madaripur | 134 | 500 | 124 | 1800
Savar | 136 | 300 | 126 | 1100 | Sariatpur | 134 | 400 | 123 | 1800
Bhasantec | 135 | 200 | 127 | 1200 | Gopalganj | 137 | 400 | 125 | 1800
Agargaon | 136 | 200 | 128 | 1200 | Bagerhat | 136 | 300 | 124 | 1300
Satmosjid | 136 | 200 | 129 | 1100 | Mongla | 131 | 100 | 123 | 1200
Tongi | 135 | 400 | 126 | 1100 | Satkhira | 134 | 200 | 123 | 1800
Kabirpur | 132 | 100 | 124 | 1200 | Gallamari | 136 | 500 | 126 | 1800
Basundhara | 134 | 200 | 124 | 1200 | Magura | 135 | 100 | 120 | 1800
Manikganj | 138 | 500 | 124 | 1200 | Norail | 134 | 400 | 119 | 1800
Joydevpur | 137 | 700 | 128 | 1200 | Chuadanga | 133 | 200 | 116 | 1800
New Tongi | 134 | 100 | 124 | 1200 | Barisal(N) | 138 | 400 | 132 | 1830
Kodda | 135 | 600 | 125 | 1200 | Barisal (S) | 137 | 400 | 129 | 1800
Dhamrai | 133 | 600 | 125 | 1200 | Patuakhali | 135 | 300 | 125 | 1800
Valuka | 128 | 600 | 123 | 1800 | Bhandaria | 135 | 100 | 126 | 1800
Tangail | 133 | 500 | 125 | 1200 | Ishurdi | 138 | 200 | 130 | 1800
Mymensing | 131 | 400 | 126 | 1800 | Ruppur Paromanobik | 138 | 100 | 131 | 1800
Kishorganj | 134 | 900 | 129 | 1800 | Natore | 136 | 500 | 128 | 1800
Netrokona | 130 | 500 | 125 | 1800 | Bogra | 138 | 400 | 130 | 1800
Jamalpur | 137 | 1830 | 124 | 800 | Noagaon | 134 | 400 | 125 | 1800
Sherpur | 136 | 2000 | 123 | 700 | Rajshahi | 134 | 600 | 125 | 1200
Srimongal | 137 | 2200 | 129 | 1200 | Rajshahi New | 133 | 400 | 123 | 1200
Shahjibazar | 135 | 1800 | 129 | 1200 | C.Nawabganj | 131 | 100 | 119 | 1200
Fenchuganj | 135 | 2100 | 126 | 1200 | Amnura | 131 | 300 | 123 | 1200
Khulawara | 134 | 1930 | 127 | 1200 | Pabna | 138 | 200 | 130 | 1800
Sylhet | 133 | 2000 | 123 | 1200 | Shahjadpur | 142 | 100 | 136 | 1800
Chatak | 132 | 2000 | 123 | 1200 | Serajganj | 139 | 300 | 130 | 1200
Sunamganj | 132 | 1600 | 123 | 1200 | Niyamatpur | 134 | 300 | 124 | 1800
Biani Bazar | 133 | 2100 | 124 | 1200 | Joypurhat | 136 | 300 | 125 | 1800
Comilla(s) | 130 | 2200 | 125 | 1800 | Sherpur(Bogura) | 137 | 100 | 130 | 1200
Comilla(n) | 140 | 700 | 135 | 1500 | Mohastangor | 135 | 400 | 126 | 1800
Chandpur | 140 | 700 | 131 | 2200 | Rangpur | 129 | 300 | 122 | 1800
Feni | 137 | 900 | 126 | 1700 | Lalmonirhat | 125 | 300 | 120 | 1100
Chowmuhani | 134 | 900 | 125 | 2000 | Saidpur | 129 | 500 | 118 | 1800
Ashuganj | 139 | 700 | 135 | 1500 | Purbasadipur | 127 | 400 | 118 | 1300
Daudkandi | 135 | 700 | 129 | 1300 | Thakurgaon | 126 | 600 | 112 | 1800
B.Baria | 135 | 400 | 130 | 1200 | Palashbari | 132 | 600 | 124 | 1200
Ramganj | 127 | 1700 | 123 | 1900 | Barapukuria | 131 | 300 | 122 | 1800
Madanhat | 133 | 600 | 126 | 1100 | Panchagar | 124 | 600 | 105 | 1800
Hathazari | 132 | 100 | 126 | 1100 | Joldhaka | 129 | 300 | 116 | 1800
Khulshi | 130 | 600 | 122 | 1100 | Kurigram | 128 | 300 | 115 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 38 | 4746 | 1826 | 6572 |  |  |  | QF-LDC-12
0:30 | 34 | 4443 | 1705 | 6148 | Date: | 2019-11-23
1:00 | 30 | 4140 | 1584 | 5724
1:30 | 24 | 4045.5 | 1561 | 5606.5
2:00 | 18 | 3951 | 1538 | 5489
2:30 | 36.5 | 3883 | 1526.5 | 5409.5 | [5 empty] | Gen. at Eve. Peak | 8827 | 8827 MW (19:00 )
3:00 | 55 | 3815 | 1515 | 5330 | [6 empty] | 19:00
3:30 | 65 | 3779.5 | 1495.5 | 5275 | [5 empty] | Gen. at Day Peak | 6731.7 | 6731.7 MW (12:00 )
4:00 | 75 | 3744 | 1476 | 5220 | [6 empty] | 12:00
4:30 | 85 | 3734.5 | 1475.5 | 5210 | [5 empty] | Highest Generation | 8827
5:00 | 95 | 3725 | 1475 | 5200 | [6 empty] | 19:00
5:30 | 90.5 | 3759 | 1525.5 | 5284.5
6:00 | 86 | 3793 | 1576 | 5369
6:30 | 43 | 3889.4855 | 1600.1 | 5489.5855
7:00 | 0 | 3985.971 | 1624.2 | 5610.171
7:30 | 50 | 4134.7155 | 1636.15 | 5770.8655
8:00 | 100 | 4283.46 | 1648.1 | 5931.56
8:30 | 132.5 | 4279.88 | 1719.5 | 5999.38
9:00 | 165 | 4276.3 | 1790.9 | 6067.2
9:30 | 261 | 4176.55 | 1816.05 | 5992.6
10:00 | 357 | 4076.8 | 1841.2 | 5918
10:30 | 384.5 | 4224.05 | 1887.5 | 6111.55
11:00 | 412 | 4371.3 | 1933.8 | 6305.1
11:30 | 363.5 | 4549.9 | 1968.5 | 6518.4
12:00 | 315 | 4728.5 | 2003.2 | 6731.7
12:30 | 229.5 | 4761.57 | 2015.05 | 6776.62
13:00 | 144 | 4794.64 | 2026.9 | 6821.54
13:30 | 222 | 4673.965 | 2008 | 6681.965
14:00 | 300 | 4553.29 | 1989.1 | 6542.39
14:30 | 330 | 4596.73 | 1978.7 | 6575.43
15:00 | 360 | 4640.17 | 1968.3 | 6608.47
15:30 | 327.5 | 4662.06 | 1956 | 6618.06
16:00 | 295 | 4683.95 | 1943.7 | 6627.65
16:30 | 301.5 | 4825.475 | 2018.9 | 6844.375
17:00 | 308 | 4967 | 2094.1 | 7061.1
17:30 | 156.5 | 5511.5 | 2410.55 | 7922.05
18:00 | 5 | 6056 | 2727 | 8783
18:30 | 27.5 | 6060 | 2745 | 8805
19:00 | 50 | 6064 | 2763 | 8827
19:30 | 45 | 6070 | 2726 | 8796
20:00 | 19 | 5958 | 2643 | 8601 |  |  |  | Executive Engineer
20:30 | 40.5 | 5850.5 | 2613 | 8463.5 |  |  |  | Network Operation Division
21:00 | 62 | 5743 | 2583 | 8326
21:30 | 94 | 5547.5 | 2490.5 | 8038
22:00 | 126 | 5352 | 2398 | 7750 |  |  |  |  | Page 6 of 7
22:30 | 139.5 | 5099 | 2290 | 7389
23:00 | 153 | 4846 | 2182 | 7028
23:30 | 95.5 | 4796 | 2004 | 6800
24:00 | 38 | 4746 | 1826 | 6572
8827 MW (19:00 )
6731.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-23 |  | Energy | 162269053
[10 empty] | 2019-11-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4187 | 251 | 1599 | 189 | 200 | 43 | 7 | 0 | 96
0:30 | 3838.5 | 247 | 1501.5 | 225.5 | 200 | 43 | 3.5 | 0 | 89 | Date: | 2019-11-23
1:00 | 3490 | 243 | 1404 | 262 | 200 | 43 | 0 | 0 | 82
1:30 | 3418.5 | 243.5 | 1371.5 | 250.5 | 200 | 42.5 | 0 | 0 | 80 | [7 empty] | Total Energy | 162.2691 | Total Energy Gen 162.269 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.269 MKWHr
2:00 | 3347 | 244 | 1339 | 239 | 200 | 42 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 3309 | 244 | 1299.5 | 239 | 200 | 42 | 0 | 0 | 76 | [7 empty] | Energy Requirement | 162.2691
3:00 | 3271 | 244 | 1260 | 239 | 200 | 42 | 0 | 0 | 74
3:30 | 3240 | 243.5 | 1235.5 | 239 | 200 | 43 | 0 | 0 | 74 | [6 empty] | Shortage
4:00 | 3209 | 243 | 1211 | 239 | 200 | 44 | 0 | 0 | 74
4:30 | 3202 | 243.5 | 1208.5 | 239 | 200 | 44 | 0 | 0 | 73
5:00 | 3195 | 244 | 1206 | 239 | 200 | 44 | 0 | 0 | 72
5:30 | 3265.5 | 244 | 1219.5 | 239 | 200 | 44.5 | 0 | 0 | 72
6:00 | 3336 | 244 | 1233 | 239 | 200 | 45 | 0 | 0 | 72
6:30 | 3423.5 | 243.5 | 1266 | 239 | 200 | 45 | 0 | 0 | 71 |  |  |  |  | Coal
7:00 | 3511 | 243 | 1299 | 239 | 200 | 45 | 0 | 0 | 70
7:30 | 3629.5 | 243 | 1333 | 239 | 200 | 45 | 0 | 0 | 74 |  |  |  | Oil |  |  |  | ,
8:00 | 3748 | 243 | 1367 | 239 | 200 | 45 | 0 | 0 | 78
8:30 | 3712 | 315.5 | 1349.5 | 287.5 | 200 | 43.5 | 0 | 0 | 77
9:00 | 3676 | 388 | 1332 | 336 | 200 | 42 | 0 | 0 | 76
9:30 | 3583.5 | 413 | 1291 | 366 | 200 | 43.5 | 0 | 0 | 75
10:00 | 3491 | 438 | 1250 | 396 | 200 | 45 | 0 | 0 | 74
10:30 | 3595.5 | 442 | 1321.5 | 405.5 | 200 | 45 | 0 | 0 | 77
11:00 | 3700 | 446 | 1393 | 415 | 200 | 45 | 0 | 0 | 80
11:30 | 3814.5 | 445 | 1463.5 | 442 | 200 | 42.5 | 2.5 | 0 | 82
12:00 | 3929 | 444 | 1534 | 469 | 200 | 40 | 5 | 0 | 84
12:30 | 3957.5 | 444.5 | 1586 | 433.5 | 200 | 40 | 6.5 | 0 | 83
13:00 | 3986 | 445 | 1638 | 398 | 200 | 40 | 8 | 0 | 82
13:30 | 3986 | 445 | 1638 | 398 | 200 | 40 | 8 | 0 | 82
14:00 | 3986 | 445 | 1638 | 398 | 200 | 40 | 8 | 0 | 82
14:30 | 3857.5 | 445 | 1685 | 378 | 200 | 38.5 | 8 | 0 | 84
15:00 | 3729 | 445 | 1732 | 358 | 200 | 37 | 8 | 0 | 86
15:30 | 3751 | 445 | 1723.5 | 358 | 200 | 37 | 8 | 0 | 86
16:00 | 3773 | 445 | 1715 | 358 | 200 | 37 | 8 | 0 | 86
16:30 | 3878.5 | 445 | 1743.5 | 440 | 200 | 37 | 8.5 | 0 | 89
17:00 | 3984 | 445 | 1772 | 522 | 200 | 37 | 9 | 0 | 92
17:30 | 4261.5 | 615 | 1878.5 | 778.5 | 200 | 37.5 | 40 | 0 | 111
18:00 | 4539 | 785 | 1985 | 1035 | 200 | 38 | 71 | 0 | 130
18:30 | 4539 | 784.5 | 2009 | 1058.5 | 200 | 41.5 | 45.5 | 0 | 127
19:00 | 4539 | 784 | 2033 | 1082 | 200 | 45 | 20 | 0 | 124
19:30 | 4545 | 784 | 2042 | 1041 | 199 | 45 | 20 | 0 | 120
20:00 | 4527 | 785 | 2040 | 875 | 200 | 45 | 7 | 0 | 122
20:30 | 4520.5 | 785 | 2011 | 774 | 200 | 45 | 7 | 0 | 121
21:00 | 4514 | 785 | 1982 | 673 | 200 | 45 | 7 | 0 | 120
21:30 | 4432 | 785 | 1934 | 518 | 200 | 45 | 7 | 0 | 117
22:00 | 4350 | 785 | 1886 | 363 | 200 | 45 | 7 | 0 | 114
22:30 | 4254 | 688.5 | 1811 | 276 | 200 | 44.5 | 7 | 0 | 108
23:00 | 4158 | 592 | 1736 | 189 | 200 | 44 | 7 | 0 | 102
23:30 | 4172.5 | 421.5 | 1667.5 | 189 | 200 | 43.5 | 7 | 0 | 99 | Max Temp. in Dhaka |  | 28.8° C
24:00 | 4187 | 251 | 1599 | 189 | 200 | 43 | 7 | 0 | 96
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
Total Energy Gen 162.269 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.269 MKWHr
Note on W13: Author:

## Generation
2019-11-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 42 | 42 | 44 | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 40 | 40 | 40 | 37 | 37 | 37 | 38 |  | 45 | 45 | 45 | 45 | 45 | 44 | 43 | 1001978
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3000000
5 | Raozan 25 MW PP | [26 empty] | 10364
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2.63 | 7.46 | 12.6 | 15.8 | 16.9 | 17.1 | 15.64 | 13 | 9 | 4 | 0 | [9 empty] | 112455
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 229 | 203 | 180 | 189 | 187 | 215 | 202 | 181 | 228 | 230 | 230 | 231 | 229 | 230 | 231 | 230 |  | 229 | 229 | 229 | 229 | 229 | 203 | 205 | 5060267
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 144 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | 80 | 120 | 80 | 80 | 80 | 80 | 144 |  | 145 | 145 | 144 | 144 | 144 | 147 | 148 | 2385173
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 1 | 34 |  | 0 | 0 | [5 empty] | 49698
12 | Hathazari 100 MW peaking PP | [10 empty] | 0 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 98788
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 51 | 51 | 17 | 17 | 17 | 17 | 75 |  | 105 | 105 | 105 | 51 | 34 |  |  | 623088
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 0 | 36 |  | 45 | 45 | 15 | 0 | 0 |  |  | 148036
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 44 |  | 44 | 44 | 44 | 44 | 44 | 36 | 8 | 401454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 822000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2520000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 220 | 250 | 230 | 280 | 320 | 350 | 320 | 320 | 320 | 320 | 340 |  | 360 | 380 | 380 | 380 | 380 | 340 | 340 | 6830536
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1650962
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 440280
33 | Ashuganj 225 MW CCPP | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 180 | 204 | 183 | 182 | 200 | 200 | 181 | 181 | 181 | 201 | 200 |  | 198 | 198 | 198 | 198 | 200 | 205 | 205 | 4327000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 235 | 235 | 235 | 290 | 290 | 260 | 275 | 360 | 345 | 305 | 275 | 275 | 275 | 275 | 320 |  | 294 | 300 | 300 | 300 | 260 | 265 | 260 | 6850500
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 220 | 220 | 220 | 220 | 285 | 285 | 260 | 275 | 305 | 355 | 320 | 285 | 265 | 260 | 265 | 350 |  | 330 | 330 | 330 | 330 | 260 | 265 | 265 | 7086700
35 | Ashuganj 55 MW PP (Precision) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 51 | 50 | 51 | 51 | 51 |  | 52 | 52 | 52 | 52 | 52 | 53 | 5 | 630720
36 | Chandpur 150 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 86 | 87 | 50 | 50 | 95 | 95 | 91 | 95 | 95 | 95 | 96 |  | 96 | 93 | 92 | 90 | 95 | 95 | 95 | 2059590
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 344 | 344 | 348 | 347 | 373 | 373 | 366 | 359 | 357 | 381 | 378 | 384 | 347 | 361 | 349 | 375 | 362 |  | 346 | 344 | 344 | 343 | 343 | 344 | 367 | 8684420
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 260 | 260 | 260 | 290 | 320 | 340 | 340 | 300 | 340 | 370 | 420 | 420 | 420 | 420 | 420 | 420 |  | 420 | 420 | 420 | 420 | 420 | 390 | 390 | 8515875
41 | Haripur 360MW CCPP(HPL) | 310 | 250 | 210 | 185 | 185 | 240 | 270 | 300 | 309 | 258 | 259 | 353 | 358 | 359 | 324 | 324 | 322 | 361 |  | 363 | 363 | 363 | 363 | 363 | 363 | 363 | 7288000
42 | RPCL 210MW CCPP | 110 | 110 | 110 | 110 | 110 | 111 | 110 | 160 | 160 | 125 | 124 | 124 | 125 | 125 | 124 | 125 | 125 | 157 |  | 159 | 160 | 159 | 160 | 160 | 160 | 160 | 3133840
43
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 248 | 240 | 238 | 248 | 252 | 263 | 267 | 253 | 238 | 252 | 255 | 268 | 252 | 258 | 256 | 260 | 305 | 313 |  | 311 | 310 | 307 | 307 | 262 | 263 | 265 | 6985000
47 | Shahjibazar GTPP Unit- 8 & 9 | [17 empty] | 5 |  | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 207648
48 | Shahjibazar 86MW PP (Shahjibazar) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 80 |  | 80 | 80 | 80 | 40 | 40 | 0 |  | 433920
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [12 empty] | 0 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 182000
52 | Sylhet 50MW PP (EPL) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 3 | 2 | 2 | 29 | 39 | 34 | 36 | 11 | 37 |  | 39 | 40 | 41 | 40 | 40 | 40 | 0 | 402800
53 | Sylhet 10MW PP (Desh) | [12 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 110700
54 | Hobiganj 11MW PP Cofidence-E | [17 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 56296
55 | Fenchugonj 51 MW PP (Barakatullah) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 53 | 53 | 53 | 11 | 53 |  | 53 | 53 | 53 | 53 | 53 | 4 | 0 | 473400
56 | Shahjahanulla 25 MW PP | [16 empty] | 0 | 24 |  | 24 | 24 | 24 | 24 | 24 |  |  | 135855
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 290 | 295 | 270 | 265 | 280 | 280 | 310 | 305 | 275 | 320 | 315 | 310 | 265 | 305 | 300 | 315 | 305 |  | 300 | 305 | 300 | 295 | 260 | 260 | 290 | 7300500
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 17 | [8 empty] | 40009
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 0 | [11 empty] | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 217200
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 |  |  | 92304
62 | Tangail 22 MW PP (Doreen) | [12 empty] | 22 | 20 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 218304
63 | Impoprt (Tripura) | 82 | 78 | 74 | 74 | 72 | 72 | 70 | 78 | 76 | 74 | 80 | 84 | 82 | 88 | 86 | 86 | 92 | 130 |  | 124 | 120 | 122 | 120 | 114 | 102 | 96 | 2124480
64 | Malancha, Ctg. EPZ (United) | 5 | 5 | 5 | 5 | 5 | 7 | 6 | 4 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 6 | 6 | 2 |  | 14 | 18 | 25 | 31 | 36 | 36 | 39 | 339840
65 | Feni 22MW PP (Doreen) | [12 empty] | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 218988
66 | Feni 11 MW PP (Doreen) | [17 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 51840
67 | Jangalia 33MW PP (Summit) | [16 empty] | 10 | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 193800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 18 | 18 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 410120
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | [7 empty] | 26 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 22 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 522180
71 | Maona 33 MW PP(Summit) | [8 empty] | 0 | 0 | 0 | [6 empty] | 14 |  | 28 | 28 | 28 | 28 | 28 | 18 | 18 | 473900
72 | Rupganj 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 628200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 115 | [14 empty] | 1442100
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [15 empty] | 0 | 14 | 52 |  | 32 | 32 | 32 | 16 |  |  |  | 180792
79 | Kodda 150MW PP | [16 empty] | 0 | 16 | [8 empty] | 18240
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 0 | 14 |  | 24 | 24 | 24 | 0 | 0 |  |  | 83520
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [8 empty] | 35 | 35 | 35 | 17 | 35 | 17 |  |  | 17 | 88 |  | 52 | 52 | 17 |  |  |  |  | 388272
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.241 | 2.4 | 1.7 | 4 | 4.4 | 4.4 | 4 | 3.29 | 2.17 | 0.95 | [10 empty] | 27360
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 | 120 | 120 | 120 | 120 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3362851
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 15 | 30 | 30 | 10 | 0 | 0 | 30 | 80 |  | 30 | 10 | 10 | 0 | 0 |  |  | 234240
92 | Fenchuganj 44MW (Energyprima) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 12 | 43 | 46 | 43 | 10 | 33 |  | 49 | 49 | 50 | 50 | 50 | 50 | 0 | 530064
93 | Ashuganj 51 MW PP (Midland) | [16 empty] | 0 | 21 |  | 35 | 35 | 35 | 35 | 35 | 0 |  | 190348
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 5 | 7 | 7 | 7 | 7 | 60 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 0 | 0 |  | 851040
95 | Patenga 50MW PP (Baraka) | [16 empty] | 2 | 18 |  | 15 | 3 | [5 empty] | 41280
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 |  | 6 | 11 | [12 empty] | 25920
97 | Katpotti 52 MW PP (Sinha) | 6 | 0 | [6 empty] | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 13 |  | 35 | 47 | 45 | 30 | 18 | 6 | 6 | 237888
98 | Bosila 108MW PP(CLC) | [17 empty] | 14 |  | 24 | 24 | [5 empty] | 58560
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 17 | [8 empty] | 43479
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 0 | [9 empty] | 0 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 1081480
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.6 | 0 | 0 | [16 empty] | 600
103 | Kamalaghat 54 MW PP(Banco Energy) | [26 empty] | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 21 | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 93 |  | 150 | 150 | 150 | 130 | 70 |  |  | 1360800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [11 empty] | 10 | 10 | 0 | 0 | [11 empty] | 28800
116 | Chandpur 200MW (Desh energy) | [16 empty] | 0 | 22 |  | 17 | 17 | 0 | 0 |  |  |  | 74880
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 354 | 292 | 291 | 295 | 303 | 321 | 317 | 388 | 355 | 301 | 328 | 278 | 235 | 113 | 208 | 270 | 292 | 373 |  | 357 | 356 | 355 | 355 | 355 | 354 | 355 | 7494000
| Jamalpur 115 MW PP (United) | [26 empty] | 0
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 4140 | 3951 | 3815 | 3744 | 3725 | 3793 | 3985.971 | 4283.46 | 4279.3 | 4076.8 | 4371.3 | 4728.5 | 4794.64 | 4553.29 | 4640.17 | 4683.95 | 4967 | 6056 |  | 6064 | 6070 | 5958 | 5743 | 5352 | 4846 | 4746 | 113907522
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 13 |  | 12 | 12 | 0 |  |  |  |  | 31680
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 0 | [5 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 35 | 17 | 17 | 478080
130
131
132
133
| Barisal 110 MW PP (Summit ) | [7 empty] | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 320640
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [17 empty] | 11 |  | 10 | 10 | 10 | 10 | 10 | 10 | 2 | 65077
| Bhola 225 MW CCPP | 171 | 166 | 177 | 178 | 176 | 176 | 177 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 177 |  | 174 | 170 | 158 | 153 | 154 | 176 | 173 | 3934387
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 19 | 19 | 19 | 19 | 19 | 10 | 11 | 14 | 14 | 14 | 17 | 16 | 15 | 16 | 20 | 21 |  | 25 | 25 | 25 | 25 | 24 | 23 | 22 | 442024
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 201000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 13 |  | 17 | 17 | 17 | 17 | 0 |  |  | 63936
146 | Bheramara HVDC | 243 | 244 | 244 | 243 | 244 | 244 | 243 | 243 | 388 | 438 | 446 | 444 | 445 | 445 | 445 | 445 | 445 | 785 |  | 784 | 784 | 785 | 785 | 785 | 592 | 251 | 10648000
147 | Bheramara 360 MW CCPP | 315 | 310 | 260 | 220 | 220 | 220 | 220 | 280 | 280 | 250 | 250 | 280 | 280 | 280 | 280 | 280 | 280 | 345 |  | 315 | 310 | 310 | 310 | 310 | 315 | 315 | 7030080
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 4888900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | [16 empty] | 30 | 40 |  | 50 | 50 | 50 | 50 | 60 | 60 | 60 | 353000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 130 | 130 | 130 | 130 | 130 | 166 | 186 | 183 | 179 | 178 | 204 | 214 | 214 | 190 | 181 | 175 | 193 | 205 |  | 202 | 202 | 201 | 198 | 187 | 190 | 203 | 4632982
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 170 | 191 | 191 | 191 | 185 | 185 | 194 | 211 | 204 | 190 | 189 | 200 | 209 |  | 210 | 205 | 206 | 203 | 187 | 184 | 179 | 4682055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 344 | 325 | 342 | 343 | 343 | 344 | 346 | 345 | 309 | 344 | 402 | 424 | 427 | 423 | 427 | 410 | 431 | 430 |  | 433 | 432 | 426 | 408 | 343 | 381 | 380 | 9174909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 5 | 5 | 5 | 5 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 |  | 407040
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 |  | 14 | 14 | 14 | 14 | 14 | 10 | 0 | 303624
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 162162
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 10 | 50 |  | 50 | 25 | 12 | 12 |  |  |  | 136680
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 6 | 8 |  | 0 | [6 empty] | 12480
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 51 | 64 |  | 109 | 113 | 71 | 40 |  |  |  | 362880
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.2 | 1.1 | 2.9 | 4.2 | 4.8 | 5.2 | 4.9 | 3.1 | 2.3 | 0.7 | 0.1 | 0 | [8 empty] | 29915
178
178