## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-25 | Monday
|  | Date (day): | 2019-11-25 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12270.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14625 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-24 | 2019-11-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under S/D
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 368 | 320 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas Shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 362 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 304 | 362 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 120 | 120 | 120 | 120 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 40 | 69 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 22 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 52 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 10 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 89 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1676 | 2143 | 3515 | 3962 | 656 | 1158
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 150 | 30 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.1 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 40 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 124 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 7 | 7 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 70 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 13 | 7 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 22 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.3 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 533.4 | 804 | 1440 | 1633 | 400 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 199 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 330 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 25 | 33 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 35 | 51 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 44 | 36 | 36 | 151 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 35 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 85 | 95 | 95
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 52 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 124 | 113 | 145
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 0 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 0 | 0 | 119 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1292 | 1404 | 1827 | 2140 | 469 | 24
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 158 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.6 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 177.6 | 288 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 30 | 52 | 52
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 270 | 257 | 270 | 270
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 78 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 34 | 41 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 395 | 365 | 400 | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1243 | 1509 | 1631 | 1631 | 0 | 159
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 591 | 784 | 601 | 797
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 305 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 17 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 941 | 1163 | 1096 | 2017 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 26 | 25 | 25 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 153 | 167 | 153 | 175
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 184 | 225 | 343 | 435 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 60 | 60 | 60 | 50 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 204 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 210 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 382 | 435 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 5 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 811 | 1006 | 1514 | 1778 | 341 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 199 | 290 | 290
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 114 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 204.8 | 313 | 411 | 437 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 7062.8 | 8855 | 12270.6 | 14625 | 1908 | 1624
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6695.1037 | 8394 | 11631.7805 | 13863.6081
A. |  | 2019-11-24 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 8855 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5470 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8855 | MW
3 | Day peak Generation : |  |  | 7062.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8394 | MW
4 | Evening peak Generation : |  |  | 8855 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 195.2055 | MKWHr | By Solar | 0.17262 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 166.4522 | MKWHr |  | By Oil: | 8.8678 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.4968 | MKWHr |  | By Hydro: | 0.9881 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1908 | MW | Dhaka | 3248 | 3248 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1624 | MW | Chittagong | 883 | 883 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3532 | MW | Khulna | 983 | 983 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1106.41 | MMCFD |  |  | Rajshahi | 823 | 823 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 157022186.612 | ii) Oil : | Taka | 57452936.08 | Comilla | 722 | 722 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 18391912 | Total | Taka | 232867034.692 | Mymensingh | 646 | 646 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.191 | MKWHr. | Sylhet | 327 | 327 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -20 | MW (E to W) at | 19:00 | hrs | Barisal | 216 | 216 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -225 | MW at | 8:00 | hrs | Rangpur | 546 | 546 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.1° C |  |  | Total | 8394 | 8394 |  | 0
B. |  | 2019-11-25 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 28.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14625 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
4 | Reserve(Generation end) |  |  |  | 5625 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 198.402 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5500 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.9076 | MKWHr. | ii) HVDC Flow at Peak Time |  | 784 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3203 | MKWHr. | iii) Maximum HVDC Flow : |  | 784 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 100.6 | 100.64 |  | (b) Today: | 100.6 |  | (c) Rule Curve: |  | 106.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 100 | 300 | 0 | 0 | 344 | 330 |  | 0 | 350 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 42 | 0 | 0 | 100 | 0 | 204 | 0 | 150 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 38 | 80 | 0 | 0 | 260 | 265 | 205 | 8 | 80 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 84 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 257 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 250 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 190 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 336 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4474 | 1695 | 6169 | 3967 | 250 | 1462 | 167 | 190 | 42 | 7 | 84 | 0 | 0 | 100.65
2:00 | 35 | 0 | 0 | 90 | 280 | 0 | 0 | 343 | 300 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 42 | 0 | 0 | 100 | 0 | 203 | 0 | 150 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 260 | 265 | 148 | 8 | 84 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 264 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 252 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4213 | 1658 | 5871 | 3830 | 252 | 1370 | 120 | 170 | 42 | 7 | 80 | 0 | 0 | 100.65
3:00 | 35 | 0 | 0 | 0 | 250 | 0 | 0 | 342 | 270 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 42 | 0 | 0 | 100 | 0 | 204 | 0 | 149 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 260 | 265 | 148 | 8 | 86 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 76 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 265 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4060 | 1655 | 5715 | 3715 | 251 | 1344 | 120 | 160 | 42 | 7 | 76 | 0 | 0 | 100.65
4:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 344 | 250 |  | 0 | 280 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 43 | 0 | 0 | 100 | 0 | 184 | 0 | 110 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 265 | 270 | 146 | 8 | 96 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 74 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 263 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3864 | 1649 | 5513 | 3542 | 251 | 1316 | 120 | 160 | 43 | 7 | 74 | 0 | 0 | 100.65
5:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 348 | 250 |  | 0 | 280 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 44 | 0 | 0 | 100 | 0 | 184 | 0 | 80 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 265 | 270 | 146 | 8 | 94 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 74 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 263 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3847 | 1623 | 5470 | 3490 | 251 | 1324 | 120 | 160 | 44 | 7 | 74 | 0 | 0 | 100.64
6:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 368 | 280 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 33 | 0 | 0 | 45 | 0 | 0 | 100 | 0 | 189 | 0 | 80 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 280 | 290 | 146 | 8 | 96 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 72 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 270 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4075 | 1666 | 5741 | 3675 | 251 | 1411 | 120 | 160 | 45 | 7 | 72 | 0 | 0 | 100.64
7:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 369 | 310 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 16 | 0 | 0 | 45 | 0 | 0 | 100 | 0 | 214 | 0 | 145 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 285 | 290 | 207 | 8 | 95 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 163 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 130 | 266 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 |  | 251 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 4333.3 | 1679.2 | 6012.5 | 3893 | 251 | 1466 | 120 | 160 | 45 | 7 | 68 | 2.5 | 0 | 100.63
8:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 368 | 360 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 16 | 0 | 0 | 45 | 0 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 4 | 80 | 0 | 0 | 290 | 320 | 205 | 8 | 90 | 34 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 72 | 168 | 0 | 22 | 0.5 | 0 | 0 | 0 | 9 | 130 | 264 | 36 | 0 | 0 | 0 | 0 | 20 | 10 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 |  | 250 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 0 | 159 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4647.9 | 1646.1 | 6294 | 4036 | 250 | 1576 | 138 | 159 | 45 | 7 | 72 | 11 | 0 | 100.63
9:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 344 | 365 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 30 | 18 | 16 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 203 | 0 | 145 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 300 | 325 | 207 | 8 | 85 | 33 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 90 | 164 | 0 | 22 | 1 | 0 | 0 | 0 | 47 | 100 | 256 | 35 | 0 | 0 | 0 | 0 | 26 | 10 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 8 | 0 | 3.2 | 0 | 0 | 0 | 0 |  | 395 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 7 | 0 | 0 | 159 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 |  | 4745.2 | 1811.3 | 6556.5 | 4016 | 395 | 1667 | 174 | 159 | 42 | 7 | 90 | 6.5 | 0 | 100.63
10:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 344 | 303 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 18 | 16 | 23 | 0 | 44 | 0 | 0 | 120 | 0 | 202 | 0 | 105 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 3 | 80 | 0 | 0 | 320 | 275 | 187 | 8 | 90 | 33 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 88 | 157 | 0 | 22 | 1.6 | 15 | 0 | 0 | 48 | 100 | 260 | 20 | 0 | 0 | 0 | 0 | 28 | 9 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 0 | 0 | 0 | 367 | 0 | 35 | 0 | 3.8 | 0 | 0 | 0 | 0 |  | 541 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 5 | 0 | 0 | 159 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 |  | 4679 | 1951.6 | 6630.6 | 3919 | 541 | 1591 | 257 | 159 | 44 | 7 | 88 | 24.6 | 0 | 100.63
11:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 351 | 303 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 18 | 16 | 25 | 0 | 42 | 0 | 0 | 120 | 0 | 210 | 0 | 105 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 3 | 80 | 0 | 0 | 345 | 305 | 182 | 8 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 92 | 154 | 0 | 22 | 1.6 | 30 | 0 | 0 | 46 | 100 | 267 | 40 | 0 | 0 | 0 | 0 | 33 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 386 | 0 | 35 | 0 | 4.3 | 0 | 0 | 0 | 0 |  | 591 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 5 | 0 | 0 | 186 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 4696 | 2075.1 | 6771.1 | 4037 | 591 | 1530 | 259 | 186 | 42 | 7 | 92 | 27.1 | 0 | 100.62
12:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 375 | 304 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 18 | 16 | 25 | 0 | 38 | 0 | 0 | 120 | 0 | 216 | 0 | 110 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 355 | 355 | 202 | 8 | 96 | 25 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 96 | 154 | 0 | 22 | 1.6 | 30 | 0 | 0 | 50 | 100 | 270 | 40 | 0 | 0 | 0 | 0 | 34 | 9 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 395 | 0 | 35 | 0 | 4.3 | 0 | 0 | 0 | 0 |  | 591 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 7 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 4922 | 2140.8 | 7062.8 | 4238 | 591 | 1606 | 259 | 200 | 38 | 7 | 96 | 27.8 | 0 | 100.62
13:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 385 | 322 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 18 | 33 | 25 | 0 | 38 | 0 | 0 | 120 | 0 | 203 | 0 | 125 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 10 | 80 | 0 | 0 | 290 | 290 | 200 | 8 | 92 | 33 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 100 | 153 | 0 | 22 | 1.5 | 30 | 0 | 0 | 50 | 163 | 265 | 65 | 4 | 0 | 0 | 0 | 36 | 9 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 371 | 0 | 35 | 0 | 4 | 0 | 0 | 0 | 0 |  | 591 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 7 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 |  | 5002.2 | 2158.6 | 7160.8 | 4137 | 591 | 1803 | 259 | 200 | 38 | 7 | 100 | 25.8 | 0 | 100.62
14:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 345 | 302 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 22 | 33 | 25 | 0 | 38 | 0 | 0 | 120 | 0 | 204 | 0 | 124 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 280 | 275 | 201 | 8 | 95 | 33 | 51 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 102 | 154 | 0 | 22 | 0.5 | 30 | 0 | 0 | 50 | 100 | 260 | 40 | 4 | 0 | 0 | 0 | 36 | 9 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.3 | 0 | 0 | 0 | 366 | 0 | 35 | 0 | 3.5 | 0 | 0 | 0 | 0 |  | 592 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 7 | 0 | 0 | 199 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 |  | 4750.3 | 2072.5 | 6822.8 | 4029 | 592 | 1576 | 259 | 199 | 38 | 7 | 102 | 20.8 | 0 | 0
15:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 350 | 283 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 22 | 33 | 25 | 0 | 38 | 0 | 0 | 120 | 0 | 204 | 0 | 124 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 4 | 80 | 0 | 0 | 280 | 275 | 200 | 8 | 95 | 33 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 108 | 153 | 0 | 22 | 0.7 | 30 | 0 | 0 | 50 | 100 | 261 | 40 | 4 | 0 | 0 | 0 | 38 | 9 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.49 | 0 | 0 | 0 | 365 | 0 | 35 | 0 | 2 | 0 | 0 | 0 | 0 |  | 592 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 7 | 0 | 0 | 199 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 |  | 4765.19 | 2103.9 | 6869.09 | 4040 | 592 | 1612 | 259 | 199 | 38 | 7 | 108 | 14.09 | 0 | 0
16:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 346 | 283 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 22 | 33 | 25 | 0 | 38 | 0 | 0 | 120 | 0 | 206 | 0 | 124 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 4 | 80 | 0 | 0 | 280 | 275 | 200 | 8 | 95 | 33 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 102 | 153 | 0 | 22 | 0.1 | 30 | 0 | 0 | 50 | 100 | 262 | 40 | 4 | 0 | 0 | 0 | 38 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 366 | 0 | 35 | 0 | 0.9 | 0 | 0 | 0 | 0 |  | 592 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 153 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 7 | 0 | 0 | 199 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 4758.3 | 2119.7 | 6878 | 4044 | 592 | 1627 | 259 | 199 | 38 | 11 | 102 | 6 | 0 | 0
17:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 359 | 283 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 22 | 33 | 27 | 0 | 38 | 0 | 0 | 120 | 0 | 212 | 0 | 123 | 0 |  | 0 | 7 | 5 | 12 | 0 | 4 | 16 | 2 | 80 | 0 | 0 | 280 | 275 | 199 | 8 | 95 | 33 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 14 | 21 | 110 | 157 | 3 | 22 | 0 | 30 | 0 | 0 | 50 | 100 | 261 | 40 | 4 | 0 | 0 | 0 | 39 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0.1 | 0 | 5 | 0 | 364 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 |  | 592 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 7 | 0 | 0 | 199 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 383 | 17 | 0 | 0 | 0 | 63 | 0 | 0.1 | 0 |  | 4884.1 | 2214.1 | 7098.2 | 4077 | 592 | 1654 | 408 | 199 | 38 | 20 | 110 | 0.2 | 0 | 0
18:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 365 | 360 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 59 | 0 | 34 | 0 | 17 | 17 | 19 | 25 | 22 | 22 | 33 | 52 | 0 | 39 | 0 | 0 | 120 | 0 | 217 | 0 | 136 | 0 |  | 0 | 7 | 34 | 70 | 8 | 24 | 16 | 8 | 80 | 0 | 0 | 360 | 350 | 199 | 44 | 95 | 33 | 50 | 0 | 10 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 128 | 157 | 8 | 22 | 0 | 30 | 30 | 50 | 50 | 163 | 274 | 63 | 78 | 0 | 0 | 0 | 40 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 47 | 0 | 401 | 0 | 88 | 36 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 177 | 24 | 16 | 0 | 40 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 426 | 17 | 0 | 0 | 4 | 109 | 0 | 0 | 0 |  | 5977 | 2721 | 8698 | 4557 | 783 | 2019 | 916 | 199 | 39 | 57 | 128 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 368 | 0 | 0 | 362 | 362 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 69 | 0 | 47 | 0 | 17 | 17 | 19 | 25 | 30 | 22 | 33 | 52 | 0 | 40 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 |  | 0 | 7 | 34 | 70 | 22 | 50 | 16 | 13 | 80 | 0 | 0 | 330 | 305 | 199 | 44 | 85 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 124 | 158 | 8 | 22 | 0 | 60 | 30 | 53 | 50 | 163 | 257 | 67 | 78 | 0 | 0 | 0 | 41 | 10 | 300 | 24 | 11 | 0 | 10 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 52 | 0 | 365 | 0 | 89 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 167 | 26 | 32 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 435 | 17 | 0 | 0 | 17 | 114 | 0 | 0 | 0 |  | 6148 | 2707 | 8855 | 4406 | 784 | 2147 | 1098 | 199 | 40 | 57 | 124 | 0 | 0 | 0
19:30 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 345 | 363 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 23 | 0 | 17 | 17 | 19 | 25 | 30 | 22 | 33 | 52 | 0 | 41 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 |  | 0 | 7 | 34 | 70 | 25 | 50 | 16 | 15 | 80 | 0 | 0 | 330 | 305 | 199 | 44 | 86 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 124 | 160 | 8 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 192 | 68 | 78 | 0 | 0 | 17 | 40 | 10 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 52 | 0 | 367 | 0 | 89 | 105 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 154 | 26 | 32 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 391 | 17 | 0 | 0 | 17 | 113 | 0 | 0 | 0 |  | 6077 | 2644 | 8721 | 4342 | 783 | 2092 | 1083 | 199 | 41 | 57 | 124 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 343 | 367 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 47 | 0 | 17 | 17 | 19 | 25 | 30 | 22 | 33 | 25 | 0 | 40 | 0 | 0 | 120 | 0 | 203 | 0 | 123 | 0 |  | 0 | 7 | 34 | 70 | 25 | 50 | 16 | 22 | 80 | 0 | 0 | 330 | 305 | 200 | 44 | 80 | 32 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 120 | 160 | 8 | 22 | 0 | 60 | 30 | 50 | 47 | 163 | 212 | 68 | 78 | 0 | 0 | 17 | 42 | 10 | 280 | 24 | 11 | 0 | 14 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 52 | 0 | 367 | 0 | 88 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 27 | 32 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 383 | 17 | 0 | 0 | 17 | 113 | 0 | 0 | 0 |  | 6079 | 2666 | 8745 | 4381 | 784 | 2085 | 1079 | 199 | 40 | 57 | 120 | 0 | 0 | 0
21:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 343 | 365 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 47 | 0 | 0 | 0 | 19 | 25 | 30 | 22 | 33 | 32 | 0 | 40 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 |  | 0 | 0 | 17 | 30 | 25 | 48 | 16 | 24 | 80 | 0 | 0 | 330 | 305 | 162 | 44 | 80 | 32 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 118 | 162 | 8 | 22 | 0 | 60 | 30 | 50 | 50 | 130 | 217 | 68 | 78 | 0 | 0 | 17 | 41 | 10 | 270 | 24 | 11 | 0 | 14 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 20 | 0 | 367 | 0 | 70 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 185 | 26 | 32 | 0 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 383 | 17 | 0 | 0 | 17 | 40 | 0 | 0 | 0 |  | 5820 | 2546 | 8366 | 4331 | 784 | 2044 | 833 | 199 | 40 | 17 | 118 | 0 | 0 | 0
22:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 343 | 365 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 19 | 25 | 31 | 0 | 33 | 0 | 0 | 41 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 29 | 80 | 0 | 0 | 330 | 305 | 158 | 44 | 92 | 32 | 52 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 108 | 161 | 0 | 22 | 0 | 60 | 30 | 50 | 50 | 130 | 215 | 69 | 78 | 0 | 0 | 17 | 41 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 17 | 53 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 25 | 16 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5349 | 2396 | 7745 | 4324 | 784 | 2002 | 286 | 200 | 41 | 0 | 108 | 0 | 0 | 0
23:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 344 | 365 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 80 | 0 | 0 | 340 | 305 | 160 | 44 | 90 | 29 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 104 | 162 | 0 | 22 | 0 | 60 | 27 | 2 | 50 | 130 | 219 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 |  | 591 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 24 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4898 | 2188 | 7086 | 4176 | 591 | 1798 | 177 | 200 | 40 | 0 | 104 | 0 | 0 | 0
24:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 344 | 365 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 22 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 80 | 0 | 0 | 340 | 305 | 165 | 44 | 95 | 29 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 94 | 160 | 0 | 22 | 0 | 60 | 27 | 2 | 2 | 130 | 215 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 22 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4853 | 1843 | 6696 | 4193 | 251 | 1770 | 150 | 200 | 38 | 0 | 94 | 0 | 0 | 0
KWH | 802000 | 0 | 0 | 0 | 7413773 | 0 | 0 | 8669400 | 7618000 |  | 0 | 8695000 | 3174167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57120 | 0 | 576960 | 0 | 324384 | 0 | 210672 | 60864 | 100980 | 600000 | 685980 | 700000 | 717000 | 376404 | 0 | 988102 | 0 | 0 | 2800000 | 0 | 4863746 | 0 | 2982765 | 0 |  | 0 | 139109 | 122713 | 263640 | 93120 | 187200 | 406080 | 419520 | 1927770 | 0 | 0 | 7570200 | 7170000 | 4423000 | 451636 | 2124710 | 569304 | 857760 | 0 | 180628 | 0 | 0 | 0 | 356724 | 56520 | 175400 | 346790 | 2320320 | 3504440 | 47040 | 352476 | 9200 | 589000 | 190000 | 244800 | 792576 | 30633600 | 5696000 | 1088352 | 441600 | 0 | 0 | 67000 | 547440 | 143640 | 7253800 | 135252 | 66000 | 0 | 42655 | 0 | 0 | 614400 | 0 | 0 | 110295 | 0 | 194880 | 0 | 8691000 | 0 | 674208 | 485925 | 27960 | 0 | 0 | 0 | 0 |  | 11907636 | 0 | 7874784 | 0 | 0 | 0 | 0 | 0 | 1440 | 0 | 146250 | 3916659 | 467600 | 307392 | 0 | 590000 | 0 | 0 | 0 | 0 | 177610 | 0 | 0 | 0 | 0 | 154320 | 177768 | 182646 | 0 | 0 | 4496800 | 0 | 4000 | 4886318 | 0 | 0 | 0 | 0 | 0 | 4838618 | 0 | 9241818 | 98400 | 0 | 0 | 52416 | 434880 | 0 | 25162 | 0 |  | 145223000 | 49982517 | 195205517 | 98130687 | 11907636 | 68321506 | 8543467 | 4496800 | 988102 | 324382 | 2320320 | 172617 | 0
Fuel Cost | 898240 | 0 | 0 | 0 | 5486192.02 | 0 | 0 | 6241968 | 5789680 |  | 0 | 6956000 | 2856750.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566059.2 | 0 | 5250336 | 0 | 3036234.24 | 0 | 2009810.88 | 606205.44 | 75735 | 450000 | 0 | 0 | 0 | 3605950.32 | 0 | 256906.52 | 0 | 0 | 4284000 | 0 | 5106933.3 | 0 | 3788111.55 | 0 |  | 0 | 1473164.31 | 1287259.37 | 2712855.6 | 885571.2 | 1752192 | 373593.6 | 1166265.6 | 2024158.5 | 0 | 0 | 5601948 | 6022800 | 4069160 | 442603.28 | 2825864.3 | 466829.28 | 883492.8 | 0 | 258298.04 | 0 | 0 | 0 | 363858.48 | 42390 | 331506 | 260092.5 | 16010208 | 2873640.8 | 447350.4 | 359525.52 | 150880 | 801040 | 258400 | 332928 | 990720 | 37985664 | 5240320 | 1621644.48 | 777216 | 0 | 0 | 106530 | 640504.8 | 337554 | 5150198 | 101439 | 50160 | 0 | 446597.85 | 0 | 0 | 5910528 | 0 | 0 | 1272804.3 | 0 | 1827974.4 | 0 | 8169540 | 0 | 6007193.28 | 4591991.25 | 0 | 0 | 0 | 0 | 0 |  | 32150617.2 | 0 | 6142331.52 | 0 | 0 | 0 | 0 | 0 | 16704 | 0 | 1446412.5 | 3133327.2 | 724780 | 3301390.08 | 0 | 1109200 | 0 | 0 | 0 | 0 | 1841815.7 | 0 | 0 | 0 | 0 | 169752 | 293317.2 | 138263.022 | 0 | 0 | 18391912 | 0 | 112920 | 4299959.84 | 0 | 0 | 0 | 0 | 0 | 4257983.84 | 0 | 6746527.14 | 930864 | 0 | 0 | 467026.56 | 4061779.2 | 0 | 0 | 0 |  | 192971567.71 | 89736883.002 | 282708450.712 | 87376685.752 | 32150617.2 | 69645500.86 | 53996829.2 | 18391912 | 256906.52 | 3456106.88 | 16010208 | 1423684.3 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 375 | 304 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 30 | 18 | 16 | 25 | 0 | 38 | 0 | 0 | 120 | 0 | 216 | 0 | 110 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 355 | 355 | 202 | 8 | 96 | 25 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 96 | 154 | 0 | 22 | 1.6 | 30 | 0 | 0 | 50 | 100 | 270 | 40 | 0 | 0 | 0 | 0 | 34 | 9 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 395 | 0 | 35 | 0 | 4.3 | 0 | 0 | 0 | 0 |  | 591 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14 | 7 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 7062.8 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 368 | 0 | 0 | 362 | 362 | 0 | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 69 | 0 | 47 | 0 | 17 | 17 | 19 | 25 | 30 | 22 | 33 | 52 | 0 | 40 | 0 | 0 | 120 | 0 | 203 | 0 | 124 | 0 | 0 | 0 | 7 | 34 | 70 | 22 | 50 | 16 | 13 | 80 | 0 | 0 | 330 | 305 | 199 | 44 | 85 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 124 | 158 | 8 | 22 | 0 | 60 | 30 | 53 | 50 | 163 | 257 | 67 | 78 | 0 | 0 | 0 | 41 | 10 | 300 | 24 | 11 | 0 | 10 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 52 | 0 | 365 | 0 | 89 | 105 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 167 | 26 | 32 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 435 | 17 | 0 | 0 | 17 | 114 | 0 | 0 | 0 |  | 8855 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 0 | 150 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 15 | 80 | 0 | 0 | 360 | 360 | 200 | 36 | 95 | 37 | 55 | 0 | 35 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 145 | 160 | 95 | 22 | 0 | 60 | 52 | 51 | 44 | 163 | 270 | 66 | 79 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 797 | 40 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 175 | 25 | 110 | 30 | 60 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 290 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 0 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 7 | 80 | 0 | 0 | 360 | 360 | 200 | 36 | 95 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 113 | 160 | 95 | 22 | 1.6 | 60 | 52 | 51 | 44 | 163 | 270 | 66 | 79 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 119 |  | 601 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 70 | 0 | 60 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 370 | 364 | 0 | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 217 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 7 | 80 | 0 | 0 | 360 | 295 | 181 | 8 | 50 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 74 | 111 | 0 | 0 | 0.4 | 60 | 30 | 2 | 2 | 130 | 226 | 67 | 5 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 7 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0
199
| Minimum Generation |  | 5470 | 5:00
| Highest Generation |  | 8855 | 19:00
| Day Peak Generation |  | 7062.8 | 12:00
| Evening Peak Generation |  | 8855 | 19:00
| HVDC Max Flow |  | 784 | 19:00
| HVDC EvPeak Flow |  | 784 | 19:00
| Load factor L.F |  | 91.85%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-25
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7062.8 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5500 | MW
Evening Peak Generation : |  | 8855 | MW Hour : | 19:00 | Available Max Generation : |  | 14625 | MW
E.P. Demand (at gen end) : |  | 8855 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8855 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5625 | MW
Total Gen. (MKWH) : |  | 195.2055 | System Load Factor : | 91.85% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -225 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-25
Actual : | 100.6 | Ft.(MSL) , | Rule curve : | 106.6 | Ft.( MSL )
Gas Consumed : | Total = | 1106.41 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157022186.612
: |  | Coal : | 18391912 | Oil : | 57452936.08 | Total : | 232867034.692
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3187.387 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1078.3739 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 965.2047 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 871.7951 |  |  | 0 | 0%
) | 0 | 0:00 | 788.0209 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 635.8911 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 362.6547 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 163.9126 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 490.3968 |  |  | 0 | 0%
Total | 0 |  | 8543.637 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,3,4,5
4) Ashuganj unit-4 & 5
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Barapukuria ST: unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Aminbazar 230/132 kV Tr-3 transformer was under shut down from 08:41 to 16:57 for A/M.
b) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 09:12 to 16:38 for A/M.
c) Haripur 230/132 kV Tr-1 transformer was under shut down from 09:52 to 14:46 for A/M.
d) Manikganj 132/33 kV T-3 & T-4 transformer along with Kabirpur Ckt-1 were under shut down from
08:37 to 16:42 for A/M.
e) Ashuganj-Shahzibazar 132 kV Ckt-3 tripped at 10:49 from both end showing dist Z2 at Shahzibazar
end and L-1,L-2,L-3 trip, dist Z1 at 3-phase of Ashuganj end and was switched on at 20:14.
f) Ashuganj 230/132 kV OAT-12 tripped along with 132 kV Bus coupler at 10:49 showing master trip,
REF at 230 kV side and TCSR-1, master trip at 132 kV side and E/F at 132 kV and 132 kV
bus coupler CB closed on at 11:17 and transformer still under checking.
g) Uttara third phase 132/33 kV T-1 transformer was under shut down from 11:04 to 14:48 for A/M.
h) Bakulia-Sikalbaha 132 kV Ckt-2 was under shut down from 08:33 to 13:12 for A/M.
i) Rangpur-Saidpur 132 kV Ckt-1 was shut down at 08:50 for A/M.
j) Bagerhat 132/33 kV T-3 transformer was under shut down from 08:08 to 16:26 for A/M.
Gallamari 132/33 kV T-2 transformer was under shut down from 09:27 to 16:38 for A/M.
k) Jhenaidah-Magura 132 kV Ckt-1 was under shut down from 08:01 to 16:43 for A/M.
l) Bogura(o)-Mahasthangarh 132 kV Ckt-2 was switched on at 11:40 after Re-conducting work.
m) Ghorashal-Ashuganj 132 kV Ckt-1 was under shut down from 09:40 to 17:14 for A/M.
n) Mirpur 132/33 kV T-1 transformer was under shut down from 09:20 to 18:02 for A/M.
o) Tangail 132/33 kV T-3 transformer was under shut down from 08:20 to 16:20 for A/M.
p) Netrokona 132/33 kV T-2 transformer was under shut down from 08:05 to 16:10 for A/M.
q) Bibiyana 400/230 kV ICT-1 was under shut down from 08:28 to 16:21 for A/M.
r) Sonargaon-Haripur 132 kV Ckt-1 was under shut down from 07:55 to 15:26 for A/M.
s) Rajshahi 132 kV Grid-Rajshahi PPP 132 kV Ckt was under shut down from 09:33 to 16:02 for A/M.
t) Bheramara HVDC-Ishurdi 230 kV Ckt-2 was under shut down from 09:21 to 16:20 for A/M.
u) Bogura-Mahasthangarh 132 kV Ckt-2 along with Bogura 132 kV auxiliary bus was under shut down
from 13:04 to 15:16 for C/M.
v) Sikalbaha 132/33 kV T-4 transformer was under shut down from 07:00(25/11/2019) to 09:40 for |  |  |  |  | About 10 MW power interruption occurred under Sikalbaha S/S area
D/W by PDB. |  |  |  |  | from 07:00(25/11/2019) to 09:40.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 802000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 368 | 7413773
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 362 | 8669400 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 362 | 7618000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8695000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3174167 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 100980
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 324384
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 57120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 210672 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 60864 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 69 | 576960 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1285980 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 700000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 717000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 376404
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 10 | 42655 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 89 | 674208 | Engine problem
| Dhaka area Total |  |  |  | 5811 | 2143 | 41499567
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110295
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 187200
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 988102 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4863746 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 124 | 2982765 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 485925
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 7 | 139109 | Low demand
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 122713 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 263640 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 406080
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 419520
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 22 | 93120 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27960
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 804 | 13890175
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1927770 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4423000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7570200 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7170000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 569304 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 857760
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 44 | 451636 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 180628 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2124710
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 52 | 194880 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 356724
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 56520
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2320320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 175400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 346790 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0
| Cumilla Area Total |  |  |  | 3005 | 1404 | 28725642
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 158 | 3504440 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 352476
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 47040 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 614400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 288 | 4527556
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 589000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 190000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 30633600
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 257 | 5696000 | Frequency control.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 244800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 792576
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 66000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1088352 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 441600
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 67000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 41 | 547440 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 135252
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7253800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 365 | 8691000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 143640
| Sylhet Area Total |  |  |  | 1949 | 1509 | 56580060
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 784 | 11907636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 1440 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 7874784 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 146250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 98400 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 17 | 52416 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1163 | 20080926
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 307392 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 467600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 167 | 3916659
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 462 | 225 | 4691651
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 60 | 590000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 177610
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 204 | 4886318 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 4838618 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 435 | 9241818 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 154320
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 177768
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 182646
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1006 | 20249098
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4496800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 4000 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 114 | 434880
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25162
| Rangpur Area Total |  |  |  | 605 | 313 | 4960842
| Total |  |  |  | 19132 | 8855 | 195205517
| Eastern Grid Total |  |  |  | 13568 | 6148 | 145223000
| Western Grid Total |  |  |  | 5564 | 2707 | 49982517
| National Grid Total |  |  |  | 19132 | 8855 | 195205517
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-24
(a) ENTIRE EASTERN GRID : |  | 5826 | MW | (b) ENTIRE WESTERN GRID : |  | 2568 | MW
i) Dhaka area |  | 3248 | MW | i) Khulna area |  | 983 | MW
ii) Chittagong area |  | 883 | MW | ii) Rajshahi area |  | 823 | MW
iii) Comilla area |  | 722 | MW | iii) Barisal area |  | 216 | MW
iv) Mymensingh area |  | 646 | MW | iv) Rangpur area |  | 546 | MW
v) Sylhet area |  | 327 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8394 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 1500 | Srimongal | 26 | 1830 | Bottail | 102 | 1800
Munsiganj | 82 | 2000 | Shahjibazar | 78 | 1800 | G.K Project | 25 | 1830
Sonargaon | 60 | 1830 | Fenchuganj | 23 | 1800 | Faridpur | 124 | 1830
Shyampur | 172 | 1300 | Kulawara | 30 | 1800 | Madaripur | 56 | 2000
Bhulta | 159 | 1930 | Sylhet | 101 | 1800 | Sariatpur | 40 | 2000
Madanganj | 40 | 1200 | Chatak | 18 | 1800 | Gopalganj | 62 | 1800
Shitalakhya | 96 | 1200 | Sunamganj | 28 | 2000 | Bagerhat | 61 | 2000
Rahim steel | 17 | 1700 | Biani Bazar | 32 | 1800 | Mongla | 34 | 1100
Matuail | 86 | 1200 | Comilla (S) | 128 | 1800 | Satkhira | 62 | 1830
Ghorasal | 68 | 1800 | Comilla(N) | 77 | 2000 | Gallamari | 30 | 1800
Narsingdi | 108 | 2000 | Chandpur | 65 | 1930 | Magura | 36 | 1800
Haripur (SBU) | 88 | 1300 | Feni | 91 | 1830 | Norail | 26 | 1800
Ullon | 53 | 1700 | Chowmuhani | 122 | 1800 | Chuadanga | 57 | 1830
Hasnabad | 152 | 1800 | Ashuganj | 40 | 1800 | Barisal(N) | 27 | 2100
Magbazar | 87 | 1500 | Daudkandi | 88 | 1930 | Barisal (S) | 68 | 2000
Maniknagar | 86 | 1300 | B.Baria | 92 | 1830 | Patuakhali | 76 | 2000
Bangabhaban | 24 | 1000 | Ramganj | 44 | 1800 | Bhandaria | 34 | 1930
Narinda | 78 | 1200 | Madunaghat | 43 | 1800 | Borhan Uddin | 26 | 2100
Dhanmondi | 114 | 1300 | Hathazari | 73 | 1830 | Ishurdi | 46 | 1800
Lalbag | 61 | 1200 | Khulshi | 154 | 1800 | Ruppur Paromanobik | 1 | 100
Madartek | 51 | 1930 | Halishahar | 106 | 1800 | Natore | 74 | 1830
Mirpur | 80 | 1800 | Baraulia | 131 | 1100 | Bogra | 138 | 1830
Kalyanpur | 78 | 1900 | Sikalbaha | 19 | 1800 | Noagaon | 77 | 1830
Gulshan | 112 | 1400 | Dohazari | 72 | 1800 | Rajshahi | 89 | 1930
Uttara | 43 | 1800 | Cox'sbazar | 67 | 1900 | Rajshahi New | 8 | 1800
Uttara New | 32 | 1100 | Chandraghona | 22 | 1800 | C.Nawabganj | 47 | 1900
Kamrangirchar | 74 | 1830 | Kaptai | 3.5 | 1800 | Amnura | 22 | 1800
Savar | 102 | 1800 | A. Khaer Stl. | 0 | 100 | Pabna | 74 | 1800
Bhasantec | 112 | 1800 | Bakulia | 80 | 1830 | Shahjadpur | 69 | 1800
Agargaon | 43 | 1300 | Julda | 18 | 800 | Serajganj | 71 | 1830
Satmosjid | 77 | 1300 | TK chemical | 10 | 1800 | Niyamatpur | 40 | 2000
Tongi | 120 | 1500 | Modern Steel | 16 | 1000 | Joypurhat | 39 | 1900
Kabirpur | 170 | 1400 | Shahmirpur | 22 | 1830 | Sherpur(Bogura) | 30 | 1900
Basundhara | 82 | 1800 | Khagrachhari | 14 | 1800 | Mohastangor | 10 | 1800
Manikganj | 56 | 1800 | Matarbari | 23 | 1900 | Rangpur | 104 | 1830
Joydevpur | 158 | 1800 | Baroiar Hat | 16 | 1800 | Lalmonirhat | 42 | 1800
New Tongi | 92 | 1900 | Rangamati | 9 | 1800 | Saidpur | 84 | 1800
Korda | 205 | 1800 | Abul Khair 230 | 58 | 1200 | Purbasadipur | 73 | 1900
Dhamrai | 52 | 1800 | BSRM | 94 | 700 | Thakurgaon | 55 | 1900
Valuka | 80 | 1830 | GPH Ispat | 5.3 | 1700 | Palashbari | 84 | 1800
Tangail | 128 | 1900 | Goalpara | 18 | 1830 | Barapukuria | 43 | 2000
Mymensing | 149 | 1830 | Central s/s | 75 | 1330 | Panchagar | 38 | 1800
Kishorganj | 80 | 2000 | Noapara | 40 | 1800 | Joldhaka | 19 | 1800
Netrokona | 65 | 1800 | Jessore | 84 | 1800 | Kurigram | 33 | 1800
Jamalpur | 82 | 1800 | Benapol | 28 | 1800
Sherpur | 64 | 1800 | Jhenida | 74 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-24 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 389 | 1:00 | 380 | 12:00 | Kaliakoir | 374 | 3:00 | 357 | 16:00
Bheramara | 409 | 8:00 | 398 | 18:00 | Bhulta | 383 | 2:00 | 365 | 16:00
Ashuganj(N) | 386 | 4:00 | 373 | 13:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 16:00
Ghorasal | 232 | 1:00 | 222 | 17:00 | Hathazari | 221 | 19:30 | 215 | 12:00
Ishurdi | 241 | 3:00 | 228 | 18:00 | Megnaghat | 225 | 3:00 | 214 | 15:00
Ashuganj | 235 | 1:00 | 227 | 12:00 | Fenchuganj | 235 | 14:00 | 229 | 16:00
Serajganj | 233 | 1:00 | 229 | 18:30 | Siddhirganj | 226 | 3:00 | 215 | 12:00
Baghabari | 240 | 2:00 | 231 | 18:30 | Maniknagar | 224 | 4:00 | 213 | 13:00
Barapukuria | 231 | 3:00 | 224 | 18:00 | Old Airport | 223 | 1:00 | 212 | 12:00
Bogra | 233 | 3:00 | 224 | 18:00 | Barisal | 231 | 3:00 | 220 | 18:00
Khulna South | 236 | 4:00 | 218 | 18:00 | AKSML | 217 | 1:00 | 210 | 13:00
Rampura | 225 | 5:00 | 216 | 15:00 | BSRM | 220 | 3:00 | 213 | 11:00
Haripur | 222 | 2:00 | 214 | 12:00 | Bibiyana | 233 | 1:00 | 227 | 17:00
Hasnabad | 224 | 5:00 | 212 | 11:00 | Bhulta | 226 | 2:00 | 215 | 16:00
Aminbazar | 225 | 4:00 | 213 | 12:00 | Ashuganj (S) | 233 | 4:00 | 224 | 16:00
Tongi | 220 | 4:00 | 207 | 12:00 | Kaliakoir | 227 | 2:00 | 216 | 15:00
Comilla (N) | 231 | 5:00 | 222 | 12:00 | GPH | 217 | 8:00 | 212 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 127 | 1200 | Halishahar | 131 | 600 | 126 | 1100
Munsiganj | 134 | 600 | 125 | 1300 | Baraulia | 129 | 2000 | 124 | 1200
Sonargaon | 131 | 100 | 125 | 1300 | Sikalbaha | 130 | 300 | 125 | 1200
Shyampur | 137 | 800 | 128 | 1300 | Dohazari | 130 | 100 | 125 | 1200
Bhulta | 130 | 600 | 125 | 1200 | Cox'sbazar | 126 | 700 | 122 | 1100
Madanganj | 136 | 100 | 125 | 1300 | Chandraghona | 130 | 200 | 126 | 1200
Shitalakhya | 138 | 600 | 127 | 1200 | Kaptai | 130 | 2000 | 126 | 900
Rahim steal | 136 | 600 | 128 | 1200 | A. Khaer Stl. | 129 | 500 | 125 | 1100
Matuail | 134 | 600 | 125 | 1300 | Bakulia | 129 | 400 | 124 | 1200
Ghorasal | 138 | 700 | 130 | 100 | Julda | 130 | 2000 | 124 | 1200
Narsinghdi | 135 | 400 | 132 | 1200 | TK Chemical | 131 | 1930 | 126 | 1200
Haripur (SBU) | 135 | 600 | 129 | 1200 | Modern Steel | 130 | 1300 | 124 | 1100
Ullon | 133 | 100 | 126 | 1500 | Shahmirpur | 130 | 2000 | 125 | 1100
Hasnabad | 136 | 300 | 128 | 1200 | Khagrachhari | 130 | 100 | 126 | 1200
Magbazar | 135 | 200 | 126 | 1600 | Matarbari | 128 | 600 | 122 | 1300
Maniknagar | 137 | 200 | 130 | 1200 | Baroiar Hat | 130 | 2100 | 126 | 1100
Bangabhaban | 137 | 200 | 130 | 1200 | Rangamati | 130 | 400 | 125 | 1200
Narinda | 137 | 200 | 130 | 1200 | Goalpara | 136 | 2300 | 126 | 1800
Dhanmondi | 135 | 100 | 127 | 1200 | Central s/s | 135 | 400 | 127 | 800
Lalbag | 137 | 200 | 127 | 1200 | Noapara | 134 | 2300 | 125 | 1200
Madartek | 135 | 200 | 126 | 1300 | Jessore | 133 | 2300 | 121 | 1800
Mirpur | 137 | 400 | 128 | 1600 | Benapol | 133 | 2300 | 122 | 1800
Kalyanpur | 138 | 300 | 131 | 1200 | Jhenida | 133 | 100 | 120 | 1800
Gulshan | 134 | 500 | 126 | 1200 | Bottail | 137 | 600 | 126 | 1800
Uttara | 133 | 500 | 123 | 1200 | G.K Project | 140 | 300 | 134 | 1800
Uttara New | 136 | 400 | 127 | 1200 | Faridpur | 135 | 500 | 123 | 1800
Kamrangirchar | 137 | 300 | 126 | 1200 | Madaripur | 134 | 600 | 122 | 1800
Savar | 135 | 500 | 128 | 1100 | Sariatpur | 135 | 400 | 124 | 1800
Bhasantec | 135 | 300 | 127 | 1200 | Gopalganj | 135 | 100 | 125 | 1800
Agargaon | 136 | 500 | 128 | 1200 | Bagerhat | 132 | 100 | 124 | 1800
Satmosjid | 135 | 200 | 127 | 1200 | Mongla | 132 | 200 | 122 | 1800
Tongi | 134 | 400 | 125 | 1500 | Satkhira | 133 | 400 | 124 | 1800
Kabirpur | 132 | 600 | 124 | 1200 | Gallamari | 134 | 300 | 127 | 1200
Basundhara | 133 | 500 | 123 | 1300 | Magura | 134 | 200 | 120 | 1830
Manikganj | 136 | 400 | 124 | 1600 | Norail | 132 | 300 | 118 | 1800
Joydevpur | 137 | 500 | 129 | 1600 | Chuadanga | 131 | 100 | 117 | 1800
New Tongi | 133 | 700 | 124 | 1600 | Barisal(N) | 137 | 300 | 130 | 1800
Kodda | 133 | 700 | 126 | 1800 | Barisal (S) | 136 | 400 | 128 | 1800
Dhamrai | 132 | 300 | 124 | 1600 | Patuakhali | 135 | 400 | 125 | 1800
Valuka | 129 | 500 | 122 | 1200 | Bhandaria | 135 | 300 | 125 | 1800
Tangail | 132 | 400 | 125 | 1300 | Ishurdi | 137 | 600 | 131 | 1800
Mymensing | 130 | 500 | 124 | 1200 | Ruppur Paromanobik | 136 | 500 | 130 | 1800
Kishorganj | 134 | 1700 | 128 | 1100 | Natore | 134 | 600 | 128 | 1830
Netrokona | 130 | 500 | 123 | 1200 | Bogra | 136 | 600 | 130 | 1800
Jamalpur | 135 | 1700 | 121 | 1200 | Noagaon | 134 | 600 | 127 | 1800
Sherpur | 137 | 1700 | 121 | 1200 | Rajshahi | 131 | 600 | 124 | 1200
Srimongal | 137 | 900 | 134 | 100 | Rajshahi New | 132 | 600 | 122 | 1200
Shahjibazar | 136 | 700 | 133 | 100 | C.Nawabganj | 129 | 2000 | 120 | 1200
Fenchuganj | 136 | 2000 | 131 | 1500 | Amnura | 130 | 600 | 120 | 1200
Khulawara | 135 | 2100 | 131 | 100 | Pabna | 138 | 300 | 130 | 1800
Sylhet | 134 | 2000 | 130 | 100 | Shahjadpur | 144 | 400 | 136 | 1200
Chatak | 134 | 2100 | 128 | 1200 | Serajganj | 136 | 500 | 130 | 2000
Sunamganj | 133 | 2200 | 128 | 1200 | Niyamatpur | 134 | 400 | 124 | 1800
Biani Bazar | 133 | 900 | 129 | 1300 | Joypurhat | 135 | 600 | 125 | 1800
Comilla(s) | 131 | 600 | 125 | 1300 | Sherpur(Bogura) | 137 | 300 | 129 | 1800
Comilla(n) | 137 | 700 | 132 | 1200 | Mohastangor | 135 | 500 | 127 | 1800
Chandpur | 134 | 800 | 130 | 2100 | Rangpur | 129 | 600 | 122 | 1800
Feni | 131 | 800 | 126 | 1200 | Lalmonirhat | 125 | 600 | 117 | 1830
Chowmuhani | 127 | 700 | 124 | 1830 | Saidpur | 129 | 600 | 120 | 1800
Ashuganj | 138 | 800 | 136 | 1100 | Purbasadipur | 130 | 600 | 118 | 1200
Daudkandi | 133 | 700 | 126 | 1300 | Thakurgaon | 126 | 600 | 113 | 1800
B.Baria | 135 | 800 | 133 | 1900 | Palashbari | 133 | 600 | 125 | 1800
Ramganj | 128 | 700 | 124 | 1800 | Barapukuria | 131 | 600 | 124 | 1800
Madanhat | 132 | 2000 | 128 | 1100 | Panchagar | 121 | 600 | 109 | 1800
Hathazari | 132 | 600 | 128 | 1200 | Joldhaka | 126 | 700 | 120 | 1800
Khulshi | 128 | 400 | 123 | 1200 | Kurigram | 126 | 1700 | 119 | 1800
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 81 | 4853 | 1843 | 6696 |  |  |  | QF-LDC-12
0:30 | 40.5 | 4663.5 | 1769 | 6432.5 | Date: | 2019-11-24
1:00 | 0 | 4474 | 1695 | 6169
1:30 | 22 | 4343.5 | 1676.5 | 6020
2:00 | 44 | 4213 | 1658 | 5871
2:30 | 61.5 | 4136.5 | 1656.5 | 5793 | [5 empty] | Gen. at Eve. Peak | 8855 | 8855 MW (19:00 )
3:00 | 79 | 4060 | 1655 | 5715 | [6 empty] | 19:00
3:30 | 89 | 3962 | 1652 | 5614 | [5 empty] | Gen. at Day Peak | 7062.8 | 7062.8 MW (12:00 )
4:00 | 99 | 3864 | 1649 | 5513 | [6 empty] | 12:00
4:30 | 99 | 3855.5 | 1636 | 5491.5 | [5 empty] | Highest Generation | 8855
5:00 | 99 | 3847 | 1623 | 5470 | [6 empty] | 19:00
5:30 | 71 | 3961 | 1644.5 | 5605.5
6:00 | 43 | 4075 | 1666 | 5741
6:30 | 95 | 4204.15 | 1672.6 | 5876.75
7:00 | 147 | 4333.3 | 1679.2 | 6012.5
7:30 | 186 | 4490.6 | 1662.65 | 6153.25
8:00 | 225 | 4647.9 | 1646.1 | 6294
8:30 | 147.5 | 4696.55 | 1728.7 | 6425.25
9:00 | 70 | 4745.2 | 1811.3 | 6556.5
9:30 | 182.5 | 4712.1 | 1881.45 | 6593.55
10:00 | 295 | 4679 | 1951.6 | 6630.6
10:30 | 335 | 4687.5 | 2013.35 | 6700.85
11:00 | 375 | 4696 | 2075.1 | 6771.1
11:30 | 350 | 4809 | 2107.95 | 6916.95
12:00 | 325 | 4922 | 2140.8 | 7062.8
12:30 | 305 | 4962.1 | 2149.7 | 7111.8
13:00 | 285 | 5002.2 | 2158.6 | 7160.8
13:30 | 298.5 | 4876.25 | 2115.55 | 6991.8
14:00 | 312 | 4750.3 | 2072.5 | 6822.8
14:30 | 361 | 4757.745 | 2088.2 | 6845.945
15:00 | 410 | 4765.19 | 2103.9 | 6869.09
15:30 | 430 | 4761.745 | 2111.8 | 6873.545
16:00 | 450 | 4758.3 | 2119.7 | 6878
16:30 | 407 | 4821.2 | 2166.9 | 6988.1
17:00 | 364 | 4884.1 | 2214.1 | 7098.2
17:30 | 190 | 5430.55 | 2467.55 | 7898.1
18:00 | 16 | 5977 | 2721 | 8698
18:30 | 18 | 6062.5 | 2714 | 8776.5
19:00 | 20 | 6148 | 2707 | 8855
19:30 | 53 | 6077 | 2644 | 8721
20:00 | 63 | 6079 | 2666 | 8745 |  |  |  | Executive Engineer
20:30 | 54.5 | 5949.5 | 2606 | 8555.5 |  |  |  | Network Operation Division
21:00 | 46 | 5820 | 2546 | 8366
21:30 | 68 | 5584.5 | 2471 | 8055.5
22:00 | 90 | 5349 | 2396 | 7745 |  |  |  |  | Page 6 of 7
22:30 | 97.5 | 5123.5 | 2292 | 7415.5
23:00 | 105 | 4898 | 2188 | 7086
23:30 | 93 | 4875.5 | 2015.5 | 6891
24:00 | 81 | 4853 | 1843 | 6696
8855 MW (19:00 )
7062.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-24 |  | Energy | 195205517
[10 empty] | 2019-11-24 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4193 | 251 | 1770 | 150 | 200 | 38 | 0 | 0 | 94
0:30 | 4080 | 250.5 | 1616 | 158.5 | 195 | 40 | 3.5 | 0 | 89 | Date: | 2019-11-24
1:00 | 3967 | 250 | 1462 | 167 | 190 | 42 | 7 | 0 | 84
1:30 | 3898.5 | 251 | 1416 | 143.5 | 180 | 42 | 7 | 0 | 82 | [7 empty] | Total Energy | 195.2055 | Total Energy Gen 195.206 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 195.206 MKWHr
2:00 | 3830 | 252 | 1370 | 120 | 170 | 42 | 7 | 0 | 80 | [7 empty] | Energy not Served | 0
2:30 | 3772.5 | 251.5 | 1357 | 120 | 165 | 42 | 7 | 0 | 78 | [7 empty] | Energy Requirement | 195.2055
3:00 | 3715 | 251 | 1344 | 120 | 160 | 42 | 7 | 0 | 76
3:30 | 3628.5 | 251 | 1330 | 120 | 160 | 42.5 | 7 | 0 | 75 | [6 empty] | Shortage
4:00 | 3542 | 251 | 1316 | 120 | 160 | 43 | 7 | 0 | 74
4:30 | 3516 | 251 | 1320 | 120 | 160 | 43.5 | 7 | 0 | 74
5:00 | 3490 | 251 | 1324 | 120 | 160 | 44 | 7 | 0 | 74
5:30 | 3582.5 | 251 | 1367.5 | 120 | 160 | 44.5 | 7 | 0 | 73
6:00 | 3675 | 251 | 1411 | 120 | 160 | 45 | 7 | 0 | 72
6:30 | 3784 | 251 | 1438.5 | 120 | 160 | 45 | 7 | 0 | 70 |  |  |  |  | Coal
7:00 | 3893 | 251 | 1466 | 120 | 160 | 45 | 7 | 0 | 68
7:30 | 3964.5 | 250.5 | 1521 | 129 | 159.5 | 45 | 7 | 0 | 70 |  |  |  | Oil |  |  |  | ,
8:00 | 4036 | 250 | 1576 | 138 | 159 | 45 | 7 | 0 | 72
8:30 | 4026 | 322.5 | 1621.5 | 156 | 159 | 43.5 | 7 | 0 | 81
9:00 | 4016 | 395 | 1667 | 174 | 159 | 42 | 7 | 0 | 90
9:30 | 3967.5 | 468 | 1629 | 215.5 | 159 | 43 | 7 | 0 | 89
10:00 | 3919 | 541 | 1591 | 257 | 159 | 44 | 7 | 0 | 88
10:30 | 3978 | 566 | 1560.5 | 258 | 172.5 | 43 | 7 | 0 | 90
11:00 | 4037 | 591 | 1530 | 259 | 186 | 42 | 7 | 0 | 92
11:30 | 4137.5 | 591 | 1568 | 259 | 193 | 40 | 7 | 0 | 94
12:00 | 4238 | 591 | 1606 | 259 | 200 | 38 | 7 | 0 | 96
12:30 | 4187.5 | 591 | 1704.5 | 259 | 200 | 38 | 7 | 0 | 98
13:00 | 4137 | 591 | 1803 | 259 | 200 | 38 | 7 | 0 | 100
13:30 | 4137 | 591 | 1803 | 259 | 200 | 38 | 7 | 0 | 100
14:00 | 4137 | 591 | 1803 | 259 | 200 | 38 | 7 | 0 | 100
14:30 | 4088.5 | 591.5 | 1707.5 | 259 | 199.5 | 38 | 7 | 0 | 104
15:00 | 4040 | 592 | 1612 | 259 | 199 | 38 | 7 | 0 | 108
15:30 | 4042 | 592 | 1619.5 | 259 | 199 | 38 | 9 | 0 | 105
16:00 | 4044 | 592 | 1627 | 259 | 199 | 38 | 11 | 0 | 102
16:30 | 4060.5 | 592 | 1640.5 | 333.5 | 199 | 38 | 15.5 | 0 | 106
17:00 | 4077 | 592 | 1654 | 408 | 199 | 38 | 20 | 0 | 110
17:30 | 4317 | 687.5 | 1836.5 | 662 | 199 | 38.5 | 38.5 | 0 | 119
18:00 | 4557 | 783 | 2019 | 916 | 199 | 39 | 57 | 0 | 128
18:30 | 4481.5 | 783.5 | 2083 | 1007 | 199 | 39.5 | 57 | 0 | 126
19:00 | 4406 | 784 | 2147 | 1098 | 199 | 40 | 57 | 0 | 124
19:30 | 4342 | 783 | 2092 | 1083 | 199 | 41 | 57 | 0 | 124
20:00 | 4381 | 784 | 2085 | 1079 | 199 | 40 | 57 | 0 | 120
20:30 | 4356 | 784 | 2064.5 | 956 | 199 | 40 | 37 | 0 | 119
21:00 | 4331 | 784 | 2044 | 833 | 199 | 40 | 17 | 0 | 118
21:30 | 4327.5 | 784 | 2023 | 559.5 | 199.5 | 40.5 | 8.5 | 0 | 113
22:00 | 4324 | 784 | 2002 | 286 | 200 | 41 | 0 | 0 | 108
22:30 | 4250 | 687.5 | 1900 | 231.5 | 200 | 40.5 | 0 | 0 | 106
23:00 | 4176 | 591 | 1798 | 177 | 200 | 40 | 0 | 0 | 104
23:30 | 4184.5 | 421 | 1784 | 163.5 | 200 | 39 | 0 | 0 | 99 | Max Temp. in Dhaka |  | 29.1° C
24:00 | 4193 | 251 | 1770 | 150 | 200 | 38 | 0 | 0 | 94
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 195.206 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 195.206 MKWHr
Note on W13: Author:

## Generation
2019-11-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 43 | 44 | 45 | 45 | 45 | 45 | 44 | 42 | 38 | 38 | 38 | 38 | 38 | 38 | 39 |  | 40 | 41 | 40 | 40 | 41 | 40 | 38 | 988102
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.8 | 8.2 |  | 15.6 | 17.1 | 17.1 | 15.7 | 13.3 | 9.49 | 4.3 | 0.1 | [9 empty] | 110295
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 204 | 184 | 184 | 189 | 214 | 203 | 203 | 202 | 210 | 216 | 203 | 204 | 204 | 206 | 212 | 217 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4863746
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 150 | 150 | 149 | 110 | 80 | 80 | 145 | 144 | 145 | 105 | 105 | 110 | 125 | 124 | 124 | 124 | 123 | 136 |  | 124 | 124 | 123 | 124 | 124 | 124 | 124 | 2982765
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 5 | 34 |  | 34 | 34 | 34 | 17 | 0 | 0 |  | 122713
12 | Hathazari 100 MW peaking PP | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 0 | 0 |  |  | 139109
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 36 |  | 105 | 105 | 105 | 105 | 53 | 15 |  | 485925
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 0 |  | 10 | 14 | 14 | 14 | 0 | 0 |  | 42655
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 451636
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 802000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 90 | 0 | 0 | 0 | 0
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 280 | 250 | 220 | 220 | 220 | 220 | 300 | 320 | 320 | 300 | 300 | 320 | 320 | 320 | 320 | 320 | 320 |  | 368 | 380 | 380 | 380 | 380 | 380 | 380 | 7413773
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1927770
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 34 | 33 | 33 | 0 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 32 | 32 | 32 | 29 | 29 | 569304
33 | Ashuganj 225 MW CCPP | 205 | 148 | 148 | 146 | 146 | 146 | 207 | 205 | 207 | 187 | 182 | 202 | 200 | 201 | 200 | 200 | 199 | 199 |  | 199 | 199 | 200 | 162 | 158 | 160 | 165 | 4423000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 270 | 270 | 290 | 290 | 320 | 325 | 275 | 305 | 355 | 290 | 275 | 275 | 275 | 275 | 350 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 7170000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 265 | 265 | 280 | 285 | 290 | 300 | 320 | 345 | 355 | 290 | 280 | 280 | 280 | 280 | 360 |  | 330 | 330 | 330 | 330 | 330 | 340 | 340 | 7570200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 52 | 52 | 0 | 35 | 50 | 51 | 50 | 50 | 50 | 50 |  | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 857760
36 | Chandpur 150 MW CCPP | 80 | 84 | 86 | 96 | 94 | 96 | 95 | 90 | 85 | 90 | 95 | 96 | 92 | 95 | 95 | 95 | 95 | 95 |  | 85 | 86 | 80 | 80 | 92 | 90 | 95 | 2124710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 344 | 343 | 342 | 344 | 348 | 368 | 369 | 368 | 344 | 344 | 351 | 375 | 385 | 345 | 350 | 346 | 359 | 365 |  | 362 | 345 | 343 | 343 | 343 | 344 | 344 | 8669400
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 320 | 320 | 280 | 280 | 330 | 330 | 360 | 360 | 360 | 330 | 330 | 380 | 360 | 360 | 360 | 360 | 360 |  | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 8695000
41 | Haripur 360MW CCPP(HPL) | 330 | 300 | 270 | 250 | 250 | 280 | 310 | 360 | 365 | 303 | 303 | 304 | 322 | 302 | 283 | 283 | 283 | 360 |  | 362 | 363 | 367 | 365 | 365 | 365 | 365 | 7618000
42 | RPCL 210MW CCPP | 160 | 110 | 110 | 111 | 110 | 162 | 163 | 168 | 164 | 157 | 154 | 154 | 153 | 154 | 153 | 153 | 157 | 157 |  | 158 | 160 | 160 | 162 | 161 | 162 | 160 | 3504440
43
44 | Fenchugonj CCPP Phase-1 | [9 empty] | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 589000
45 | Fenchugonj CCPP Phase-2 | [17 empty] | 30 |  | 30 | 30 | 30 | 30 | 30 | 27 | 27 | 190000
46 | Shajibazar 330 MW CCPP | 257 | 264 | 265 | 263 | 263 | 270 | 266 | 264 | 256 | 260 | 267 | 270 | 265 | 260 | 261 | 262 | 261 | 274 |  | 257 | 192 | 212 | 217 | 215 | 219 | 215 | 5696000
47 | Shahjibazar GTPP Unit- 8 & 9 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 20 | 40 | 40 | 65 | 40 | 40 | 40 | 40 | 63 |  | 67 | 68 | 68 | 68 | 69 | 40 | 40 | 1088352
48 | Shahjibazar 86MW PP (Shahjibazar) | [11 empty] | 0 | 4 | 4 | 4 | 4 | 4 | 78 |  | 78 | 78 | 78 | 78 | 78 | 5 | 5 | 441600
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [20 empty] | 17 | 17 | 17 | 17 | 0 | 0 | 67000
52 | Sylhet 50MW PP (EPL) | [7 empty] | 20 | 26 | 28 | 33 | 34 | 36 | 36 | 38 | 38 | 39 | 40 |  | 41 | 40 | 42 | 41 | 41 | 0 | 0 | 547440
53 | Sylhet 10MW PP (Desh) | [7 empty] | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 143640
54 | Hobiganj 11MW PP Cofidence-E | [17 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 66000
55 | Fenchugonj 51 MW PP (Barakatullah) | [17 empty] | 50 |  | 53 | 50 | 50 | 50 | 50 | 2 | 2 | 244800
56 | Shahjahanulla 25 MW PP | [17 empty] | 24 |  | 24 | 24 | 24 | 24 | 24 |  |  | 135252
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 270 | 270 | 270 | 280 | 285 | 280 | 295 | 285 | 270 | 285 | 315 | 320 | 265 | 295 | 300 | 310 | 310 |  | 300 | 290 | 280 | 270 | 280 | 280 | 300 | 7253800
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  |  | 60864
59 | Sikalbaha 51 MW PP(Energis) | [11 empty] | 0
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 406080
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 |  |  | 100980
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 352476
63 | Impoprt (Tripura) | 84 | 80 | 76 | 74 | 74 | 72 | 68 | 72 | 90 | 88 | 92 | 96 | 100 | 102 | 108 | 102 | 110 | 128 |  | 124 | 124 | 120 | 118 | 108 | 104 | 94 | 2320320
64 | Malancha, Ctg. EPZ (United) | 38 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 3 | 3 | 3 | 5 | 10 | 5 | 4 | 4 | 2 | 8 |  | 13 | 15 | 22 | 24 | 29 | 16 | 15 | 419520
65 | Feni 22MW PP (Doreen) | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 356724
66 | Feni 11 MW PP (Doreen) | [17 empty] | 5 |  | 11 | 11 | 11 | 11 | 11 |  |  | 56520
67 | Jangalia 33MW PP (Summit) | [16 empty] | 14 | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 175400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 16 | 16 | 16 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 |  |  |  | 0 |  |  |  |  | 346790
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 22 |  | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 685980
71 | Maona 33 MW PP(Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 |  |  | 22 | 700000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 717000
73 | Ghorashal 108MW PP (Regent)
Feni Lanka Power
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [9 empty] | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 52 |  | 52 | 52 | 25 | 32 |  |  |  | 376404
79 | Kodda 150MW PP | [16 empty] | 8 | 16 |  | 16 | 16 | 16 |  |  |  |  | 57120
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 3 | 8 |  | 8 | 8 | 8 | 8 | 0 | 0 |  | 47040
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [8 empty] | 8 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 52 | 88 |  | 89 | 89 | 88 | 70 | 17 |  |  | 674208
| Kaptai 7 MW Solar PP | [6 empty] | 0.4 | 1.2 | 3.2 | 3.8 | 4.3 | 4.3 | 4 | 3.5 | 2 | 0.9 | 0 | 0 | [8 empty] | 27960
| Jodiac Power | [26 empty] | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3174167
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 12 | 70 |  | 70 | 70 | 70 | 30 | 0 | 0 |  | 263640
92 | Fenchuganj 44MW (Energyprima) | [7 empty] | 9 | 47 | 48 | 46 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 47 | 50 | 50 | 50 | 2 | 792576
93 | Ashuganj 51 MW PP (Midland) | [17 empty] | 10 |  | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 180628
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [16 empty] | 4 | 24 |  | 50 | 50 | 50 | 48 |  |  |  | 187200
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 8 |  | 22 | 25 | 25 | 25 |  |  |  | 93120
97 | Katpotti 52 MW PP (Sinha) | [7 empty] | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 34 |  | 47 | 23 | 47 | 47 | 30 | 18 | 6 | 324384
98 | Bosila 108MW PP(CLC) | [8 empty] | 24 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 59 |  | 69 | 72 | 72 | 44 |  |  |  | 576960
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  |  | 210672
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 163 | 100 | 100 | 100 | 100 | 163 |  | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 30633600
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.5 | 1 | 1.6 | 1.6 | 1.6 | 1.5 | 0.5 | 0.7 | 0.1 | 0 | 0 | [8 empty] | 9200
103 | Kamalaghat 54 MW PP(Banco Energy) | [26 empty] | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 26 | 100 |  | 100 | 100 | 100 | 100 | 50 | 24 | 24 | 614400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn)
116 | Chandpur 200MW (Desh energy) | [16 empty] | 5 | 47 |  | 52 | 52 | 52 | 20 | 0 | 0 |  | 194880
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 353 | 355 | 354 | 294 | 295 | 318 | 387 | 364 | 366 | 367 | 386 | 395 | 371 | 366 | 365 | 366 | 364 | 401 |  | 365 | 367 | 367 | 367 | 365 | 366 | 363 | 8691000
| Jamalpur 115 MW PP (United) | [26 empty] | 0
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 4474 | 4213 | 4060 | 3864 | 3847 | 4075 | 4333.3 | 4647.9 | 4748.2 | 4679 | 4696 | 4922 | 5002.2 | 4750.3 | 4765.19 | 4758.3 | 4884.1 | 5977 |  | 6148 | 6077 | 6079 | 5820 | 5349 | 4898 | 4853 | 145223000
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 0 | [9 empty] | 1440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 0 | [14 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 98400
130
131
132
133
| Barisal 110 MW PP (Summit ) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 16 | 0 |  | 307392
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 153 | 153 | 153 | 176 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 177 |  | 167 | 154 | 183 | 185 | 183 | 183 | 183 | 3916659
140 | Bhola 33 MW PP (Venture) | 20 | 20 | 19 | 19 | 18 | 19 | 19 | 17 | 17 | 16 | 16 | 15 | 18 | 17 | 18 | 18 | 19 | 24 |  | 26 | 26 | 27 | 26 | 25 | 24 | 22 | 467600
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 0 |  |  | 146250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 4 |  | 17 | 17 | 17 | 17 | 0 |  |  | 52416
146 | Bheramara HVDC | 250 | 252 | 251 | 251 | 251 | 251 | 251 | 250 | 395 | 541 | 591 | 591 | 591 | 592 | 592 | 592 | 592 | 783 |  | 784 | 783 | 784 | 784 | 784 | 591 | 251 | 11907636
147 | Bheramara 360 MW CCPP | 305 | 310 | 310 | 310 | 320 | 340 | 340 | 310 | 310 | 310 | 345 | 350 | 325 | 310 | 310 | 315 | 320 | 370 |  | 305 | 315 | 315 | 310 | 320 | 305 | 315 | 7874784
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 190 | 170 | 160 | 160 | 160 | 160 | 160 | 159 | 159 | 159 | 186 | 200 | 200 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 200 | 200 | 200 | 4496800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 60 | 60 | 60 | 0 | 0 | 0 | [11 empty] | 40 |  | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 590000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 188 | 186 | 190 | 189 | 177 | 185 | 186 | 187 | 174 | 171 | 176 | 205 | 205 | 198 | 202 | 200 | 203 | 205 |  | 204 | 193 | 193 | 187 | 186 | 191 | 184 | 4886318
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 171 | 157 | 157 | 157 | 158 | 171 | 184 | 188 | 184 | 183 | 186 | 198 | 206 | 208 | 212 | 213 | 206 | 214 |  | 210 | 207 | 206 | 195 | 198 | 196 | 197 | 4838618
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 336 | 345 | 350 | 382 | 381 | 382 | 381 | 350 | 380 | 380 | 383 | 382 | 414 | 350 | 374 | 383 | 383 | 426 |  | 435 | 391 | 383 | 383 | 377 | 416 | 433 | 9241818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [11 empty] | 5 | 5 | 5 | 5 | 5 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 |  | 154320
163 | Bogura 20 MW PP (Energyprima) | [7 empty] | 8 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 177768
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 7 | 5 | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 182646
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 50 | 50 | 50 | 24 | 0 |  |  | 177610
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [26 empty] | 4000
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 63 | 109 |  | 114 | 113 | 113 | 40 | 0 |  |  | 434880
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1.1 | 2.3 | 3.6 | 4.1 | 4.8 | 4.6 | 3.5 | 1.9 | 0.7 | 0.1 | 0 |  | 0 | [6 empty] | 25162
178
178