## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-28 | Thursday
|  | Date (day): | 2019-11-28 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11999.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14483 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-27 | 2019-11-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 128 | 129 | 135 | 135
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 320 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas Shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 376 | 363 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 358 | 363 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 120 | 120 | 120 | 120 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 5 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 16 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 90 | 42 | 100 | 100 | 105 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 53 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 52 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 107 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 34 | 17 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2001 | 2284 | 3750 | 4197 | 581 | 988
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 21 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 93 | 92 | 93 | 93 | 137 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 145 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 20 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 50 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 5 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 618.9 | 935 | 1491 | 1651 | 377 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 85 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 199 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under S/D
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 25 | 49 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 44 | 44 | 44 | 44 | 151 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 9 | 43 | 35 | 35 |  | 16 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 87 | 95 | 95
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 70 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 128 | 113 | 143
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 956 | 1294 | 1396 | 1826 | 429 | 24
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 124 | 154 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 50 | 192 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 198 | 376 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 57 | 52 | 52
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 97 | 201 | 212 | 250
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 26 | 50 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 31 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 76 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 30 | 40 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 366 | 400 | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1233 | 1502 | 1573 | 1611 | 0 | 159
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 592 | 783 | 603 | 799
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 310 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 17 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 942 | 1185 | 1098 | 2019 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 25 | 25 | 25 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 152 | 182 | 153 | 182
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 202 | 239 | 343 | 442 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 45 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 32 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 205 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 212 | 210 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 425 | 408 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 100 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 941 | 1047 | 1524 | 1788 | 320 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 210 | 210 | 210
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 175.3 | 323 | 331 | 357 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 7267.2 | 9185 | 11999.6 | 14483 | 1749 | 1454
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6854.192 | 8663 | 11317.6412 | 13659.9052
A. |  | 2019-11-27 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9185 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5687 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9185 | MW
3 | Day peak Generation : |  |  | 7267.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8663 | MW
4 | Evening peak Generation : |  |  | 9185 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 172.3597 | MKWHr | By Solar | 0.20785 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 140.7037 | MKWHr |  | By Oil: | 10.5203 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.4761 | MKWHr |  | By Hydro: | 2.186 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1749 | MW | Dhaka | 3442 | 3442 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1454 | MW | Chittagong | 959 | 959 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3203 | MW | Khulna | 996 | 996 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1167.52 | MMCFD |  |  | Rajshahi | 838 | 838 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129570545.208 | ii) Oil : | Taka | 77974748.32 | Comilla | 738 | 738 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 18307249 | Total | Taka | 225852542.528 | Mymensingh | 630 | 630 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.427 | MKWHr. | Sylhet | 334 | 334 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 57 | MW (E to W) at | 19:00 | hrs | Barisal | 221 | 221 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -190 | MW at | 7:00 | hrs | Rangpur | 505 | 505 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.5° C |  |  | Total | 8663 | 8663 |  | 0
B. |  | 2019-11-28 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14483 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 5183 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 174.5177 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5752 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.9185 | MKWHr. | ii) HVDC Flow at Peak Time |  | 783 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3472 | MKWHr. | iii) Maximum HVDC Flow : |  | 784 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 100.22 | 100.37 |  | (b) Today: | 100.22 |  | (c) Rule Curve: |  | 106.3
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 114 | 0 | 0 | 250 | 0 | 0 | 350 | 283 |  | 0 | 350 | 150 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 30 | 0 | 0 | 41 | 50 | 0 | 120 | 0 | 203 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 100 | 0 | 0 | 0 | 320 | 202 | 36 | 95 | 37 | 51 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 15 | 88 | 157 | 0 | 22 | 0 | 60 | 60 | 2 | 5 | 130 | 98 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 247 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4579 | 1785 | 6364 | 3919 | 247 | 1630 | 179 | 210 | 91 | 0 | 88 | 0 | 0 | 100.39
2:00 | 35 | 115 | 0 | 0 | 250 | 0 | 0 | 350 | 283 |  | 0 | 350 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 30 | 0 | 0 | 41 | 50 | 0 | 120 | 0 | 207 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 100 | 0 | 0 | 0 | 335 | 202 | 8 | 96 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 84 | 157 | 0 | 22 | 0 | 60 | 57 | 2 | 5 | 130 | 98 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 247 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 21 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 181 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4368 | 1738 | 6106 | 3868 | 247 | 1525 | 110 | 181 | 91 | 0 | 84 | 0 | 0 | 100.39
3:00 | 35 | 114 | 0 | 0 | 250 | 0 | 0 | 350 | 283 |  | 0 | 320 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 30 | 0 | 0 | 40 | 50 | 0 | 120 | 0 | 204 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 100 | 0 | 0 | 0 | 315 | 171 | 8 | 90 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 84 | 157 | 0 | 22 | 0 | 60 | 57 | 2 | 5 | 130 | 95 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 248 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4257 | 1635 | 5892 | 3721 | 248 | 1469 | 110 | 170 | 90 | 0 | 84 | 0 | 0 | 100.38
4:00 | 35 | 114 | 0 | 0 | 250 | 0 | 0 | 342 | 283 |  | 0 | 320 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 30 | 0 | 0 | 40 | 50 | 0 | 120 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 90 | 0 | 0 | 0 | 265 | 151 | 8 | 90 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 82 | 160 | 0 | 22 | 0 | 60 | 57 | 2 | 5 | 130 | 96 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 248 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4138 | 1625 | 5763 | 3609 | 248 | 1454 | 110 | 170 | 90 | 0 | 82 | 0 | 0 | 100.38
5:00 | 35 | 114 | 0 | 0 | 250 | 0 | 0 | 344 | 254 |  | 0 | 320 | 110 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 30 | 0 | 0 | 40 | 50 | 0 | 120 | 0 | 177 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 80 | 0 | 0 | 0 | 275 | 150 | 8 | 95 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 82 | 159 | 0 | 22 | 0 | 60 | 57 | 2 | 5 | 100 | 95 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 248 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4033 | 1654 | 5687 | 3569 | 248 | 1418 | 110 | 170 | 90 | 0 | 82 | 0 | 0 | 100.37
6:00 | 35 | 115 | 0 | 0 | 250 | 0 | 0 | 369 | 254 |  | 0 | 320 | 110 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 29 | 0 | 0 | 43 | 50 | 0 | 120 | 0 | 189 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 80 | 0 | 0 | 0 | 295 | 151 | 8 | 95 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 80 | 158 | 0 | 22 | 0 | 60 | 60 | 2 | 5 | 130 | 97 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 248 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4212 | 1666 | 5878 | 3709 | 248 | 1468 | 110 | 170 | 93 | 0 | 80 | 0 | 0 | 100.37
7:00 | 35 | 113 | 0 | 0 | 250 | 0 | 0 | 379 | 324 |  | 0 | 390 | 110 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 29 | 0 | 0 | 43 | 50 | 0 | 120 | 0 | 189 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 0 | 325 | 180 | 8 | 95 | 10 | 5 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 78 | 160 | 0 | 22 | 0.1 | 60 | 60 | 2 | 5 | 163 | 98 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 |  | 247 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 4470 | 1751.2 | 6221.2 | 3843 | 247 | 1676 | 110 | 170 | 93 | 0 | 78 | 4.2 | 0 | 100.36
8:00 | 35 | 135 | 0 | 0 | 300 | 0 | 0 | 375 | 363 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 25 | 29 | 0 | 0 | 43 | 50 | 0 | 120 | 0 | 214 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 80 | 0 | 0 | 0 | 340 | 192 | 8 | 95 | 20 | 5 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 82 | 157 | 0 | 22 | 0.7 | 58 | 60 | 2 | 5 | 163 | 100 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 0 | 0 | 394 | 0 | 2 | 0 | 1.8 | 0 | 0 | 0 | 0 |  | 249 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 4728.1 | 1792.4 | 6520.5 | 4037 | 249 | 1754 | 122 | 170 | 93 | 0 | 82 | 13.5 | 0 | 100.36
9:00 | 35 | 128 | 0 | 0 | 300 | 0 | 0 | 361 | 327 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 25 | 29 | 2 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 0 | 360 | 188 | 8 | 95 | 30 | 25 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 18 | 88 | 108 | 0 | 22 | 1.3 | 58 | 59 | 2 | 5 | 130 | 90 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 14.2 | 0 | 0 | 0 | 364 | 0 | 18 | 0 | 3 | 0 | 0 | 0 | 0 |  | 442 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 17 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4540.5 | 2008.8 | 6549.3 | 3949 | 442 | 1619 | 168 | 170 | 92 | 0 | 88 | 21.3 | 0 | 0
10:00 | 35 | 128 | 0 | 0 | 300 | 0 | 0 | 349 | 308 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 0 | 305 | 201 | 8 | 96 | 33 | 25 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 88 | 125 | 0 | 22 | 1.9 | 60 | 58 | 2 | 5 | 100 | 97 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 17.71 | 0 | 0 | 0 | 375 | 0 | 52 | 0 | 3.9 | 0 | 0 | 0 | 0 |  | 591 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 17 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 170 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4556.51 | 2215.2 | 6771.71 | 3971 | 591 | 1566 | 265 | 170 | 93 | 0 | 88 | 27.71 | 0 | 0
11:00 | 35 | 128 | 0 | 0 | 300 | 0 | 0 | 373 | 355 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 0 | 305 | 200 | 8 | 96 | 33 | 25 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 88 | 125 | 0 | 22 | 2.1 | 60 | 58 | 2 | 5 | 100 | 97 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 0 | 0 | 394 | 0 | 34 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 591 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 |  | 4768.5 | 2230 | 6998.5 | 4087 | 591 | 1694 | 245 | 170 | 93 | 0 | 88 | 30.5 | 0 | 0
12:00 | 35 | 128 | 0 | 0 | 300 | 0 | 0 | 376 | 358 |  | 0 | 420 | 120 | 0 | 0 | 5 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 216 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 0 | 335 | 198 | 44 | 96 | 33 | 25 | 0 | 9 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 94 | 124 | 0 | 22 | 2 | 60 | 60 | 26 | 31 | 130 | 97 | 63 | 5 | 0 | 0 | 0 | 30 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19.5 | 0 | 0 | 0 | 401 | 0 | 34 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 592 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 |  | 5006.9 | 2260.3 | 7267.2 | 4158 | 592 | 1863 | 266 | 170 | 93 | 0 | 94 | 31.2 | 0 | 0
13:00 | 35 | 128 | 20 | 0 | 300 | 0 | 0 | 371 | 358 |  | 0 | 420 | 125 | 0 | 0 | 15 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 20 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 216 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 0 | 300 | 198 | 44 | 85 | 33 | 47 | 0 | 15 | 0 | 0 | 0 | 22 | 8 | 33 | 20 | 94 | 124 | 0 | 22 | 1.9 | 60 | 57 | 47 | 50 | 130 | 90 | 63 | 40 | 0 | 0 | 16 | 34 | 10 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 18.3 | 0 | 0 | 0 | 367 | 0 | 34 | 0 | 4 | 15 | 0 | 0 | 0 |  | 591 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 32 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 10 | 0 | 0 | 169 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 |  | 5158.2 | 2226.9 | 7385.1 | 4116 | 591 | 1997 | 296 | 169 | 93 | 0 | 94 | 29.1 | 0 | 0
14:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 300 | 337 |  | 0 | 420 | 125 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 19 | 25 | 20 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 0 | 265 | 198 | 44 | 88 | 33 | 50 | 0 | 25 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 100 | 126 | 0 | 22 | 1.6 | 58 | 57 | 47 | 50 | 100 | 101 | 63 | 40 | 0 | 0 | 16 | 36 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 15.3 | 0 | 0 | 0 | 366 | 0 | 34 | 0 | 3.3 | 8 | 0 | 0 | 0 |  | 590 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 10 | 0 | 0 | 170 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 4927.2 | 2125.8 | 7053 | 3894 | 590 | 1887 | 294 | 170 | 93 | 0 | 100 | 25 | 0 | 0
15:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 325 | 337 |  | 0 | 420 | 125 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 27 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 63 | 0 | 0 | 275 | 198 | 44 | 96 | 33 | 48 | 0 | 36 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 102 | 124 | 0 | 22 | 1.1 | 58 | 58 | 47 | 50 | 130 | 102 | 63 | 40 | 0 | 0 | 17 | 36 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 11.1 | 0 | 0 | 0 | 370 | 0 | 34 | 0 | 2.2 | 0 | 0 | 0 | 0 |  | 590 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 10 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 5093.4 | 2139.8 | 7233.2 | 4033 | 590 | 1935 | 293 | 170 | 93 | 0 | 102 | 17.2 | 0 | 0
16:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 347 | 307 |  | 0 | 380 | 125 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 16 | 25 | 27 | 25 | 33 | 25 | 0 | 40 | 50 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 80 | 0 | 0 | 265 | 196 | 44 | 93 | 33 | 48 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 102 | 124 | 0 | 22 | 0.4 | 57 | 57 | 22 | 50 | 130 | 103 | 64 | 20 | 0 | 0 | 17 | 36 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 5.4 | 0 | 0 | 0 | 364 | 0 | 34 | 14 | 0.12 | 0 | 0 | 0 | 0 |  | 590 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 10 | 0 | 0 | 170 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 5008.92 | 2107.1 | 7116.02 | 4027 | 590 | 1823 | 307 | 170 | 90 | 0 | 102 | 7.02 | 0 | 100.32
17:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 353 | 276 |  | 0 | 350 | 120 | 0 | 0 | 15 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 12 | 0 | 10 | 17 | 16 | 25 | 27 | 33 | 33 | 25 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 115 | 0 |  | 0 | 0 | 34 | 25 | 6 | 1 | 19 | 5 | 80 | 80 | 0 | 0 | 270 | 197 | 44 | 85 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 104 | 152 | 0 | 22 | 0 | 60 | 58 | 25 | 50 | 100 | 170 | 65 | 20 | 0 | 0 | 17 | 37 | 10 | 305 | 24 | 8 | 0 | 12 | 0 | 0 | 64 | 0 | 0 | 0.2 | 0 | 6 | 3 | 367 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 |  | 589 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 17 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 175 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 383 | 0 | 0 | 12 | 0 | 35 | 0 | 0.1 | 0 |  | 5216.2 | 2212.1 | 7428.3 | 4143 | 589 | 1750 | 541 | 175 | 92 | 34 | 104 | 0.3 | 0 | 0
18:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 370 | 358 |  | 0 | 450 | 120 | 0 | 0 | 15 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 28 | 0 | 17 | 35 | 16 | 25 | 17 | 33 | 33 | 45 | 0 | 42 | 50 | 0 | 120 | 0 | 218 | 0 | 142 | 0 |  | 0 | 0 | 34 | 70 | 25 | 11 | 19 | 3 | 80 | 85 | 0 | 0 | 360 | 197 | 44 | 95 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 126 | 152 | 0 | 22 | 0 | 60 | 61 | 50 | 50 | 163 | 183 | 65 | 76 | 0 | 0 | 17 | 37 | 10 | 280 | 24 | 8 | 0 | 75 | 0 | 0 | 99 | 0 | 0 | 0 | 12 | 57 | 46 | 410 | 0 | 34 | 99 | 0 | 0 | 0 | 0 | 0 |  | 782 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 25 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 416 | 35 | 0 | 60 | 17 | 80 | 0 | 0 | 0 |  | 6162 | 2740 | 8902 | 4422 | 782 | 2090 | 1156 | 200 | 92 | 34 | 126 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 363 | 363 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 17 | 35 | 16 | 25 | 28 | 33 | 33 | 52 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 20 | 100 | 50 | 21 | 19 | 10 | 80 | 85 | 0 | 0 | 320 | 199 | 44 | 87 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 128 | 154 | 8 | 22 | 0 | 60 | 57 | 50 | 50 | 163 | 201 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 310 | 24 | 11 | 0 | 107 | 0 | 0 | 192 | 0 | 0 | 0 | 50 | 70 | 70 | 366 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 25 | 32 | 0 | 0 | 45 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 408 | 35 | 0 | 100 | 17 | 113 | 0 | 0 | 0 |  | 6391 | 2794 | 9185 | 4323 | 783 | 2127 | 1502 | 210 | 92 | 20 | 128 | 0 | 0 | 0
19:30 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 345 | 363 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 30 | 0 | 17 | 35 | 16 | 25 | 28 | 33 | 33 | 52 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 50 | 0 | 19 | 12 | 80 | 80 | 0 | 0 | 320 | 200 | 44 | 90 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 128 | 156 | 8 | 22 | 0 | 60 | 57 | 50 | 50 | 100 | 206 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 315 | 24 | 11 | 0 | 115 | 0 | 0 | 200 | 0 | 0 | 0 | 50 | 50 | 30 | 367 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 24 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 422 | 35 | 0 | 113 | 17 | 105 | 0 | 0 | 0 |  | 6204 | 2780 | 8984 | 4279 | 783 | 2084 | 1408 | 210 | 92 | 0 | 128 | 0 | 0 | 0
20:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 354 | 363 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 0 | 0 | 17 | 16 | 25 | 30 | 33 | 33 | 33 | 0 | 42 | 50 | 0 | 120 | 0 | 222 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 10 | 0 | 19 | 18 | 80 | 80 | 0 | 0 | 360 | 198 | 44 | 95 | 33 | 50 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 124 | 155 | 0 | 22 | 0 | 60 | 57 | 50 | 50 | 100 | 214 | 65 | 76 | 0 | 0 | 17 | 38 | 10 | 300 | 24 | 11 | 0 | 115 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 50 | 13 | 416 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 26 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 427 | 21 | 0 | 113 | 0 | 75 | 0 | 0 | 0 |  | 6150 | 2532 | 8682 | 4248 | 783 | 2081 | 1144 | 210 | 92 | 0 | 124 | 0 | 0 | 0
21:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 371 | 364 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 0 | 0 | 17 | 16 | 25 | 31 | 33 | 33 | 33 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 100 | 0 | 0 | 19 | 26 | 120 | 80 | 0 | 0 | 320 | 200 | 44 | 81 | 33 | 50 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 120 | 157 | 0 | 22 | 0 | 59 | 57 | 50 | 50 | 100 | 201 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 310 | 24 | 11 | 0 | 115 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 50 | 0 | 364 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 27 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 410 | 17 | 0 | 113 | 0 | 70 | 0 | 0 | 0 |  | 6098 | 2471 | 8569 | 4180 | 783 | 2086 | 1098 | 210 | 92 | 0 | 120 | 0 | 0 | 0
22:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 344 | 303 |  | 0 | 420 | 105 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 16 | 25 | 31 | 33 | 25 | 0 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 40 | 0 | 0 | 19 | 33 | 120 | 80 | 0 | 0 | 320 | 200 | 44 | 95 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 116 | 154 | 0 | 22 | 0 | 60 | 57 | 50 | 50 | 100 | 201 | 69 | 76 | 0 | 0 | 17 | 40 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 17 | 0 | 365 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 |  | 784 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 183 | 26 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 394 | 0 | 0 | 56 | 0 | 35 | 0 | 0 | 0 |  | 5658 | 2301 | 7959 | 4161 | 784 | 1954 | 642 | 210 | 92 | 0 | 116 | 0 | 0 | 100.29
23:00 | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 349 | 304 |  | 0 | 420 | 105 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 16 | 25 | 31 | 33 | 25 | 0 | 0 | 43 | 50 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 40 | 0 | 0 | 19 | 36 | 120 | 0 | 0 | 0 | 320 | 200 | 44 | 95 | 33 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 106 | 154 | 0 | 22 | 0 | 60 | 57 | 47 | 50 | 100 | 204 | 68 | 76 | 0 | 0 | 17 | 40 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 |  | 589 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 23 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 404 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5397 | 2054 | 7451 | 4098 | 589 | 1979 | 376 | 210 | 93 | 0 | 106 | 0 | 0 | 100.28
24:00 | 35 | 131 | 0 | 0 | 240 | 0 | 0 | 352 | 303 |  | 0 | 420 | 95 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 16 | 25 | 31 | 33 | 25 | 0 | 0 | 44 | 50 | 0 | 120 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 120 | 0 | 0 | 0 | 320 | 200 | 44 | 95 | 30 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 96 | 157 | 0 | 22 | 0 | 60 | 57 | 44 | 50 | 100 | 201 | 68 | 76 | 0 | 0 | 17 | 40 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 |  | 248 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 22 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 430 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5236 | 1739 | 6975 | 4038 | 248 | 2013 | 276 | 210 | 94 | 0 | 96 | 0 | 0 | 100.28
KWH | 790000 | 3143000 | 0 | 0 | 6828582 | 0 | 0 | 8636420 | 7586000 |  | 0 | 9114875 | 2694429 | 0 | 0 | 116386 | 0 | 0 | 1603000 | 0 | 0 | 0 | 0 | 0 | 377280 | 0 | 243312 | 0 | 47319 | 137986 | 186084 | 600000 | 639000 | 738300 | 779000 | 392940 | 0 | 1001978 | 1184000 | 0 | 2900000 | 0 | 4856961 | 0 | 3109851 | 0 |  | 0 | 0 | 79583 | 482280 | 123840 | 43200 | 432912 | 437760 | 2184806 | 653070 | 0 | 108000 | 7531500 | 4617000 | 719272 | 2182950 | 640584 | 816000 | 0 | 572912 | 0 | 0 | 0 | 370620 | 112680 | 405900 | 486990 | 2347200 | 3423160 | 19200 | 524916 | 12650 | 1416000 | 1396560 | 585600 | 746640 | 3156561 | 2872000 | 1283520 | 806400 | 0 | 0 | 234000 | 513300 | 138420 | 7570500 | 290064 | 105648 | 0 | 526909 | 0 | 0 | 1620000 | 0 | 0 | 134460 | 101760 | 296440 | 180654 | 9069000 | 0 | 390108 | 730145 | 28440 | 25091 | 0 | 0 | 0 |  | 11918545 | 0 | 7864992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162375 | 3947168 | 471545 | 393600 | 0 | 0 | 1185000 | 0 | 0 | 0 | 140230 | 0 | 0 | 0 | 0 | 252720 | 169128 | 232164 | 0 | 0 | 4476100 | 0 | 0 | 4061445 | 0 | 0 | 0 | 0 | 0 | 4976709 | 0 | 9626545 | 111360 | 0 | 532128 | 38160 | 513600 | 0 | 32299 | 0 |  | 121253908 | 51105813 | 172359721 | 97419556 | 11918545 | 43284178 | 10440732 | 4476100 | 2185978 | 79583 | 2347200 | 207849 | 0
Fuel Cost | 884800 | 3394440 | 0 | 0 | 5053150.68 | 0 | 0 | 6218222.4 | 5765360 |  | 0 | 7291900 | 2424986.1 | 0 | 0 | 1194120.36 | 0 | 0 | 2003750 | 0 | 0 | 0 | 0 | 0 | 3433248 | 0 | 2277400.32 | 0 | 451423.26 | 1374340.56 | 139563 | 450000 | 0 | 0 | 0 | 3764365.2 | 0 | 260514.28 | 307840 | 0 | 4437000 | 0 | 5099809.05 | 0 | 3949510.77 | 0 |  | 0 | 0 | 834825.67 | 4962661.2 | 1177718.4 | 404352 | 398279.04 | 1216972.8 | 2294046.3 | 685723.5 | 0 | 79920 | 6326460 | 4247640 | 704886.56 | 2903323.5 | 525278.88 | 840480 | 0 | 819264.16 | 0 | 0 | 0 | 378032.4 | 84510 | 767151 | 365242.5 | 16195680 | 2806991.2 | 182592 | 535414.32 | 207460 | 1925760 | 1899321.6 | 796416 | 933300 | 3914135.64 | 2642240 | 1912444.8 | 1419264 | 0 | 0 | 372060 | 600561 | 325287 | 5375055 | 217548 | 80292.48 | 0 | 5516737.23 | 0 | 0 | 15584400 | 0 | 0 | 1551668.4 | 948403.2 | 2780607.2 | 1692727.98 | 8524860 | 0 | 3475862.28 | 6899870.25 | 0 | 231339.02 | 0 | 0 | 0 |  | 32180071.5 | 0 | 6134693.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1605888.75 | 3157734.4 | 730894.75 | 4227264 | 0 | 0 | 2227800 | 0 | 0 | 0 | 1454185.1 | 0 | 0 | 0 | 0 | 277992 | 279061.2 | 175748.148 | 0 | 0 | 18307249 | 0 | 0 | 3574071.6 | 0 | 0 | 0 | 0 | 0 | 4379503.92 | 0 | 7027377.85 | 1053465.6 | 0 | 4884935.04 | 340005.6 | 4797024 | 0 | 0 | 0 |  | 179740810.49 | 96814966.218 | 276555776.708 | 91252337.248 | 32180071.5 | 38318207.96 | 77139922.65 | 18307249 | 568354.28 | 834825.67 | 16195680 | 1759128.4 | 0
Yesterday Day Peak | 35 | 128 | 0 | 0 | 300 | 0 | 0 | 376 | 358 |  | 0 | 420 | 120 | 0 | 0 | 5 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 25 | 33 | 25 | 0 | 43 | 50 | 0 | 120 | 0 | 216 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 0 | 335 | 198 | 44 | 96 | 33 | 25 | 0 | 9 | 0 | 0 | 0 | 22 | 0 | 0 | 20 | 94 | 124 | 0 | 22 | 2 | 60 | 60 | 26 | 31 | 130 | 97 | 63 | 5 | 0 | 0 | 0 | 30 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19.5 | 0 | 0 | 0 | 401 | 0 | 34 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 592 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 |  | 7267.2 | DayPeak
Yesterday Evening Peak | 35 | 129 | 0 | 0 | 300 | 0 | 0 | 363 | 363 | 0 | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 17 | 35 | 16 | 25 | 28 | 33 | 33 | 52 | 0 | 42 | 50 | 0 | 120 | 0 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 20 | 100 | 50 | 21 | 19 | 10 | 80 | 85 | 0 | 0 | 320 | 199 | 44 | 87 | 33 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 128 | 154 | 8 | 22 | 0 | 60 | 57 | 50 | 50 | 163 | 201 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 310 | 24 | 11 | 0 | 107 | 0 | 0 | 192 | 0 | 0 | 0 | 50 | 70 | 70 | 366 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 783 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 25 | 32 | 0 | 0 | 45 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 408 | 35 | 0 | 100 | 17 | 113 | 0 | 0 | 0 |  | 9185 | EvPeak
Forecast for Evening | 35 | 135 | 0 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 43 | 50 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 10 | 120 | 0 | 0 | 0 | 360 | 200 | 44 | 95 | 37 | 55 | 0 | 35 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 143 | 160 | 95 | 22 | 0 | 60 | 52 | 51 | 44 | 163 | 250 | 66 | 79 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 799 | 40 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 182 | 25 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 210 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 135 | 0 | 0 | 320 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 43 | 50 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 5 | 120 | 0 | 0 | 0 | 360 | 200 | 44 | 95 | 37 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 113 | 160 | 95 | 22 | 1.6 | 60 | 52 | 51 | 44 | 163 | 212 | 66 | 79 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 0 |  | 603 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 109 | 0 | 0 | 200 | 0 | 0 | 382 | 366 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 42 | 50 | 0 | 120 | 0 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 120 | 0 | 0 | 0 | 360 | 192 | 44 | 95 | 30 | 5 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 84 | 147 | 0 | 22 | 0.4 | 40 | 20 | 2 | 2 | 100 | 212 | 40 | 5 | 0 | 0 | 0 | 2 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 9.47 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0
199
| Minimum Generation |  | 5687 | 5:00
| Highest Generation |  | 9185 | 19:00
| Day Peak Generation |  | 7267.2 | 12:00
| Evening Peak Generation |  | 9185 | 19:00
| HVDC Max Flow |  | 784 | 22:00
| HVDC EvPeak Flow |  | 783 | 19:00
| Load factor L.F |  | 78.19%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-28
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7267.2 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5752 | MW
Evening Peak Generation : |  | 9185 | MW Hour : | 19:00 | Available Max Generation : |  | 14483 | MW
E.P. Demand (at gen end) : |  | 9185 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 9185 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5183 | MW
Total Gen. (MKWH) : |  | 172.3597 | System Load Factor : | 78.19% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -190 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-28
Actual : | 100.22 | Ft.(MSL) , | Rule curve : | 106.3 | Ft.( MSL )
Gas Consumed : | Total = | 1167.52 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129570545.208
: |  | Coal : | 18307249 | Oil : | 77974748.32 | Total : | 225852542.528
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3276.006 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1109.1518 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 992.8952 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 896.8564 |  |  | 0 | 0%
) | 0 | 0:00 | 810.6461 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 654.1504 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 372.0377 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 168.592 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 504.4833 |  |  | 0 | 0%
Total | 0 |  | 8784.8187 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,4,5
4) Ashuganj unit-4 & 5
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Barapukuria ST: unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sherpur-Sirajganj 132 kV Ckt-1 was under shut down from 08:33 to 16:49 for project work.
b) Hathhazari-Kaptai 132 kV Ckt-1 was under shut down from 08:16 to 15:58 for A/M.
c) Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 08:33 to 14:17 for A/M.
d) Rampura-Bashundhara 132 kV Ckt-1 was under shut down from 09:37 to 16:31 for A/M.
e) Jamalpur 132/33 kV T-2 transformer was under shut down from 08:29 to 15:45 for A/M.
f) Kaliakoir-Dhamrai 132 kV Ckt-2 was under shut down from 09:30 to14:39 for A/M.
g) Netrokona 132/33 kV T-3 transformer was under shut down from 08:11 to 16:10 for A/M.
h) Sherpur 132/33 kV T-1 transformer was under shut down from 08:17 to 15:53 for A/M.
i) RPCL-Mymensingh 132 kV Ckt-2 was under shut down from 09:04 to 16:40 for A/M.
j) Srimangal 132/33 kV T-1 transformers was under shut down from 08:38 to 16:43 for A/M.
k) Kabirpur-Manikganj 132 kV Ckt-1 & T3,T4 transformers were under shut down from 08:16
to15:53 for A/M.
l) Haripur 230/132 kV T-3 transformer was under shut down from 09:02 to 12:58 for A/M.
m) Rangpur-Saidpur 132 kV Ckt-2 was under shut down from 08:25 to 17:03 for A/M.
n) Jhenaidah-Magura 132 kV Ckt-2 was under shut down from 08:14 to 15:59 for A/M.
o) Noapara-Noapara B.T 100 MW 132 kV Ckt was under shut down from 09:56 to 16:50 for A/M.
p) Tongi-Kaliakoir 132 kV Ckt-2 was under shut down from 08:56 to 14:26 for A/M.
q) Khulna©-Noapara 132 kV Ckt-1 was under shut down from 09:58 to 13:13 for C/M.
r) Bibiyana 400/230 kV T-1 transformer was under shut down from 09:10 to 16:22 for D/W.
s) Ashuganj unit-4 was synchronized at 12:40.
t) Shahjibazar 330 MW GT-1 was synchronized at 13:48.
u) Sirajganj unit-1 tripped at 19:59 due to internal fault.
v) Gopalganj 400/132 kV T1 transformer was switched on at 14:02.
w) Gopalganj 400 kV Bus was switched on at 14:18 and was shut down at 16:33.
x) Kushiara 163 MW ST was shut down at 19:38.
y) Meghnaghat Summit CCPP GT-2 was force shut down at 00:49(28/11/2019) for high DP.
z) Sirajganj 225 MW unit-1 GT was synchronized at 02:34(28/11/2019).
aa) Sirajganj 225 MW unit-1 STG was synchronized at 05:14(28/11/2019).
ab) Ghorasal unit-7 STG was shut down at 05:39(28/11/2019) for maintenance work.
ac) Hasnabad 230/132 kV TR-1 transformer was shut down at 07:07(28/11/2019) for A/M.
ad) Ashuganj Unit-4 tripped at 22:10 due to condensate pump trip

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 790000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 129 | 3143000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6828582
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 363 | 8636420 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 363 | 7586000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9114875
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 2694429 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 116386 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 186084
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 42 | 1603000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 243312
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 47319 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 137986 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 377280 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1239000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 738300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 779000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 392940
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 107 | 526909 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 390108 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2284 | 45570930
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134460
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 21 | 43200 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 2185978 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4856961 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3109851 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 730145
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 20 | 79583 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 482280
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 101760 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 432912
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 437760
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 123840 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 25091 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 935 | 15672261
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2184806 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 85 | 653070 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4617000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 108000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7531500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 640584 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 49 | 816000
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 44 | 719272 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 572912 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 180654 | Low demand
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 2182950
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 70 | 296440 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 370620
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 112680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2347200
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 405900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 486990 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3005 | 1294 | 24226578
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 154 | 3423160 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 524916
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 19200 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12650
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 1620000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 376 | 5599926
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1416000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1396560
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3156561
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 201 | 2872000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 585600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 746640
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 105648
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1283520 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 806400
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 234000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 40 | 513300 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 290064
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7570500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 366 | 9069000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 138420
| Sylhet Area Total |  |  |  | 1949 | 1502 | 30184213
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 783 | 11918545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 7864992 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 162375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 111360 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 17 | 38160 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1185 | 20095432
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 393600 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 471545 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 182 | 3947168
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Line over load
| Barisal Area Total |  |  |  | 462 | 239 | 4812313
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 45 | 1185000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 32 | 140230 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 205 | 4061445 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 4976709 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 9626545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 252720
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 169128
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232164
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 100 | 532128
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 1047 | 21176069
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4476100
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 513600
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32299
| Rangpur Area Total |  |  |  | 605 | 323 | 5021999
| Total |  |  |  | 19132 | 9185 | 172359721
| Eastern Grid Total |  |  |  | 13568 | 6391 | 121253908
| Western Grid Total |  |  |  | 5564 | 2794 | 51105813
| National Grid Total |  |  |  | 19132 | 9185 | 172359721
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-27
(a) ENTIRE EASTERN GRID : |  | 6103 | MW | (b) ENTIRE WESTERN GRID : |  | 2560 | MW
i) Dhaka area |  | 3442 | MW | i) Khulna area |  | 996 | MW
ii) Chittagong area |  | 959 | MW | ii) Rajshahi area |  | 838 | MW
iii) Comilla area |  | 738 | MW | iii) Barisal area |  | 221 | MW
iv) Mymensingh area |  | 630 | MW | iv) Rangpur area |  | 505 | MW
v) Sylhet area |  | 334 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8663 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 18:00 | Srimongal | 27 | 18:30 | Bottail | 102 | 18:00
Munsiganj | 76 | 18:00 | Shahjibazar | 85 | 18:00 | G.K Project | 24 | 18:00
Sonargaon | 82 | 18:30 | Fenchuganj | 25 | 18:30 | Faridpur | 124 | 18:00
Shyampur | 180 | 7:00 | Kulawara | 32 | 18:30 | Madaripur | 57 | 20:00
Bhulta | 173 | 19:00 | Sylhet | 99 | 18:00 | Sariatpur | 38 | 21:00
Madanganj | 43 | 18:00 | Chatak | 17 | 18:00 | Gopalganj | 56 | 18:30
Shitalakhya | 106 | 16:00 | Sunamganj | 28 | 18:30 | Bagerhat | 62 | 20:00
Rahim steel | 17 | 7:00 | Biani Bazar | 32 | 19:00 | Mongla | 36 | 11:00
Matuail | 86 | 12:00 | Comilla (S) | 132 | 18:30 | Satkhira | 65 | 19:30
Ghorasal | 64 | 20:00 | Comilla(N) | 59 | 18:30 | Gallamari | 36 | 13:00
Narsingdi | 100 | 18:30 | Chandpur | 70 | 19:00 | Magura | 36 | 18:30
Haripur (SBU) | 96 | 19:00 | Feni | 97 | 18:00 | Norail | 26 | 18:30
Ullon | 59 | 18:00 | Chowmuhani | 114 | 19:00 | Chuadanga | 60 | 18:30
Hasnabad | 155 | 18:00 | Ashuganj | 40 | 18:00 | Barisal(N) | 28 | 19:30
Magbazar | 99 | 13:00 | Daudkandi | 90 | 18:30 | Barisal (S) | 70 | 21:00
Maniknagar | 96 | 18:00 | B.Baria | 92 | 18:00 | Patuakhali | 79 | 19:30
Bangabhaban | 24 | 13:00 | Ramganj | 52 | 18:30 | Bhandaria | 34 | 21:00
Narinda | 84 | 13:00 | Madunaghat | 51 | 18:00 | Borhan Uddin | 23 | 19:30
Dhanmondi | 123 | 13:00 | Hathazari | 74 | 18:30 | Ishurdi | 44 | 18:00
Lalbag | 63 | 18:00 | Khulshi | 154 | 10:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 52 | 19:00 | Halishahar | 116 | 15:00 | Natore | 86 | 18:00
Mirpur | 83 | 19:00 | Baraulia | 121 | 10:00 | Bogra | 136 | 19:00
Kalyanpur | 81 | 18:30 | Sikalbaha | 20 | 18:30 | Noagaon | 79 | 19:00
Gulshan | 122 | 13:00 | Dohazari | 66 | 18:00 | Rajshahi | 81 | 20:00
Uttara | 43 | 18:00 | Cox'sbazar | 74 | 18:30 | Rajshahi New | 9 | 18:30
Uttara New | 33 | 18:00 | Chandraghona | 24 | 18:00 | C.Nawabganj | 50 | 19:30
Kamrangirchar | 80 | 18:00 | Kaptai | 3.8 | 18:00 | Amnura | 21 | 18:00
Savar | 109 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Pabna | 73 | 18:00
Bhasantec | 138 | 12:00 | Bakulia | 84 | 19:00 | Shahjadpur | 81 | 18:30
Agargaon | 43 | 13:00 | Julda | 22 | 18:00 | Serajganj | 66 | 19:00
Satmosjid | 81 | 13:00 | TK chemical | 12 | 18:00 | Niyamatpur | 41 | 19:30
Tongi | 125 | 18:00 | Modern Steel | 17 | 17:00 | Joypurhat | 43 | 18:30
Kabirpur | 166 | 18:00 | Shahmirpur | 23 | 18:00 | Sherpur(Bogura) | 32 | 18:00
Basundhara | 75 | 18:00 | Khagrachhari | 16 | 18:00 | Mohastangor | 11 | 18:30
Manikganj | 56 | 18:00 | Matarbari | 20 | 18:30 | Rangpur | 107 | 18:30
Joydevpur | 184 | 18:30 | Baroiar Hat | 16 | 18:00 | Lalmonirhat | 42 | 18:00
New Tongi | 85 | 18:30 | Rangamati | 10 | 18:00 | Saidpur | 84 | 18:00
Korda | 213 | 18:30 | Abul Khair 230 | 62 | 8:00 | Purbasadipur | 60 | 8:00
Dhamrai | 58 | 18:00 | BSRM | 100 | 2:00 | Thakurgaon | 35 | 18:00
Valuka | 68 | 18:00 | GPH Ispat | 6 | 18:00 | Palashbari | 85 | 18:00
Tangail | 130 | 18:30 | Goalpara | 20 | 18:30 | Barapukuria | 40 | 19:00
Mymensing | 155 | 18:30 | Central s/s | 72 | 18:30 | Panchagar | 26 | 17:00
Kishorganj | 80 | 18:00 | Noapara | 44 | 18:00 | Joldhaka | 20 | 18:30
Netrokona | 70 | 18:00 | Jessore | 86 | 18:00 | Kurigram | 36 | 18:00
Jamalpur | 84 | 18:30 | Benapol | 28 | 18:00
Sherpur | 68 | 18:00 | Jhenida | 76 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-27 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 389 | 3:00 | 282 | 9:00 | Kaliakoir | 371 | 4:00 | 355 | 12:00
Bheramara | 406 | 2:00 | 396 | 10:00 | Bhulta | 373 | 5:00 | 359 | 11:00
Ashuganj(N) | 376 | 4:00 | 360 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 226 | 1:00 | 222 | 7:00 | Hathazari | 220 | 3:00 | 212 | 11:00
Ishurdi | 240 | 5:00 | 227 | 18:00 | Megnaghat | 222 | 3:00 | 212 | 13:00
Ashuganj | 232 | 3:00 | 225 | 11:00 | Fenchuganj | 233 | 7:00 | 229 | 11:00
Serajganj | 234 | 4:00 | 229 | 12:00 | Siddhirganj | 222 | 5:00 | 213 | 11:00
Baghabari | 239 | 4:00 | 231 | 20:00 | Maniknagar | 221 | 4:00 | 211 | 12:00
Barapukuria | 230 | 4:00 | 226 | 8:00 | Old Airport | 221 | 4:00 | 209 | 12:00
Bogra | 233 | 2:00 | 225 | 8:00 | Barisal | 231 | 4:00 | 220 | 20:00
Khulna South | 238 | 4:00 | 218 | 18:00 | AKSML | 215 | 6:00 | 206 | 12:00
Rampura | 221 | 7:00 | 214 | 11:00 | BSRM | 219 | 4:00 | 209 | 12:00
Haripur | 220 | 3:00 | 212 | 12:00 | Bibiyana | 232 | 3:00 | 226 | 10:00
Hasnabad | 220 | 5:00 | 210 | 12:00 | Bhulta | 223 | 5:00 | 213 | 12:00
Aminbazar | 221 | 4:00 | 211 | 12:00 | Ashuganj (S) | 229 | 1:00 | 222 | 11:00
Tongi | 215 | 4:00 | 207 | 11:00 | Kaliakoir | 222 | 3:00 | 209 | 10:00
Comilla (N) | 228 | 2:00 | 220 | 12:00 | GPH | 215 | 7:00 | 207 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 1:00 | 126 | 12:00 | Halishahar | 130 | 3:00 | 123 | 12:00
Munsiganj | 132 | 4:00 | 124 | 12:00 | Baraulia | 128 | 4:00 | 123 | 11:00
Sonargaon | 130 | 1:00 | 125 | 11:00 | Sikalbaha | 130 | 19:00 | 124 | 12:00
Shyampur | 133 | 3:00 | 127 | 12:00 | Dohazari | 129 | 6:00 | 122 | 12:00
Bhulta | 124 | 2:00 | 120 | 11:00 | Cox'sbazar | 126 | 7:00 | 119 | 12:00
Madanganj | 131 | 24:00 | 125 | 11:00 | Chandraghona | 130 | 3:00 | 125 | 12:00
Shitalakhya | 135 | 3:00 | 126 | 12:00 | Kaptai | 130 | 1:00 | 128 | 9:00
Rahim steal | 134 | 3:00 | 127 | 10:00 | A. Khaer Stl. | 128 | 4:00 | 124 | 11:00
Matuail | 133 | 4:00 | 124 | 12:00 | Bakulia | 128 | 2:00 | 123 | 12:00
Ghorasal | 135 | 1:00 | 132 | 12:00 | Julda | 128 | 18:00 | 125 | 10:00
Narsinghdi | 134 | 12:00 | 130 | 18:00 | TK Chemical | 129 | 19:00 | 124 | 12:00
Haripur (SBU) | 133 | 3:00 | 127 | 11:00 | Modern Steel | 129 | 19:30 | 123 | 12:00
Ullon | 131 | 6:00 | 124 | 12:00 | Shahmirpur | 129 | 19:00 | 123 | 12:00
Hasnabad | 135 | 6:00 | 127 | 12:00 | Khagrachhari | 130 | 4:00 | 124 | 12:00
Magbazar | 134 | 6:00 | 125 | 12:00 | Matarbari | 127 | 6:00 | 120 | 11:00
Maniknagar | 136 | 6:00 | 130 | 12:00 | Baroiar Hat | 129 | 1:00 | 124 | 10:00
Bangabhaban | 136 | 7:00 | 130 | 13:00 | Rangamati | 130 | 4:00 | 125 | 11:00
Narinda | 136 | 8:00 | 130 | 14:00 | Goalpara | 137 | 6:00 | 128 | 12:00
Dhanmondi | 131 | 6:00 | 124 | 12:00 | Central s/s | 136 | 6:00 | 124 | 18:30
Lalbag | 135 | 6:00 | 125 | 12:00 | Noapara | 137 | 5:00 | 126 | 12:00
Madartek | 132 | 6:00 | 124 | 12:00 | Jessore | 133 | 6:00 | 120 | 13:00
Mirpur | 135 | 2:00 | 127 | 12:00 | Benapol | 135 | 4:00 | 122 | 13:00
Kalyanpur | 137 | 3:00 | 130 | 12:00 | Jhenida | 133 | 6:00 | 120 | 18:00
Gulshan | 132 | 5:00 | 124 | 11:00 | Bottail | 136 | 4:00 | 127 | 18:00
Uttara | 132 | 4:00 | 124 | 11:00 | G.K Project | 140 | 6:00 | 135 | 12:00
Uttara New | 133 | 2:00 | 126 | 12:00 | Faridpur | 134 | 5:00 | 123 | 20:00
Kamrangirchar | 133 | 3:00 | 124 | 12:00 | Madaripur | 133 | 1:00 | 125 | 21:00
Savar | 134 | 4:00 | 126 | 13:00 | Sariatpur | 134 | 5:00 | 124 | 20:00
Bhasantec | 133 | 3:00 | 124 | 12:00 | Gopalganj | 138 | 5:00 | 126 | 20:00
Agargaon | 134 | 3:00 | 125 | 12:00 | Bagerhat | 135 | 6:00 | 122 | 18:00
Satmosjid | 134 | 3:00 | 125 | 12:00 | Mongla | 132 | 23:00 | 123 | 19:30
Tongi | 132 | 4:00 | 126 | 15:00 | Satkhira | 137 | 3:00 | 125 | 18:00
Kabirpur | 132 | 4:00 | 124 | 11:00 | Gallamari | 139 | 4:00 | 127 | 18:00
Basundhara | 131 | 1:00 | 123 | 13:00 | Magura | 135 | 5:00 | 120 | 18:00
Manikganj | 134 | 5:00 | 124 | 12:00 | Norail | 133 | 6:00 | 119 | 18:00
Joydevpur | 134 | 6:0 | 127 | 15:00 | Chuadanga | 132 | 4:00 | 117 | 18:00
New Tongi | 133 | 4:00 | 124 | 15:00 | Barisal(N) | 137 | 5:00 | 129 | 20:00
Kodda | 131 | 6:00 | 122 | 12:00 | Barisal (S) | 136 | 5:00 | 128 | 20:00
Dhamrai | 131 | 4:00 | 122 | 12:00 | Patuakhali | 136 | 5:00 | 125 | 20:00
Valuka | 129 | 22:00 | 124 | 13:00 | Bhandaria | 135 | 6:00 | 125 | 18:00
Tangail | 130 | 3:00 | 126 | 18:30 | Ishurdi | 137 | 2:00 | 131 | 20:00
Mymensing | 132 | 22:00 | 125 | 18:00 | Ruppur Paromanobik | 136 | 4:00 | 130 | 17:00
Kishorganj | 132 | 22:00 | 127 | 18:00 | Natore | 136 | 5:00 | 128 | 18:00
Netrokona | 131 | 22:00 | 125 | 18:00 | Bogra | 137 | 5:00 | 131 | 11:00
Jamalpur | 138 | 22:00 | 126 | 1:00 | Noagaon | 133 | 4:00 | 128 | 18:00
Sherpur | 137 | 22:00 | 123 | 1:00 | Rajshahi | 132 | 2:00 | 124 | 12:00
Srimongal | 136 | 1:00 | 134 | 11:00 | Rajshahi New | 133 | 4:00 | 124 | 12:00
Shahjibazar | 136 | 24:00 | 132 | 11:00 | C.Nawabganj | 131 | 1:00 | 122 | 18:00
Fenchuganj | 135 | 22:00 | 130 | 11:00 | Amnura | 131 | 4:00 | 122 | 12:00
Khulawara | 135 | 1:00 | 131 | 10:00 | Pabna | 138 | 3:00 | 131 | 18:00
Sylhet | 134 | 1:00 | 129 | 10:00 | Shahjadpur | 143 | 2:00 | 135 | 18:00
Chatak | 134 | 24:00 | 128 | 11:00 | Serajganj | 137 | 1:00 | 130 | 18:00
Sunamganj | 133 | 23:00 | 129 | 10:00 | Niyamatpur | 133 | 2:00 | 125 | 18:00
Biani Bazar | 134 | 24:00 | 128 | 10:00 | Joypurhat | 135 | 2:00 | 127 | 18:00
Comilla(s) | 130 | 6:00 | 125 | 12:00 | Sherpur(Bogura) | 138 | 4:00 | 131 | 18:00
Comilla(n) | 136 | 21:00 | 131 | 13:00 | Mohastangor | 135 | 4:00 | 129 | 12:00
Chandpur | 130 | 20:00 | 128 | 14:00 | Rangpur | 129 | 3:00 | 124 | 12:00
Feni | 127 | 24:00 | 123 | 18:00 | Lalmonirhat | 126 | 4:00 | 120 | 18:00
Chowmuhani | 128 | 8:00 | 122 | 15:00 | Saidpur | 128 | 6:00 | 122 | 18:00
Ashuganj | 137 | 24:00 | 135 | 13:00 | Purbasadipur | 130 | 4:00 | 118 | 13:00
Daudkandi | 129 | 21:00 | 125 | 12:00 | Thakurgaon | 124 | 4:00 | 117 | 13:00
B.Baria | 134 | 22:00 | 132 | 11:00 | Palashbari | 134 | 5:00 | 125 | 10:00
Ramganj | 124 | 9:00 | 122 | 18:00 | Barapukuria | 130 | 4:00 | 126 | 8:00
Madanhat | 131 | 3:00 | 126 | 12:00 | Panchagar | 124 | 4:00 | 112 | 13:00
Hathazari | 131 | 6:00 | 127 | 11:00 | Joldhaka | 128 | 4:00 | 121 | 12:00
Khulshi | 127 | 4:00 | 121 | 12:00 | Kurigram | 128 | 4:00 | 120 | 7:00
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 60 | 5236 | 1739 | 6975 |  |  |  | QF-LDC-12
0:30 | 37.5 | 4907.5 | 1762 | 6669.5 | Date: | 2019-11-27
1:00 | 15 | 4579 | 1785 | 6364
1:30 | 23 | 4473.5 | 1761.5 | 6235
2:00 | 31 | 4368 | 1738 | 6106
2:30 | 33 | 4312.5 | 1686.5 | 5999 | [5 empty] | Gen. at Eve. Peak | 9185 | 9185 MW (19:00 )
3:00 | 35 | 4257 | 1635 | 5892 | [6 empty] | 19:00
3:30 | 67.5 | 4197.5 | 1630 | 5827.5 | [5 empty] | Gen. at Day Peak | 7267.2 | 7267.2 MW (12:00 )
4:00 | 100 | 4138 | 1625 | 5763 | [6 empty] | 12:00
4:30 | 95 | 4085.5 | 1639.5 | 5725 | [5 empty] | Highest Generation | 9185
5:00 | 90 | 4033 | 1654 | 5687 | [6 empty] | 19:00
5:30 | 55 | 4122.5 | 1660 | 5782.5
6:00 | 20 | 4212 | 1666 | 5878
6:30 | 105 | 4341 | 1708.6 | 6049.6
7:00 | 190 | 4470 | 1751.2 | 6221.2
7:30 | 110 | 4599.05 | 1771.8 | 6370.85
8:00 | 30 | 4728.1 | 1792.4 | 6520.5
8:30 | 147 | 4634.3 | 1900.6 | 6534.9
9:00 | 264 | 4540.5 | 2008.8 | 6549.3
9:30 | 390 | 4548.505 | 2112 | 6660.505
10:00 | 516 | 4556.51 | 2215.2 | 6771.71
10:30 | 496.5 | 4662.505 | 2222.6 | 6885.105
11:00 | 477 | 4768.5 | 2230 | 6998.5
11:30 | 441 | 4887.7 | 2245.15 | 7132.85
12:00 | 405 | 5006.9 | 2260.3 | 7267.2
12:30 | 350 | 5082.55 | 2243.6 | 7326.15
13:00 | 295 | 5158.2 | 2226.9 | 7385.1
13:30 | 334.5 | 5042.7 | 2176.35 | 7219.05
14:00 | 374 | 4927.2 | 2125.8 | 7053
14:30 | 387 | 5010.3 | 2132.8 | 7143.1
15:00 | 400 | 5093.4 | 2139.8 | 7233.2
15:30 | 412.5 | 5051.16 | 2123.45 | 7174.61
16:00 | 425 | 5008.92 | 2107.1 | 7116.02
16:30 | 412.5 | 5112.56 | 2159.6 | 7272.16
17:00 | 400 | 5216.2 | 2212.1 | 7428.3
17:30 | 229 | 5689.1 | 2476.05 | 8165.15
18:00 | 58 | 6162 | 2740 | 8902
18:30 | 57.5 | 6276.5 | 2767 | 9043.5
19:00 | 57 | 6391 | 2794 | 9185
19:30 | 61 | 6204 | 2780 | 8984
20:00 | 103 | 6150 | 2532 | 8682 |  |  |  | Executive Engineer
20:30 | 84 | 6124 | 2501.5 | 8625.5 |  |  |  | Network Operation Division
21:00 | 65 | 6098 | 2471 | 8569
21:30 | 44 | 5878 | 2386 | 8264
22:00 | 23 | 5658 | 2301 | 7959 |  |  |  |  | Page 6 of 7
22:30 | 15 | 5527.5 | 2177.5 | 7705
23:00 | 7 | 5397 | 2054 | 7451
23:30 | 33.5 | 5316.5 | 1896.5 | 7213
24:00 | 60 | 5236 | 1739 | 6975
9185 MW (19:00 )
7267.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-27 |  | Energy | 172359721
[10 empty] | 2019-11-27 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4038 | 248 | 2013 | 276 | 210 | 94 | 0 | 0 | 96
0:30 | 3978.5 | 247.5 | 1821.5 | 227.5 | 210 | 92.5 | 0 | 0 | 92 | Date: | 2019-11-27
1:00 | 3919 | 247 | 1630 | 179 | 210 | 91 | 0 | 0 | 88
1:30 | 3893.5 | 247 | 1577.5 | 144.5 | 195.5 | 91 | 0 | 0 | 86 | [7 empty] | Total Energy | 172.3597 | Total Energy Gen 172.360 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 172.360 MKWHr
2:00 | 3868 | 247 | 1525 | 110 | 181 | 91 | 0 | 0 | 84 | [7 empty] | Energy not Served | 0
2:30 | 3794.5 | 247.5 | 1497 | 110 | 175.5 | 90.5 | 0 | 0 | 84 | [7 empty] | Energy Requirement | 172.3597
3:00 | 3721 | 248 | 1469 | 110 | 170 | 90 | 0 | 0 | 84
3:30 | 3665 | 248 | 1461.5 | 110 | 170 | 90 | 0 | 0 | 83 | [6 empty] | Shortage
4:00 | 3609 | 248 | 1454 | 110 | 170 | 90 | 0 | 0 | 82
4:30 | 3589 | 248 | 1436 | 110 | 170 | 90 | 0 | 0 | 82
5:00 | 3569 | 248 | 1418 | 110 | 170 | 90 | 0 | 0 | 82
5:30 | 3639 | 248 | 1443 | 110 | 170 | 91.5 | 0 | 0 | 81
6:00 | 3709 | 248 | 1468 | 110 | 170 | 93 | 0 | 0 | 80
6:30 | 3776 | 247.5 | 1572 | 110 | 170 | 93 | 0 | 0 | 79 |  |  |  |  | Coal
7:00 | 3843 | 247 | 1676 | 110 | 170 | 93 | 0 | 0 | 78
7:30 | 3940 | 248 | 1715 | 116 | 170 | 93 | 0 | 0 | 80 |  |  |  | Oil |  |  |  | ,
8:00 | 4037 | 249 | 1754 | 122 | 170 | 93 | 0 | 0 | 82
8:30 | 3993 | 345.5 | 1686.5 | 145 | 170 | 92.5 | 0 | 0 | 85
9:00 | 3949 | 442 | 1619 | 168 | 170 | 92 | 0 | 0 | 88
9:30 | 3960 | 516.5 | 1592.5 | 216.5 | 170 | 92.5 | 0 | 0 | 88
10:00 | 3971 | 591 | 1566 | 265 | 170 | 93 | 0 | 0 | 88
10:30 | 4029 | 591 | 1630 | 255 | 170 | 93 | 0 | 0 | 88
11:00 | 4087 | 591 | 1694 | 245 | 170 | 93 | 0 | 0 | 88
11:30 | 4122.5 | 591.5 | 1778.5 | 255.5 | 170 | 93 | 0 | 0 | 91
12:00 | 4158 | 592 | 1863 | 266 | 170 | 93 | 0 | 0 | 94
12:30 | 4137 | 591.5 | 1930 | 281 | 169.5 | 93 | 0 | 0 | 94
13:00 | 4116 | 591 | 1997 | 296 | 169 | 93 | 0 | 0 | 94
13:30 | 4116 | 591 | 1997 | 296 | 169 | 93 | 0 | 0 | 94
14:00 | 4116 | 591 | 1997 | 296 | 169 | 93 | 0 | 0 | 94
14:30 | 4074.5 | 590.5 | 1966 | 294.5 | 169.5 | 93 | 0 | 0 | 98
15:00 | 4033 | 590 | 1935 | 293 | 170 | 93 | 0 | 0 | 102
15:30 | 4030 | 590 | 1879 | 300 | 170 | 91.5 | 0 | 0 | 102
16:00 | 4027 | 590 | 1823 | 307 | 170 | 90 | 0 | 0 | 102
16:30 | 4085 | 589.5 | 1786.5 | 424 | 172.5 | 91 | 17 | 0 | 103
17:00 | 4143 | 589 | 1750 | 541 | 175 | 92 | 34 | 0 | 104
17:30 | 4282.5 | 685.5 | 1920 | 848.5 | 187.5 | 92 | 34 | 0 | 115
18:00 | 4422 | 782 | 2090 | 1156 | 200 | 92 | 34 | 0 | 126
18:30 | 4372.5 | 782.5 | 2108.5 | 1329 | 205 | 92 | 27 | 0 | 127
19:00 | 4323 | 783 | 2127 | 1502 | 210 | 92 | 20 | 0 | 128
19:30 | 4279 | 783 | 2084 | 1408 | 210 | 92 | 0 | 0 | 128
20:00 | 4248 | 783 | 2081 | 1144 | 210 | 92 | 0 | 0 | 124
20:30 | 4214 | 783 | 2083.5 | 1121 | 210 | 92 | 0 | 0 | 122
21:00 | 4180 | 783 | 2086 | 1098 | 210 | 92 | 0 | 0 | 120
21:30 | 4170.5 | 783.5 | 2020 | 870 | 210 | 92 | 0 | 0 | 118
22:00 | 4161 | 784 | 1954 | 642 | 210 | 92 | 0 | 0 | 116
22:30 | 4129.5 | 686.5 | 1966.5 | 509 | 210 | 92.5 | 0 | 0 | 111
23:00 | 4098 | 589 | 1979 | 376 | 210 | 93 | 0 | 0 | 106
23:30 | 4068 | 418.5 | 1996 | 326 | 210 | 93.5 | 0 | 0 | 101 | Max Temp. in Dhaka |  | 30.5° C
24:00 | 4038 | 248 | 2013 | 276 | 210 | 94 | 0 | 0 | 96
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 172.360 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 172.360 MKWHr
Note on W13: Author:

## Generation
2019-11-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 41 | 41 | 40 | 40 | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 43 | 44 | 1001978
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1184000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3.6 | 9.6 | 14.2 | 17.71 | 19 | 19.5 | 18.3 | 15.3 | 11.1 | 5.4 | 0.2 | [9 empty] | 134460
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 207 | 204 | 203 | 177 | 189 | 189 | 214 | 203 | 203 | 215 | 216 | 216 | 204 | 204 | 203 | 203 | 218 |  | 203 | 203 | 222 | 203 | 203 | 203 | 203 | 4856961
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 147 | 120 | 120 | 100 | 80 | 100 | 100 | 120 | 120 | 120 | 139 | 145 | 140 | 139 | 144 | 144 | 115 | 142 |  | 145 | 144 | 144 | 145 | 144 | 144 | 144 | 3109851
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 34 | 34 |  | 20 | 0 | 0 |  |  |  |  | 79583
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | [14 empty] | 14 | 34 | 99 |  | 105 | 105 | 105 | 105 | 68 | 68 | 68 | 730145
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 60 | 40 | 40 | 40 | 40 | 60 | 92 | 90 | 70 | 70 | 90 | 90 | 90 | 40 | 40 | 40 | 42 | 42 |  | 42 | 42 | 62 | 90 | 87 | 90 | 90 | 1603000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 12 | 75 |  | 107 | 115 | 115 | 115 | 45 | 0 |  | 526909
19 | Ashuganj 195MW PP (APSCL-United) | 36 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 719272
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 790000
21 | Ghorasal Repowered CCPP Unit-3 | 114 | 115 | 114 | 114 | 114 | 115 | 113 | 135 | 128 | 128 | 128 | 128 | 128 | 129 | 129 | 129 | 129 | 129 |  | 129 | 129 | 129 | 129 | 129 | 129 | 131 | 3143000
22 | Ghorasal Repowered CCPP Unit-4 | [12 empty] | 20
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 240 | 6828582
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 120 | 120 | 120 | 120 | 2184806
29 | Ashuganj TPP Unit- 4 | [13 empty] | 0 | 63 | 80 | 80 | 85 |  | 85 | 80 | 80 | 80 | 80 | 0 |  | 653070
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 640584
33 | Ashuganj 225 MW CCPP | 202 | 202 | 171 | 151 | 150 | 151 | 180 | 192 | 188 | 201 | 200 | 198 | 198 | 198 | 198 | 196 | 197 | 197 |  | 199 | 200 | 198 | 200 | 200 | 200 | 200 | 4617000
34 | Ashuganj 450 MW CCPP(South) | 320 | 335 | 315 | 265 | 275 | 295 | 325 | 340 | 360 | 305 | 305 | 335 | 300 | 265 | 275 | 265 | 270 | 360 |  | 320 | 320 | 360 | 320 | 320 | 320 | 320 | 7531500
| Ashuganj 450 MW CCPP(North) | [26 empty] | 108000
35 | Ashuganj 55 MW PP (Precision) | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 47 | 50 | 48 | 48 | 49 | 49 |  | 49 | 49 | 50 | 50 | 49 | 51 | 52 | 816000
36 | Chandpur 150 MW CCPP | 95 | 96 | 90 | 90 | 95 | 95 | 95 | 95 | 95 | 96 | 96 | 96 | 85 | 88 | 96 | 93 | 85 | 95 |  | 87 | 90 | 95 | 81 | 95 | 95 | 95 | 2182950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 350 | 350 | 342 | 344 | 369 | 379 | 375 | 361 | 349 | 373 | 376 | 371 | 300 | 325 | 347 | 353 | 370 |  | 363 | 345 | 354 | 371 | 344 | 349 | 352 | 8636420
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 320 | 320 | 320 | 320 | 390 | 420 | 380 | 350 | 420 | 420 | 420 | 420 | 420 | 380 | 350 | 450 |  | 450 | 450 | 450 | 450 | 420 | 420 | 420 | 9114875
41 | Haripur 360MW CCPP(HPL) | 283 | 283 | 283 | 283 | 254 | 254 | 324 | 363 | 327 | 308 | 355 | 358 | 358 | 337 | 337 | 307 | 276 | 358 |  | 363 | 363 | 363 | 364 | 303 | 304 | 303 | 7586000
42 | RPCL 210MW CCPP | 157 | 157 | 157 | 160 | 159 | 158 | 160 | 157 | 108 | 125 | 125 | 124 | 124 | 126 | 124 | 124 | 152 | 152 |  | 154 | 156 | 155 | 157 | 154 | 154 | 157 | 3423160
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 60 | 60 | 60 | 60 | 58 | 58 | 57 | 60 | 60 |  | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 1416000
45 | Fenchugonj CCPP Phase-2 | 60 | 57 | 57 | 57 | 57 | 60 | 60 | 60 | 59 | 58 | 58 | 60 | 57 | 57 | 58 | 57 | 58 | 61 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1396560
46 | Shajibazar 330 MW CCPP | 98 | 98 | 95 | 96 | 95 | 97 | 98 | 100 | 90 | 97 | 97 | 97 | 90 | 101 | 102 | 103 | 170 | 183 |  | 201 | 206 | 214 | 201 | 201 | 204 | 201 | 2872000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 63 | 63 | 63 | 63 | 64 | 65 | 65 |  | 67 | 67 | 65 | 67 | 69 | 68 | 68 | 1283520
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 20 | 20 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 806400
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [12 empty] | 16 | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 234000
52 | Sylhet 50MW PP (EPL) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 30 | 34 | 36 | 36 | 36 | 37 | 37 |  | 40 | 40 | 38 | 40 | 40 | 40 | 40 | 513300
53 | Sylhet 10MW PP (Desh) | [11 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 138420
54 | Hobiganj 11MW PP Cofidence-E | [12 empty] | 11 | 11 | 11 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 105648
55 | Fenchugonj 51 MW PP (Barakatullah) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 26 | 47 | 47 | 47 | 22 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 47 | 44 | 585600
56 | Shahjahanulla 25 MW PP | [12 empty] | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 290064
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 300 | 300 | 295 | 280 | 300 | 315 | 320 | 300 | 300 | 320 | 320 | 320 | 290 | 300 | 310 | 305 | 280 |  | 310 | 315 | 300 | 310 | 280 | 295 | 305 | 7570500
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 35 |  | 35 | 35 | 17 | 17 | 0 |  |  | 137986
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 432912
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 19 | 19 | 19 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 186084
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524916
63 | Impoprt (Tripura) | 88 | 84 | 84 | 82 | 82 | 80 | 78 | 82 | 88 | 88 | 88 | 94 | 94 | 100 | 102 | 102 | 104 | 126 |  | 128 | 128 | 124 | 120 | 116 | 106 | 96 | 2347200
64 | Malancha, Ctg. EPZ (United) | 34 | 37 | 36 | 31 | 42 | 40 | 36 | 10 | 3 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 5 | 3 |  | 10 | 12 | 18 | 26 | 33 | 36 | 38 | 437760
65 | Feni 22MW PP (Doreen) | 22 | [6 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 370620
66 | Feni 11 MW PP (Doreen) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 112680
67 | Jangalia 33MW PP (Summit) | [12 empty] | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 405900
68 | Cumilla 25 MW PP (Summit) | 15 | 20 | 20 | 20 | 17 | 17 | 14 | 18 | 18 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 486990
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 30 | 30 | 25 | 25 | 25 | 22 | 23 | 26 | 27 | 27 | 27 | 20 | 20 | 27 | 27 | 27 | 17 |  | 28 | 28 | 30 | 31 | 31 | 31 | 31 | 639000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 738300
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 779000
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [8 empty] | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 45 |  | 52 | 52 | 33 | 33 | 0 |  |  | 392940
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 0 |  | 8 | 8 | 0 | 0 |  |  |  | 19200
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [7 empty] | 2 | 18 | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 17 | [6 empty] | 390108
| Kaptai 7 MW Solar PP | [6 empty] | 0.3 | 1.8 | 3 | 3.9 | 4.4 | 4.4 | 4 | 3.3 | 2.2 | 0.12 | [10 empty] | 28440
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 150 | 110 | 110 | 110 | 110 | 110 | 110 | 120 | 120 | 120 | 120 | 120 | 125 | 125 | 125 | 125 | 120 | 120 |  | 120 | 120 | 120 | 120 | 105 | 105 | 95 | 2694429
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 25 | 70 |  | 100 | 100 | 100 | 100 | 40 | 40 | 0 | 482280
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 31 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 746640
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 15 | 25 | 36 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 572912
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [16 empty] | 1 | 11 |  | 21 | 0 | [5 empty] | 43200
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 6 | 25 |  | 50 | 50 | 10 |  |  |  |  | 123840
97 | Katpotti 52 MW PP (Sinha) | 12 | [12 empty] | 5 | 12 | 12 | 12 | 28 |  | 47 | 30 | 12 | 12 | 12 | 12 | 12 | 243312
98 | Bosila 108MW PP(CLC) | [16 empty] | 66 | 72 |  | 72 | 72 | 72 | 72 | 40 | 0 |  | 377280
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 |  | 0 | 0 | [5 empty] | 116386
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 10 | 17 |  | 17 | 17 | [5 empty] | 47319
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 100 | 130 | 163 | 163 | 130 | 100 | 100 | 130 | 130 | 100 | 130 | 130 | 100 | 163 |  | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 3156561
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.7 | 1.3 | 1.9 | 2.1 | 2 | 1.9 | 1.6 | 1.1 | 0.4 | [10 empty] | 12650
103 | Kamalaghat 54 MW PP(Banco Energy) | [26 empty] | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 12 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 64 | 99 |  | 192 | 200 | 200 | 200 | 200 | 100 | 50 | 1620000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 0 | 12 |  | 50 | 50 | 0 | 0 |  |  |  | 101760
116 | Chandpur 200MW (Desh energy) | [16 empty] | 6 | 57 |  | 70 | 50 | 50 | 50 | 17 | 0 |  | 296440
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 3 | 46 |  | 70 | 30 | 13 |  |  |  |  | 180654
118 | Bibiyana-III 400 MW CCPP | 368 | 377 | 362 | 365 | 368 | 396 | 380 | 394 | 364 | 375 | 394 | 401 | 367 | 366 | 370 | 364 | 367 | 410 |  | 366 | 367 | 416 | 364 | 365 | 366 | 364 | 9069000
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [12 empty] | 15 | 8 | [6 empty] | 0 | [5 empty] | 25091
120 | Eastern Zone Total | 4579 | 4368 | 4257 | 4138 | 4033 | 4212 | 4470 | 4728.1 | 4541.5 | 4556.51 | 4768.5 | 5006.9 | 5158.2 | 4927.2 | 5093.4 | 5008.92 | 5216.2 | 6162 |  | 6391 | 6204 | 6150 | 6098 | 5658 | 5397 | 5236 | 121253908
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 0 | 35 |  | 35 | 35 | 21 | 17 | 0 |  |  | 111360
130
131
132
133
| Barisal 110 MW PP (Summit ) | [7 empty] | 0 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 393600
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 175 | 183 |  | 182 | 182 | 182 | 182 | 183 | 183 | 183 | 3947168
140 | Bhola 33 MW PP (Venture) | 22 | 21 | 20 | 20 | 19 | 20 | 19 | 12 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 25 |  | 25 | 24 | 26 | 27 | 26 | 23 | 22 | 471545
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 8 | 0 |  | 162375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 17 |  | 17 | 17 | 0 |  |  |  |  | 38160
146 | Bheramara HVDC | 247 | 247 | 248 | 248 | 248 | 248 | 247 | 249 | 442 | 591 | 591 | 592 | 591 | 590 | 590 | 590 | 589 | 782 |  | 783 | 783 | 783 | 783 | 784 | 589 | 248 | 11918545
147 | Bheramara 360 MW CCPP | 310 | 335 | 280 | 280 | 280 | 280 | 340 | 330 | 310 | 340 | 345 | 350 | 310 | 307 | 320 | 310 | 315 | 360 |  | 310 | 305 | 340 | 300 | 320 | 320 | 320 | 7864992
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 210 | 181 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 169 | 170 | 170 | 170 | 175 | 200 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4476100
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70 | 70 | 65 | 50 | 50 | 50 | 50 | 50 |  | 45 | 35 | 25 | 25 | 25 | 25 | 25 | 1185000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 205 | 191 | 178 | 175 | 179 | 183 | 184 | 185 | 205 | 202 | 214 | 214 | 205 | 182 | 184 | 177 | 180 | 189 |  | 205 | 202 | 0 |  |  |  |  | 4061445
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 183 | 183 | 183 | 181 | 179 | 185 | 186 | 180 | 206 | 209 | 215 | 212 | 208 | 193 | 194 | 194 | 191 | 193 |  | 210 | 196 | 195 | 213 | 197 | 202 | 203 | 4976709
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 397 | 369 | 345 | 340 | 368 | 369 | 394 | 431 | 407 | 434 | 424 | 425 | 428 | 383 | 383 | 369 | 383 | 416 |  | 408 | 422 | 427 | 410 | 394 | 404 | 430 | 9626545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [11 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 252720
163 | Bogura 20 MW PP (Energyprima) | [11 empty] | 10 | 12 | 12 | 12 | 12 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 169128
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 232164
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 12 | 32 |  | 32 | 32 | 32 | 18 | 0 |  |  | 140230
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 12 | 60 |  | 100 | 113 | 113 | 113 | 56 | 0 |  | 532128
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 80 |  | 113 | 105 | 75 | 70 | 35 | 35 | 35 | 513600
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1.4 | 2.8 | 4.2 | 5 | 5.3 | 4.9 | 4.8 | 2.8 | 1.1 | 0.1 | [9 empty] | 32299
178
178