## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-11-30 | Saturday
|  | Date (day): | 2019-11-30 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11653.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14223 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-29 | 2019-11-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 94 | 94 | 130 | 130
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | S/D for S/S maintenance work.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 230 | 260 | 320 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas Shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 372 | 363 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 360 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 120 | 120 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 85 | 97 | 100 | 100 | 105 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 49 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 71 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 34 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1614 | 2066 | 3747 | 4194 | 581 | 796
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 100 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.68 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 96 | 92 | 90 | 92 | 138 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 215 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 144 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 21 | 35 | 5 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 10 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.432 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 634.112 | 741 | 1488 | 1650 | 378 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 55 | 100 | 80 | 80 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 198 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under S/D
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 310 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 52 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 68 | 68 | 68 | 68 | 127 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 81 | 95 | 95
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 35 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 112 | 113 | 132
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 10 | 21 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 889 | 1223 | 1508 | 1927 | 405 | 376
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 183 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 0 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 16 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 80 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 153.1 | 301 | 471.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 61 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 56 | 58 | 58
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 212 | 168 | 212 | 250
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 46 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 0 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 4 | 37 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 315 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 343 | 364 | 400 | 400
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1207 | 1468 | 1555 | 1614 | 0 | 162
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 172 | 433 | 190 | 438
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 340 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 18 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 472 | 826 | 685 | 1658 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 25 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 152 | 170 | 153 | 182
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 232 | 227 | 344 | 443 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 32 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 195 | 207 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 213 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 428 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 697 | 962 | 1524 | 1788 | 320 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 210 | 210
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 205 | 235 | 331 | 357 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 6103.212 | 8049 | 11653.6 | 14223 | 1726 | 1617
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5793.0848 | 7640 | 11061.4367 | 13500.2758
A. |  | 2019-11-29 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8049 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5597 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8049 | MW
3 | Day peak Generation : |  |  | 6103.212 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7640 | MW
4 | Evening peak Generation : |  |  | 8049 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 156.2902 | MKWHr | By Solar | 0.20788 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 137.261 | MKWHr |  | By Oil: | 4.8243 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.8501 | MKWHr |  | By Hydro: | 2.216 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1726 | MW | Dhaka | 2843 | 2843 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1617 | MW | Chittagong | 815 | 815 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3343 | MW | Khulna | 907 | 907 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1106.95 | MMCFD |  |  | Rajshahi | 771 | 771 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 125742839.628 | ii) Oil : | Taka | 47332594.99 | Comilla | 696 | 696 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19836909 | Total | Taka | 192912343.618 | Mymensingh | 608 | 608 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.4125 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -233 | MW (E to W) at | 19:00 | hrs | Barisal | 214 | 214 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -315 | MW at | 2:00 | hrs | Rangpur | 470 | 470 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.3° C |  |  | Total | 7640 | 7640 |  | 0
B. |  | 2019-11-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 29.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14223 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7100 | MW
4 | Reserve(Generation end) |  |  |  | 5123 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 176.6978 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5433 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 4.792 | MKWHr. | ii) HVDC Flow at Peak Time |  | 433 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1389 | MKWHr. | iii) Maximum HVDC Flow : |  | 433 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 99.92 | 101.08 |  | (b) Today: | 99.92 |  | (c) Rule Curve: |  | 106.1
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 130 | 0 | 0 | 265 | 0 | 0 | 345 | 330 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 50 | 0 | 120 | 0 | 207 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 0 | 280 | 162 | 98 | 95 | 37 | 50 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 21 | 90 | 157 | 0 | 22 | 0 | 60 | 56 | 50 | 50 | 100 | 240 | 68 | 76 | 0 | 0 | 17 | 40 | 10 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 |  | 105 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5113 | 1482 | 6595 | 4014 | 105 | 2048 | 46 | 200 | 92 | 0 | 90 | 0 | 0 | 101.12
2:00 | 35 | 130 | 0 | 0 | 268 | 0 | 0 | 346 | 330 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 41 | 50 | 0 | 120 | 0 | 203 | 0 | 93 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 0 | 280 | 161 | 98 | 95 | 37 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 20 | 19 | 86 | 159 | 0 | 22 | 0 | 59 | 56 | 50 | 50 | 100 | 235 | 68 | 50 | 0 | 0 | 17 | 39 | 10 | 300 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 105 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 201 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4925 | 1403 | 6328 | 3880 | 105 | 1942 | 23 | 201 | 91 | 0 | 86 | 0 | 0 | 101.11
3:00 | 35 | 130 | 0 | 0 | 268 | 0 | 0 | 342 | 329 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 0 | 120 | 0 | 203 | 0 | 95 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 0 | 285 | 168 | 98 | 95 | 37 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 84 | 159 | 0 | 0 | 0 | 59 | 56 | 0 | 20 | 100 | 243 | 67 | 5 | 0 | 0 | 0 | 3 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 104 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4632 | 1404 | 6036 | 3820 | 104 | 1715 | 23 | 200 | 90 | 0 | 84 | 0 | 0 | 101.11
4:00 | 35 | 130 | 0 | 0 | 268 | 0 | 0 | 343 | 329 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 39 | 50 | 0 | 120 | 0 | 204 | 0 | 96 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 80 | 0 | 0 | 0 | 280 | 161 | 68 | 95 | 37 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 84 | 158 | 0 | 0 | 0 | 60 | 56 | 0 | 0 | 100 | 242 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 103 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4504 | 1418 | 5922 | 3803 | 103 | 1643 | 0 | 200 | 89 | 0 | 84 | 0 | 0 | 101.1
5:00 | 35 | 95 | 0 | 0 | 265 | 0 | 0 | 353 | 288 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 39 | 50 | 0 | 120 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 80 | 0 | 0 | 0 | 280 | 180 | 68 | 95 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 82 | 159 | 0 | 0 | 0 | 60 | 56 | 0 | 0 | 100 | 244 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4375 | 1418 | 5793 | 3729 | 105 | 1588 | 0 | 200 | 89 | 0 | 82 | 0 | 0 | 101.09
6:00 | 35 | 94 | 0 | 0 | 265 | 0 | 0 | 360 | 289 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 39 | 50 | 0 | 120 | 0 | 203 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 80 | 0 | 0 | 0 | 275 | 171 | 68 | 95 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 80 | 160 | 0 | 0 | 0 | 60 | 56 | 0 | 0 | 100 | 235 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4355 | 1449 | 5804 | 3733 | 104 | 1598 | 0 | 200 | 89 | 0 | 80 | 0 | 0 | 101.08
7:00 | 35 | 95 | 0 | 0 | 230 | 0 | 0 | 344 | 289 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 33 | 33 | 0 | 0 | 45 | 50 | 0 | 120 | 0 | 202 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 80 | 0 | 0 | 0 | 265 | 164 | 68 | 94 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 74 | 160 | 0 | 0 | 0.1 | 60 | 56 | 0 | 0 | 100 | 245 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 |  | 104 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 4274.43 | 1447.2 | 5721.63 | 3673 | 104 | 1572 | 0 | 200 | 95 | 0 | 74 | 3.63 | 0 | 101.07
8:00 | 35 | 94 | 0 | 0 | 230 | 0 | 0 | 350 | 290 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 120 | 0 | 205 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 26 | 80 | 0 | 0 | 0 | 275 | 175 | 68 | 96 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 66 | 158 | 0 | 0 | 0.4 | 60 | 56 | 0 | 0 | 100 | 244 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.75 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 1.573 | 0 | 0 | 0 | 0 |  | 102 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 4308.723 | 1517.4 | 5826.123 | 3733 | 102 | 1570 | 48 | 200 | 94 | 0 | 66 | 13.123 | 0 | 0
9:00 | 35 | 94 | 0 | 0 | 230 | 0 | 0 | 344 | 290 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 45 | 50 | 0 | 120 | 0 | 203 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 24 | 80 | 0 | 0 | 0 | 270 | 165 | 68 | 94 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 70 | 157 | 0 | 0 | 1.4 | 60 | 56 | 0 | 0 | 100 | 216 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.58 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 3.02 | 0 | 0 | 0 | 0 |  | 102 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 199 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 4094 | 1503 | 5597 | 3610 | 102 | 1451 | 48 | 199 | 95 | 0 | 70 | 22 | 0 | 0
10:00 | 35 | 94 | 0 | 0 | 230 | 0 | 0 | 344 | 290 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 45 | 50 | 0 | 120 | 0 | 216 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 24 | 80 | 0 | 16 | 0 | 265 | 161 | 68 | 88 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 76 | 155 | 0 | 0 | 1.8 | 60 | 56 | 0 | 0 | 130 | 214 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.85 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 3.934 | 0 | 0 | 0 | 0 |  | 102 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 200 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 4122.584 | 1462.1 | 5584.684 | 3574 | 102 | 1462 | 48 | 200 | 95 | 0 | 76 | 27.684 | 0 | 0
11:00 | 35 | 95 | 0 | 0 | 230 | 0 | 0 | 350 | 290 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 17 | 33 | 0 | 0 | 45 | 50 | 0 | 120 | 0 | 230 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 80 | 0 | 30 | 0 | 305 | 182 | 68 | 95 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84 | 153 | 0 | 0 | 1.9 | 60 | 56 | 0 | 0 | 130 | 222 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.24 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 4.398 | 0 | 0 | 0 | 0 |  | 102 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 200 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 |  | 4268.538 | 1452.9 | 5721.438 | 3697 | 102 | 1465 | 48 | 200 | 95 | 0 | 84 | 30.438 | 0 | 0
12:00 | 35 | 94 | 0 | 0 | 230 | 0 | 0 | 372 | 330 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 28 | 0 | 0 | 46 | 50 | 0 | 120 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 80 | 0 | 55 | 0 | 300 | 181 | 68 | 96 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84 | 151 | 0 | 0 | 2.1 | 60 | 60 | 0 | 0 | 163 | 212 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.68 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 4.432 | 0 | 0 | 0 | 0 |  | 172 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 |  | 4497.212 | 1606 | 6103.212 | 3854 | 172 | 1602 | 64 | 200 | 96 | 0 | 84 | 31.212 | 0 | 0
13:00 | 35 | 94 | 0 | 0 | 250 | 0 | 0 | 381 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 28 | 0 | 0 | 43 | 50 | 0 | 120 | 0 | 214 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 80 | 0 | 55 | 0 | 290 | 182 | 68 | 93 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92 | 150 | 0 | 0 | 2 | 60 | 56 | 0 | 0 | 163 | 219 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.03 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 4.084 | 0 | 0 | 0 | 0 |  | 172 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 200 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 4565.114 | 1691.8 | 6256.914 | 3903 | 172 | 1703 | 65 | 200 | 93 | 0 | 92 | 28.914 | 0 | 0
14:00 | 35 | 94 | 0 | 0 | 220 | 0 | 0 | 347 | 300 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 25 | 0 | 0 | 43 | 50 | 0 | 120 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 26 | 80 | 0 | 55 | 0 | 270 | 162 | 68 | 85 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 88 | 150 | 0 | 0 | 1.4 | 60 | 56 | 0 | 0 | 130 | 212 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.88 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 |  | 172 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 4204.58 | 1599.1 | 5803.68 | 3662 | 172 | 1493 | 71 | 200 | 93 | 0 | 88 | 24.68 | 0 | 0
15:00 | 35 | 94 | 0 | 0 | 220 | 0 | 0 | 348 | 300 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 12 | 17 | 25 | 0 | 0 | 45 | 50 | 0 | 120 | 0 | 205 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 80 | 0 | 55 | 0 | 285 | 183 | 68 | 95 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 88 | 149 | 0 | 0 | 1.1 | 60 | 56 | 0 | 0 | 130 | 210 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 |  | 172 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 4190.1 | 1553 | 5743.1 | 3668 | 172 | 1448 | 54 | 200 | 95 | 0 | 88 | 18.1 | 0 | 0
16:00 | 35 | 94 | 0 | 0 | 220 | 0 | 0 | 353 | 300 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 12 | 17 | 25 | 0 | 0 | 45 | 50 | 0 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 80 | 0 | 55 | 0 | 270 | 182 | 68 | 93 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 82 | 149 | 0 | 0 | 0.4 | 61 | 56 | 0 | 0 | 100 | 177 | 40 | 5 | 0 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 |  | 168 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4113.9 | 1564.1 | 5678 | 3636 | 168 | 1435 | 54 | 200 | 95 | 0 | 82 | 8 | 0 | 0
17:00 | 35 | 94 | 0 | 0 | 220 | 0 | 0 | 357 | 300 |  | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 6 | 0 | 17 | 0 | 0 | 25 | 12 | 33 | 25 | 0 | 0 | 42 | 50 | 0 | 120 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 12 | 8 | 0 | 0 | 19 | 26 | 80 | 0 | 70 | 0 | 270 | 182 | 68 | 90 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 82 | 152 | 0 | 0 | 0 | 61 | 56 | 0 | 0 | 100 | 165 | 66 | 5 | 0 | 0 | 0 | 3 | 0 | 310 | 0 | 0 | 0 | 16 | 0 | 0 | 26 | 0 | 0 | 0.2 | 0 | 4 | 0 | 316 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 |  | 168 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 282 | 0 | 0 | 6 | 0 | 35 | 0 | 0.1 | 0 |  | 4283.2 | 1625.1 | 5908.3 | 3691 | 168 | 1461 | 202 | 200 | 92 | 12 | 82 | 0.3 | 0 | 0
18:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 358 | 340 |  | 0 | 450 | 0 | 0 | 0 | 8 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 38 | 0 | 17 | 17 | 19 | 25 | 12 | 33 | 25 | 8 | 0 | 42 | 50 | 0 | 100 | 0 | 208 | 0 | 144 | 0 |  | 0 | 0 | 17 | 10 | 10 | 4 | 19 | 39 | 100 | 0 | 100 | 0 | 330 | 199 | 68 | 90 | 36 | 30 | 0 | 18 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 112 | 153 | 8 | 22 | 0 | 59 | 56 | 49 | 34 | 130 | 175 | 66 | 76 | 0 | 0 | 17 | 38 | 10 | 270 | 24 | 11 | 0 | 56 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 34 | 0 | 385 | 0 | 34 | 105 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 415 | 17 | 0 | 35 | 18 | 35 | 0 | 0 | 0 |  | 5588 | 2226 | 7814 | 4268 | 433 | 2028 | 664 | 200 | 92 | 17 | 112 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 363 | 360 |  | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 17 | 17 | 19 | 25 | 24 | 33 | 25 | 8 | 0 | 42 | 50 | 0 | 100 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 17 | 10 | 10 | 6 | 19 | 35 | 100 | 0 | 100 | 0 | 310 | 198 | 68 | 81 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 183 | 16 | 22 | 0 | 61 | 56 | 53 | 46 | 163 | 168 | 67 | 76 | 0 | 0 | 17 | 37 | 10 | 315 | 24 | 11 | 0 | 71 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 35 | 0 | 364 | 0 | 34 | 105 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 428 | 35 | 0 | 35 | 18 | 35 | 0 | 0 | 0 |  | 5799 | 2250 | 8049 | 4268 | 433 | 2197 | 730 | 200 | 92 | 17 | 112 | 0 | 0 | 0
19:30 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 345 | 360 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 17 | 17 | 19 | 25 | 31 | 33 | 25 | 0 | 0 | 42 | 50 | 0 | 100 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 10 | 6 | 19 | 35 | 100 | 0 | 100 | 0 | 310 | 199 | 68 | 90 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 208 | 16 | 22 | 0 | 60 | 56 | 53 | 50 | 163 | 172 | 67 | 76 | 0 | 0 | 17 | 37 | 10 | 315 | 24 | 11 | 0 | 95 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 34 | 0 | 366 | 0 | 34 | 105 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 409 | 24 | 0 | 35 | 18 | 35 | 0 | 0 | 0 |  | 5816 | 2219 | 8035 | 4297 | 433 | 2182 | 719 | 200 | 92 | 0 | 112 | 0 | 0 | 0
20:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 346 | 363 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 0 | 17 | 19 | 25 | 31 | 33 | 31 | 0 | 0 | 44 | 50 | 0 | 100 | 0 | 209 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 10 | 0 | 19 | 37 | 100 | 0 | 100 | 0 | 320 | 199 | 68 | 90 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 193 | 16 | 22 | 0 | 60 | 56 | 53 | 50 | 163 | 172 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 367 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 433 | 17 | 0 | 35 | 18 | 35 | 0 | 0 | 0 |  | 5775 | 2218 | 7993 | 4308 | 433 | 2209 | 635 | 200 | 94 | 0 | 114 | 0 | 0 | 0
21:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 353 | 363 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 38 | 0 | 0 | 14 | 19 | 25 | 31 | 33 | 31 | 0 | 0 | 43 | 50 | 0 | 100 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 10 | 0 | 19 | 38 | 100 | 0 | 100 | 0 | 310 | 200 | 68 | 88 | 37 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 183 | 0 | 22 | 0 | 59 | 56 | 53 | 50 | 163 | 169 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 17 | 0 | 364 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 423 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 0 |  | 5713 | 2128 | 7841 | 4247 | 433 | 2200 | 560 | 200 | 93 | 0 | 108 | 0 | 0 | 0
22:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 343 | 364 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 31 | 0 | 0 | 43 | 50 | 0 | 100 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 100 | 0 | 100 | 0 | 310 | 200 | 68 | 80 | 37 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 182 | 0 | 22 | 0 | 61 | 56 | 53 | 50 | 130 | 169 | 67 | 76 | 0 | 0 | 17 | 40 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5375 | 2018 | 7393 | 4184 | 433 | 2162 | 213 | 200 | 93 | 0 | 108 | 0 | 0 | 0
23:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 357 | 364 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 211 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 100 | 0 | 100 | 0 | 345 | 200 | 68 | 91 | 30 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 98 | 182 | 0 | 22 | 0 | 60 | 56 | 53 | 50 | 100 | 172 | 67 | 73 | 0 | 0 | 17 | 39 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 190 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5175 | 1729 | 6904 | 4182 | 190 | 2075 | 65 | 200 | 94 | 0 | 98 | 0 | 0 | 0
24:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 354 | 367 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 31 | 22 | 17 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 100 | 0 | 100 | 0 | 280 | 200 | 68 | 89 | 33 | 52 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 90 | 183 | 0 | 22 | 0 | 60 | 56 | 53 | 50 | 100 | 173 | 69 | 73 | 0 | 0 | 17 | 39 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 189 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4919 | 1642 | 6561 | 3974 | 189 | 1996 | 18 | 200 | 94 | 0 | 90 | 0 | 0 | 0
KWH | 780000 | 2571000 | 0 | 0 | 5955800 | 0 | 0 | 8603650 | 7656000 |  | 0 | 9820250 | 0 | 0 | 0 | 34545 | 0 | 0 | 1669000 | 0 | 0 | 0 | 0 | 0 | 296640 | 0 | 335376 | 0 | 55420 | 750072 | 114876 | 600000 | 540000 | 794800 | 720500 | 19200 | 0 | 1027985 | 1188000 | 0 | 2800000 | 0 | 4902307 | 0 | 2780816 | 0 |  | 0 | 0 | 39120 | 50760 | 47040 | 14880 | 442512 | 820800 | 2066174 | 0 | 1021836 | 0 | 7122500 | 4336000 | 1773090 | 2121250 | 539424 | 598080 | 0 | 421608 | 0 | 0 | 0 | 206244 | 79560 | 309300 | 448830 | 2138880 | 3794440 | 61440 | 207360 | 12700 | 1430000 | 1367520 | 462600 | 549504 | 3084864 | 4734000 | 1251648 | 787200 | 0 | 0 | 170000 | 423460 | 95580 | 7530750 | 193632 | 98928 | 0 | 408982 | 0 | 0 | 456000 | 0 | 0 | 136080 | 0 | 136800 | 0 | 8479000 | 0 | 104916 | 688327 | 27960 | 0 | 0 | 0 | 0 |  | 4792000 | 0 | 7554528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3844570 | 434700 | 729600 | 0 | 0 | 0 | 0 | 0 | 0 | 97100 | 0 | 0 | 0 | 0 | 193680 | 137628 | 228744 | 0 | 0 | 4850100 | 0 | 0 | 4712809 | 0 | 0 | 0 | 0 | 0 | 4733582 | 0 | 8144091 | 102720 | 0 | 172800 | 43056 | 179520 | 0 | 31140 | 0 |  | 115307816 | 40982368 | 156290184 | 94327140 | 4792000 | 42933885 | 4785194 | 4850100 | 2215985 | 39120 | 2138880 | 207880 | 0
Fuel Cost | 873600 | 2776680 | 0 | 0 | 4407292 | 0 | 0 | 6194628 | 5818560 |  | 0 | 7856200 | 0 | 0 | 0 | 354431.7 | 0 | 0 | 2086250 | 0 | 0 | 0 | 0 | 0 | 2699424 | 0 | 3139119.36 | 0 | 528706.8 | 7470717.12 | 86157 | 450000 | 0 | 0 | 0 | 183936 | 0 | 267276.1 | 308880 | 0 | 4284000 | 0 | 5147422.35 | 0 | 3531636.32 | 0 |  | 0 | 0 | 410368.8 | 522320.4 | 447350.4 | 139276.8 | 407111.04 | 2281824 | 2169482.7 | 0 | 1072927.8 | 0 | 5982900 | 3989120 | 1737628.2 | 2821262.5 | 442327.68 | 616022.4 | 0 | 602899.44 | 0 | 0 | 0 | 210368.88 | 59670 | 584577 | 336622.5 | 14758272 | 3111440.8 | 584294.4 | 211507.2 | 208280 | 1944800 | 1859827.2 | 629136 | 686880 | 3825231.36 | 4355280 | 1864955.52 | 1385472 | 0 | 0 | 270300 | 495448.2 | 224613 | 5346832.5 | 145224 | 75185.28 | 0 | 4282041.54 | 0 | 0 | 4386720 | 0 | 0 | 1570363.2 | 0 | 1283184 | 0 | 7970260 | 0 | 934801.56 | 6504690.15 | 0 | 0 | 0 | 0 | 0 |  | 12938400 | 0 | 5892531.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3075656 | 673785 | 7835904 | 0 | 0 | 0 | 0 | 0 | 0 | 1006927 | 0 | 0 | 0 | 0 | 213048 | 227086.2 | 173159.208 | 0 | 0 | 19836909 | 0 | 0 | 4147271.92 | 0 | 0 | 0 | 0 | 0 | 4165552.16 | 0 | 5945186.43 | 971731.2 | 0 | 1586304 | 383628.96 | 1676716.8 | 0 | 0 | 0 |  | 152214017.2 | 70749797.718 | 222963814.918 | 87176986.898 | 12938400 | 38565852.73 | 46922226.19 | 19836909 | 576156.1 | 410368.8 | 14758272 | 1778643.2 | 0
Yesterday Day Peak | 35 | 94 | 0 | 0 | 230 | 0 | 0 | 372 | 330 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 33 | 28 | 0 | 0 | 46 | 50 | 0 | 120 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 80 | 0 | 55 | 0 | 300 | 181 | 68 | 96 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84 | 151 | 0 | 0 | 2.1 | 60 | 60 | 0 | 0 | 163 | 212 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.68 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 4.432 | 0 | 0 | 0 | 0 |  | 172 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 |  | 6103.212 | DayPeak
Yesterday Evening Peak | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 363 | 360 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 17 | 17 | 19 | 25 | 24 | 33 | 25 | 8 | 0 | 42 | 50 | 0 | 100 | 0 | 203 | 0 | 144 | 0 | 0 | 0 | 0 | 17 | 10 | 10 | 6 | 19 | 35 | 100 | 0 | 100 | 0 | 310 | 198 | 68 | 81 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 183 | 16 | 22 | 0 | 61 | 56 | 53 | 46 | 163 | 168 | 67 | 76 | 0 | 0 | 17 | 37 | 10 | 315 | 24 | 11 | 0 | 71 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 35 | 0 | 364 | 0 | 34 | 105 | 0 | 0 | 0 | 0 | 0 |  | 433 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 428 | 35 | 0 | 35 | 18 | 35 | 0 | 0 | 0 |  | 8049 | EvPeak
Forecast for Evening | 35 | 130 | 0 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 50 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 10 | 120 | 0 | 80 | 0 | 360 | 200 | 68 | 95 | 37 | 55 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 132 | 160 | 95 | 22 | 0 | 60 | 58 | 51 | 44 | 163 | 250 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 438 | 40 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 182 | 26 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 210 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 130 | 0 | 0 | 320 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 40 | 50 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 5 | 120 | 0 | 80 | 0 | 360 | 200 | 68 | 95 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 113 | 160 | 95 | 0 | 1.6 | 60 | 58 | 51 | 44 | 163 | 212 | 66 | 76 | 0 | 0 | 20 | 40 | 0 | 341 | 24 | 0 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 0 |  | 190 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 26 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 365 | 366 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 24 | 17 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 202 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 80 | 0 | 80 | 0 | 305 | 168 | 8 | 50 | 26 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 185 | 0 | 0 | 0.6 | 30 | 60 | 5 | 10 | 163 | 168 | 68 | 5 | 0 | 0 | 0 | 32 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.57 | 0 | 168 | 0 | 366 | 0 | 0 | 0 | 0.94 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 8 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0
199
| Minimum Generation |  | 5597 | 9:00
| Highest Generation |  | 8049 | 19:00
| Day Peak Generation |  | 6103.212 | 12:00
| Evening Peak Generation |  | 8049 | 19:00
| HVDC Max Flow |  | 433 | 18:00
| HVDC EvPeak Flow |  | 433 | 19:00
| Load factor L.F |  | 80.91%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-11-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6103.212 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5433 | MW
Evening Peak Generation : |  | 8049 | MW Hour : | 19:00 | Available Max Generation : |  | 14223 | MW
E.P. Demand (at gen end) : |  | 8049 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9100 | MW
Maximum Generation : |  | 8049 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5123 | MW
Total Gen. (MKWH) : |  | 156.2902 | System Load Factor : | 80.91% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -315 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-11-30
Actual : | 99.92 | Ft.(MSL) , | Rule curve : | 106.1 | Ft.( MSL )
Gas Consumed : | Total = | 1106.95 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 125742839.628
: |  | Coal : | 19836909 | Oil : | 47332594.99 | Total : | 192912343.618
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3226.2695 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1091.878 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 977.3542 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 882.791 |  |  | 0 | 0%
) | 0 | 0:00 | 797.948 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 643.9026 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 366.7716 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 165.9658 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 496.5774 |  |  | 0 | 0%
Total | 0 |  | 8649.4581 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,4
4) Ashuganj unit-4
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Barapukuria ST: unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ashuganj Unit-5 was synchronized at 09:45.
b) Barishal (N) 132/33 kV T5 transformer was under shut down from 07:49 to 14:38 for D/W.
c) Rampura 230 kV Bus-2 was under shut down from 08:16 to 14:12 for A/M.
d) Tangail 132/33 kV T2 transformer was under shut down from 08:48 to 16:03 for A/M.
e) Rangpur-Lalmonirhat 132 kV Ckt was under shut down from 08:15 to 16:23 for A/M. |  |  |  |  | About 44 MW power interruption occurred under Lalmonirhat S/S
area from 08:15 to 16:23.
f) Maniknagar-Bangabhaban 132 kV Ckt-2 was under shut down from 09:17 to 16:34 for A/M.
g) Madunaghat 132/33 kV T2 transformer was under shut down from 10:14 to 11:51 for oil
leakage at LT bushing.
h) Siddhirganj 132/33 kV T1 transformer was under shut down from 09:58 to 10:35 for changing
33 kV fuse.
i) Sherpur (Bogura)-Sirajganj 132 kV Ckt-2 was under shut down from 11:25 to 14:22 for D/W.
j) Naogaon-Joypurhat 132 kV Ckt was under shut down from 08:10 to 14:39 for A/M. |  |  |  |  | About 20 MW power interruption occurred under Joypurhat S/S
area from 08:10 to 14:39.
k) Khulna (C) -Khulna (S) 132 kV Ckt-1 was under shut down from 08:46 to 13:47 for red
maintenance.
l) Khulna (c)-Noapara 132 kV Ckt-2 was under shut down from 17:17 to 20:02 for testing.
m) Barishal (N)-Barishal 132 kV Ckt-2 was shut down at 07:04 (30/11/19) for D/W.
n) Haripur-Siddhirganj 230 kV Ckt-2 was shut down at 07:38 (30/11/19) for A/M.
o) Hasnabad 230/132 kV T01 was shut down at 07:28 (30/11/19) for A/M.
p) Ishurdi-Natore 132 kV Ckt-2 was shut down at 07:53 (30/11/19) for A/M.
q) Comilla (S) - Surjamoninagar 132 kV Ckt-1 & 2 were shut down at 07:37 (30/11/19) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 780000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 94 | 2571000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 5955800 | ST under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 363 | 8603650 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 360 | 7656000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9820250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 34545 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 114876
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 1669000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 335376 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 55420 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 750072 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 296640 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1140000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 794800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 720500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 19200 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 71 | 408982 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 104916 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2066 | 41831027
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 100 | 2800000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 136080
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 14880 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 2215985 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4902307 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 144 | 2780816 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 688327
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 39120 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 50760 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 442512
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 820800
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 10 | 47040 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27960
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 741 | 14966587
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2066174 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 1021836 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4336000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7122500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 539424 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 598080
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1773090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 421608 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 2121250
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 35 | 136800 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 206244
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 79560
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 2138880
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 309300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 448830 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | On test
| Cumilla Area Total |  |  |  | 3005 | 1223 | 23319576
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 183 | 3794440 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 207360
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 61440 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12700
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 80 | 456000 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 301 | 4531940
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 61 | 1430000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 56 | 1367520
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3084864
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 168 | 4734000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 462600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 549504
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 98928
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1251648 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 787200
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 170000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 37 | 423460 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 193632
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7530750 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 364 | 8479000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 95580
| Sylhet Area Total |  |  |  | 1949 | 1468 | 30658686
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 433 | 4792000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 7554528 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 102720 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 18 | 43056 | Low demand
| Khulna Area Total |  |  |  | 2314 | 826 | 12492304
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 729600 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 434700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 170 | 3844570
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Line over load
| Barisal Area Total |  |  |  | 462 | 227 | 5008870
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 32 | 97100 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 207 | 4712809 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 213 | 4733582 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 428 | 8144091 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 193680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 137628
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228744
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 172800 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 962 | 18420434
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4850100
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 179520 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31140
| Rangpur Area Total |  |  |  | 605 | 235 | 5060760
| Total |  |  |  | 19132 | 8049 | 156290184
| Eastern Grid Total |  |  |  | 13568 | 5799 | 115307816
| Western Grid Total |  |  |  | 5564 | 2250 | 40982368
| National Grid Total |  |  |  | 19132 | 8049 | 156290184
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-29
(a) ENTIRE EASTERN GRID : |  | 5278 | MW | (b) ENTIRE WESTERN GRID : |  | 2362 | MW
i) Dhaka area |  | 2843 | MW | i) Khulna area |  | 907 | MW
ii) Chittagong area |  | 815 | MW | ii) Rajshahi area |  | 771 | MW
iii) Comilla area |  | 696 | MW | iii) Barisal area |  | 214 | MW
iv) Mymensingh area |  | 608 | MW | iv) Rangpur area |  | 470 | MW
v) Sylhet area |  | 316 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7640 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 90 | 0.041667 | Srimongal | 26 | 0.77083 | Bottail | 84 | 0.77083
Munsiganj | 86 | 0.8125 | Shahjibazar | 78 | 0.79167 | G.K Project | 23 | 0.77083
Sonargaon | 70 | 0.75 | Fenchuganj | 23 | 0.75 | Faridpur | 108 | 0.75
Shyampur | 166 | 0.041667 | Kulawara | 30 | 0.75 | Madaripur | 55 | 0.83333
Bhulta | 148 | 0.041667 | Sylhet | 86 | 0.83333 | Sariatpur | 38 | 0.875
Madanganj | 43 | 0.83333 | Chatak | 16 | 0.79167 | Gopalganj | 56 | 0.75
Shitalakhya | 84 | 0.041667 | Sunamganj | 28 | 0.79167 | Bagerhat | 59 | 0.79167
Rahim steel | 14 | 0.58333 | Biani Bazar | 31 | 0.79167 | Mongla | 32 | 0.083333
Matuail | 72 | 0.041667 | Comilla (S) | 114 | 0.83333 | Satkhira | 62 | 0.8125
Ghorasal | 56 | 0.8125 | Comilla(N) | 65 | 0.8125 | Gallamari | 35 | 0.54167
Narsingdi | 99 | 0.041667 | Chandpur | 66 | 0.83333 | Magura | 36 | 0.77083
Haripur (SBU) | 72 | 0.45833 | Feni | 93 | 0.75 | Norail | 20 | 0.75
Ullon | 56 | 0.75 | Chowmuhani | 110 | 0.8125 | Chuadanga | 56 | 0.75
Hasnabad | 122 | 0.75 | Ashuganj | 41 | 1904-01-02 | Barisal(N) | 27 | 0.8125
Magbazar | 76 | 0.75 | Daudkandi | 88 | 0.8125 | Barisal (S) | 62 | 0.75
Maniknagar | 74 | 0.77083 | B.Baria | 93 | 0.8125 | Patuakhali | 74 | 0.83333
Bangabhaban | 10 | 0.77083 | Ramganj | 52 | 0.75 | Bhandaria | 35 | 0.79167
Narinda | 66 | 0.75 | Madunaghat | 38 | 0.75 | Borhan Uddin | 22 | 0.8125
Dhanmondi | 97 | 0.75 | Hathazari | 67 | 0.75 | Ishurdi | 37 | 0.75
Lalbag | 46 | 0.041667 | Khulshi | 148 | 0.5 | Ruppur Paromanobik | 2 | 0.625
Madartek | 51 | 0.875 | Halishahar | 105 | 0.75 | Natore | 81 | 0.75
Mirpur | 73 | 0.75 | Baraulia | 122 | 0.041667 | Bogra | 129 | 0.79167
Kalyanpur | 78 | 0.77083 | Sikalbaha | 29 | 0.79167 | Noagaon | 73 | 0.77083
Gulshan | 94 | 0.75 | Dohazari | 64 | 0.75 | Rajshahi | 84 | 0.79167
Uttara | 43 | 0.79167 | Cox'sbazar | 80 | 0.16667 | Rajshahi New | 7 | 0.83333
Uttara New | 26 | 0.77083 | Chandraghona | 24 | 0.75 | C.Nawabganj | 49 | 0.83333
Kamrangirchar | 55 | 0.77083 | Kaptai | 4 | 0.75 | Amnura | 21 | 0.79167
Savar | 78 | 0.75 | A. Khaer Stl. | 0 | 0.041667 | Pabna | 65 | 0.75
Bhasantec | 118 | 0.75 | Bakulia | 68 | 0.75 | Shahjadpur | 68 | 0.79167
Agargaon | 41 | 0.75 | Julda | 19 | 0.041667 | Serajganj | 46 | 0.75
Satmosjid | 77 | 0.70833 | TK chemical | 8 | 0.041667 | Niyamatpur | 41 | 0.77083
Tongi | 96 | 0.79167 | Modern Steel | 12 | 0.083333 | Joypurhat | 44 | 0.75
Kabirpur | 95 | 0.5 | Shahmirpur | 21 | 0.083333 | Sherpur(Bogura) | 31 | 0.75
Basundhara | 75 | 0.75 | Khagrachhari | 16 | 0.75 | Mohastangor | 10 | 0.79167
Manikganj | 60 | 0.8125 | Matarbari | 21 | 0.77083 | Rangpur | 96 | 0.77083
Joydevpur | 133 | 0.83333 | Baroiar Hat | 16 | 0.75 | Lalmonirhat | 48 | 0.75
New Tongi | 58 | 0.5 | Rangamati | 10 | 0.75 | Saidpur | 69 | 0.75
Korda | 144 | 0.041667 | Abul Khair 230 | 69 | 0.375 | Purbasadipur | 56 | 0.8125
Dhamrai | 38 | 0.875 | BSRM | 101 | 0.83333 | Thakurgaon | 36 | 0.375
Valuka | 56 | 0.75 | GPH Ispat | 4 | 0.041667 | Palashbari | 78 | 0.75
Tangail | 132 | 0.79167 | Goalpara | 15 | 0.5 | Barapukuria | 36 | 0.75
Mymensing | 147 | 0.75 | Central s/s | 60 | 0.75 | Panchagar | 26 | 0.79167
Kishorganj | 74 | 0.8125 | Noapara | 37 | 0.83333 | Joldhaka | 18 | 0.79167
Netrokona | 72 | 0.75 | Jessore | 76 | 0.75 | Kurigram | 38 | 0.75
Jamalpur | 82 | 0.83333 | Benapol | 28 | 0.75
Sherpur | 62 | 0.75 | Jhenida | 72 | 0.75
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-29 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 387 | 0.16667 | 382 | 0.625 | Kaliakoir | 368 | 0.16667 | 361 | 0.5
Bheramara | 411 | 0.29167 | 390 | 0.5 | Bhulta | 371 | 0.083333 | 365 | 0.45833
Ashuganj(N) | 374 | 0.083333 | 368 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 226 | 0.33333 | 222 | 0.45833 | Hathazari | 221 | 0.70833 | 215 | 0.45833
Ishurdi | 241 | 0.20833 | 226 | 0.75 | Megnaghat | 222 | 0.41667 | 220 | 0.041667
Ashuganj | 232 | 0.29167 | 228 | 0.45833 | Fenchuganj | 234 | 0.91667 | 230 | 0.625
Serajganj | 234 | 0.16667 | 230 | 0.33333 | Siddhirganj | 221 | 0.16667 | 217 | 0.5
Baghabari | 240 | 0.25 | 232 | 0.77083 | Maniknagar | 219 | 0.16667 | 215 | 0.5
Barapukuria | 231 | 0.58333 | 225 | 0.75 | Old Airport | 219 | 0.25 | 214 | 0.5
Bogra | 233 | 0.20833 | 224 | 0.75 | Barisal | 233 | 0.29167 | 221 | 0.83333
Khulna South | 238 | 0.16667 | 216 | 0.8125 | AKSML | 217 | 0.66667 | 211 | 0.083333
Rampura | 220 | 0.041667 | 218 | 0.5 | BSRM | 218 | 0.66667 | 212 | 0.54167
Haripur | 220 | 24:00 | 216 | 0.625 | Bibiyana | 231 | 0.79167 | 227 | 0.29167
Hasnabad | 218 | 0.77083 | 215 | 0.5 | Bhulta | 222 | 0.29167 | 217 | 0.5
Aminbazar | 220 | 0.20833 | 216 | 0.41667 | Ashuganj (S) | 230 | 0.083333 | 226 | 0.5
Tongi | 215 | 0.29167 | 210 | 0.45833 | Kaliakoir | 222 | 0.29167 | 215 | 0.83333
Comilla (N) | 227 | 0.70833 | 224 | 0.54167 | GPH | 215 | 0.041667 | 210 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 0.25 | 131 | 0.041667 | Halishahar | 130 | 0.25 | 128 | 0.16667
Munsiganj | 132 | 0.70833 | 129 | 0.041667 | Baraulia | 130 | 0.70833 | 126 | 0.041667
Sonargaon | 130 | 0.041667 | 128 | 0.5 | Sikalbaha | 130 | 0.70833 | 127 | 0.041667
Shyampur | 134 | 0.125 | 130 | 0.5 | Dohazari | 130 | 0.33333 | 127 | 0.5
Bhulta | 129 | 0.375 | 126 | 0.041667 | Cox'sbazar | 125 | 0.375 | 120 | 0.54167
Madanganj | 135 | 0.79167 | 128 | 0.041667 | Chandraghona | 130 | 0.25 | 128 | 0.041667
Shitalakhya | 135 | 0.79167 | 130 | 0.45833 | Kaptai | 130 | 0.041667 | 128 | 0.29167
Rahim steal | 133 | 0.16667 | 132 | 0.041667 | A. Khaer Stl. | 130 | 0.20833 | 127 | 0.75
Matuail | 132 | 0.125 | 130 | 0.041667 | Bakulia | 127 | 0.041667 | 126 | 0.083333
Ghorasal | 136 | 0.29167 | 133 | 0.5 | Julda | 129 | 0.70833 | 126 | 0.5
Narsinghdi | 134 | 0.33333 | 131 | 0.5 | TK Chemical | 129 | 0.33333 | 127 | 0.125
Haripur (SBU) | 134 | 0.70833 | 130 | 0.041667 | Modern Steel | 130 | 0.70833 | 125 | 0.125
Ullon | 131 | 0.25 | 128 | 0.5 | Shahmirpur | 129 | 0.70833 | 126 | 0.041667
Hasnabad | 134 | 0.25 | 130 | 0.5 | Khagrachhari | 130 | 0.33333 | 127 | 0.54167
Magbazar | 132 | 0.25 | 128 | 0.5 | Matarbari | 127 | 0.375 | 122 | 0.83333
Maniknagar | 135 | 0.25 | 133 | 0.5 | Baroiar Hat | 129 | 0.70833 | 125 | 0.5
Bangabhaban | 135 | 0.25 | 133 | 0.5 | Rangamati | 130 | 0.70833 | 127 | 0.54167
Narinda | 135 | 0.25 | 133 | 0.5 | Goalpara | 139 | 0.29167 | 137 | 0.125
Dhanmondi | 131 | 0.25 | 128 | 0.5 | Central s/s | 138 | 0.25 | 126 | 0.83333
Lalbag | 135 | 0.25 | 130 | 0.5 | Noapara | 136 | 0.16667 | 124 | 0.83333
Madartek | 132 | 0.29167 | 128 | 0.5 | Jessore | 133 | 0.16667 | 121 | 0.75
Mirpur | 134 | 0.20833 | 130 | 0.5 | Benapol | 135 | 0.125 | 124 | 0.75
Kalyanpur | 136 | 0.25 | 127 | 0.54167 | Jhenida | 134 | 0.16667 | 120 | 0.75
Gulshan | 130 | 0.25 | 127 | 0.54167 | Bottail | 137 | 0.25 | 127 | 0.75
Uttara | 130 | 0.25 | 125 | 0.5 | G.K Project | 140 | 0.125 | 134 | 0.75
Uttara New | 134 | 0.25 | 129 | 0.5 | Faridpur | 135 | 0.16667 | 125 | 0.79167
Kamrangirchar | 134 | 0.25 | 128 | 0.5 | Madaripur | 135 | 0.33333 | 125 | 0.83333
Savar | 133 | 0.79167 | 129 | 0.5 | Sariatpur | 134 | 0.25 | 125 | 0.83333
Bhasantec | 132 | 0.25 | 128 | 0.5 | Gopalganj | 138 | 0.25 | 128 | 0.83333
Agargaon | 133 | 0.25 | 129 | 0.5 | Bagerhat | 136 | 0.20833 | 124 | 0.83333
Satmosjid | 132 | 0.25 | 129 | 0.5 | Mongla | 134 | 0.25 | 122 | 0.875
Tongi | 132 | 0.33333 | 128 | 0.45833 | Satkhira | 138 | 0.25 | 124 | 0.75
Kabirpur | 132 | 1904-01-02 | 128 | 0.54167 | Gallamari | 140 | 0.25 | 128 | 0.77083
Basundhara | 131 | 0.25 | 126 | 0.5 | Magura | 136 | 0.20833 | 121 | 0.79167
Manikganj | 134 | 0.33333 | 129 | 0.5 | Norail | 134 | 0.25 | 118 | 0.75
Joydevpur | 135 | 0.58333 | 131 | 0.041667 | Chuadanga | 133 | 0.20833 | 117 | 0.75
New Tongi | 131 | 0.20833 | 127 | 0.625 | Barisal(N) | 139 | 0.41667 | 131 | 0.79167
Kodda | 133 | 1904-01-02 | 126 | 0.041667 | Barisal (S) | 138 | 0.29167 | 130 | 0.79167
Dhamrai | 130 | 0.083333 | 126 | 0.54167 | Patuakhali | 137 | 0.58333 | 125 | 0.83333
Valuka | 130 | 0.083333 | 124 | 0.625 | Bhandaria | 137 | 0.25 | 125 | 0.83333
Tangail | 132 | 1904-01-02 | 127 | 0.54167 | Ishurdi | 138 | 0.20833 | 130 | 0.83333
Mymensing | 130 | 0.16667 | 124 | 0.54167 | Ruppur Paromanobik | 137 | 0.25 | 130 | 0.83333
Kishorganj | 132 | 1904-01-02 | 128 | 0.54167 | Natore | 136 | 0.25 | 127 | 0.75
Netrokona | 129 | 0.041667 | 124 | 0.54167 | Bogra | 137 | 0.58333 | 130 | 0.75
Jamalpur | 133 | 0.77083 | 122 | 0.54167 | Noagaon | 135 | 0.25 | 126 | 0.75
Sherpur | 133 | 0.79167 | 122 | 0.5 | Rajshahi | 133 | 0.25 | 125 | 0.75
Srimongal | 137 | 0.95833 | 133 | 0.45833 | Rajshahi New | 133 | 0.25 | 123 | 0.83333
Shahjibazar | 136 | 0.95833 | 132 | 0.5 | C.Nawabganj | 131 | 0.58333 | 123 | 0.75
Fenchuganj | 136 | 0.041667 | 131 | 0.58333 | Amnura | 130 | 0.25 | 123 | 0.83333
Khulawara | 135 | 0.041667 | 131 | 0.66667 | Pabna | 138 | 0.25 | 131 | 0.75
Sylhet | 134 | 0.041667 | 129 | 0.5 | Shahjadpur | 142 | 0.25 | 137 | 0.79167
Chatak | 134 | 1904-01-02 | 129 | 0.45833 | Serajganj | 138 | 0.25 | 130 | 0.75
Sunamganj | 134 | 0.041667 | 128 | 0.45833 | Niyamatpur | 134 | 0.58333 | 123 | 0.75
Biani Bazar | 135 | 0.083333 | 129 | 0.5 | Joypurhat | 137 | 0.20833 | 125 | 0.77083
Comilla(s) | 128 | 0.29167 | 125 | 0.54167 | Sherpur(Bogura) | 138 | 0.16667 | 130 | 0.75
Comilla(n) | 135 | 0.79167 | 132 | 0.5 | Mohastangor | 135 | 0.25 | 129 | 0.75
Chandpur | 132 | 0.375 | 130 | 0.58333 | Rangpur | 130 | 0.58333 | 122 | 0.75
Feni | 128 | 0.70833 | 123 | 0.54167 | Lalmonirhat | 126 | 0.70833 | 117 | 0.75
Chowmuhani | 127 | 0.29167 | 123 | 0.5 | Saidpur | 129 | 0.58333 | 123 | 0.75
Ashuganj | 135 | 0.041667 | 133 | 0.54167 | Purbasadipur | 124 | 0.58333 | 118 | 0.75
Daudkandi | 132 | 0.29167 | 129 | 0.5 | Thakurgaon | 123 | 0.58333 | 116 | 0.75
B.Baria | 134 | 0.375 | 132 | 0.75 | Palashbari | 134 | 0.25 | 125 | 0.75
Ramganj | 123 | 0.29167 | 120 | 0.66667 | Barapukuria | 131 | 0.70833 | 125 | 0.75
Madanhat | 131 | 0.70833 | 128 | 0.125 | Panchagar | 122 | 0.58333 | 110 | 0.75
Hathazari | 131 | 0.70833 | 129 | 0.041667 | Joldhaka | 128 | 0.25 | 120 | 0.75
Khulshi | 127 | 0.29167 | 124 | 0.5 | Kurigram | 130 | 0.70833 | 122 | 0.77083
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 200 | 4919 | 1642 | 6561 |  |  |  | QF-LDC-12
0:30 | 255 | 5016 | 1562 | 6578 | Date: | 2019-11-29
1:00 | 310 | 5113 | 1482 | 6595
1:30 | 312.5 | 5019 | 1442.5 | 6461.5
2:00 | 315 | 4925 | 1403 | 6328
2:30 | 266 | 4778.5 | 1403.5 | 6182 | [5 empty] | Gen. at Eve. Peak | 8049 | 8049 MW (19:00 )
3:00 | 217 | 4632 | 1404 | 6036 | [6 empty] | 19:00
3:30 | 181 | 4568 | 1411 | 5979 | [5 empty] | Gen. at Day Peak | 6103.212 | 6103.212 MW (12:00 )
4:00 | 145 | 4504 | 1418 | 5922 | [6 empty] | 12:00
4:30 | 141 | 4439.5 | 1418 | 5857.5 | [5 empty] | Highest Generation | 8049
5:00 | 137 | 4375 | 1418 | 5793 | [6 empty] | 19:00
5:30 | 140 | 4365 | 1433.5 | 5798.5
6:00 | 143 | 4355 | 1449 | 5804
6:30 | 137 | 4314.715 | 1448.1 | 5762.815
7:00 | 131 | 4274.43 | 1447.2 | 5721.63
7:30 | 198 | 4291.5765 | 1482.3 | 5773.8765
8:00 | 265 | 4308.723 | 1517.4 | 5826.123
8:30 | 148.5 | 4201.3615 | 1510.2 | 5711.5615
9:00 | 32 | 4094 | 1503 | 5597
9:30 | 26.5 | 4108.292 | 1482.55 | 5590.842
10:00 | 21 | 4122.584 | 1462.1 | 5584.684
10:30 | 22 | 4195.561 | 1457.5 | 5653.061
11:00 | 23 | 4268.538 | 1452.9 | 5721.438
11:30 | 15 | 4382.875 | 1529.45 | 5912.325
12:00 | 7 | 4497.212 | 1606 | 6103.212
12:30 | 18 | 4531.163 | 1648.9 | 6180.063
13:00 | 29 | 4565.114 | 1691.8 | 6256.914
13:30 | 88.5 | 4384.847 | 1645.45 | 6030.297
14:00 | 148 | 4204.58 | 1599.1 | 5803.68
14:30 | 151.5 | 4197.34 | 1576.05 | 5773.39
15:00 | 155 | 4190.1 | 1553 | 5743.1
15:30 | 154 | 4152 | 1558.55 | 5710.55
16:00 | 153 | 4113.9 | 1564.1 | 5678
16:30 | 116.5 | 4198.55 | 1594.6 | 5793.15
17:00 | 80 | 4283.2 | 1625.1 | 5908.3
17:30 | 165 | 4935.6 | 1925.55 | 6861.15
18:00 | 250 | 5588 | 2226 | 7814
18:30 | 241.5 | 5693.5 | 2238 | 7931.5
19:00 | 233 | 5799 | 2250 | 8049
19:30 | 243 | 5816 | 2219 | 8035
20:00 | 233 | 5775 | 2218 | 7993 |  |  |  | Executive Engineer
20:30 | 232.5 | 5744 | 2173 | 7917 |  |  |  | Network Operation Division
21:00 | 232 | 5713 | 2128 | 7841
21:30 | 196 | 5544 | 2073 | 7617
22:00 | 160 | 5375 | 2018 | 7393 |  |  |  |  | Page 6 of 7
22:30 | 189 | 5275 | 1873.5 | 7148.5
23:00 | 218 | 5175 | 1729 | 6904
23:30 | 209 | 5047 | 1685.5 | 6732.5
24:00 | 200 | 4919 | 1642 | 6561
8049 MW (19:00 )
6103.212 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-29 |  | Energy | 156290184
[10 empty] | 2019-11-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3974 | 189 | 1996 | 65 | 200 | 94 | 0 | 0 | 90
0:30 | 3994 | 147 | 2022 | 55.5 | 200 | 93 | 0 | 0 | 90 | Date: | 2019-11-29
1:00 | 4014 | 105 | 2048 | 46 | 200 | 92 | 0 | 0 | 90
1:30 | 3947 | 105 | 1995 | 34.5 | 200.5 | 91.5 | 0 | 0 | 88 | [7 empty] | Total Energy | 156.2902 | Total Energy Gen 156.290 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 156.290 MKWHr
2:00 | 3880 | 105 | 1942 | 23 | 201 | 91 | 0 | 0 | 86 | [7 empty] | Energy not Served | 0
2:30 | 3850 | 104.5 | 1828.5 | 23 | 200.5 | 90.5 | 0 | 0 | 85 | [7 empty] | Energy Requirement | 156.2902
3:00 | 3820 | 104 | 1715 | 23 | 200 | 90 | 0 | 0 | 84
3:30 | 3811.5 | 103.5 | 1679 | 11.5 | 200 | 89.5 | 0 | 0 | 84 | [6 empty] | Shortage
4:00 | 3803 | 103 | 1643 | 0 | 200 | 89 | 0 | 0 | 84
4:30 | 3766 | 104 | 1615.5 | 0 | 200 | 89 | 0 | 0 | 83
5:00 | 3729 | 105 | 1588 | 0 | 200 | 89 | 0 | 0 | 82
5:30 | 3731 | 104.5 | 1593 | 0 | 200 | 89 | 0 | 0 | 81
6:00 | 3733 | 104 | 1598 | 0 | 200 | 89 | 0 | 0 | 80
6:30 | 3703 | 104 | 1585 | 0 | 200 | 92 | 0 | 0 | 77 |  |  |  |  | Coal
7:00 | 3673 | 104 | 1572 | 0 | 200 | 95 | 0 | 0 | 74
7:30 | 3703 | 103 | 1571 | 24 | 200 | 94.5 | 0 | 0 | 70 |  |  |  | Oil |  |  |  | ,
8:00 | 3733 | 102 | 1570 | 48 | 200 | 94 | 0 | 0 | 66
8:30 | 3671.5 | 102 | 1510.5 | 48 | 199.5 | 94.5 | 0 | 0 | 68
9:00 | 3610 | 102 | 1451 | 48 | 199 | 95 | 0 | 0 | 70
9:30 | 3592 | 102 | 1456.5 | 48 | 199.5 | 95 | 0 | 0 | 73
10:00 | 3574 | 102 | 1462 | 48 | 200 | 95 | 0 | 0 | 76
10:30 | 3635.5 | 102 | 1463.5 | 48 | 200 | 95 | 0 | 0 | 80
11:00 | 3697 | 102 | 1465 | 48 | 200 | 95 | 0 | 0 | 84
11:30 | 3775.5 | 137 | 1533.5 | 56 | 200 | 95.5 | 0 | 0 | 84
12:00 | 3854 | 172 | 1602 | 64 | 200 | 96 | 0 | 0 | 84
12:30 | 3878.5 | 172 | 1652.5 | 64.5 | 200 | 94.5 | 0 | 0 | 88
13:00 | 3903 | 172 | 1703 | 65 | 200 | 93 | 0 | 0 | 92
13:30 | 3903 | 172 | 1703 | 65 | 200 | 93 | 0 | 0 | 92
14:00 | 3903 | 172 | 1703 | 65 | 200 | 93 | 0 | 0 | 92
14:30 | 3785.5 | 172 | 1575.5 | 59.5 | 200 | 94 | 0 | 0 | 90
15:00 | 3668 | 172 | 1448 | 54 | 200 | 95 | 0 | 0 | 88
15:30 | 3652 | 170 | 1441.5 | 54 | 200 | 95 | 0 | 0 | 85
16:00 | 3636 | 168 | 1435 | 54 | 200 | 95 | 0 | 0 | 82
16:30 | 3663.5 | 168 | 1448 | 128 | 200 | 93.5 | 6 | 0 | 82
17:00 | 3691 | 168 | 1461 | 202 | 200 | 92 | 12 | 0 | 82
17:30 | 3979.5 | 300.5 | 1744.5 | 433 | 200 | 92 | 14.5 | 0 | 97
18:00 | 4268 | 433 | 2028 | 664 | 200 | 92 | 17 | 0 | 112
18:30 | 4268 | 433 | 2112.5 | 697 | 200 | 92 | 17 | 0 | 112
19:00 | 4268 | 433 | 2197 | 730 | 200 | 92 | 17 | 0 | 112
19:30 | 4297 | 433 | 2182 | 719 | 200 | 92 | 0 | 0 | 112
20:00 | 4308 | 433 | 2209 | 635 | 200 | 94 | 0 | 0 | 114
20:30 | 4277.5 | 433 | 2204.5 | 597.5 | 200 | 93.5 | 0 | 0 | 111
21:00 | 4247 | 433 | 2200 | 560 | 200 | 93 | 0 | 0 | 108
21:30 | 4215.5 | 433 | 2181 | 386.5 | 200 | 93 | 0 | 0 | 108
22:00 | 4184 | 433 | 2162 | 213 | 200 | 93 | 0 | 0 | 108
22:30 | 4183 | 311.5 | 2118.5 | 139 | 200 | 93.5 | 0 | 0 | 103
23:00 | 4182 | 190 | 2075 | 65 | 200 | 94 | 0 | 0 | 98
23:30 | 4078 | 189.5 | 2035.5 | 65 | 200 | 94 | 0 | 0 | 94 | Max Temp. in Dhaka |  | 31.3° C
24:00 | 3974 | 189 | 1996 | 65 | 200 | 94 | 0 | 0 | 90
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 156.290 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 156.290 MKWHr
Note on W13: Author:

## Generation
2019-11-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 41 | 40 | 39 | 39 | 39 | 45 | 44 | 45 | 45 | 45 | 46 | 43 | 43 | 45 | 45 | 42 | 42 |  | 42 | 42 | 44 | 43 | 43 | 44 | 44 | 1027985
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1188000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 2800000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9.75 | 14.58 | 17.85 | 19.24 | 19.68 | 18.03 | 15.88 | 11.8 | 5.6 | 0.2 | [9 empty] | 136080
6 | Sikalbaha 225MW CCPP (Gas) | 207 | 203 | 203 | 204 | 203 | 203 | 202 | 205 | 203 | 216 | 230 | 215 | 214 | 204 | 205 | 204 | 205 | 208 |  | 203 | 203 | 209 | 203 | 203 | 211 | 204 | 4902307
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 148 | 93 | 95 | 96 | 100 | 94 | 94 | 94 | 94 | 94 | 94 | 139 | 139 | 139 | 105 | 104 | 104 | 144 |  | 144 | 145 | 145 | 145 | 144 | 105 | 105 | 2780816
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 12 | 17 |  | 17 | 0 | 0 |  |  |  |  | 39120
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | 17 | 0 | [12 empty] | 16 | 105 |  | 105 | 105 | 105 | 105 | 85 | 17 | 0 | 688327
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 84 | 83 | 83 | 86 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 85 | 85 | 53 | 57 | 57 | 52 | 97 |  | 97 | 97 | 97 | 97 | 97 | 60 | 60 | 1669000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 16 | 56 |  | 71 | 95 | 95 | 95 | 45 | 0 | 0 | 408982
19 | Ashuganj 195MW PP (APSCL-United) | 98 | 98 | 98 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1773090
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 780000
21 | Ghorasal Repowered CCPP Unit-3 | 130 | 130 | 130 | 130 | 95 | 94 | 95 | 94 | 94 | 94 | 95 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2571000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 265 | 268 | 268 | 268 | 265 | 265 | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 220 | 220 | 220 | 220 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5955800
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2066174
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | [9 empty] | 16 | 30 | 55 | 55 | 55 | 55 | 55 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1021836
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 36 |  | 37 | 37 | 37 | 37 | 37 | 30 | 33 | 539424
33 | Ashuganj 225 MW CCPP | 162 | 161 | 168 | 161 | 180 | 171 | 164 | 175 | 165 | 161 | 182 | 181 | 182 | 162 | 183 | 182 | 182 | 199 |  | 198 | 199 | 199 | 200 | 200 | 200 | 200 | 4336000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 285 | 280 | 280 | 275 | 265 | 275 | 270 | 265 | 305 | 300 | 290 | 270 | 285 | 270 | 270 | 330 |  | 310 | 310 | 320 | 310 | 310 | 345 | 280 | 7122500
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 50 | 49 | 48 | 31 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 |  | 52 | 52 | 52 | 51 | 51 | 52 | 52 | 598080
36 | Chandpur 150 MW CCPP | 95 | 95 | 95 | 95 | 95 | 95 | 94 | 96 | 94 | 88 | 95 | 96 | 93 | 85 | 95 | 93 | 90 | 90 |  | 81 | 90 | 90 | 88 | 80 | 91 | 89 | 2121250
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 346 | 342 | 343 | 353 | 360 | 344 | 350 | 344 | 344 | 350 | 372 | 381 | 347 | 348 | 353 | 357 | 358 |  | 363 | 345 | 346 | 353 | 343 | 357 | 354 | 8603650
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 370 | 340 | 340 | 370 | 400 | 330 | 330 | 330 | 330 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9820250
41 | Haripur 360MW CCPP(HPL) | 330 | 330 | 329 | 329 | 288 | 289 | 289 | 290 | 290 | 290 | 290 | 330 | 330 | 300 | 300 | 300 | 300 | 340 |  | 360 | 360 | 363 | 363 | 364 | 364 | 367 | 7656000
42 | RPCL 210MW CCPP | 157 | 159 | 159 | 158 | 159 | 160 | 160 | 158 | 157 | 155 | 153 | 151 | 150 | 150 | 149 | 149 | 152 | 153 |  | 183 | 208 | 193 | 183 | 182 | 182 | 183 | 3794440
43
44 | Fenchugonj CCPP Phase-1 | 60 | 59 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 61 | 61 | 59 |  | 61 | 60 | 60 | 59 | 61 | 60 | 60 | 1430000
45 | Fenchugonj CCPP Phase-2 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 60 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1367520
46 | Shajibazar 330 MW CCPP | 240 | 235 | 243 | 242 | 244 | 235 | 245 | 244 | 216 | 214 | 222 | 212 | 219 | 212 | 210 | 177 | 165 | 175 |  | 168 | 172 | 172 | 169 | 169 | 172 | 173 | 4734000
47 | Shahjibazar GTPP Unit- 8 & 9 | 68 | 68 | 67 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 66 |  | 67 | 67 | 67 | 67 | 67 | 67 | 69 | 1251648
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 76 |  | 76 | 76 | 76 | 76 | 76 | 73 | 73 | 787200
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 17 | 17 | 0 | [14 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 170000
52 | Sylhet 50MW PP (EPL) | 40 | 39 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 38 |  | 37 | 37 | 40 | 40 | 40 | 39 | 39 | 423460
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 0 | [14 empty] | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 95580
54 | Hobiganj 11MW PP Cofidence-E | 11 | 0 | [15 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 98928
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 0 | [6 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 49 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 462600
56 | Shahjahanulla 25 MW PP | 23 | 5 | 0 | [14 empty] | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 193632
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 290 | 300 | 310 | 320 | 300 | 305 | 270 | 280 | 305 | 320 | 325 | 290 | 285 | 300 | 310 | 270 |  | 315 | 315 | 310 | 310 | 300 | 290 | 290 | 7530750
58 | Nababganj 55 MW PP (Southern power ) | 0 | [16 empty] | 17 |  | 17 | 17 | 17 | 14 |  |  | 0 | 750072
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442512
61 | Narshingdi 22 MW PP (Doreen) | 19 | 0 | [15 empty] | 19 |  | 19 | 19 | 19 | 19 |  |  | 0 | 114876
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 0 | [14 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 207360
63 | Impoprt (Tripura) | 90 | 86 | 84 | 84 | 82 | 80 | 74 | 66 | 70 | 76 | 84 | 84 | 92 | 88 | 88 | 82 | 82 | 112 |  | 112 | 112 | 114 | 108 | 108 | 98 | 90 | 2138880
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 36 | 36 | 38 | 38 | 35 | 26 | 24 | 24 | 22 | 21 | 37 | 26 | 23 | 25 | 26 | 39 |  | 35 | 35 | 37 | 38 | 38 | 40 | 40 | 820800
65 | Feni 22MW PP (Doreen) | 22 | 22 | 0 | [14 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 206244
66 | Feni 11 MW PP (Doreen) | 0 | [16 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 79560
67 | Jangalia 33MW PP (Summit) | 33 | 20 | 0 | [10 empty] | 0 |  |  |  | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 309300
68 | Cumilla 25 MW PP (Summit) | 21 | 19 | 21 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 10 | 10 | 10 | 15 | 15 | 15 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 448830
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 23 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 24 | 31 | 31 | 31 | 31 | 31 | 31 | 540000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 33 | 33 | 33 | 17 | 17 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 22 | 794800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 28 | 28 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 31 | 31 | 31 | 31 | 17 | 720500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [17 empty] | 8 |  | 8 | [5 empty] | 0 | 19200
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 8 |  | 16 | 16 | 16 | 0 | 0 |  |  | 61440
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 34 |  | 34 | 34 | 17 | 17 |  |  |  | 104916
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.33 | 1.573 | 3.02 | 3.934 | 4.398 | 4.432 | 4.084 | 3.3 | 2.2 | 0.9 | 0 | [9 empty] | 27960
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 8 | 10 |  | 10 | 10 | 10 | 10 | 0 | 0 |  | 50760
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 20 | 0 | [9 empty] | 0 | 0 | 0 |  | 34 |  | 46 | 50 | 50 | 50 | 50 | 50 | 50 | 549504
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 0 | [14 empty] | 18 |  | 43 | 43 | 43 | 43 | 43 | 43 | 5 | 421608
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [17 empty] | 4 |  | 6 | 6 |  |  |  |  | 0 | 14880
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 0 | 10 |  | 10 | 10 | 10 | 10 |  |  | 0 | 47040
97 | Katpotti 52 MW PP (Sinha) | 12 | 6 | 6 | 0 | [8 empty] | 1 | 6 | 6 | 6 | 6 | 38 |  | 47 | 47 | 47 | 38 | 32 | 32 | 18 | 335376
98 | Bosila 108MW PP(CLC) | [16 empty] | 20 | 72 |  | 72 | 72 | 72 | 72 |  |  | 0 | 296640
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 0 | 8 |  | 15 | 0 | 0 |  |  |  |  | 34545
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 55420
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 130 | 130 | 100 | 100 | 130 |  | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 3084864
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.4 | 1.4 | 1.8 | 1.9 | 2.1 | 2 | 1.4 | 1.1 | 0.4 | 0 | [9 empty] | 12700
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 26 | 58 |  | 80 | 80 | 80 | 80 | 35 | 16 | 0 | 456000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn)
116 | Chandpur 200MW (Desh energy) | [16 empty] | 4 | 34 |  | 35 | 34 | 17 | 17 | 0 | 0 |  | 136800
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 364 | 366 | 369 | 365 | 372 | 365 | 363 | 370 | 321 | 319 | 344 | 343 | 338 | 319 | 317 | 315 | 316 | 385 |  | 364 | 366 | 367 | 364 | 366 | 379 | 300 | 8479000
| Jamalpur 115 MW PP (United) | [25 empty] | 0 | 0
| Anwara 300 MW PP (United) | [20 empty] | 0 |  |  |  |  | 0 | 0
120 | Eastern Zone Total | 5113 | 4925 | 4632 | 4504 | 4375 | 4355 | 4274.43 | 4308.723 | 4094 | 4122.584 | 4268.538 | 4497.212 | 4565.114 | 4204.58 | 4190.1 | 4113.9 | 4283.2 | 5588 |  | 5799 | 5816 | 5775 | 5713 | 5375 | 5175 | 4919 | 115307816
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [13 empty] | 17 | 0 |  |  | 17 |  | 35 | 24 | 17 | 0 |  |  |  | 102720
130
131
132
133
| Barisal 110 MW PP (Summit ) | [6 empty] | 0 | 48 | 48 | 48 | 48 | 64 | 64 | 48 | 48 | 48 | 48 | 48 |  | 32 | 32 | 32 | 32 | 16 | 0 |  | 729600
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 153 | 152 | 152 | 152 | 152 | 152 | 153 | 153 | 153 | 183 |  | 170 | 165 | 178 | 172 | 150 | 153 | 153 | 3844570
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 18 | 18 | 16 | 17 | 14 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 10 | 25 |  | 25 | 25 | 25 | 26 | 25 | 24 | 22 | 434700
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 18 |  | 18 | 18 | 18 | 0 |  |  |  | 43056
146 | Bheramara HVDC | 105 | 105 | 104 | 103 | 105 | 104 | 104 | 102 | 102 | 102 | 102 | 172 | 172 | 172 | 172 | 168 | 168 | 433 |  | 433 | 433 | 433 | 433 | 433 | 190 | 189 | 4792000
147 | Bheramara 360 MW CCPP | 255 | 255 | 270 | 290 | 290 | 310 | 320 | 340 | 340 | 300 | 280 | 300 | 340 | 300 | 300 | 300 | 300 | 340 |  | 340 | 340 | 340 | 310 | 310 | 340 | 310 | 7554528
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 201 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4850100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 181 | 171 | 161 | 163 | 167 | 173 | 165 | 170 | 163 | 162 | 171 | 195 | 196 | 188 | 189 | 200 | 205 | 204 |  | 207 | 214 | 203 | 205 | 203 | 192 | 184 | 4712809
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 176 | 174 | 173 | 181 | 175 | 182 | 181 | 178 | 170 | 168 | 189 | 192 | 187 | 174 | 181 | 187 | 188 | 194 |  | 213 | 210 | 210 | 210 | 206 | 200 | 196 | 4733582
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 349 | 304 | 304 | 303 | 305 | 303 | 303 | 303 | 300 | 300 | 280 | 300 | 350 | 320 | 283 | 284 | 282 | 415 |  | 428 | 409 | 433 | 423 | 428 | 383 | 341 | 8144091
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 0 | [14 empty] | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 193680
163 | Bogura 20 MW PP (Energyprima) | 14 | 14 | 14 | 0 | [13 empty] | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 137628
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228744
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 32 |  | 32 | 32 | 12 | 0 |  |  |  | 97100
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 6 | 35 |  | 35 | 35 | 35 | 35 | 0 |  | 0 | 172800
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 35 |  | 35 | 35 | 35 | 35 | 0 |  |  | 179520
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.2 | 1.4 | 3 | 4.1 | 4.9 | 5 | 4.8 | 4.1 | 3 | 1.1 | 0.1 | [9 empty] | 31140
178
178