## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-01 | Sunday
|  | Date (day): | 2019-12-01 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11301.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13747 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-11-30 | 2019-12-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 154 | 188 | 150 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under S/D
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 260 | 0 | 0 |  |  | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas Shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Gas Shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 379 | 347 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 362 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 120 | 120 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 39 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 60 | 85 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 40 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 56 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 8 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 111 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 34 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1743 | 2392 | 3547 | 3989 | 478 | 796
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.54 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 95 | 92 | 92 | 92 | 138 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 220 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 145 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 13 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 8 | 5 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 60 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.45 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 53 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 608.99 | 1075 | 1490 | 1650 | 378 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 120 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 80 | 80 | 80 | 54 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 196 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under S/D
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 52 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 63 | 68 | 68 | 132 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 100 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract Expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 80 | 95 | 95
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 150 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 0 | 110 | 105 | 134
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1090 | 1488 | 1500 | 1929 | 330 | 376
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 147 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 100 | 72 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.8 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 268.8 | 341 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 58 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 62 | 58 | 58
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 169 | 156 | 0 | 0 |  |  | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 0 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 79 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 38 | 37 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 285 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 397 | 367 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1324 | 1433 | 1353 | 1364 | 0 | 162
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 188 | 438 | 294 | 443
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 305 | 375 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 0 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 17 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 560 | 835 | 789 | 1663 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 25 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 153 | 153 | 153 | 153
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 11 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 234 | 221 | 344 | 414 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 71
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 200 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 182 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 365 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 110 | 0 | 113
| Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 0 | 0 | 0 | 0 | 113 | 113 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 838 | 954 | 1454 | 1789 | 320 | 8
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 210 | 210
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 50 | 113 | 113
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.1 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 204.1 | 250 | 331 | 357 | 0 | 170
| Total |  |  |  |  | 19428 | 18905 | 6870.89 | 8989 | 11301.6 | 13747 | 1548 | 1617
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6453.5459 | 8443 | 10615.1306 | 12911.9948
A. |  | 2019-11-30 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8989 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5433 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8989 | MW
3 | Day peak Generation : |  |  | 6870.89 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8443 | MW
4 | Evening peak Generation : |  |  | 8989 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 166.4475 | MKWHr | By Solar | 0.1967 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 141.0706 | MKWHr |  | By Oil: | 11.8444 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.8889 | MKWHr |  | By Hydro: | 2.1525 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1548 | MW | Dhaka | 3318 | 3318 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1617 | MW | Chittagong | 941 | 941 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3165 | MW | Khulna | 978 | 978 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1162.58 | MMCFD |  |  | Rajshahi | 812 | 812 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 128664273.456 | ii) Oil : | Taka | 113529907.67 | Comilla | 690 | 690 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19995601 | Total | Taka | 262189782.126 | Mymensingh | 637 | 637 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.6605 | MKWHr. | Sylhet | 342 | 342 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -410 | MW (E to W) at | 19:00 | hrs | Barisal | 228 | 228 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -416 | MW at | 18:30 | hrs | Rangpur | 497 | 497 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.9° C |  |  | Total | 8443 | 8443 |  | 0
B. |  | 2019-12-01 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 28.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13747 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
4 | Reserve(Generation end) |  |  |  | 4647 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 168.5029 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5630 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 5.0887 | MKWHr. | ii) HVDC Flow at Peak Time |  | 438 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.2058 | MKWHr. | iii) Maximum HVDC Flow : |  | 438 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | 99.83 | 99.92 |  | (b) Today: | 99.83 |  | (c) Rule Curve: |  | 106
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-11-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 300 | 367 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 28 | 22 | 8 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 214 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 100 | 0 | 100 | 0 | 300 | 199 | 68 | 89 | 30 | 43 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 86 | 197 | 0 | 0 | 0 | 60 | 56 | 5 | 5 | 100 | 172 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 114 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 8 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4444 | 1615 | 6059 | 3821 | 114 | 1732 | 12 | 200 | 94 | 0 | 86 | 0 | 0 | 99.97
2:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 300 | 366 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 90 | 0 | 90 | 0 | 260 | 164 | 8 | 89 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 82 | 199 | 0 | 0 | 0 | 60 | 56 | 5 | 5 | 100 | 167 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 91 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4193 | 1550 | 5743 | 3629 | 91 | 1645 | 6 | 200 | 90 | 0 | 82 | 0 | 0 | 99.96
3:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 300 | 365 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 80 | 0 | 80 | 0 | 265 | 158 | 8 | 89 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 78 | 199 | 0 | 0 | 0 | 27 | 56 | 5 | 5 | 100 | 170 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 91 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 201 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4116 | 1536 | 5652 | 3555 | 91 | 1637 | 0 | 201 | 90 | 0 | 78 | 0 | 0 | 99.95
4:00 | 35 | 94 | 0 | 0 | 200 | 0 | 0 | 300 | 288 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 202 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 80 | 0 | 80 | 0 | 280 | 174 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 76 | 200 | 0 | 0 | 0 | 30 | 56 | 5 | 5 | 100 | 167 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 91 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3897 | 1557 | 5454 | 3517 | 91 | 1480 | 0 | 200 | 90 | 0 | 76 | 0 | 0 | 99.94
5:00 | 35 | 94 | 0 | 0 | 200 | 0 | 0 | 282 | 289 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 186 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 80 | 0 | 80 | 0 | 285 | 177 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 76 | 212 | 0 | 0 | 0 | 30 | 56 | 5 | 5 | 100 | 171 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 90 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3908 | 1525 | 5433 | 3488 | 90 | 1489 | 0 | 200 | 90 | 0 | 76 | 0 | 0 | 99.93
6:00 | 35 | 94 | 0 | 0 | 200 | 0 | 0 | 286 | 290 |  | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 188 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 80 | 0 | 80 | 0 | 265 | 169 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 76 | 212 | 0 | 0 | 0 | 30 | 56 | 5 | 5 | 100 | 172 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 91 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3962 | 1619 | 5581 | 3564 | 91 | 1560 | 0 | 200 | 90 | 0 | 76 | 0 | 0 | 99.92
7:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 365 | 335 |  | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 24 | 17 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 190 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 20 | 80 | 0 | 80 | 0 | 305 | 182 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 76 | 213 | 0 | 0 | 0.1 | 30 | 60 | 5 | 5 | 100 | 180 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 20 | 0 | 396 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  | 89 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 8 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 4293.9 | 1646.2 | 5940.1 | 3840 | 89 | 1662 | 20 | 200 | 50 | 0 | 76 | 3.1 | 0 | 99.91
8:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 365 | 366 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 24 | 17 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 80 | 0 | 80 | 0 | 305 | 168 | 8 | 50 | 26 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 185 | 0 | 0 | 0.6 | 30 | 60 | 5 | 10 | 163 | 168 | 68 | 5 | 0 | 0 | 0 | 32 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.57 | 0 | 168 | 0 | 366 | 0 | 0 | 0 | 0.94 | 0 | 0 | 0 | 0 |  | 90 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 8 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4597.11 | 1668.1 | 6265.21 | 3831 | 90 | 1823 | 216 | 200 | 93 | 0 | 0 | 12.21 | 0 | 99.91
9:00 | 35 | 94 | 0 | 0 | 260 | 0 | 0 | 347 | 368 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 24 | 8 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 203 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 80 | 0 | 295 | 160 | 45 | 50 | 23 | 52 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 166 | 16 | 22 | 1.3 | 30 | 60 | 5 | 47 | 130 | 168 | 67 | 5 | 0 | 0 | 17 | 39 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.37 | 0 | 200 | 0 | 366 | 0 | 0 | 0 | 1.81 | 0 | 0 | 0 | 0 |  | 188 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 |  | 4632.48 | 1737.4 | 6369.88 | 3819 | 188 | 1770 | 280 | 200 | 93 | 0 | 0 | 19.88 | 0 | 99.9
10:00 | 35 | 94 | 0 | 0 | 220 | 0 | 0 | 344 | 305 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 25 | 8 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 215 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 80 | 0 | 80 | 0 | 305 | 171 | 45 | 50 | 27 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 164 | 16 | 22 | 1.7 | 29 | 60 | 5 | 47 | 130 | 172 | 65 | 5 | 0 | 0 | 17 | 21 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9 | 0 | 200 | 0 | 369 | 0 | 0 | 0 | 3.652 | 0 | 0 | 0 | 0 |  | 188 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 |  | 4553.252 | 1776.9 | 6330.152 | 3763 | 188 | 1767 | 292 | 200 | 93 | 0 | 0 | 27.152 | 0 | 99.9
11:00 | 35 | 94 | 0 | 0 | 220 | 0 | 0 | 366 | 305 |  | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 21 | 25 | 0 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 216 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 90 | 0 | 0 | 0 | 335 | 180 | 45 | 50 | 30 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 162 | 53 | 22 | 1.8 | 29 | 60 | 5 | 47 | 130 | 170 | 64 | 5 | 0 | 0 | 17 | 21 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.51 | 0 | 200 | 0 | 401 | 0 | 0 | 0 | 4.42 | 0 | 0 | 0 | 0 |  | 188 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 |  | 4662.73 | 1789.4 | 6452.13 | 3824 | 188 | 1798 | 319 | 200 | 94 | 0 | 0 | 29.13 | 0 | 99.89
12:00 | 35 | 154 | 0 | 0 | 260 | 0 | 0 | 379 | 335 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 0 | 25 | 30 | 25 | 17 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 220 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 100 | 0 | 0 | 0 | 330 | 199 | 63 | 50 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 145 | 100 | 22 | 1.8 | 30 | 60 | 5 | 47 | 163 | 169 | 63 | 5 | 0 | 0 | 17 | 38 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.54 | 0 | 200 | 0 | 397 | 0 | 0 | 13 | 4.45 | 0 | 0 | 0 | 0 |  | 188 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 397 | 17 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 5034.79 | 1836.1 | 6870.89 | 4007 | 188 | 1934 | 417 | 200 | 95 | 0 | 0 | 29.89 | 0 | 99.89
13:00 | 35 | 190 | 0 | 0 | 260 | 0 | 0 | 383 | 334 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 0 | 25 | 30 | 25 | 8 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 208 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 8 | 115 | 0 | 0 | 0 | 300 | 197 | 63 | 50 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 142 | 100 | 22 | 1.7 | 29 | 60 | 5 | 50 | 163 | 170 | 63 | 5 | 0 | 0 | 17 | 39 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.33 | 0 | 200 | 0 | 376 | 0 | 17 | 25 | 4.095 | 0 | 0 | 0 | 0 |  | 188 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 396 | 17 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 |  | 5048.125 | 1822.9 | 6871.025 | 3968 | 188 | 1936 | 456 | 200 | 95 | 0 | 0 | 28.025 | 0 | 99.88
14:00 | 35 | 190 | 0 | 0 | 260 | 0 | 0 | 349 | 334 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 0 | 25 | 30 | 25 | 17 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 5 | 115 | 0 | 0 | 0 | 295 | 197 | 63 | 51 | 37 | 51 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 142 | 100 | 22 | 1.2 | 29 | 60 | 5 | 50 | 163 | 160 | 65 | 5 | 0 | 0 | 17 | 38 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8 | 0 | 200 | 0 | 368 | 0 | 17 | 34 | 3.3 | 0 | 0 | 0 | 0 |  | 188 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4970.3 | 1738.8 | 6709.1 | 3897 | 188 | 1841 | 465 | 200 | 95 | 0 | 0 | 23.1 | 0 | 99.88
15:00 | 35 | 188 | 0 | 0 | 260 | 0 | 0 | 359 | 335 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 19 | 25 | 23 | 25 | 17 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 4 | 120 | 0 | 0 | 0 | 295 | 193 | 63 | 87 | 37 | 50 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 0 | 142 | 100 | 22 | 0.7 | 29 | 60 | 45 | 50 | 163 | 157 | 64 | 40 | 0 | 0 | 17 | 38 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8 | 0 | 34 | 0 | 366 | 0 | 17 | 34 | 2.2 | 0 | 0 | 0 | 0 |  | 188 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 15 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 405 | 17 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 |  | 5047.7 | 1797.9 | 6845.6 | 4062 | 188 | 1986 | 299 | 200 | 94 | 0 | 0 | 16.6 | 0 | 99.87
16:00 | 35 | 189 | 0 | 0 | 260 | 0 | 0 | 346 | 333 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 19 | 25 | 24 | 25 | 17 | 0 | 0 | 44 | 50 | 0 | 95 | 0 | 208 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 6 | 120 | 0 | 8 | 0 | 295 | 195 | 63 | 89 | 37 | 49 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 0 | 155 | 100 | 22 | 0.3 | 29 | 56 | 50 | 50 | 163 | 165 | 65 | 40 | 0 | 0 | 17 | 36 | 10 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 0 | 34 | 0 | 367 | 0 | 17 | 34 | 1 | 0 | 0 | 0 | 0 |  | 188 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 |  | 5087.4 | 1739.7 | 6827.1 | 4102 | 188 | 1936 | 299 | 200 | 94 | 0 | 0 | 8.1 | 0 | 99.87
17:00 | 35 | 168 | 0 | 0 | 260 | 0 | 0 | 351 | 334 |  | 0 | 400 | 0 | 1 | 0 | 7 | 0 | 0 | 95 | 0 | 5 | 2 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | 30 | 19 | 25 | 24 | 25 | 17 | 0 | 0 | 42 | 50 | 0 | 90 | 0 | 205 | 0 | 144 | 0 |  | 0 | 0 | 9 | 35 | 0 | 3 | 19 | 2 | 120 | 0 | 70 | 0 | 295 | 195 | 63 | 80 | 37 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 18 | 0 | 155 | 100 | 22 | 0 | 30 | 63 | 50 | 50 | 130 | 154 | 67 | 40 | 0 | 0 | 17 | 36 | 10 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0.2 | 15 | 35 | 3 | 365 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 0 |  | 188 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 153 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 202 | 0 | 0 | 0 | 8 | 0 | 196 | 0 | 365 | 17 | 0 | 6 | 17 | 5 | 0 | 0.1 | 0 |  | 5206.2 | 1832.1 | 7038.3 | 4126 | 188 | 1926 | 497 | 200 | 92 | 9 | 0 | 0.3 | 0 | 99.86
18:00 | 35 | 189 | 0 | 0 | 260 | 0 | 0 | 366 | 361 |  | 0 | 450 | 0 | 22 | 0 | 20 | 0 | 0 | 85 | 0 | 48 | 16 | 0 | 23 | 72 | 0 | 34 | 17 | 55 | 35 | 19 | 25 | 28 | 33 | 31 | 2 | 0 | 42 | 50 | 0 | 90 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 41 | 100 | 27 | 45 | 19 | 6 | 120 | 0 | 80 | 0 | 335 | 197 | 63 | 90 | 37 | 50 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 0 | 156 | 100 | 22 | 0 | 60 | 61 | 50 | 50 | 130 | 164 | 66 | 79 | 0 | 0 | 17 | 37 | 10 | 285 | 24 | 8 | 0 | 42 | 0 | 0 | 86 | 0 | 0 | 0 | 76 | 105 | 75 | 380 | 0 | 50 | 95 | 0 | 0 | 23 | 0 | 0 |  | 437 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 204 | 0 | 0 | 0 | 11 | 0 | 185 | 0 | 401 | 35 | 0 | 97 | 17 | 13 | 0 | 0 | 0 |  | 6341 | 2301 | 8642 | 4309 | 437 | 2086 | 1477 | 200 | 92 | 41 | 0 | 0 | 0 | 99.86
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 188 | 0 | 0 | 260 | 0 | 0 | 347 | 362 |  | 0 | 450 | 0 | 50 | 0 | 39 | 0 | 0 | 85 | 0 | 40 | 7 | 0 | 10 | 72 | 0 | 47 | 17 | 55 | 35 | 19 | 25 | 31 | 33 | 32 | 8 | 0 | 42 | 50 | 0 | 90 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 50 | 100 | 60 | 50 | 19 | 8 | 120 | 0 | 80 | 0 | 320 | 196 | 63 | 80 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 147 | 72 | 22 | 0 | 58 | 62 | 53 | 50 | 163 | 156 | 67 | 79 | 0 | 0 | 17 | 37 | 10 | 285 | 24 | 5 | 0 | 111 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 200 | 100 | 367 | 0 | 34 | 105 | 0 | 0 | 53 | 0 | 0 |  | 438 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 365 | 35 | 0 | 110 | 17 | 50 | 0 | 0 | 0 |  | 6729 | 2260 | 8989 | 4208 | 438 | 2092 | 1799 | 200 | 92 | 50 | 110 | 0 | 0 | 99.85
19:30 | 35 | 166 | 0 | 0 | 260 | 0 | 0 | 349 | 364 |  | 0 | 450 | 0 | 0 | 0 | 42 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 10 | 72 | 0 | 47 | 17 | 55 | 35 | 19 | 25 | 31 | 33 | 32 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 202 | 0 | 145 | 0 |  | 0 | 0 | 10 | 100 | 98 | 18 | 19 | 10 | 120 | 0 | 80 | 0 | 320 | 196 | 63 | 90 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 118 | 146 | 40 | 22 | 0 | 60 | 62 | 53 | 50 | 163 | 161 | 66 | 79 | 0 | 0 | 17 | 38 | 10 | 320 | 24 | 11 | 0 | 117 | 0 | 0 | 142 | 0 | 0 | 0 | 100 | 200 | 100 | 366 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 438 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 193 | 0 | 0 | 0 | 11 | 0 | 183 | 0 | 401 | 17 | 0 | 113 | 17 | 50 | 0 | 0 | 0 |  | 6597 | 2255 | 8852 | 4216 | 438 | 2168 | 1609 | 200 | 93 | 10 | 118 | 0 | 0 | 0
20:00 | 35 | 130 | 0 | 0 | 260 | 0 | 0 | 347 | 362 |  | 0 | 450 | 0 | 0 | 0 | 42 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 10 | 72 | 0 | 47 | 0 | 35 | 35 | 19 | 25 | 31 | 33 | 32 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 100 | 98 | 0 | 19 | 13 | 120 | 0 | 80 | 0 | 330 | 196 | 63 | 90 | 37 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 118 | 146 | 16 | 22 | 0 | 60 | 62 | 53 | 50 | 163 | 165 | 68 | 79 | 0 | 0 | 17 | 39 | 10 | 280 | 24 | 11 | 0 | 117 | 0 | 0 | 132 | 0 | 0 | 0 | 100 | 140 | 100 | 370 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 438 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 153 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 199 | 0 | 0 | 0 | 11 | 0 | 190 | 0 | 388 | 0 | 0 | 113 | 18 | 50 | 0 | 0 | 0 |  | 6365 | 2224 | 8589 | 4217 | 438 | 2117 | 1406 | 200 | 93 | 0 | 118 | 0 | 0 | 99.85
21:00 | 35 | 112 | 0 | 0 | 260 | 0 | 0 | 347 | 362 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 0 | 35 | 16 | 25 | 31 | 33 | 25 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 202 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 98 | 0 | 19 | 22 | 120 | 0 | 80 | 0 | 320 | 196 | 63 | 84 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 118 | 147 | 0 | 22 | 0 | 60 | 62 | 53 | 50 | 163 | 161 | 68 | 79 | 0 | 0 | 17 | 40 | 10 | 300 | 24 | 11 | 0 | 117 | 0 | 0 | 165 | 0 | 0 | 0 | 80 | 34 | 100 | 366 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 438 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 153 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 11 | 0 | 200 | 0 | 424 | 0 | 0 | 113 | 4 | 35 | 0 | 0 | 0 |  | 6147 | 2229 | 8376 | 4173 | 438 | 2185 | 1169 | 200 | 93 | 0 | 118 | 0 | 0 | 99.84
22:00 | 35 | 115 | 0 | 0 | 260 | 0 | 0 | 346 | 363 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 24 | 0 | 0 | 0 | 16 | 25 | 31 | 33 | 25 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 209 | 0 | 144 | 0 |  | 0 | 0 | 0 | 60 | 53 | 0 | 19 | 30 | 120 | 0 | 80 | 0 | 340 | 196 | 63 | 85 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 142 | 0 | 22 | 0 | 60 | 62 | 53 | 50 | 130 | 168 | 68 | 79 | 0 | 0 | 17 | 40 | 10 | 285 | 24 | 11 | 0 | 30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 30 | 375 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 438 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 199 | 0 | 0 | 200 | 0 | 0 | 0 | 11 | 0 | 199 | 0 | 431 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 5657 | 2099 | 7756 | 4197 | 438 | 2151 | 570 | 199 | 93 | 0 | 108 | 0 | 0 | 99.84
23:00 | 35 | 116 | 0 | 0 | 260 | 0 | 0 | 346 | 363 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 0 | 0 | 0 | 16 | 25 | 22 | 33 | 25 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 205 | 0 | 144 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 30 | 120 | 0 | 80 | 0 | 320 | 200 | 63 | 85 | 37 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 142 | 0 | 22 | 0 | 60 | 58 | 53 | 50 | 130 | 170 | 68 | 79 | 0 | 0 | 17 | 41 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 193 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 202 | 0 | 0 | 0 | 11 | 0 | 206 | 0 | 431 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 5438 | 1820 | 7258 | 4134 | 193 | 2159 | 379 | 200 | 93 | 0 | 100 | 0 | 0 | 99.83
24:00 | 35 | 114 | 0 | 0 | 260 | 0 | 0 | 345 | 363 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 16 | 25 | 31 | 33 | 25 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 32 | 120 | 0 | 80 | 0 | 330 | 200 | 68 | 84 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 94 | 148 | 0 | 22 | 0 | 60 | 58 | 53 | 50 | 130 | 168 | 69 | 10 | 0 | 0 | 17 | 40 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 193 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 198 | 0 | 0 | 0 | 11 | 0 | 206 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5121 | 1760 | 6881 | 4155 | 193 | 2073 | 73 | 200 | 93 | 0 | 94 | 0 | 0 | 99.83
KWH | 752000 | 3249000 | 0 | 0 | 5877800 | 0 | 0 | 8293370 | 8096000 |  | 0 | 9716625 | 0 | 103680 | 0 | 134979 | 0 | 0 | 1647000 | 0 | 96960 | 36000 | 0 | 75086 | 438720 | 0 | 314928 | 49680 | 156949 | 265880 | 156708 | 600000 | 645660 | 713400 | 444600 | 177840 | 0 | 964451 | 1188000 | 0 | 2200000 | 0 | 4842065 | 0 | 3038933 | 0 |  | 0 | 0 | 99443 | 540720 | 336000 | 121440 | 443040 | 353280 | 2501158 | 0 | 1512718 | 0 | 7738400 | 4514000 | 1120727 | 1649170 | 636480 | 929280 | 0 | 735408 | 0 | 0 | 0 | 223452 | 94140 | 342200 | 480300 | 1205760 | 3955080 | 948480 | 351900 | 11200 | 954000 | 1411320 | 558000 | 883800 | 3363938 | 3838000 | 1373952 | 763000 | 0 | 0 | 293000 | 625660 | 161280 | 7547750 | 218160 | 83956 | 0 | 509345 | 0 | 0 | 880800 | 0 | 0 | 135270 | 360000 | 2339520 | 471709 | 8645000 | 0 | 177840 | 902436 | 26160 | 0 | 90874 | 0 | 0 |  | 5088727 | 0 | 7937280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 3727752 | 446600 | 813024 | 0 | 0 | 0 | 0 | 0 | 0 | 159380 | 0 | 0 | 33120 | 0 | 368160 | 259992 | 231048 | 0 | 0 | 4888900 | 0 | 0 | 4992582 | 0 | 0 | 0 | 76335 | 0 | 4921555 | 0 | 9534545 | 176160 | 0 | 620352 | 68544 | 179520 | 0 | 24075 | 0 |  | 121734860 | 44712651 | 166447511 | 95530179 | 5088727 | 45540380 | 11744966 | 4888900 | 2152451 | 99443 | 1205760 | 196705 | 0
Fuel Cost | 842240 | 3508920 | 0 | 0 | 4349572 | 0 | 0 | 5971226.4 | 6152960 |  | 0 | 7773300 | 0 | 1057536 | 0 | 1384884.54 | 0 | 0 | 2058750 | 0 | 1076256 | 365760 | 0 | 786901.28 | 3992352 | 0 | 2947726.08 | 476431.2 | 1497293.46 | 2648164.8 | 117531 | 450000 | 0 | 0 | 0 | 1703707.2 | 0 | 250757.26 | 308880 | 0 | 3366000 | 0 | 5084168.25 | 0 | 3859444.91 | 0 |  | 0 | 0 | 1043157.07 | 5564008.8 | 3195360 | 1136678.4 | 407596.8 | 982118.4 | 2626215.9 | 0 | 1588353.9 | 0 | 6500256 | 4152880 | 1098312.46 | 2193396.1 | 521913.6 | 957158.4 | 0 | 1051633.44 | 0 | 0 | 0 | 227921.04 | 70605 | 646758 | 360225 | 8319744 | 3243165.6 | 9020044.8 | 358938 | 183680 | 1297440 | 1919395.2 | 758880 | 1104750 | 4171283.12 | 3530960 | 2047188.48 | 1342880 | 0 | 0 | 465870 | 732022.2 | 379008 | 5358902.5 | 163620 | 63806.56 | 0 | 5332842.15 | 0 | 0 | 8473296 | 0 | 0 | 1561015.8 | 3355200 | 21944697.6 | 4419913.33 | 8126300 | 0 | 1584554.4 | 8528020.2 | 0 | 0 | 0 | 0 | 0 |  | 13739562.9 | 0 | 6191078.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1631850 | 2982201.6 | 692230 | 8731877.76 | 0 | 0 | 0 | 0 | 0 | 0 | 1652770.6 | 0 | 0 | 329875.2 | 0 | 404976 | 428986.8 | 174903.336 | 0 | 0 | 19995601 | 0 | 0 | 4393472.16 | 0 | 0 | 0 | 121372.65 | 0 | 4330968.4 | 0 | 6960217.85 | 1666473.6 | 0 | 5694831.36 | 610727.04 | 1676716.8 | 0 | 0 | 0 |  | 204142728.63 | 82410693.456 | 286553422.086 | 88193281.636 | 13739562.9 | 40470991.82 | 112486750.6 | 19995601 | 559637.26 | 1043157.07 | 8319744 | 1744695.8 | 0
Yesterday Day Peak | 35 | 154 | 0 | 0 | 260 | 0 | 0 | 379 | 335 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 0 | 25 | 30 | 25 | 17 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 220 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 100 | 0 | 0 | 0 | 330 | 199 | 63 | 50 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 145 | 100 | 22 | 1.8 | 30 | 60 | 5 | 47 | 163 | 169 | 63 | 5 | 0 | 0 | 17 | 38 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.54 | 0 | 200 | 0 | 397 | 0 | 0 | 13 | 4.45 | 0 | 0 | 0 | 0 |  | 188 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 397 | 17 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 6870.89 | DayPeak
Yesterday Evening Peak | 35 | 188 | 0 | 0 | 260 | 0 | 0 | 347 | 362 | 0 | 0 | 450 | 0 | 50 | 0 | 39 | 0 | 0 | 85 | 0 | 40 | 7 | 0 | 10 | 72 | 0 | 47 | 17 | 55 | 35 | 19 | 25 | 31 | 33 | 32 | 8 | 0 | 42 | 50 | 0 | 90 | 0 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 50 | 100 | 60 | 50 | 19 | 8 | 120 | 0 | 80 | 0 | 320 | 196 | 63 | 80 | 37 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 147 | 72 | 22 | 0 | 58 | 62 | 53 | 50 | 163 | 156 | 67 | 79 | 0 | 0 | 17 | 37 | 10 | 285 | 24 | 5 | 0 | 111 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 200 | 100 | 367 | 0 | 34 | 105 | 0 | 0 | 53 | 0 | 0 |  | 438 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 11 | 0 | 182 | 0 | 365 | 35 | 0 | 110 | 17 | 50 | 0 | 0 | 0 |  | 8989 | EvPeak
Forecast for Evening | 35 | 190 | 0 | 0 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 50 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 10 | 120 | 0 | 80 | 0 | 360 | 200 | 68 | 95 | 37 | 55 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 134 | 160 | 95 | 22 | 0 | 60 | 58 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 443 | 40 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 153 | 26 | 110 | 30 | 0 | 71 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 210 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 150 | 0 | 0 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 120 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 42 | 50 | 0 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 5 | 120 | 0 | 80 | 0 | 360 | 200 | 68 | 95 | 37 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 105 | 160 | 95 | 22 | 1.6 | 60 | 58 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 |  | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 0 |  | 294 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 26 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 112 | 0 | 0 | 0 | 0 | 0 | 385 | 366 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 23 | 31 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 210 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 120 | 0 | 0 | 0 | 345 | 201 | 8 | 90 | 33 | 40 | 0 | 8 | 0 | 0 | 0 | 19 | 0 | 33 | 21 | 78 | 162 | 0 | 22 | 0.6 | 60 | 56 | 42 | 46 | 163 | 83 | 68 | 76 | 0 | 0 | 17 | 34 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 9.8 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0
199
| Minimum Generation |  | 5433 | 5:00
| Highest Generation |  | 8989 | 19:00
| Day Peak Generation |  | 6870.89 | 12:00
| Evening Peak Generation |  | 8989 | 19:00
| HVDC Max Flow |  | 438 | 19:00
| HVDC EvPeak Flow |  | 438 | 19:00
| Load factor L.F |  | 77.15%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-11-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6870.89 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5630 | MW
Evening Peak Generation : |  | 8989 | MW Hour : | 19:00 | Available Max Generation : |  | 13747 | MW
E.P. Demand (at gen end) : |  | 8989 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9100 | MW
Maximum Generation : |  | 8989 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4647 | MW
Total Gen. (MKWH) : |  | 166.4475 | System Load Factor : | 77.15% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -416 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-01
Actual : | 99.83 | Ft.(MSL) , | Rule curve : | 106 | Ft.( MSL )
Gas Consumed : | Total = | 1162.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 128664273.456
: |  | Coal : | 19995601 | Oil : | 113529907.67 | Total : | 262189782.126
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3193.9916 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1080.6677 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 967.2685 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 873.6628 |  |  | 0 | 0%
) | 0 | 0:00 | 789.7072 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 637.2519 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 363.354 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 164.2614 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 491.4467 |  |  | 0 | 0%
Total | 0 |  | 8561.6117 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,4
4) Ashuganj unit-4
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Barapukuria ST: unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi 132/33 kV T1 transformer was under shut down from 08:50 to 13:19 for A/M.
b) Sikalbaha-Dohazari 132 kV Ckt-2 was under shut down from 09:17 to 15:53 for A/M.
c) Rampura-Bashundhara 132 kV Ckt-1 was under shut down from 08:02 to 15:08 for A/M.
d) Kabirpur 132/33 kV T1 transformer was under shut down from 10:10 to 15:41 for A/M.
e) Kaliakoir-Tangail 132 kV Ckt-2 was under shut down from 08:33 to 16:29 for A/M.
f) Kishoreganj-Ashuganj 132 kV Ckt-1 was under shut down from 09:43 to 16:53 for A/M.
g) Netrokona-Mymensingh 132 kV Ckt-1 was under shut down from 09:47 to 17:14 for A/M.
h) Manikganj 132/33 kV T2 transformer along with Kabirpur 132 kV Ckt-2 was under shut down
from 08:12 to 17:03 for A/M.
i) Siddhirganj-Maniknagar 230 kV Ckt-1 along with 230/132 kV T01 transformer was under shut
down from 08:18 to 16:22 for A/M.
j) Rangpur-Lalmonirhat 132 kV single Ckt was under shut down from 08:20 to 16:05 for A/M. |  |  |  |  | About 48 MW power interruption occurred under Lalmonirhat S/S
area from 08:20 to 16:05.
k) HVDC-Bahrampur 400 kV Ckt-1 was under shut down from 09:04 to 16:28 for A/M.
l) Khulna (c)-Noapara 132 kV Ckt-2 was shut down at 09:33 for D/W.
m) Noapara S/S-Noapara Bangla Track 132 kV Ckt was under shut down from 10:14 to 14:00 for A/M.
n) Chattak 132/33 kV T1 transformer tripped at 10:22 showing O/C, lookout O/C at 33 kV side
and was switched on at 10:32.
o) Ashuganj unit-5 tripped at 10:42 due to burner trip and was synchronized at 15:58.
p) Choddogram 132/33 kV T1 transformer was shut down at 13:03 for D/W.
q) Cumilla(S)-Tripura 132 kV Ckt-1 & Ckt-2 were switched on at 18:39.
r) HVDC Bheramara filter Bank 20DF42 tripped at 17:17 showing capacitor unbalance.
s) Choddogram 132/33 kV T2 transformer was charged at 16:49.
t) Choddogram 132/33 kV T1 transformer was switched on at 17:57.
u) Ashuganj(N) 450 MW CCPP unit transformer was normalized at 20:18.
v) HVDC Bheramara 230 kV bus-2 was normalized at 20:33.
w) Shahzibazar 330 MW GT-2 tripped at 23:59 due to gas line problem.
x) Ghorashal unit-7 was shut down at 00:29(01/12/2019) for A/M.
y) Ashuganj-Kishoreganj 132 kV Ckt-1 was shut down at 07:29(01/12/19) for A/M.
z) Ashuganj unit-5 tripped at 00:29(01/12/2019) for A/M.
aa) Aminbazar 230/132 kV T01 transformer was shut down at 07:40(01/12/2019) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-11-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 752000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 188 | 3249000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 5877800 | ST under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8293370 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 362 | 8096000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9716625
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 103680 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 39 | 134979 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 10 | 75086 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 156708
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 85 | 1647000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 40 | 96960 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 36000 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 314928
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 49680 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 156949
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 265880 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 438720 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1245660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 713400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 444600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 8 | 177840 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 111 | 509345 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 177840 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2392 | 42730050
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 90 | 2200000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 135270
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 121440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 2152451 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4842065 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3038933 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 902436
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 99443 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 540720
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 360000
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 443040
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 353280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 336000 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26160
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 53 | 90874
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1075 | 15642112
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2501158 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1512718 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4514000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7738400 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 636480 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 929280
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 63 | 1120727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 735408 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 471709 | Low demand
| B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1649170
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2339520
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 223452
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 94140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 1205760
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 342200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 480300 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 3005 | 1488 | 26494422
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 147 | 3955080 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 351900
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 948480 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 880800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 341 | 6147460
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 954000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1411320
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3363938
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 156 | 3838000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 558000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 883800
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 83956 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1373952 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 763000 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 293000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 37 | 625660 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 218160
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7547750 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8645000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 161280
| Sylhet Area Total |  |  |  | 1949 | 1433 | 30720816
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 438 | 5088727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 305 | 7937280 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 165000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 176160 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 17 | 68544 | Low demand
| Khulna Area Total |  |  |  | 2314 | 835 | 13435711
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 813024 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 446600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 153 | 3727752 | Line over load
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 76335 | Line over load
| Barisal Area Total |  |  |  | 462 | 221 | 5063711
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 159380
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 200 | 4992582 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4921555 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 365 | 9534545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 368160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 259992
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231048
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 33120 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 110 | 620352
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 2183 | 954 | 21120734
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4888900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 50 | 179520 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24075
| Rangpur Area Total |  |  |  | 605 | 250 | 5092495
| Total |  |  |  | 19132 | 8989 | 166447511
| Eastern Grid Total |  |  |  | 13568 | 6729 | 121734860
| Western Grid Total |  |  |  | 5564 | 2260 | 44712651
| National Grid Total |  |  |  | 19132 | 8989 | 166447511
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-11-30
(a) ENTIRE EASTERN GRID : |  | 5928 | MW | (b) ENTIRE WESTERN GRID : |  | 2515 | MW
i) Dhaka area |  | 3318 | MW | i) Khulna area |  | 978 | MW
ii) Chittagong area |  | 941 | MW | ii) Rajshahi area |  | 812 | MW
iii) Comilla area |  | 690 | MW | iii) Barisal area |  | 228 | MW
iv) Mymensingh area |  | 637 | MW | iv) Rangpur area |  | 497 | MW
v) Sylhet area |  | 342 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8443 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 0.77083 | Srimongal | 26 | 0.77083 | Bottail | 102 | 0.75
Munsiganj | 84 | 0.79167 | Shahjibazar | 88 | 0.79167 | G.K Project | 26 | 0.75
Sonargaon | 78 | 0.8125 | Fenchuganj | 25 | 0.77083 | Faridpur | 122 | 0.79167
Shyampur | 180 | 0.29167 | Kulawara | 30 | 0.77083 | Madaripur | 55 | 0.8125
Bhulta | 170 | 0.79167 | Sylhet | 98 | 0.77083 | Sariatpur | 38 | 0.8125
Madanganj | 40 | 0.83333 | Chatak | 17 | 0.79167 | Gopalganj | 55 | 0.75
Shitalakhya | 97 | 0.75 | Sunamganj | 29 | 0.77083 | Bagerhat | 62 | 0.77083
Rahim steel | 14 | 0.75 | Biani Bazar | 32 | 0.8125 | Mongla | 36 | 0.375
Matuail | 82 | 0.625 | Comilla (S) | 118 | 0.8125 | Satkhira | 63 | 0.77083
Ghorasal | 67 | 0.75 | Comilla(N) | 93 | 0.75 | Gallamari | 34 | 0.75
Narsingdi | 105 | 0.77083 | Chandpur | 70 | 0.8125 | Magura | 37 | 0.75
Haripur (SBU) | 79 | 0.8125 | Feni | 91 | 0.79167 | Norail | 21 | 0.75
Ullon | 59 | 0.75 | Chowmuhani | 116 | 0.8125 | Chuadanga | 58 | 0.75
Hasnabad | 149 | 0.75 | Ashuganj | 44 | 0.54167 | Barisal(N) | 30 | 0.83333
Magbazar | 88 | 0.54167 | Daudkandi | 90 | 0.83333 | Barisal (S) | 64 | 0.75
Maniknagar | 86 | 0.75 | B.Baria | 88 | 0.8125 | Patuakhali | 80 | 0.875
Bangabhaban | 16 | 0.45833 | Ramganj | 54 | 0.79167 | Bhandaria | 38 | 0.83333
Narinda | 82 | 0.54167 | Madunaghat | 55 | 0.58333 | Borhan Uddin | 24 | 0.79167
Dhanmondi | 109 | 0.54167 | Hathazari | 81 | 0.75 | Ishurdi | 42 | 0.79167
Lalbag | 61 | 0.54167 | Khulshi | 174 | 0.625 | Ruppur Paromanobik | 1 | 0.041667
Madartek | 53 | 0.77083 | Halishahar | 110 | 0.75 | Natore | 80 | 0.75
Mirpur | 83 | 0.75 | Baraulia | 150 | 1904-01-02 | Bogra | 142 | 0.75
Kalyanpur | 84 | 0.75 | Sikalbaha | 32 | 0.77083 | Noagaon | 76 | 0.79167
Gulshan | 104 | 0.54167 | Dohazari | 68 | 0.75 | Rajshahi | 91 | 0.83333
Uttara | 48 | 0.75 | Cox'sbazar | 75 | 0.75 | Rajshahi New | 9 | 0.77083
Uttara New | 30 | 0.75 | Chandraghona | 24 | 0.75 | C.Nawabganj | 45 | 0.75
Kamrangirchar | 76 | 0.75 | Kaptai | 3.8 | 0.75 | Amnura | 21 | 0.75
Savar | 102 | 0.5 | A. Khaer Stl. | 0 | 0.041667 | Pabna | 69 | 0.83333
Bhasantec | 127 | 0.75 | Bakulia | 88 | 0.75 | Shahjadpur | 74 | 0.77083
Agargaon | 42 | 0.77083 | Julda | 17 | 0.75 | Serajganj | 58 | 0.77083
Satmosjid | 71 | 0.77083 | TK chemical | 2.4 | 0.45833 | Niyamatpur | 41 | 0.8125
Tongi | 126 | 0.79167 | Modern Steel | 14 | 0.083333 | Joypurhat | 42 | 0.75
Kabirpur | 164 | 0.66667 | Shahmirpur | 23 | 0.75 | Sherpur(Bogura) | 34 | 0.75
Basundhara | 82 | 0.54167 | Khagrachhari | 16 | 0.75 | Mohastangor | 10 | 0.75
Manikganj | 58 | 0.79167 | Matarbari | 22 | 0.79167 | Rangpur | 101 | 0.77083
Joydevpur | 172 | 0.75 | Baroiar Hat | 16 | 0.75 | Lalmonirhat | 47 | 0.77083
New Tongi | 93 | 0.45833 | Rangamati | 10 | 0.75 | Saidpur | 81 | 0.75
Korda | 203 | 0.625 | Abul Khair 230 | 76 | 0.45833 | Purbasadipur | 57 | 0.29167
Dhamrai | 62 | 0.625 | BSRM | 104 | 0.125 | Thakurgaon | 36 | 0.041667
Valuka | 72 | 0.75 | GPH Ispat | 7 | 0.70833 | Palashbari | 78 | 0.77083
Tangail | 134 | 0.75 | Goalpara | 19 | 0.77083 | Barapukuria | 41 | 0.83333
Mymensing | 156 | 0.75 | Central s/s | 69 | 0.75 | Panchagar | 26 | 0.70833
Kishorganj | 78 | 0.83333 | Noapara | 45 | 0.75 | Joldhaka | 20 | 0.77083
Netrokona | 69 | 0.75 | Jessore | 85 | 0.77083 | Kurigram | 34 | 0.75
Jamalpur | 80 | 0.79167 | Benapol | 26 | 0.75
Sherpur | 66 | 0.75 | Jhenida | 74 | 0.79167
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-11-30 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 387 | 0.375 | 380 | 0.45833 | Kaliakoir | 370 | 0.16667 | 355 | 0.5
Bheramara | 411 | 24:00 | 394 | 0.41667 | Bhulta | 371 | 0.125 | 355 | 0.5
Ashuganj(N) | 374 | 0.125 | 359 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 226 | 0.041667 | 220 | 0.45833 | Hathazari | 220 | 0.77083 | 211 | 0.66667
Ishurdi | 240 | 0.125 | 225 | 0.75 | Megnaghat | 222 | 0.16667 | 213 | 0.45833
Ashuganj | 231 | 0.041667 | 226 | 0.5 | Fenchuganj | 235 | 0.79167 | 231 | 0.45833
Serajganj | 233 | 0.16667 | 229 | 0.33333 | Siddhirganj | 221 | 0.083333 | 210 | 0.54167
Baghabari | 239 | 0.125 | 230 | 0.75 | Maniknagar | 220 | 0.125 | 209 | 0.5
Barapukuria | 231 | 0.125 | 224 | 0.75 | Old Airport | 219 | 0.083333 | 210 | 0.45833
Bogra | 232 | 0.16667 | 224 | 0.75 | Barisal | 233 | 0.375 | 223 | 0.83333
Khulna South | 238 | 0.16667 | 215 | 0.83333 | AKSML | 216 | 0.83333 | 208 | 0.66667
Rampura | 221 | 0.16667 | 212 | 0.5 | BSRM | 218 | 0.79167 | 211 | 0.70833
Haripur | 220 | 0.041667 | 212 | 0.5 | Bibiyana | 232 | 0.95833 | 225 | 0.45833
Hasnabad | 220 | 0.083333 | 211 | 0.5 | Bhulta | 221 | 0.125 | 212 | 0.5
Aminbazar | 221 | 0.125 | 211 | 0.5 | Ashuganj (S) | 229 | 0.16667 | 224 | 0.45833
Tongi | 217 | 0.16667 | 206 | 0.625 | Kaliakoir | 222 | 0.29167 | 214 | 0.5
Comilla (N) | 228 | 0.125 | 221 | 0.5 | GPH | 217 | 0.8125 | 209 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 0.083333 | 127 | 0.5 | Halishahar | 132 | 0.79167 | 125 | 0.66667
Munsiganj | 132 | 0.77083 | 125 | 0.5 | Baraulia | 130 | 0.77083 | 125 | 0.625
Sonargaon | 130 | 0.75 | 125 | 0.45833 | Sikalbaha | 133 | 0.79167 | 125 | 0.79167
Shyampur | 134 | 0.083333 | 126 | 0.5 | Dohazari | 128 | 0.16667 | 123 | 0.625
Bhulta | 127 | 0.20833 | 122 | 0.5 | Cox'sbazar | 125 | 0.29167 | 119 | 0.625
Madanganj | 134 | 0.083333 | 125 | 0.5 | Chandraghona | 131 | 0.75 | 126 | 0.66667
Shitalakhya | 134 | 0.041667 | 125 | 0.45833 | Kaptai | 131 | 0.83333 | 128 | 0.45833
Rahim steal | 134 | 0.125 | 128 | 0.45833 | A. Khaer Stl. | 130 | 0.79167 | 125 | 0.45833
Matuail | 133 | 0.16667 | 126 | 0.5 | Bakulia | 130 | 0.8125 | 124 | 0.625
Ghorasal | 135 | 0.041667 | 130 | 0.5 | Julda | 131 | 0.79167 | 125 | 0.5
Narsinghdi | 134 | 0.125 | 132 | 0.45833 | TK Chemical | 132 | 0.79167 | 126 | 0.45833
Haripur (SBU) | 133 | 0.20833 | 129 | 0.41667 | Modern Steel | 131 | 0.875 | 124 | 0.625
Ullon | 131 | 0.083333 | 125 | 0.58333 | Shahmirpur | 131 | 0.79167 | 125 | 0.625
Hasnabad | 134 | 0.041667 | 126 | 0.45833 | Khagrachhari | 131 | 0.875 | 126 | 0.625
Magbazar | 132 | 0.16667 | 125 | 0.45833 | Matarbari | 127 | 0.33333 | 121 | 0.58333
Maniknagar | 135 | 0.041667 | 125 | 0.5 | Baroiar Hat | 130 | 0.29167 | 125 | 0.66667
Bangabhaban | 135 | 0.041667 | 125 | 0.5 | Rangamati | 131 | 0.79167 | 126 | 0.625
Narinda | 135 | 0.041667 | 125 | 0.5 | Goalpara | 138 | 0.041667 | 125 | 0.83333
Dhanmondi | 131 | 0.083333 | 125 | 0.58333 | Central s/s | 139 | 0.20833 | 125 | 0.83333
Lalbag | 136 | 0.125 | 124 | 0.5 | Noapara | 136 | 0.20833 | 123 | 0.77083
Madartek | 132 | 0.125 | 125 | 0.45833 | Jessore | 133 | 0.20833 | 120 | 0.75
Mirpur | 132 | 0.25 | 126 | 0.5 | Benapol | 135 | 0.083333 | 123 | 0.75
Kalyanpur | 136 | 0.083333 | 130 | 0.45833 | Jhenida | 135 | 0.20833 | 120 | 0.75
Gulshan | 133 | 0.25 | 124 | 0.5 | Bottail | 137 | 0.16667 | 126 | 0.75
Uttara | 131 | 0.20833 | 120 | 0.5 | G.K Project | 142 | 0.125 | 133 | 0.75
Uttara New | 133 | 0.125 | 126 | 0.625 | Faridpur | 135 | 0.125 | 125 | 0.75
Kamrangirchar | 134 | 0.16667 | 121 | 0.5 | Madaripur | 136 | 0.375 | 125 | 0.875
Savar | 133 | 0.125 | 125 | 0.5 | Sariatpur | 135 | 0.041667 | 129 | 0.75
Bhasantec | 132 | 0.125 | 125 | 0.5 | Gopalganj | 139 | 0.041667 | 128 | 0.875
Agargaon | 133 | 0.125 | 127 | 0.54167 | Bagerhat | 136 | 0.16667 | 124 | 0.83333
Satmosjid | 133 | 0.083333 | 126 | 0.45833 | Mongla | 132 | 0.041667 | 122 | 0.75
Tongi | 133 | 0.16667 | 123 | 0.5 | Satkhira | 137 | 0.20833 | 122 | 0.83333
Kabirpur | 132 | 1:0 | 123 | 0.5 | Gallamari | 139 | 0.125 | 125 | 0.83333
Basundhara | 131 | 2:0 | 120 | 0.5 | Magura | 135 | 0.041667 | 120 | 0.75
Manikganj | 133 | 1904-01-02 | 120 | 0.41667 | Norail | 134 | 0.25 | 117 | 0.75
Joydevpur | 135 | 0.25 | 128 | 0.5 | Chuadanga | 134 | 0.125 | 117 | 0.75
New Tongi | 130 | 0.95833 | 121 | 0.5 | Barisal(N) | 139 | 0.375 | 131 | 0.83333
Kodda | 133 | 0.041667 | 123 | 0.5 | Barisal (S) | 138 | 0.29167 | 128 | 0.75
Dhamrai | 131 | 0.125 | 124 | 0.625 | Patuakhali | 139 | 0.375 | 126 | 0.875
Valuka | 133 | 0.45833 | 125 | 0.8125 | Bhandaria | 136 | 0.125 | 125 | 0.83333
Tangail | 133 | 0.20833 | 127 | 0.5 | Ishurdi | 137 | 0.083333 | 130 | 0.75
Mymensing | 135 | 0.45833 | 127 | 0.79167 | Ruppur Paromanobik | 137 | 0.041667 | 132 | 0.54167
Kishorganj | 134 | 0.375 | 129 | 0.79167 | Natore | 135 | 0.20833 | 128 | 0.5
Netrokona | 133 | 0.45833 | 126 | 0.79167 | Bogra | 137 | 0.041667 | 131 | 0.75
Jamalpur | 140 | 0.70833 | 126 | 0.33333 | Noagaon | 134 | 0.041667 | 127 | 0.75
Sherpur | 138 | 0.70833 | 126 | 0.041667 | Rajshahi | 132 | 0.25 | 125 | 0.45833
Srimongal | 137 | 0.33333 | 135 | 0.41667 | Rajshahi New | 134 | 0.70833 | 123 | 0.5
Shahjibazar | 135 | 0.16667 | 133 | 0.5 | C.Nawabganj | 131 | 0.083333 | 122 | 0.5
Fenchuganj | 136 | 0.95833 | 132 | 0.041667 | Amnura | 132 | 0.70833 | 122 | 0.5
Khulawara | 135 | 0.33333 | 132 | 0.45833 | Pabna | 138 | 0.16667 | 130 | 0.75
Sylhet | 134 | 0.375 | 131 | 0.375 | Shahjadpur | 141 | 0.041667 | 136 | 0.75
Chatak | 134 | 0.95833 | 130 | 0.5 | Serajganj | 136 | 0.041667 | 130 | 0.75
Sunamganj | 133 | 0.95833 | 129 | 0.77083 | Niyamatpur | 131 | 0.041667 | 125 | 0.75
Biani Bazar | 134 | 0.375 | 131 | 0.083333 | Joypurhat | 134 | 0.083333 | 127 | 0.75
Comilla(s) | 131 | 0.25 | 126 | 0.79167 | Sherpur(Bogura) | 137 | 0.041667 | 131 | 0.75
Comilla(n) | 135 | 0.29167 | 132 | 0.5 | Mohastangor | 135 | 0.125 | 130 | 0.33333
Chandpur | 142 | 0.29167 | 127 | 0.875 | Rangpur | 129 | 0.125 | 122 | 0.75
Feni | 130 | 0.29167 | 125 | 0.70833 | Lalmonirhat | 125 | 0.041667 | 116 | 0.75
Chowmuhani | 129 | 0.83333 | 117 | 0.70833 | Saidpur | 129 | 0.20833 | 122 | 0.75
Ashuganj | 136 | 0.16667 | 134 | 0.54167 | Purbasadipur | 126 | 0.16667 | 116 | 0.75
Daudkandi | 132 | 0.29167 | 127 | 0.625 | Thakurgaon | 124 | 0.25 | 116 | 0.75
B.Baria | 135 | 0.041667 | 132 | 0.5 | Palashbari | 131 | 0.125 | 125 | 0.75
Ramganj | 130 | 0.77083 | 122 | 0.29167 | Barapukuria | 131 | 0.125 | 124 | 0.75
Madanhat | 133 | 0.79167 | 127 | 0.625 | Panchagar | 121 | 0.25 | 112 | 0.75
Hathazari | 132 | 0.79167 | 127 | 0.66667 | Joldhaka | 127 | 0.083333 | 119 | 0.75
Khulshi | 129 | 0.8125 | 123 | 0.66667 | Kurigram | 129 | 0.20833 | 118 | 0.75
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-11-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 150 | 5121 | 1760 | 6881 |  |  |  | QF-LDC-12
0:30 | 107 | 4782.5 | 1687.5 | 6470 | Date: | 2019-11-30
1:00 | 64 | 4444 | 1615 | 6059
1:30 | 55.5 | 4318.5 | 1582.5 | 5901
2:00 | 47 | 4193 | 1550 | 5743
2:30 | 35.5 | 4154.5 | 1543 | 5697.5 | [5 empty] | Gen. at Eve. Peak | 8989 | 8989 MW (19:00 )
3:00 | 24 | 4116 | 1536 | 5652 | [6 empty] | 19:00
3:30 | 42 | 4006.5 | 1546.5 | 5553 | [5 empty] | Gen. at Day Peak | 6870.89 | 6870.89 MW (12:00 )
4:00 | 60 | 3897 | 1557 | 5454 | [6 empty] | 12:00
4:30 | 50 | 3902.5 | 1541 | 5443.5 | [5 empty] | Highest Generation | 8989
5:00 | 40 | 3908 | 1525 | 5433 | [6 empty] | 19:00
5:30 | 30 | 3935 | 1572 | 5507
6:00 | 20 | 3962 | 1619 | 5581
6:30 | 61.5 | 4127.95 | 1632.6 | 5760.55
7:00 | 103 | 4293.9 | 1646.2 | 5940.1
7:30 | 176.5 | 4445.505 | 1657.15 | 6102.655
8:00 | 250 | 4597.11 | 1668.1 | 6265.21
8:30 | 140 | 4614.795 | 1702.75 | 6317.545
9:00 | 30 | 4632.48 | 1737.4 | 6369.88
9:30 | 101.5 | 4592.866 | 1757.15 | 6350.016
10:00 | 173 | 4553.252 | 1776.9 | 6330.152
10:30 | 176.5 | 4607.991 | 1783.15 | 6391.141
11:00 | 180 | 4662.73 | 1789.4 | 6452.13
11:30 | 124 | 4848.76 | 1812.75 | 6661.51
12:00 | 68 | 5034.79 | 1836.1 | 6870.89
12:30 | 58.5 | 5041.4575 | 1829.5 | 6870.9575
13:00 | 49 | 5048.125 | 1822.9 | 6871.025
13:30 | 29.5 | 5009.2125 | 1780.85 | 6790.0625
14:00 | 10 | 4970.3 | 1738.8 | 6709.1
14:30 | 71.5 | 5009 | 1768.35 | 6777.35
15:00 | 133 | 5047.7 | 1797.9 | 6845.6
15:30 | 115 | 5067.55 | 1768.8 | 6836.35
16:00 | 97 | 5087.4 | 1739.7 | 6827.1
16:30 | 89.5 | 5146.8 | 1785.9 | 6932.7
17:00 | 82 | 5206.2 | 1832.1 | 7038.3
17:30 | 212 | 5773.6 | 2066.55 | 7840.15
18:00 | 342 | 6341 | 2301 | 8642
18:30 | 376 | 6535 | 2280.5 | 8815.5
19:00 | 410 | 6729 | 2260 | 8989
19:30 | 365 | 6597 | 2255 | 8852
20:00 | 364 | 6365 | 2224 | 8589 |  |  |  | Executive Engineer
20:30 | 221 | 6256 | 2226.5 | 8482.5 |  |  |  | Network Operation Division
21:00 | 78 | 6147 | 2229 | 8376
21:30 | 56 | 5902 | 2164 | 8066
22:00 | 34 | 5657 | 2099 | 7756 |  |  |  |  | Page 6 of 7
22:30 | 113 | 5547.5 | 1959.5 | 7507
23:00 | 192 | 5438 | 1820 | 7258
23:30 | 171 | 5279.5 | 1790 | 7069.5
24:00 | 150 | 5121 | 1760 | 6881
8989 MW (19:00 )
6870.89 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-11-30 |  | Energy | 166447511
[10 empty] | 2019-11-30 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4155 | 193 | 2073 | 379 | 200 | 93 | 0 | 0 | 94
0:30 | 3988 | 153.5 | 1902.5 | 195.5 | 200 | 93.5 | 0 | 0 | 90 | Date: | 2019-11-30
1:00 | 3821 | 114 | 1732 | 12 | 200 | 94 | 0 | 0 | 86
1:30 | 3725 | 102.5 | 1688.5 | 9 | 200 | 92 | 0 | 0 | 84 | [7 empty] | Total Energy | 166.4475 | Total Energy Gen 166.448 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 166.448 MKWHr
2:00 | 3629 | 91 | 1645 | 6 | 200 | 90 | 0 | 0 | 82 | [7 empty] | Energy not Served | 0
2:30 | 3592 | 91 | 1641 | 3 | 200.5 | 90 | 0 | 0 | 80 | [7 empty] | Energy Requirement | 166.4475
3:00 | 3555 | 91 | 1637 | 0 | 201 | 90 | 0 | 0 | 78
3:30 | 3536 | 91 | 1558.5 | 0 | 200.5 | 90 | 0 | 0 | 77 | [6 empty] | Shortage
4:00 | 3517 | 91 | 1480 | 0 | 200 | 90 | 0 | 0 | 76
4:30 | 3502.5 | 90.5 | 1484.5 | 0 | 200 | 90 | 0 | 0 | 76
5:00 | 3488 | 90 | 1489 | 0 | 200 | 90 | 0 | 0 | 76
5:30 | 3526 | 90.5 | 1524.5 | 0 | 200 | 90 | 0 | 0 | 76
6:00 | 3564 | 91 | 1560 | 0 | 200 | 90 | 0 | 0 | 76
6:30 | 3702 | 90 | 1611 | 10 | 200 | 70 | 0 | 0 | 76 |  |  |  |  | Coal
7:00 | 3840 | 89 | 1662 | 20 | 200 | 50 | 0 | 0 | 76
7:30 | 3835.5 | 89.5 | 1742.5 | 118 | 200 | 71.5 | 0 | 0 | 38 |  |  |  | Oil |  |  |  | ,
8:00 | 3831 | 90 | 1823 | 216 | 200 | 93 | 0 | 0 | 0
8:30 | 3825 | 139 | 1796.5 | 248 | 200 | 93 | 0 | 0 | 0
9:00 | 3819 | 188 | 1770 | 280 | 200 | 93 | 0 | 0 | 0
9:30 | 3791 | 188 | 1768.5 | 286 | 200 | 93 | 0 | 0 | 0
10:00 | 3763 | 188 | 1767 | 292 | 200 | 93 | 0 | 0 | 0
10:30 | 3793.5 | 188 | 1782.5 | 305.5 | 200 | 93.5 | 0 | 0 | 0
11:00 | 3824 | 188 | 1798 | 319 | 200 | 94 | 0 | 0 | 0
11:30 | 3915.5 | 188 | 1866 | 368 | 200 | 94.5 | 0 | 0 | 0
12:00 | 4007 | 188 | 1934 | 417 | 200 | 95 | 0 | 0 | 0
12:30 | 3987.5 | 188 | 1935 | 436.5 | 200 | 95 | 0 | 0 | 0
13:00 | 3968 | 188 | 1936 | 456 | 200 | 95 | 0 | 0 | 0
13:30 | 3968 | 188 | 1936 | 456 | 200 | 95 | 0 | 0 | 0
14:00 | 3968 | 188 | 1936 | 456 | 200 | 95 | 0 | 0 | 0
14:30 | 4015 | 188 | 1961 | 377.5 | 200 | 94.5 | 0 | 0 | 0
15:00 | 4062 | 188 | 1986 | 299 | 200 | 94 | 0 | 0 | 0
15:30 | 4082 | 188 | 1961 | 299 | 200 | 94 | 0 | 0 | 0
16:00 | 4102 | 188 | 1936 | 299 | 200 | 94 | 0 | 0 | 0
16:30 | 4114 | 188 | 1931 | 398 | 200 | 93 | 4.5 | 0 | 0
17:00 | 4126 | 188 | 1926 | 497 | 200 | 92 | 9 | 0 | 0
17:30 | 4217.5 | 312.5 | 2006 | 987 | 200 | 92 | 25 | 0 | 0
18:00 | 4309 | 437 | 2086 | 1477 | 200 | 92 | 41 | 0 | 0
18:30 | 4258.5 | 437.5 | 2089 | 1638 | 200 | 92 | 45.5 | 0 | 55
19:00 | 4208 | 438 | 2092 | 1799 | 200 | 92 | 50 | 0 | 110
19:30 | 4216 | 438 | 2168 | 1609 | 200 | 93 | 10 | 0 | 118
20:00 | 4217 | 438 | 2117 | 1406 | 200 | 93 | 0 | 0 | 118
20:30 | 4195 | 438 | 2151 | 1287.5 | 200 | 93 | 0 | 0 | 118
21:00 | 4173 | 438 | 2185 | 1169 | 200 | 93 | 0 | 0 | 118
21:30 | 4185 | 438 | 2168 | 869.5 | 199.5 | 93 | 0 | 0 | 113
22:00 | 4197 | 438 | 2151 | 570 | 199 | 93 | 0 | 0 | 108
22:30 | 4165.5 | 315.5 | 2155 | 474.5 | 199.5 | 93 | 0 | 0 | 104
23:00 | 4134 | 193 | 2159 | 379 | 200 | 93 | 0 | 0 | 100
23:30 | 4144.5 | 193 | 2116 | 379 | 200 | 93 | 0 | 0 | 97 | Max Temp. in Dhaka |  | 30.9° C
24:00 | 4155 | 193 | 2073 | 379 | 200 | 93 | 0 | 0 | 94
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 166.448 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 166.448 MKWHr
Note on W13: Author:

## Generation
2019-11-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 40 | 40 | 40 | 40 | 40 | 0 | 43 | 43 | 43 | 44 | 45 | 45 | 45 | 44 | 44 | 42 | 42 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 964451
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1188000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 95 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2200000
5 | Raozan 25 MW PP
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2.6 | 9.57 | 14.37 | 17.9 | 19.51 | 19.54 | 18.33 | 15.8 | 11.8 | 6.1 | 0.2 | [9 empty] | 135270
6 | Sikalbaha 225MW CCPP (Gas) | 214 | 203 | 202 | 202 | 186 | 188 | 190 | 202 | 203 | 215 | 216 | 220 | 208 | 204 | 204 | 208 | 205 | 204 |  | 203 | 202 | 203 | 202 | 209 | 205 | 203 | 4842065
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 105 | 104 | 104 | 105 | 105 | 103 | 108 | 104 | 116 | 115 | 144 | 145 | 145 | 144 | 144 | 145 | 144 | 144 |  | 145 | 145 | 145 | 144 | 144 | 144 | 144 | 3038933
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 9 | 41 |  | 50 | 10 | 0 | 0 |  |  |  | 99443
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [10 empty] | 0 | 13 | 25 | 34 | 34 | 34 | 35 | 95 |  | 105 | 105 | 105 | 105 | 105 | 105 | 51 | 902436
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 36 | 37 | 37 | 37 | 37 | 37 | 38 | 97 | 92 | 60 | 60 | 60 | 60 | 60 | 85 | 95 | 95 | 85 |  | 85 | 95 | 95 | 95 | 62 | 60 | 60 | 1647000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 0 | 42 |  | 111 | 117 | 117 | 117 | 30 | 0 |  | 509345
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 68 | 1120727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 752000
21 | Ghorasal Repowered CCPP Unit-3 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 154 | 190 | 190 | 188 | 189 | 168 | 189 |  | 188 | 166 | 130 | 112 | 115 | 116 | 114 | 3249000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 200 | 200 | 200 | 260 | 260 | 260 | 220 | 220 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5877800
26
28 | Ashuganj TPP Unit- 3 | 100 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 100 | 115 | 115 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2501158
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 |  |  |  |  | 8 | 70 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1512718
32 | Ashuganj 50 MW PP | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 26 | 23 | 27 | 30 | 33 | 33 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 636480
33 | Ashuganj 225 MW CCPP | 199 | 164 | 158 | 174 | 177 | 169 | 182 | 168 | 160 | 171 | 180 | 199 | 197 | 197 | 193 | 195 | 195 | 197 |  | 196 | 196 | 196 | 196 | 196 | 200 | 200 | 4514000
34 | Ashuganj 450 MW CCPP(South) | 300 | 260 | 265 | 280 | 285 | 265 | 305 | 305 | 295 | 305 | 335 | 330 | 300 | 295 | 295 | 295 | 295 | 335 |  | 320 | 320 | 330 | 320 | 340 | 320 | 330 | 7738400
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision) | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 52 | 52 | 52 | 52 | 52 | 51 | 50 | 49 | 51 | 50 |  | 52 | 52 | 51 | 52 | 52 | 51 | 52 | 929280
36 | Chandpur 150 MW CCPP | 89 | 89 | 89 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 87 | 89 | 80 | 90 |  | 80 | 90 | 90 | 84 | 85 | 85 | 84 | 1649170
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 300 | 300 | 300 | 300 | 282 | 286 | 365 | 365 | 347 | 344 | 366 | 379 | 383 | 349 | 359 | 346 | 351 | 366 |  | 347 | 349 | 347 | 347 | 346 | 346 | 345 | 8293370
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 350 | 350 | 350 | 390 | 420 | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 400 | 400 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9716625
41 | Haripur 360MW CCPP(HPL) | 367 | 366 | 365 | 288 | 289 | 290 | 335 | 366 | 368 | 305 | 305 | 335 | 334 | 334 | 335 | 333 | 334 | 361 |  | 362 | 364 | 362 | 362 | 363 | 363 | 363 | 8096000
42 | RPCL 210MW CCPP | 197 | 199 | 199 | 200 | 212 | 212 | 213 | 185 | 166 | 164 | 162 | 145 | 142 | 142 | 142 | 155 | 155 | 156 |  | 147 | 146 | 146 | 147 | 142 | 142 | 148 | 3955080
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 30 | 29 | 29 | 29 | 29 | 30 | 60 |  | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 954000
45 | Fenchugonj CCPP Phase-2 | 56 | 56 | 56 | 56 | 56 | 56 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 56 | 63 | 61 |  | 62 | 62 | 62 | 62 | 62 | 58 | 58 | 1411320
46 | Shajibazar 330 MW CCPP | 172 | 167 | 170 | 167 | 171 | 172 | 180 | 168 | 168 | 172 | 170 | 169 | 170 | 160 | 157 | 165 | 154 | 164 |  | 156 | 161 | 165 | 161 | 168 | 170 | 168 | 3838000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 68 | 67 | 65 | 64 | 63 | 63 | 65 | 64 | 65 | 67 | 66 |  | 67 | 66 | 68 | 68 | 68 | 68 | 69 | 1373952
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 10 | 763000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [6 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 293000
52 | Sylhet 50MW PP (EPL) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 32 | 39 | 21 | 21 | 38 | 39 | 38 | 38 | 36 | 36 | 37 |  | 37 | 38 | 39 | 40 | 40 | 41 | 40 | 625660
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 161280
54 | Hobiganj 11MW PP Cofidence-E | 0 | [14 empty] | 5 | 5 | 8 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 83956
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 50 | 50 | 50 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 558000
56 | Shahjahanulla 25 MW PP | [14 empty] | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 218160
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 305 | 300 | 290 | 300 | 315 | 320 | 315 | 280 | 290 | 310 | 320 | 315 | 280 | 290 | 290 | 290 | 285 |  | 285 | 320 | 280 | 300 | 285 | 295 | 280 | 7547750
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 30 | 35 |  | 35 | 35 | 35 | 35 | 0 |  |  | 265880
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 443040
61 | Narshingdi 22 MW PP (Doreen) | [14 empty] | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 156708
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 351900
63 | Impoprt (Tripura) | 86 | 82 | 78 | 76 | 76 | 76 | 76 | 0 | [11 empty] | 110 | 118 | 118 | 118 | 108 | 100 | 94 | 1205760
64 | Malancha, Ctg. EPZ (United) | 8 | 8 | 8 | 8 | 8 | 10 | 20 | 7 | 2 | 2 | 2 | 3 | 8 | 5 | 4 | 6 | 2 | 6 |  | 8 | 10 | 13 | 22 | 30 | 30 | 32 | 353280
65 | Feni 22MW PP (Doreen) | [14 empty] | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 223452
66 | Feni 11 MW PP (Doreen) | [14 empty] | 11 | 11 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 94140
67 | Jangalia 33MW PP (Summit) | 8 | [13 empty] | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 342200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 18 | 18 | 18 | 18 | 20 | 20 | 14 | 14 | 18 | 20 | 15 | 18 | 18 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 480300
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 21 | 24 | 21 | 21 | 30 | 30 | 30 | 23 | 24 | 24 | 28 |  | 31 | 31 | 31 | 31 | 31 | 22 | 31 | 645660
71 | Maona 33 MW PP(Summit) | 22 | 18 | 18 | 18 | 18 | 18 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 713400
72 | Rupganj 33 MW PP(Summit) | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 0 | 17 | 8 | 17 | 17 | 17 | 17 | 31 |  | 32 | 32 | 32 | 25 | 25 | 25 | 25 | 444600
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 5 | 48 |  | 40 | [6 empty] | 96960
78 | Gazipur 52 MW PP | [17 empty] | 2 |  | 8 | [6 empty] | 177840
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 0 | 16 | 16 | 53 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 72 | 40 | 16 | 0 |  |  |  | 948480
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [11 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 50 |  | 34 | 17 | [5 empty] | 177840
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.2 | 0.94 | 1.81 | 3.652 | 4.42 | 4.45 | 4.095 | 3.3 | 2.2 | 1 | 0 | [9 empty] | 26160
| Jodiac Power | [17 empty] | 23 |  | 53 | [6 empty] | 90874
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 23 |  | 10 | 10 | 10 |  |  |  |  | 75086
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 22 |  | 50 | [6 empty] | 103680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 0 | 10 | 10 | 10 | 10 | 35 | 100 |  | 100 | 100 | 100 | 100 | 60 | 10 | 10 | 540720
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 883800
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 18 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 735408
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 2 | 16 |  | 7 | 0 | 0 |  |  |  |  | 36000
95 | Patenga 50MW PP (Baraka) | [16 empty] | 3 | 45 |  | 50 | 18 | [5 empty] | 121440
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 27 |  | 60 | 98 | 98 | 98 | 53 | 0 |  | 336000
97 | Katpotti 52 MW PP (Sinha) | 12 | 6 | [7 empty] | 0 | 2 | 6 | 6 | 6 | 6 | 6 |  | 34 |  | 47 | 47 | 47 | 47 | 24 | 12 | 12 | 314928
98 | Bosila 108MW PP(CLC) | [16 empty] | 35 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 438720
99 | Madanganj-55 MW PP(Summit) | [15 empty] | 0 | 7 | 20 |  | 39 | 42 | 42 | 0 |  |  |  | 134979
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 10 | 55 |  | 55 | 55 | 35 |  |  |  |  | 156949
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 130 | 130 |  | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 3363938
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.6 | 1.3 | 1.7 | 1.8 | 1.8 | 1.7 | 1.2 | 0.7 | 0.3 | 0 | [9 empty] | 11200
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | 17 | [5 empty] | 49680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 19 | 86 |  | 100 | 142 | 132 | 165 | 130 | 130 | 0 | 880800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 15 | 76 |  | 100 | 100 | 100 | 80 | 0 |  |  | 360000
116 | Chandpur 200MW (Desh energy) | [6 empty] | 20 | 168 | 200 | 200 | 200 | 200 | 200 | 200 | 34 | 34 | 35 | 105 |  | 200 | 200 | 140 | 34 | 0 |  |  | 2339520
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 3 | 75 |  | 100 | 100 | 100 | 100 | 30 | 0 |  | 471709
118 | Bibiyana-III 400 MW CCPP | 320 | 299 | 293 | 299 | 309 | 368 | 396 | 366 | 366 | 369 | 401 | 397 | 376 | 368 | 366 | 367 | 365 | 380 |  | 367 | 366 | 370 | 366 | 375 | 361 | 365 | 8645000
Jamalpur 115 MW PP (United)
Anwara 300 MW PP (United)
120 | Eastern Zone Total | 4444 | 4193 | 4116 | 3897 | 3908 | 3962 | 4293.9 | 4597.11 | 4632.48 | 4553.252 | 4662.73 | 5034.79 | 5048.125 | 4970.3 | 5047.7 | 5087.4 | 5206.2 | 6341 |  | 6729 | 6597 | 6365 | 6147 | 5657 | 5438 | 5121 | 121734860
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 17 | 0 |  |  |  |  | 176160
130
131
132
133
| Barisal 110 MW PP (Summit ) | [7 empty] | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 32 |  | 32 | 32 | 32 | 32 | 16 | 0 |  | 813024
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [16 empty] | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 76335
| Bhola 225 MW CCPP | 153 | 153 | 152 | 152 | 152 | 152 | 152 | 152 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 |  | 153 | 153 | 153 | 153 | 153 | 152 | 153 | 3727752
140 | Bhola 33 MW PP (Venture) | 20 | 18 | 17 | 16 | 15 | 16 | 15 | 18 | 16 | 16 | 17 | 17 | 18 | 19 | 15 | 17 | 18 | 24 |  | 25 | 25 | 26 | 27 | 25 | 23 | 23 | 446600
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 16 | 40 |  | 40 | 40 | 32 | 32 | 0 |  |  | 165000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 17 | 17 |  | 17 | 17 | 18 | 4 | 0 |  |  | 68544
146 | Bheramara HVDC | 114 | 91 | 91 | 91 | 90 | 91 | 89 | 90 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 437 |  | 438 | 438 | 438 | 438 | 438 | 193 | 193 | 5088727
147 | Bheramara 360 MW CCPP | 353 | 315 | 310 | 335 | 300 | 335 | 360 | 320 | 315 | 325 | 345 | 355 | 325 | 310 | 310 | 310 | 310 | 330 |  | 305 | 310 | 315 | 310 | 330 | 305 | 310 | 7937280
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 201 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 199 | 200 | 200 | 4888900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 188 | 187 | 181 | 178 | 185 | 192 | 190 | 195 | 193 | 189 | 188 | 205 | 207 | 197 | 205 | 201 | 202 | 204 |  | 200 | 193 | 199 | 203 | 200 | 202 | 198 | 4992582
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 191 | 191 | 190 | 190 | 189 | 187 | 191 | 197 | 213 | 190 | 185 | 190 | 206 | 203 | 194 | 193 | 196 | 185 |  | 182 | 183 | 190 | 200 | 199 | 206 | 206 | 4921555
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 381 | 381 | 380 | 381 | 380 | 432 | 434 | 432 | 347 | 390 | 400 | 397 | 396 | 340 | 405 | 350 | 365 | 401 |  | 365 | 401 | 388 | 424 | 431 | 431 | 422 | 9534545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 368160
163 | Bogura 20 MW PP (Energyprima) | 4 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 259992
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 231048
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 0 | 12 | 0 | [5 empty] | 20 | 50 |  | 50 | 25 | 12 | 0 |  |  |  | 159380
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 25 |  | 0 | 0 | [5 empty] | 33120
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 6 | 97 |  | 110 | 113 | 113 | 113 | 50 | 50 | 0 | 620352
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 5 | 13 |  | 50 | 50 | 50 | 35 | 0 |  |  | 179520
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.2 | 1.1 | 2.4 | 3.9 | 3.4 | 4.1 | 3.9 | 2.8 | 1.9 | 0.7 | 0.1 |  |  | 0 | [6 empty] | 24075
178
178