## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-03 | Tuesday
|  | Date (day): | 2019-12-03 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11415.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13845 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-02 | 2019-12-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 158 | 188 | 150 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under S/D
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  |  | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  |  | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 110 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 380 | 353 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 322 | 332 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 87 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 234 | 236 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 57 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 33 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 150 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1705 | 2305 | 3663 | 4204 | 520 | 461
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 24 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 91 | 94 | 94 | 94 | 136 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 108 | 144 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 11 | 5 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 82 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 557.2 | 1006 | 1472 | 1632 | 396 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 120 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 130 | 100 | 130 | 4
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 129 | 131 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under S/D
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 120 | 102 | 102 | 75 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 100 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 9 | 8 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 80 | 95 | 95 |  |  | ST under S/D
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 120 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 112 | 104 | 133
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 21 | 21
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1110 | 1364 | 1561 | 2012 | 223 | 376
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 123 | 162 | 164 | 164 | 38 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 14 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.8 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 200 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 186.8 | 398 | 497.6 | 596 | 38 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 60 | 60 | 60
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  |  | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 69 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 35 | 39 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 406 | 365 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1195 | 1251 | 1366 | 1366 | 0 | 162
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 298 | 445 | 300 | 449
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 2 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 235 | 225 | 270 | 270 |  |  | ST under S/D
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 0 | 20 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 552 | 710 | 710 | 1529 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 18 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 178 | 153 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 20 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 222 | 191 | 371 | 441 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 40 | 0 | 0 | 0 |  |  | Under maint.
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 203 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 191 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 424 | 407 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 15 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 111 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 933 | 1060 | 1454 | 1718 | 320 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 57 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 204.6 | 257 | 321 | 347 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6665.6 | 8542 | 11415.6 | 13845 | 1497 | 1282
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6343.3227 | 8129 | 10863.6634 | 13175.6035
A. |  | 2019-12-02 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 8542 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5471 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8542 | MW
3 | Day peak Generation : |  |  | 6665.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8129 | MW
4 | Evening peak Generation : |  |  | 8542 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 162.5051 | MKWHr | By Solar | 0.12229 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 139.4416 | MKWHr |  | By Oil: | 7.1513 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.8861 | MKWHr |  | By Hydro: | 2.2249 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1497 | MW | Dhaka | 3215 | 3215 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1282 | MW | Chittagong | 772 | 772 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2779 | MW | Khulna | 958 | 958 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1153.25 | MMCFD |  |  | Rajshahi | 823 | 823 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 131847374.716 | ii) Oil : | Taka | 67056987.78 | Comilla | 714 | 714 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19984149 | Total | Taka | 218888511.496 | Mymensingh | 643 | 643 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.8615 | MKWHr. | Sylhet | 319 | 319 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -370 | MW (E to W) at | 19:00 | hrs | Barisal | 210 | 210 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -380 | MW at | 20:00 | hrs | Rangpur | 475 | 475 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.9° C |  |  | Total | 8129 | 8129 |  | 0
B. |  | 2019-12-03 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 26.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13845 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6800 | MW
4 | Reserve(Generation end) |  |  |  | 5145 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 165.5109 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5287 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 6.5055 | MKWHr. | ii) HVDC Flow at Peak Time |  | 445 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1734 | MKWHr. | iii) Maximum HVDC Flow : |  | 446 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.73 |  | (b) Today: | 99.49 |  | (c) Rule Curve: |  | 105.82
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 188 | 0 | 0 | 0 | 109 | 0 | 345 | 366 |  | 0 | 380 | 0 | 0 | 0 | 0 | 237 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 202 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 120 | 0 | 0 | 0 | 265 | 134 | 148 | 83 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 98 | 161 | 0 | 0 | 0 | 60 | 56 | 2 | 2 | 130 | 0 | 40 | 40 | 0 | 0 | 0 | 6 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4465 | 1564 | 6029 | 3601 | 140 | 1889 | 6 | 200 | 95 | 0 | 98 | 0 | 0 | 99.75
2:00 | 35 | 189 | 0 | 0 | 0 | 53 | 0 | 360 | 331 |  | 0 | 380 | 0 | 0 | 0 | 0 | 233 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 211 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 120 | 0 | 0 | 0 | 275 | 134 | 52 | 80 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 84 | 161 | 0 | 0 | 0 | 60 | 56 | 2 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4272 | 1479 | 5751 | 3561 | 140 | 1672 | 0 | 200 | 94 | 0 | 84 | 0 | 0 | 99.75
3:00 | 35 | 189 | 0 | 0 | 0 | 13 | 0 | 349 | 331 |  | 0 | 360 | 0 | 0 | 0 | 0 | 238 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 204 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 120 | 0 | 0 | 0 | 265 | 135 | 52 | 82 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 78 | 163 | 0 | 0 | 0 | 60 | 56 | 2 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4161 | 1516 | 5677 | 3610 | 140 | 1555 | 0 | 200 | 94 | 0 | 78 | 0 | 0 | 99.74
4:00 | 35 | 158 | 0 | 0 | 0 | 13 | 0 | 344 | 303 |  | 0 | 330 | 0 | 0 | 0 | 0 | 235 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 32 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 120 | 0 | 0 | 0 | 275 | 135 | 28 | 86 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 78 | 163 | 0 | 0 | 0 | 60 | 56 | 2 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3969 | 1543 | 5512 | 3526 | 140 | 1475 | 0 | 200 | 93 | 0 | 78 | 0 | 0 | 99.74
5:00 | 35 | 159 | 0 | 0 | 0 | 13 | 0 | 342 | 283 |  | 0 | 330 | 0 | 0 | 0 | 0 | 236 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 25 | 32 | 0 | 0 | 43 | 50 | 0 | 90 | 0 | 211 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 120 | 0 | 0 | 0 | 265 | 135 | 28 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 163 | 0 | 0 | 0 | 60 | 56 | 2 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3941 | 1530 | 5471 | 3494 | 140 | 1468 | 0 | 200 | 93 | 0 | 76 | 0 | 0 | 99.73
6:00 | 35 | 159 | 0 | 0 | 0 | 13 | 0 | 365 | 303 |  | 0 | 360 | 0 | 0 | 0 | 0 | 236 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 25 | 32 | 0 | 0 | 42 | 50 | 0 | 90 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 120 | 0 | 0 | 0 | 265 | 135 | 28 | 91 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 163 | 0 | 0 | 0 | 60 | 56 | 2 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4013 | 1586 | 5599 | 3595 | 140 | 1496 | 0 | 200 | 92 | 0 | 76 | 0 | 0 | 99.73
7:00 | 35 | 159 | 0 | 0 | 0 | 13 | 0 | 363 | 313 |  | 0 | 380 | 0 | 0 | 0 | 0 | 235 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 25 | 32 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 223 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 120 | 0 | 0 | 0 | 305 | 136 | 28 | 90 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 162 | 0 | 0 | 0.1 | 60 | 64 | 2 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 |  | 140 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4203.2 | 1632.1 | 5835.3 | 3713 | 140 | 1613 | 0 | 200 | 90 | 0 | 76 | 3.3 | 0 | 99.72
8:00 | 35 | 159 | 0 | 0 | 0 | 25 | 0 | 381 | 313 |  | 0 | 420 | 0 | 0 | 0 | 0 | 236 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 25 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 120 | 0 | 0 | 0 | 315 | 134 | 102 | 90 | 33 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 8 | 20 | 14 | 80 | 162 | 0 | 22 | 0.5 | 60 | 56 | 28 | 19 | 130 | 0 | 69 | 50 | 0 | 0 | 17 | 36 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 7.7 | 0 | 0 | 0 | 363 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 140 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 12 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 4649.2 | 1674.6 | 6323.8 | 3894 | 140 | 1895 | 15 | 200 | 90 | 0 | 80 | 9.8 | 0 | 99.72
9:00 | 35 | 159 | 0 | 0 | 0 | 52 | 0 | 330 | 282 |  | 0 | 380 | 0 | 0 | 0 | 0 | 238 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 31 | 0 | 17 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 204 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 120 | 0 | 55 | 0 | 310 | 135 | 102 | 82 | 33 | 0 | 0 | 35 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 82 | 162 | 0 | 22 | 1.1 | 60 | 56 | 53 | 50 | 100 | 0 | 67 | 50 | 0 | 0 | 17 | 37 | 10 | 280 | 16 | 11 | 0 | 7 | 0 | 0 | 40 | 0 | 0 | 14.5 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 1.6 | 0 | 0 | 0 | 0 |  | 297 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 12 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 377 | 17 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 |  | 4616.2 | 1835.3 | 6451.5 | 3780 | 297 | 1862 | 121 | 200 | 90 | 0 | 82 | 19.5 | 0 | 99.71
10:00 | 35 | 159 | 0 | 0 | 0 | 52 | 0 | 300 | 282 |  | 0 | 380 | 0 | 0 | 0 | 0 | 200 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 197 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 120 | 0 | 55 | 0 | 315 | 133 | 102 | 91 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 33 | 16 | 80 | 157 | 0 | 22 | 1.5 | 60 | 64 | 53 | 50 | 100 | 0 | 65 | 10 | 0 | 0 | 17 | 37 | 10 | 285 | 16 | 11 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 2.7 | 0 | 0 | 0 | 0 |  | 297 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 11 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 390 | 17 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 |  | 4524.2 | 1826.6 | 6350.8 | 3700 | 297 | 1847 | 129 | 200 | 90 | 0 | 80 | 7.8 | 0 | 99.71
11:00 | 35 | 159 | 0 | 0 | 0 | 52 | 0 | 370 | 284 |  | 0 | 380 | 0 | 0 | 0 | 0 | 138 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 50 | 0 | 90 | 0 | 195 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 120 | 0 | 80 | 0 | 305 | 130 | 102 | 90 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 82 | 157 | 0 | 22 | 1.8 | 59 | 60 | 53 | 50 | 100 | 0 | 65 | 10 | 0 | 0 | 17 | 34 | 10 | 305 | 15 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17 | 4.3 | 0 | 0 | 0 | 0 |  | 297 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 177 | 11 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 432 | 17 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4600.1 | 1926.2 | 6526.3 | 3809 | 297 | 1908 | 129 | 200 | 90 | 1 | 82 | 10.3 | 0 | 99.7
12:00 | 35 | 158 | 0 | 0 | 0 | 52 | 0 | 380 | 322 |  | 0 | 380 | 0 | 0 | 0 | 0 | 180 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 50 | 0 | 90 | 0 | 218 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 120 | 0 | 80 | 0 | 355 | 129 | 102 | 90 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 84 | 123 | 0 | 22 | 1.8 | 60 | 60 | 53 | 50 | 100 | 0 | 63 | 10 | 0 | 0 | 17 | 35 | 10 | 305 | 15 | 11 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 5.2 | 0 | 0 | 0 | 0 |  | 298 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 178 | 12 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 424 | 17 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 |  | 4754 | 1911.6 | 6665.6 | 3907 | 298 | 1943 | 129 | 200 | 91 | 2 | 84 | 11.6 | 0 | 99.69
13:00 | 35 | 159 | 0 | 0 | 0 | 100 | 0 | 380 | 361 |  | 0 | 450 | 0 | 0 | 0 | 0 | 230 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 42 | 50 | 0 | 90 | 0 | 209 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 120 | 0 | 80 | 0 | 355 | 129 | 120 | 88 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 90 | 124 | 0 | 22 | 1.7 | 60 | 56 | 53 | 50 | 163 | 0 | 65 | 72 | 0 | 0 | 17 | 37 | 10 | 310 | 24 | 8 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 3.14 | 0 | 0 | 0 | 0 |  | 297 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 176 | 12 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 423 | 17 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 5158.84 | 1860.2 | 7019.04 | 3930 | 297 | 2254 | 145 | 200 | 92 | 2 | 90 | 9.04 | 0 | 99.69
14:00 | 35 | 160 | 0 | 0 | 0 | 107 | 0 | 365 | 333 |  | 0 | 420 | 0 | 0 | 0 | 0 | 224 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 33 | 25 | 0 | 0 | 42 | 50 | 0 | 90 | 0 | 212 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 120 | 0 | 80 | 0 | 290 | 129 | 120 | 90 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 19 | 8 | 33 | 14 | 92 | 153 | 0 | 22 | 1.4 | 60 | 60 | 53 | 50 | 100 | 0 | 64 | 72 | 0 | 0 | 17 | 37 | 10 | 275 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 15.7 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 298 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 177 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 |  | 4825.1 | 1741.5 | 6566.6 | 3739 | 298 | 2089 | 24 | 200 | 92 | 11 | 92 | 21.6 | 0 | 99.69
15:00 | 35 | 159 | 0 | 0 | 0 | 107 | 0 | 370 | 333 |  | 0 | 420 | 0 | 0 | 0 | 0 | 229 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 120 | 0 | 80 | 0 | 270 | 129 | 120 | 90 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 19 | 5 | 33 | 18 | 90 | 155 | 0 | 22 | 0.9 | 60 | 60 | 53 | 50 | 130 | 0 | 65 | 73 | 0 | 0 | 17 | 38 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 12.3 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 |  | 299 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 175 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4858.9 | 1756.8 | 6615.7 | 3713 | 299 | 2166 | 24 | 200 | 94 | 12 | 90 | 17.7 | 0 | 99.69
16:00 | 35 | 159 | 0 | 0 | 0 | 107 | 0 | 355 | 333 |  | 0 | 420 | 0 | 0 | 0 | 0 | 228 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 120 | 0 | 80 | 0 | 260 | 131 | 120 | 90 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 19 | 8 | 33 | 12 | 86 | 156 | 0 | 20 | 0.3 | 59 | 56 | 53 | 49 | 130 | 0 | 65 | 73 | 0 | 0 | 17 | 38 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 5.9 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 |  | 298 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 |  | 4819.5 | 1728.8 | 6548.3 | 3658 | 298 | 2173 | 24 | 200 | 94 | 8 | 86 | 7.3 | 0 | 99.68
17:00 | 35 | 178 | 0 | 0 | 0 | 107 | 0 | 362 | 303 |  | 0 | 380 | 0 | 0 | 0 | 0 | 227 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | 0 | 14 | 19 | 25 | 31 | 33 | 33 | 3 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 28 | 3 | 1 | 19 | 6 | 120 | 0 | 80 | 0 | 265 | 131 | 120 | 85 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 19 | 8 | 33 | 18 | 98 | 158 | 0 | 22 | 0 | 59 | 60 | 53 | 46 | 130 | 0 | 68 | 76 | 0 | 0 | 17 | 38 | 10 | 310 | 24 | 8 | 0 | 15 | 0 | 0 | 86 | 0 | 0 | 0 | 10 | 10 | 5 | 340 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 167 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 186 | 0 | 0 | 0 | 10 | 0 | 195 | 0 | 427 | 0 | 0 | 8 | 0 | 30 | 0 | 0.1 | 0 |  | 5007 | 1867.1 | 6874.1 | 3774 | 299 | 2108 | 293 | 200 | 94 | 8 | 98 | 0.1 | 0 | 99.67
18:00 | 35 | 189 | 0 | 0 | 0 | 110 | 0 | 367 | 332 |  | 0 | 400 | 0 | 0 | 0 | 15 | 228 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 30 | 17 | 17 | 35 | 19 | 25 | 24 | 33 | 33 | 33 | 0 | 44 | 50 | 0 | 90 | 0 | 216 | 0 | 145 | 0 |  | 0 | 0 | 0 | 100 | 33 | 18 | 19 | 6 | 120 | 0 | 130 | 0 | 330 | 131 | 128 | 90 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 18 | 112 | 160 | 0 | 22 | 0 | 59 | 60 | 53 | 50 | 130 | 0 | 67 | 76 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 8 | 0 | 115 | 0 | 0 | 160 | 0 | 0 | 0 | 75 | 80 | 60 | 396 | 0 | 0 | 105 | 0 | 0 | 9 | 15 | 0 |  | 445 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 177 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 200 | 0 | 0 | 194 | 0 | 0 | 0 | 30 | 0 | 191 | 0 | 423 | 0 | 0 | 87 | 0 | 54 | 0 | 0 | 3 |  | 6135 | 2185 | 8320 | 4053 | 445 | 2185 | 1223 | 200 | 94 | 8 | 112 | 0 | 0 | 99.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 188 | 0 | 0 | 0 | 110 | 0 | 353 | 332 |  | 0 | 400 | 0 | 0 | 0 | 15 | 234 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 17 | 55 | 35 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 82 | 24 | 19 | 11 | 120 | 0 | 130 | 0 | 305 | 131 | 120 | 80 | 37 | 0 | 0 | 43 | 0 | 9 | 0 | 22 | 11 | 33 | 21 | 112 | 162 | 14 | 22 | 0 | 60 | 60 | 53 | 50 | 130 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 290 | 24 | 8 | 0 | 150 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 120 | 70 | 365 | 0 | 0 | 105 | 0 | 0 | 17 | 17 | 0 |  | 445 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 20 | 0 | 191 | 0 | 407 | 0 | 0 | 111 | 0 | 57 | 0 | 0 | 50 |  | 6324 | 2218 | 8542 | 3955 | 445 | 2146 | 1581 | 200 | 94 | 9 | 112 | 0 | 0 | 99.66
19:30 | 35 | 188 | 0 | 0 | 0 | 110 | 0 | 340 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 35 | 35 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 52 | 9 | 19 | 18 | 120 | 0 | 130 | 0 | 325 | 131 | 120 | 90 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 21 | 112 | 147 | 16 | 22 | 0 | 60 | 60 | 53 | 50 | 130 | 0 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 310 | 24 | 8 | 0 | 145 | 0 | 0 | 200 | 0 | 0 | 0 | 50 | 70 | 35 | 373 | 0 | 0 | 105 | 0 | 0 | 17 | 3 | 0 |  | 445 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 176 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 193 | 0 | 0 | 0 | 32 | 0 | 190 | 0 | 441 | 0 | 0 | 113 | 0 | 57 | 0 | 0 | 70 |  | 6073 | 2271 | 8344 | 3972 | 445 | 2218 | 1295 | 200 | 94 | 8 | 112 | 0 | 0 | 0
20:00 | 35 | 209 | 0 | 0 | 0 | 110 | 0 | 346 | 331 |  | 0 | 400 | 0 | 0 | 0 | 0 | 234 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 35 | 35 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 52 | 12 | 19 | 20 | 120 | 0 | 130 | 0 | 305 | 131 | 128 | 83 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 21 | 118 | 148 | 16 | 22 | 0 | 60 | 56 | 53 | 50 | 130 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 200 | 0 | 0 | 0 | 50 | 70 | 30 | 363 | 0 | 0 | 105 | 0 | 0 | 17 | 0 | 0 |  | 445 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 154 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 198 | 0 | 0 | 0 | 32 | 0 | 190 | 0 | 407 | 0 | 0 | 113 | 0 | 57 | 0 | 0 | 40 |  | 6068 | 2191 | 8259 | 3950 | 445 | 2184 | 1260 | 200 | 94 | 8 | 118 | 0 | 0 | 99.65
21:00 | 35 | 240 | 0 | 0 | 0 | 107 | 0 | 349 | 333 |  | 0 | 400 | 0 | 0 | 0 | 0 | 234 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 50 | 50 | 0 | 19 | 32 | 120 | 0 | 130 | 0 | 310 | 131 | 128 | 90 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 21 | 114 | 148 | 0 | 22 | 0 | 60 | 56 | 53 | 50 | 130 | 0 | 69 | 76 | 0 | 0 | 17 | 40 | 10 | 300 | 24 | 11 | 0 | 80 | 0 | 0 | 200 | 0 | 0 | 0 | 10 | 0 | 30 | 364 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 446 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 177 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 61 | 0 | 186 | 0 | 444 | 0 | 0 | 113 | 0 | 35 | 0 | 0 | 0 |  | 5758 | 2199 | 7957 | 4011 | 446 | 2263 | 821 | 200 | 94 | 8 | 114 | 0 | 0 | 99.64
22:00 | 35 | 238 | 0 | 0 | 0 | 109 | 0 | 344 | 322 |  | 0 | 400 | 0 | 0 | 0 | 0 | 236 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 20 | 120 | 0 | 130 | 0 | 305 | 131 | 120 | 80 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 21 | 106 | 148 | 0 | 22 | 0 | 60 | 28 | 53 | 50 | 130 | 0 | 69 | 76 | 0 | 0 | 17 | 40 | 10 | 295 | 24 | 11 | 0 | 15 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 445 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 62 | 0 | 190 | 0 | 443 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 |  | 5333 | 2026 | 7359 | 3955 | 445 | 2228 | 323 | 200 | 94 | 8 | 106 | 0 | 0 | 99.63
23:00 | 35 | 235 | 0 | 0 | 0 | 110 | 0 | 344 | 317 |  | 0 | 400 | 0 | 0 | 0 | 0 | 235 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 212 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 120 | 0 | 130 | 0 | 335 | 131 | 128 | 84 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 0 | 0 | 21 | 98 | 148 | 0 | 22 | 0 | 60 | 58 | 53 | 50 | 130 | 0 | 70 | 76 | 0 | 0 | 17 | 40 | 10 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 204 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 199 | 0 | 0 | 0 | 62 | 0 | 190 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5051 | 1720 | 6771 | 3952 | 204 | 2191 | 23 | 200 | 95 | 8 | 98 | 0 | 0 | 99.62
24:00 | 35 | 233 | 0 | 0 | 0 | 110 | 0 | 347 | 305 |  | 0 | 380 | 0 | 0 | 0 | 0 | 240 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 50 | 0 | 90 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 24 | 120 | 0 | 130 | 0 | 310 | 131 | 120 | 80 | 37 | 0 | 0 | 43 | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 90 | 149 | 0 | 0 | 0 | 60 | 58 | 53 | 50 | 130 | 0 | 70 | 76 | 0 | 0 | 0 | 10 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 174 | 0 | 0 | 0 | 57 | 0 | 184 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4842 | 1562 | 6404 | 3800 | 202 | 2009 | 0 | 200 | 95 | 8 | 90 | 0 | 0 | 99.61
KWH | 711000 | 4581800 | 0 | 0 | 0 | 1693636 | 0 | 8616930 | 7604000 |  | 0 | 9350250 | 0 | 0 | 0 | 36984 | 5536311 | 0 | 1586000 | 0 | 0 | 0 | 0 | 0 | 336000 | 0 | 216288 | 43668 | 98417 | 128595 | 258228 | 600000 | 697500 | 727000 | 744300 | 74469 | 0 | 1032873 | 1192000 | 0 | 2100000 | 0 | 4864315 | 0 | 3018774 | 0 |  | 0 | 0 | 0 | 413640 | 248640 | 56640 | 439056 | 381120 | 2955914 | 0 | 1502700 | 0 | 7289500 | 3207000 | 2375272 | 2073770 | 787032 | 0 | 0 | 759368 | 0 | 104512 | 0 | 334080 | 126900 | 500200 | 430400 | 2173440 | 3646160 | 34560 | 368460 | 11300 | 1428000 | 1370520 | 874800 | 869832 | 3159572 | 0 | 1407680 | 1128960 | 0 | 0 | 299000 | 661700 | 169740 | 7578300 | 328536 | 131128 | 0 | 750218 | 0 | 0 | 1432800 | 0 | 0 | 61425 | 218880 | 328800 | 244218 | 8805000 | 0 | 0 | 725127 | 24720 | 0 | 46438 | 45999 | 0 |  | 6505455 | 0 | 5646240 | 0 | 0 | 0 | 0 | 0 | 0 | 9344 | 182625 | 4167076 | 333900 | 168960 | 0 | 0 | 605000 | 0 | 0 | 0 | 143790 | 0 | 0 | 0 | 0 | 317760 | 228564 | 226278 | 0 | 0 | 4886100 | 0 | 0 | 4881300 | 0 | 0 | 0 | 312951 | 0 | 4901264 | 0 | 9741545 | 91200 | 0 | 550656 | 0 | 265920 | 0 | 24840 | 153888 |  | 118160395 | 44344656 | 162505051 | 91900352 | 6505455 | 47541270 | 7037420 | 4886100 | 2224873 | 113856 | 2173440 | 122285 | 0
Fuel Cost | 796320 | 4948344 | 0 | 0 | 0 | 1642826.92 | 0 | 6204189.6 | 5779040 |  | 0 | 7480200 | 0 | 0 | 0 | 379455.84 | 6865025.64 | 0 | 1982500 | 0 | 0 | 0 | 0 | 0 | 3057600 | 0 | 2024455.68 | 418776.12 | 938898.18 | 1280806.2 | 193671 | 450000 | 0 | 0 | 0 | 713413.02 | 0 | 268546.98 | 309920 | 0 | 3213000 | 0 | 5107530.75 | 0 | 3833842.98 | 0 |  | 0 | 0 | 0 | 4256355.6 | 2364566.4 | 530150.4 | 403931.52 | 1059513.6 | 3103709.7 | 0 | 1577835 | 0 | 6123180 | 2950440 | 2327766.56 | 2758114.1 | 645366.24 | 0 | 0 | 1085896.24 | 0 | 1224880.64 | 0 | 340761.6 | 95175 | 945378 | 322800 | 14996736 | 2989851.2 | 328665.6 | 375829.2 | 185320 | 1942080 | 1863907.2 | 1189728 | 1087290 | 3917869.28 | 0 | 2097443.2 | 1986969.6 | 0 | 0 | 475410 | 774189 | 398889 | 5380593 | 246402 | 99657.28 | 0 | 7854782.46 | 0 | 0 | 13783536 | 0 | 0 | 708844.5 | 2039961.6 | 3084144 | 2288322.66 | 8276700 | 0 | 0 | 6852450.15 | 0 | 0 | 0 | 0 | 0 |  | 17564728.5 | 0 | 4404067.2 | 0 | 0 | 0 | 0 | 0 | 0 | 122406.4 | 1806161.25 | 3333660.8 | 517545 | 1814630.4 | 0 | 0 | 1137400 | 0 | 0 | 0 | 1491102.3 | 0 | 0 | 0 | 0 | 349536 | 377130.6 | 171292.446 | 0 | 0 | 19984149 | 0 | 0 | 4295544 | 0 | 0 | 0 | 497592.09 | 0 | 4313112.32 | 0 | 7111327.85 | 862752 | 0 | 5055022.08 | 0 | 2483692.8 | 0 | 0 | 0 |  | 175229754.44 | 77692853.036 | 252922607.476 | 88883471.976 | 17564728.5 | 42963902.74 | 65709700.74 | 19984149 | 578466.98 | 1347287.04 | 14996736 | 894164.5 | 0
Yesterday Day Peak | 35 | 158 | 0 | 0 | 0 | 52 | 0 | 380 | 322 |  | 0 | 380 | 0 | 0 | 0 | 0 | 180 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 41 | 50 | 0 | 90 | 0 | 218 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 120 | 0 | 80 | 0 | 355 | 129 | 102 | 90 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 84 | 123 | 0 | 22 | 1.8 | 60 | 60 | 53 | 50 | 100 | 0 | 63 | 10 | 0 | 0 | 17 | 35 | 10 | 305 | 15 | 11 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 5.2 | 0 | 0 | 0 | 0 |  | 298 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 178 | 12 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 424 | 17 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 |  | 6665.6 | DayPeak
Yesterday Evening Peak | 35 | 188 | 0 | 0 | 0 | 110 | 0 | 353 | 332 | 0 | 0 | 400 | 0 | 0 | 0 | 15 | 234 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 17 | 55 | 35 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 100 | 82 | 24 | 19 | 11 | 120 | 0 | 130 | 0 | 305 | 131 | 120 | 80 | 37 | 0 | 0 | 43 | 0 | 9 | 0 | 22 | 11 | 33 | 21 | 112 | 162 | 14 | 22 | 0 | 60 | 60 | 53 | 50 | 130 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 290 | 24 | 8 | 0 | 150 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 120 | 70 | 365 | 0 | 0 | 105 | 0 | 0 | 17 | 17 | 0 |  | 445 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 153 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 20 | 0 | 191 | 0 | 407 | 0 | 0 | 111 | 0 | 57 | 0 | 0 | 50 |  | 8542 | EvPeak
Forecast for Evening | 35 | 190 | 0 | 0 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 50 | 0 | 100 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 10 | 120 | 0 | 130 | 0 | 360 | 200 | 102 | 95 | 37 | 55 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 133 | 164 | 95 | 22 | 0 | 60 | 60 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 449 | 40 | 270 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 26 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 210 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 150 | 0 | 0 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 236 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 52 | 0 | 44 | 50 | 0 | 100 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 5 | 120 | 0 | 100 | 0 | 360 | 200 | 102 | 95 | 37 | 55 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 21 | 104 | 164 | 95 | 22 | 1.6 | 60 | 60 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 0 |  | 300 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 210 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 0 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 0 | 114 | 0 | 0 | 0 | 65 | 0 | 363 | 370 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 240 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 44 | 50 | 0 | 90 | 0 | 203 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 330 | 46 | 8 | 90 | 30 | 0 | 0 | 43 | 0 | 8 | 0 | 22 | 8 | 25 | 16 | 76 | 164 | 0 | 20 | 0.2 | 60 | 60 | 50 | 50 | 163 | 0 | 37 | 71 | 0 | 0 | 17 | 31 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 8.7 | 0 | 0 | 0 | 362 | 0 | 0 | 5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 8 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 0 | 0 | 11 | 0 | 208 | 0 | 429 | 17 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0
199
| Minimum Generation |  | 5471 | 5:00
| Highest Generation |  | 8542 | 19:00
| Day Peak Generation |  | 6665.6 | 12:00
| Evening Peak Generation |  | 8542 | 19:00
| HVDC Max Flow |  | 446 | 21:00
| HVDC EvPeak Flow |  | 445 | 19:00
| Load factor L.F |  | 79.27%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-03
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6665.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5287 | MW
Evening Peak Generation : |  | 8542 | MW Hour : | 19:00 | Available Max Generation : |  | 13855 | MW
E.P. Demand (at gen end) : |  | 8542 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8542 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4855 | MW
Total Gen. (MKWH) : |  | 162.5051 | System Load Factor : | 79.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -380 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-03
Actual : | 99.49 | Ft.(MSL) , | Rule curve : | 105.82 | Ft.( MSL )
Gas Consumed : | Total = | 1143.38 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 131847374.716
: |  | Coal : | 19984149 | Oil : | 67056987.78 | Total : | 218888511.496
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3199.319 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1082.518 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 968.9331 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 875.1694 |  |  | 0 | 0%
) | 0 | 0:00 | 791.0673 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 638.3496 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 363.9181 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 164.5427 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 492.2935 |  |  | 0 | 0%
Total | 0 |  | 8576.1106 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,4
4) Ashuganj unit-4
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Barapukuria ST: unit-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Joydevpur 132/33 kV T-4 transformer was under shut down from 09:11 to 15:33 for A/M.
b) Bakulia 132 kV Bus-B was under shut down from 08:38 to 12:07 for A/M.
c) Hathazari-Kaptai 132 kV Ckt-2 was under shut down from 08:30 to 15:41 for A/M.
d) Kaliakoir-Tangail 132 kV Ckt-2 was under shut down from 08:22 to 15:44 for A/M.
e) Cumilla(N) 230/132 kV T-O1 transformer was under shut down from 08:13 to 15:24 for A/M.
f) Netrokona-Mymensingh 132 kV Ckt-1 was under shut down from 08:17 to 16:09 for A/M.
g) Mymensingh-Jamalpur 132 kV Ckt-1 was under shut down from 09:11 to 16:28 for A/M.
h) Ashuganj-Kishorganj 132 kV Ckt-1 was under shut down from 08:38 to 15:49 for A/M.
i) Manikganj-Kabirpur 132 kV Ckt-2 & Manikgabj 132/33 kV T2 trabsformer were under shut down
from 08:25 to 16:40 for A/M.
j) Sreemangal 132/33 kV T2 transformer was under shut down from 09:15 to 15:08 for A/M.
k) Haripur 230 kV Busbar-2 was under shut down from 09:40 to 14:50 for A/M.
l) Naogaon-Niyamtpur 132 kV Ckt was under shut down from 08:11 to 16:46 for A/M. |  |  |  |  | About 18 MW power interruption occurred under Naogaon S/S area
from 08:11 to 16:51.
m) GK project 132/33 kV T-1 transformer was under shut down from 08:11 to 13:19 for A/M.
n) Baghabari-Ishwardi 230 kV Ckt-1 was under shut down from 08:45 to 17:39 for A/M.
o) Khulna(s)-Khulna© 132 kV Ckt-1 was under shut down from 08:34 to 15:18 for A/M.
p) Gopalganj-Madaripur 132 kV Ckt-1 was under shut down from 08:29 to 16:04 for A/M.
q) Bheramara HVDC-Bahrampur 400 kV Ckt-2 was under shut down from 09:18 to 17:06 for A/M.
r) Ashuganj unit-5 was synchronized at 08:12.
s) Feni 132/33 kV T2 transformer was under shut down from 12:27 to 13L:44 for oil leakage from
132 kV R-phase bushing.
t) Siddhirganj GT-1 was synchronized at 15:16.
u) Siddhirganj GT-2 was synchronized at 15:22.
v) Aminbazar 230/132 kV TR-1 transformer was shut down at 07:12(03/12/19) for A/M.
w) Comilla(N) 230/132 kV TR-2 transformer was shut down at 07:40(03/12/19) for A/M.
x) Ghorasal unit-2 tripped at 02:50(03/12/2019) due toline leakage & breakage of steam line diaphram.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 711000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 188 | 4581800
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 1693636
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8616930 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 332 | 7604000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9350250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 36984 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 258228
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 87 | 1586000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 234 | 5536311 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 216288
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 43668 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 98417
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 128595 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 336000 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1297500 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 727000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 744300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 33 | 74469 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 150 | 750218 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2305 | 44391594
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 61425
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 56640 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 94 | 2224873 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4864315 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 144 | 3018774 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 725127
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 413640
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 218880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 439056
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 11 | 381120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 248640 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24720
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 46438 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 45999 | Low demand
| Chattogram area Total |  |  |  | 2166 | 1006 | 14869647
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2955914 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 130 | 1502700
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 131 | 3207000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7289500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 787032 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 120 | 2375272 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 759368 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 244218 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 9 | 104512 | Low demand
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2073770 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 328800 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 334080
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 126900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 2173440
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 500200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 430400 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1364 | 25193106
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 162 | 3646160 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 368460
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 14 | 34560 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11300
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 1432800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 398 | 5493280
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1428000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1370520
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3159572 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 874800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 869832
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 131128
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1407680 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1128960 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 299000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 39 | 661700 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 328536
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7578300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 365 | 8805000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 169740
| Sylhet Area Total |  |  |  | 1949 | 1251 | 28212768
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 445 | 6505455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9344 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 225 | 5646240 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 182625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 91200 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 710 | 12434864
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 168960 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 18 | 333900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 153 | 4167076 | Line over load
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 20 | 312951 | Line over load
| Barisal Area Total |  |  |  | 462 | 191 | 4982887
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 605000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 143790
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 203 | 4881300 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 191 | 4901264 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 407 | 9741545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 317760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 15 | 228564
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226278
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 550656
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 153888 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1060 | 21750045
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4886100
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 57 | 265920 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24840
| Rangpur Area Total |  |  |  | 605 | 257 | 5176860
| Total |  |  |  | 19047 | 8542 | 162505051
| Eastern Grid Total |  |  |  | 13483 | 6324 | 118160395
| Western Grid Total |  |  |  | 5564 | 2218 | 44344656
| National Grid Total |  |  |  | 19047 | 8542 | 162505051
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-02
(a) ENTIRE EASTERN GRID : |  | 5663 | MW | (b) ENTIRE WESTERN GRID : |  | 2466 | MW
i) Dhaka area |  | 3215 | MW | i) Khulna area |  | 958 | MW
ii) Chittagong area |  | 772 | MW | ii) Rajshahi area |  | 823 | MW
iii) Comilla area |  | 714 | MW | iii) Barisal area |  | 210 | MW
iv) Mymensingh area |  | 643 | MW | iv) Rangpur area |  | 475 | MW
v) Sylhet area |  | 319 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8129 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 0.75 | Srimongal | 25 | 0.77083 | Bottail | 98 | 0.75
Munsiganj | 76 | 0.77083 | Shahjibazar | 80 | 0.75 | G.K Project | 24 | 0.75
Sonargaon | 77 | 0.77083 | Fenchuganj | 26 | 0.75 | Faridpur | 124 | 0.79167
Shyampur | 176 | 1904-01-02 | Kulawara | 30 | 0.77083 | Madaripur | 57 | 0.8125
Bhulta | 165 | 0.77083 | Sylhet | 93 | 0.79167 | Sariatpur | 36 | 0.79167
Madanganj | 43 | 0.41667 | Chatak | 17 | 0.77083 | Gopalganj | 54 | 0.77083
Shitalakhya | 95 | 0.70833 | Sunamganj | 28 | 0.77083 | Bagerhat | 61 | 0.8125
Rahim steel | 6 | 0.375 | Biani Bazar | 32 | 0.8125 | Mongla | 32 | 0.41667
Matuail | 86 | 0.41667 | Comilla (S) | 118 | 0.83333 | Satkhira | 61 | 0.8125
Ghorasal | 71 | 0.75 | Comilla(N) | 65 | 0.8125 | Gallamari | 36 | 0.54167
Narsingdi | 99 | 0.8125 | Chandpur | 65 | 0.8125 | Magura | 35 | 0.77083
Haripur (SBU) | 78 | 0.041667 | Feni | 97 | 0.75 | Norail | 21 | 0.77083
Ullon | 56 | 0.75 | Chowmuhani | 114 | 0.8125 | Chuadanga | 59 | 0.75
Hasnabad | 175 | 0.77083 | Ashuganj | 37 | 0.79167 | Barisal(N) | 28 | 0.79167
Magbazar | 84 | 0.58333 | Daudkandi | 98 | 0.79167 | Barisal (S) | 64 | 0.75
Maniknagar | 82 | 0.5 | B.Baria | 86 | 0.77083 | Patuakhali | 71 | 0.8125
Bangabhaban | 22 | 0.5 | Ramganj | 52 | 0.77083 | Bhandaria | 36 | 0.875
Narinda | 78 | 0.70833 | Madunaghat | 42 | 0.77083 | Borhan Uddin | 23 | 0.83333
Dhanmondi | 112 | 0.54167 | Hathazari | 69 | 0.79167 | Ishurdi | 45 | 0.77083
Lalbag | 63 | 0.54167 | Khulshi | 160 | 0.54167 | Ruppur Paromanobik | 1 | 0.041667
Madartek | 47 | 0.75 | Halishahar | 102 | 0.75 | Natore | 78 | 0.77083
Mirpur | 75 | 0.77083 | Baraulia | 103 | 0.041667 | Bogra | 138 | 0.75
Kalyanpur | 75 | 0.75 | Sikalbaha | 29 | 0.77083 | Noagaon | 75 | 0.79167
Gulshan | 112 | 0.58333 | Dohazari | 66 | 0.75 | Rajshahi | 89 | 0.8125
Uttara | 41 | 0.54167 | Cox'sbazar | 70 | 0.75 | Rajshahi New | 9 | 0.75
Uttara New | 30 | 0.58333 | Chandraghona | 22 | 0.75 | C.Nawabganj | 46 | 0.77083
Kamrangirchar | 66 | 0.77083 | Kaptai | 3.5 | 0.75 | Amnura | 21 | 0.75
Savar | 109 | 0.77083 | A. Khaer Stl. | 0 | 0.041667 | Pabna | 69 | 0.75
Bhasantec | 115 | 0.54167 | Bakulia | 79 | 0.75 | Shahjadpur | 77 | 0.75
Agargaon | 41 | 0.54167 | Julda | 18 | 0.33333 | Serajganj | 64 | 0.77083
Satmosjid | 74 | 0.54167 | TK chemical | 0.6 | 0.75 | Niyamatpur | 50 | 0.75
Tongi | 123 | 0.41667 | Modern Steel | 17 | 1904-01-02 | Joypurhat | 48 | 0.77083
Kabirpur | 151 | 0.77083 | Shahmirpur | 21 | 0.75 | Sherpur(Bogura) | 36 | 0.75
Basundhara | 90 | 0.75 | Khagrachhari | 16 | 0.75 | Mohastangor | 10 | 0.75
Manikganj | 62 | 0.79167 | Matarbari | 20 | 0.77083 | Rangpur | 99 | 0.77083
Joydevpur | 167 | 0.83333 | Baroiar Hat | 16 | 0.77083 | Lalmonirhat | 39 | 0.75
New Tongi | 91 | 0.5 | Rangamati | 8 | 0.75 | Saidpur | 79 | 0.77083
Korda | 190 | 0.625 | Abul Khair 230 | 138 | 0.54167 | Purbasadipur | 58 | 0.77083
Dhamrai | 52 | 0.54167 | BSRM | 101 | 0.20833 | Thakurgaon | 35 | 0.041667
Valuka | 80 | 0.77083 | GPH Ispat | 4 | 0.45833 | Palashbari | 81 | 0.75
Tangail | 125 | 0.75 | Goalpara | 19 | 0.54167 | Barapukuria | 42 | 0.75
Mymensing | 146 | 0.75 | Central s/s | 66 | 0.75 | Panchagar | 24 | 0.75
Kishorganj | 78 | 0.79167 | Noapara | 47 | 0.77083 | Joldhaka | 19 | 0.75
Netrokona | 67 | 0.77083 | Jessore | 82 | 0.75 | Kurigram | 40 | 0.75
Jamalpur | 85 | 0.77083 | Benapol | 26 | 0.77083
Sherpur | 70 | 0.75 | Jhenida | 74 | 0.75
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-02 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 387 | 0.125 | 379 | 0.5 | Kaliakoir | 370 | 0.16667 | 353 | 0.5
Bheramara | 411 | 0.16667 | 392 | 0.41667 | Bhulta | 372 | 0.125 | 364 | 0.5
Ashuganj(N) | 375 | 0.041667 | 365 | 0.45833
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 0.041667 | 220 | 0.54167 | Hathazari | 224 | 0.77083 | 214 | 0.45833
Ishurdi | 237 | 1904-01-02 | 226 | 0.77083 | Megnaghat | 220 | 0.041667 | 213 | 0.45833
Ashuganj | 232 | 0.75 | 226 | 0.45833 | Fenchuganj | 236 | 0.77083 | 229 | 0.45833
Serajganj | 232 | 0.041667 | 230 | 0.33333 | Siddhirganj | 223 | 0.20833 | 213 | 0.5
Baghabari | 238 | 0.125 | 231 | 0.75 | Maniknagar | 221 | 0.25 | 211 | 0.5
Barapukuria | 230 | 0.041667 | 29 | 0.875 | Old Airport | 220 | 0.125 | 209 | 0.5
Bogra | 231 | 0.083333 | 225 | 0.33333 | Barisal | 232 | 0.16667 | 219 | 0.8125
Khulna South | 236 | 0.70833 | 214 | 0.8125 | AKSML | 219 | 0.77083 | 209 | 0.54167
Rampura | 221 | 0.125 | 212 | 0.5 | BSRM | 221 | 0.8125 | 213 | 0.20833
Haripur | 220 | 0.041667 | 212 | 0.5 | Bibiyana | 231 | 0.041667 | 224 | 0.5
Hasnabad | 220 | 0.083333 | 210 | 0.5 | Bhulta | 222 | 0.125 | 212 | 0.5
Aminbazar | 221 | 0.083333 | 211 | 0.5 | Ashuganj (S) | 229 | 0.041667 | 224 | 0.45833
Tongi | 216 | 0.16667 | 203 | 0.5 | Kaliakoir | 224 | 0.16667 | 213 | 0.5
Comilla (N) | 229 | 1904-01-02 | 222 | 0.45833 | GPH | 219 | 0.79167 | 209 | 0.45833
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 0.041667 | 128 | 0.5 | Halishahar | 134 | 0.83333 | 127 | 0.45833
Munsiganj | 133 | 0.83333 | 127 | 0.45833 | Baraulia | 131 | 0.83333 | 123 | 0.54167
Sonargaon | 132 | 1904-01-02 | 126 | 0.41667 | Sikalbaha | 134 | 0.79167 | 127 | 0.45833
Shyampur | 134 | 0.83333 | 128 | 0.54167 | Dohazari | 131 | 0.83333 | 126 | 0.58333
Bhulta | 128 | 0.125 | 122 | 0.5 | Cox'sbazar | 126 | 0.375 | 122 | 0.125
Madanganj | 132 | 0.79167 | 127 | 0.66667 | Chandraghona | 133 | 0.79167 | 128 | 0.41667
Shitalakhya | 135 | 0.16667 | 126 | 0.5 | Kaptai | 132 | 0.29167 | 128 | 0.41667
Rahim steal | 134 | 0.125 | 129 | 0.45833 | A. Khaer Stl. | 130 | 0.75 | 125 | 0.41667
Matuail | 133 | 0.125 | 127 | 0.5 | Bakulia | 131 | 0.77083 | 125 | 0.41667
Ghorasal | 136 | 0.041667 | 130 | 0.45833 | Julda | 132 | 0.8125 | 125 | 0.5
Narsinghdi | 133 | 0.041667 | 128 | 0.5 | TK Chemical | 133 | 0.79167 | 126 | 0.70833
Haripur (SBU) | 134 | 0.20833 | 128 | 0.5 | Modern Steel | 133 | 0.79167 | 126 | 0.58333
Ullon | 132 | 0.20833 | 124 | 0.5 | Shahmirpur | 134 | 0.79167 | 125 | 0.625
Hasnabad | 135 | 0.25 | 128 | 0.5 | Khagrachhari | 132 | 0.83333 | 127 | 0.45833
Magbazar | 133 | 0.25 | 124 | 0.5 | Matarbari | 128 | 0.41667 | 124 | 0.041667
Maniknagar | 136 | 0.25 | 130 | 0.5 | Baroiar Hat | 130 | 0.79167 | 125 | 0.58333
Bangabhaban | 136 | 0.29167 | 130 | 0.54167 | Rangamati | 132 | 0.79167 | 127 | 0.5
Narinda | 136 | 0.33333 | 130 | 0.58333 | Goalpara | 138 | 0.16667 | 125 | 0.8125
Dhanmondi | 132 | 0.20833 | 124 | 0.5 | Central s/s | 136 | 0.125 | 125 | 0.77083
Lalbag | 136 | 0.25 | 126 | 0.5 | Noapara | 131 | 0.875 | 120 | 0.54167
Madartek | 132 | 0.25 | 124 | 0.5 | Jessore | 132 | 0.25 | 119 | 0.77083
Mirpur | 131 | 0.041667 | 129 | 0.625 | Benapol | 135 | 0.95833 | 120 | 0.77083
Kalyanpur | 136 | 0.041667 | 129 | 0.5 | Jhenida | 132 | 0.16667 | 119 | 0.75
Gulshan | 134 | 0.125 | 123 | 0.5 | Bottail | 136 | 0.25 | 125 | 0.75
Uttara | 130 | 0.041667 | 120 | 0.5 | G.K Project | 139 | 0.125 | 132 | 0.77083
Uttara New | 134 | 0.83333 | 125 | 0.45833 | Faridpur | 134 | 0.20833 | 122 | 0.79167
Kamrangirchar | 134 | 0.041667 | 125 | 0.5 | Madaripur | 134 | 0.25 | 122 | 0.79167
Savar | 134 | 0.83333 | 125 | 0.5 | Sariatpur | 136 | 0.95833 | 120 | 0.8125
Bhasantec | 133 | 0.125 | 125 | 0.5 | Gopalganj | 140 | 0.95833 | 126 | 0.79167
Agargaon | 134 | 0.125 | 127 | 0.45833 | Bagerhat | 135 | 0.95833 | 120 | 0.77083
Satmosjid | 133 | 0.125 | 126 | 0.45833 | Mongla | 132 | 0.083333 | 120 | 0.8125
Tongi | 132 | 0.16667 | 123 | 0.45833 | Satkhira | 136 | 0.20833 | 123 | 0.75
Kabirpur | 132 | 0.083333 | 124 | 0.5 | Gallamari | 138 | 0.20833 | 126 | 0.77083
Basundhara | 131 | 1904-01-02 | 120 | 0.45833 | Magura | 133 | 0.16667 | 117 | 0.77083
Manikganj | 134 | 0.25 | 120 | 0.625 | Norail | 133 | 0.20833 | 117 | 0.75
Joydevpur | 135 | 0.33333 | 126 | 0.66667 | Chuadanga | 130 | 0.25 | 115 | 0.75
New Tongi | 132 | 1904-01-02 | 121 | 0.5 | Barisal(N) | 138 | 0.20833 | 129 | 0.77083
Kodda | 132 | 0.875 | 121 | 0.5 | Barisal (S) | 139 | 0.95833 | 127 | 0.79167
Dhamrai | 132 | 0.25 | 124 | 0.5 | Patuakhali | 136 | 0.20833 | 125 | 0.77083
Valuka | 130 | 0.91667 | 119 | 0.5 | Bhandaria | 135 | 0.20833 | 122 | 0.8125
Tangail | 131 | 0.875 | 122 | 0.5 | Ishurdi | 136 | 0.20833 | 130 | 0.75
Mymensing | 130 | 0.041667 | 122 | 0.5 | Ruppur Paromanobik | 137 | 0.125 | 129 | 0.75
Kishorganj | 131 | 0.041667 | 123 | 0.5 | Natore | 133 | 0.041667 | 128 | 0.54167
Netrokona | 131 | 0.041667 | 119 | 0.5 | Bogra | 136 | 0.16667 | 131 | 0.54167
Jamalpur | 135 | 0.77083 | 122 | 0.95833 | Noagaon | 134 | 0.20833 | 127 | 0.33333
Sherpur | 135 | 0.8125 | 120 | 0.58333 | Rajshahi | 130 | 0.041667 | 125 | 0.5
Srimongal | 136 | 0.33333 | 135 | 0.45833 | Rajshahi New | 133 | 0.25 | 123 | 0.33333
Shahjibazar | 134 | 0.29167 | 130 | 0.5 | C.Nawabganj | 130 | 0.16667 | 122 | 0.54167
Fenchuganj | 136 | 0.375 | 133 | 0.29167 | Amnura | 130 | 0.125 | 123 | 0.33333
Khulawara | 136 | 1904-01-02 | 134 | 0.041667 | Pabna | 136 | 0.125 | 128 | 0.79167
Sylhet | 135 | 0.041667 | 131 | 0.5 | Shahjadpur | 143 | 0.125 | 136 | 0.75
Chatak | 134 | 0.041667 | 131 | 0.45833 | Serajganj | 136 | 0.041667 | 131 | 0.33333
Sunamganj | 134 | 0.33333 | 130 | 0.5 | Niyamatpur | 134 | 0.16667 | 126 | 0.33333
Biani Bazar | 134 | 0.70833 | 132 | 0.083333 | Joypurhat | 135 | 0.20833 | 127 | 0.33333
Comilla(s) | 130 | 0.125 | 127 | 0.33333 | Sherpur(Bogura) | 137 | 0.125 | 131 | 0.5
Comilla(n) | 137 | 1904-01-02 | 132 | 0.375 | Mohastangor | 135 | 0.125 | 130 | 0.5
Chandpur | 132 | 0.75 | 130 | 0.8125 | Rangpur | 130 | 0.20833 | 124 | 0.33333
Feni | 128 | 0.33333 | 125 | 0.625 | Lalmonirhat | 126 | 0.20833 | 120 | 0.375
Chowmuhani | 135 | 1904-01-02 | 124 | 0.66667 | Saidpur | 130 | 0.125 | 122 | 0.5
Ashuganj | 136 | 0.29167 | 130 | 0.54167 | Purbasadipur | 126 | 0.25 | 117 | 0.33333
Daudkandi | 132 | 0.91667 | 127 | 0.5 | Thakurgaon | 123 | 0.16667 | 118 | 0.375
B.Baria | 133 | 0.33333 | 128 | 0.5 | Palashbari | 134 | 0.20833 | 125 | 0.5
Ramganj | 125 | 0.95833 | 120 | 0.875 | Barapukuria | 130 | 0.041667 | 126 | 0.75
Madanhat | 135 | 0.79167 | 128 | 0.58333 | Panchagar | 123 | 0.16667 | 112 | 0.29167
Hathazari | 134 | 0.79167 | 128 | 0.45833 | Joldhaka | 129 | 0.125 | 122 | 0.5
Khulshi | 131 | 0.79167 | 124 | 0.45833 | Kurigram | 130 | 0.16667 | 121 | 0.33333
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-12-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 247 | 4842 | 1562 | 6404 |  |  |  | QF-LDC-12
0:30 | 168.5 | 4653.5 | 1563 | 6216.5 | Date: | 2019-12-02
1:00 | 90 | 4465 | 1564 | 6029
1:30 | 107 | 4368.5 | 1521.5 | 5890
2:00 | 124 | 4272 | 1479 | 5751
2:30 | 102 | 4216.5 | 1497.5 | 5714 | [5 empty] | Gen. at Eve. Peak | 8542 | 8542 MW (19:00 )
3:00 | 80 | 4161 | 1516 | 5677 | [6 empty] | 19:00
3:30 | 40 | 4065 | 1529.5 | 5594.5 | [5 empty] | Gen. at Day Peak | 6665.6 | 6665.6 MW (12:00 )
4:00 | 0 | 3969 | 1543 | 5512 | [6 empty] | 12:00
4:30 | 25 | 3955 | 1536.5 | 5491.5 | [5 empty] | Highest Generation | 8542
5:00 | 50 | 3941 | 1530 | 5471 | [6 empty] | 19:00
5:30 | 25 | 3977 | 1558 | 5535
6:00 | 0 | 4013 | 1586 | 5599
6:30 | 15 | 4108.1 | 1609.05 | 5717.15
7:00 | 30 | 4203.2 | 1632.1 | 5835.3
7:30 | 126.5 | 4426.2 | 1653.35 | 6079.55
8:00 | 223 | 4649.2 | 1674.6 | 6323.8
8:30 | 111.5 | 4632.7 | 1754.95 | 6387.65
9:00 | 0 | 4616.2 | 1835.3 | 6451.5
9:30 | 112.5 | 4570.2 | 1830.95 | 6401.15
10:00 | 225 | 4524.2 | 1826.6 | 6350.8
10:30 | 225 | 4562.15 | 1876.4 | 6438.55
11:00 | 225 | 4600.1 | 1926.2 | 6526.3
11:30 | 189 | 4677.05 | 1918.9 | 6595.95
12:00 | 153 | 4754 | 1911.6 | 6665.6
12:30 | 103.5 | 4956.42 | 1885.9 | 6842.32
13:00 | 54 | 5158.84 | 1860.2 | 7019.04
13:30 | 42 | 4991.97 | 1800.85 | 6792.82
14:00 | 30 | 4825.1 | 1741.5 | 6566.6
14:30 | 65 | 4842 | 1749.15 | 6591.15
15:00 | 100 | 4858.9 | 1756.8 | 6615.7
15:30 | 100 | 4839.2 | 1742.8 | 6582
16:00 | 100 | 4819.5 | 1728.8 | 6548.3
16:30 | 86.5 | 4913.25 | 1797.95 | 6711.2
17:00 | 73 | 5007 | 1867.1 | 6874.1
17:30 | 216.5 | 5571 | 2026.05 | 7597.05
18:00 | 360 | 6135 | 2185 | 8320
18:30 | 365 | 6229.5 | 2201.5 | 8431
19:00 | 370 | 6324 | 2218 | 8542
19:30 | 317 | 6073 | 2271 | 8344
20:00 | 380 | 6068 | 2191 | 8259 |  |  |  | Executive Engineer
20:30 | 315 | 5913 | 2195 | 8108 |  |  |  | Network Operation Division
21:00 | 250 | 5758 | 2199 | 7957
21:30 | 220 | 5545.5 | 2112.5 | 7658
22:00 | 190 | 5333 | 2026 | 7359 |  |  |  |  | Page 6 of 7
22:30 | 223 | 5192 | 1873 | 7065
23:00 | 256 | 5051 | 1720 | 6771
23:30 | 251.5 | 4946.5 | 1641 | 6587.5
24:00 | 247 | 4842 | 1562 | 6404
8542 MW (19:00 )
6665.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-02 |  | Energy | 162505051
[10 empty] | 2019-12-02 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3800 | 202 | 2009 | 23 | 200 | 95 | 8 | 0 | 90
0:30 | 3700.5 | 171 | 1949 | 14.5 | 200 | 95 | 4 | 0 | 94 | Date: | 2019-12-02
1:00 | 3601 | 140 | 1889 | 6 | 200 | 95 | 0 | 0 | 98
1:30 | 3581 | 140 | 1780.5 | 3 | 200 | 94.5 | 0 | 0 | 91 | [7 empty] | Total Energy | 162.5051 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3561 | 140 | 1672 | 0 | 200 | 94 | 0 | 0 | 84 | [7 empty] | Energy not Served | 0
2:30 | 3585.5 | 140 | 1613.5 | 0 | 200 | 94 | 0 | 0 | 81 | [7 empty] | Energy Requirement | 162.5051
3:00 | 3610 | 140 | 1555 | 0 | 200 | 94 | 0 | 0 | 78
3:30 | 3568 | 140 | 1515 | 0 | 200 | 93.5 | 0 | 0 | 78 | [6 empty] | Shortage
4:00 | 3526 | 140 | 1475 | 0 | 200 | 93 | 0 | 0 | 78
4:30 | 3510 | 140 | 1471.5 | 0 | 200 | 93 | 0 | 0 | 77
5:00 | 3494 | 140 | 1468 | 0 | 200 | 93 | 0 | 0 | 76
5:30 | 3544.5 | 140 | 1482 | 0 | 200 | 92.5 | 0 | 0 | 76
6:00 | 3595 | 140 | 1496 | 0 | 200 | 92 | 0 | 0 | 76
6:30 | 3654 | 140 | 1554.5 | 0 | 200 | 91 | 0 | 0 | 76 |  |  |  |  | Coal
7:00 | 3713 | 140 | 1613 | 0 | 200 | 90 | 0 | 0 | 76
7:30 | 3803.5 | 140 | 1754 | 7.5 | 200 | 90 | 0 | 0 | 78 |  |  |  | Oil |  |  |  | ,
8:00 | 3894 | 140 | 1895 | 15 | 200 | 90 | 0 | 0 | 80
8:30 | 3837 | 218.5 | 1878.5 | 68 | 200 | 90 | 0 | 0 | 81
9:00 | 3780 | 297 | 1862 | 121 | 200 | 90 | 0 | 0 | 82
9:30 | 3740 | 297 | 1854.5 | 125 | 200 | 90 | 0 | 0 | 81
10:00 | 3700 | 297 | 1847 | 129 | 200 | 90 | 0 | 0 | 80
10:30 | 3754.5 | 297 | 1877.5 | 129 | 200 | 90 | 0.5 | 0 | 81
11:00 | 3809 | 297 | 1908 | 129 | 200 | 90 | 1 | 0 | 82
11:30 | 3858 | 297.5 | 1925.5 | 129 | 200 | 90.5 | 1.5 | 0 | 83
12:00 | 3907 | 298 | 1943 | 129 | 200 | 91 | 2 | 0 | 84
12:30 | 3918.5 | 297.5 | 2098.5 | 137 | 200 | 91.5 | 2 | 0 | 87
13:00 | 3930 | 297 | 2254 | 145 | 200 | 92 | 2 | 0 | 90
13:30 | 3930 | 297 | 2254 | 145 | 200 | 92 | 2 | 0 | 90
14:00 | 3930 | 297 | 2254 | 145 | 200 | 92 | 2 | 0 | 90
14:30 | 3821.5 | 298 | 2210 | 84.5 | 200 | 93 | 7 | 0 | 90
15:00 | 3713 | 299 | 2166 | 24 | 200 | 94 | 12 | 0 | 90
15:30 | 3685.5 | 298.5 | 2169.5 | 24 | 200 | 94 | 10 | 0 | 88
16:00 | 3658 | 298 | 2173 | 24 | 200 | 94 | 8 | 0 | 86
16:30 | 3716 | 298.5 | 2140.5 | 158.5 | 200 | 94 | 8 | 0 | 92
17:00 | 3774 | 299 | 2108 | 293 | 200 | 94 | 8 | 0 | 98
17:30 | 3913.5 | 372 | 2146.5 | 758 | 200 | 94 | 8 | 0 | 105
18:00 | 4053 | 445 | 2185 | 1223 | 200 | 94 | 8 | 0 | 112
18:30 | 4004 | 445 | 2165.5 | 1402 | 200 | 94 | 8.5 | 0 | 112
19:00 | 3955 | 445 | 2146 | 1581 | 200 | 94 | 9 | 0 | 112
19:30 | 3972 | 445 | 2218 | 1295 | 200 | 94 | 8 | 0 | 112
20:00 | 3950 | 445 | 2184 | 1260 | 200 | 94 | 8 | 0 | 118
20:30 | 3980.5 | 445.5 | 2223.5 | 1040.5 | 200 | 94 | 8 | 0 | 116
21:00 | 4011 | 446 | 2263 | 821 | 200 | 94 | 8 | 0 | 114
21:30 | 3983 | 445.5 | 2245.5 | 572 | 200 | 94 | 8 | 0 | 110
22:00 | 3955 | 445 | 2228 | 323 | 200 | 94 | 8 | 0 | 106
22:30 | 3953.5 | 324.5 | 2209.5 | 173 | 200 | 94.5 | 8 | 0 | 102
23:00 | 3952 | 204 | 2191 | 23 | 200 | 95 | 8 | 0 | 98
23:30 | 3876 | 203 | 2100 | 23 | 200 | 95 | 8 | 0 | 94 | Max Temp. in Dhaka |  | 29.0° C
24:00 | 3800 | 202 | 2009 | 23 | 200 | 95 | 8 | 0 | 90
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-12-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 44 | 44 | 43 | 43 | 42 | 40 | 40 | 40 | 40 | 40 | 41 | 42 | 42 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 45 | 45 | 1032873
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1192000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
5 | Raozan 25 MW PP
| Teknaf 20MW PP (Solartech) | [6 empty] | 2.7 | 7.7 | 14.5 |  |  |  |  | 15.7 | 12.3 | 5.9 | 0 | [9 empty] | 61425
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 211 | 204 | 204 | 211 | 206 | 223 | 204 | 204 | 197 | 195 | 218 | 209 | 212 | 203 | 203 | 203 | 216 |  | 203 | 203 | 203 | 203 | 203 | 212 | 204 | 4864315
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 145 | 150 | 150 | 104 | 104 | 104 | 115 | 139 | 106 | 120 | 108 | 108 | 145 | 104 | 104 | 104 | 105 | 145 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3018774
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 1 | 17 | 17 | 17 | 17 | 17 |  |  |  | 11 | 105 |  | 105 | 105 | 105 | 105 | 105 | 17 | 0 | 725127
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [13 empty] | 8 | 8 | 8 | 8 | 8 |  | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 104512
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 60 | 60 | 60 | 37 | 37 | 62 | 62 | 87 | 60 | 39 | 37 | 37 | 90 | 35 | 35 | 37 | 70 | 97 |  | 87 | 87 | 87 | 87 | 87 | 87 | 85 | 1586000
17 | Siddhirganj 335 MW CCPP | 237 | 233 | 238 | 235 | 236 | 236 | 235 | 236 | 238 | 200 | 138 | 180 | 230 | 224 | 229 | 228 | 227 | 228 |  | 234 | 230 | 234 | 234 | 236 | 235 | 240 | 5536311
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 0 | 7 | 15 | 15 | 15 | 15 | 0 |  |  | 15 | 115 |  | 150 | 145 | 145 | 80 | 15 | 0 | 0 | 750218
19 | Ashuganj 195MW PP (APSCL-United) | 148 | 52 | 52 | 28 | 28 | 28 | 28 | 102 | 102 | 102 | 102 | 102 | 120 | 120 | 120 | 120 | 120 | 128 |  | 120 | 120 | 128 | 128 | 120 | 128 | 120 | 2375272
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 711000
21 | Ghorasal Repowered CCPP Unit-3 | 188 | 189 | 189 | 158 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 158 | 159 | 160 | 159 | 159 | 178 | 189 |  | 188 | 188 | 209 | 240 | 238 | 235 | 233 | 4581800
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2955914
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | [7 empty] | 0 | 55 | 55 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 1502700
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 787032
33 | Ashuganj 225 MW CCPP | 134 | 134 | 135 | 135 | 135 | 135 | 136 | 134 | 135 | 133 | 130 | 129 | 129 | 129 | 129 | 131 | 131 | 131 |  | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 3207000
34 | Ashuganj 450 MW CCPP(South) | 265 | 275 | 265 | 275 | 265 | 265 | 305 | 315 | 310 | 315 | 305 | 355 | 355 | 290 | 270 | 260 | 265 | 330 |  | 305 | 325 | 305 | 310 | 305 | 335 | 310 | 7289500
Ashuganj 450 MW CCPP(North)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 83 | 80 | 82 | 86 | 87 | 91 | 90 | 90 | 82 | 91 | 90 | 90 | 88 | 90 | 90 | 90 | 85 | 90 |  | 80 | 90 | 83 | 90 | 80 | 84 | 80 | 2073770
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 360 | 349 | 344 | 342 | 365 | 363 | 381 | 330 | 300 | 370 | 380 | 380 | 365 | 370 | 355 | 362 | 367 |  | 353 | 340 | 346 | 349 | 344 | 344 | 347 | 8616930
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 360 | 330 | 330 | 360 | 380 | 420 | 380 | 380 | 380 | 380 | 450 | 420 | 420 | 420 | 380 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 380 | 9350250
41 | Haripur 360MW CCPP(HPL) | 366 | 331 | 331 | 303 | 283 | 303 | 313 | 313 | 282 | 282 | 284 | 322 | 361 | 333 | 333 | 333 | 303 | 332 |  | 332 | 332 | 331 | 333 | 322 | 317 | 305 | 7604000
42 | RPCL 210MW CCPP | 161 | 161 | 163 | 163 | 163 | 163 | 162 | 162 | 162 | 157 | 157 | 123 | 124 | 153 | 155 | 156 | 158 | 160 |  | 162 | 147 | 148 | 148 | 148 | 148 | 149 | 3646160
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 60 | 59 | 59 | 59 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1428000
45 | Fenchugonj CCPP Phase-2 | 56 | 56 | 56 | 56 | 56 | 56 | 64 | 56 | 56 | 64 | 60 | 60 | 56 | 60 | 60 | 56 | 60 | 60 |  | 60 | 60 | 56 | 56 | 28 | 58 | 58 | 1370520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 69 | 67 | 65 | 65 | 63 | 65 | 64 | 65 | 65 | 68 | 67 |  | 69 | 68 | 69 | 69 | 69 | 70 | 70 | 1407680
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 10 | 10 | 10 | 72 | 72 | 73 | 73 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1128960
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 299000
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 36 | 37 | 37 | 34 | 35 | 37 | 37 | 38 | 38 | 38 | 39 |  | 39 | 39 | 39 | 40 | 40 | 40 | 10 | 661700
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 169740
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 11 | 11 | 11 |  | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 |  |  | 131128
55 | Fenchugonj 51 MW PP (Barakatullah) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 28 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 874800
56 | Shahjahanulla 25 MW PP | [7 empty] | 16 | 16 | 16 | 15 | 15 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 |  |  | 328536
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 295 | 285 | 280 | 295 | 300 | 315 | 315 | 280 | 285 | 305 | 305 | 310 | 275 | 310 | 320 | 310 | 300 |  | 290 | 310 | 300 | 300 | 295 | 285 | 285 | 7578300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 14 | 35 |  | 35 | 35 | 35 |  |  |  |  | 128595
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439056
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 |  |  | 258228
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 368460
63 | Impoprt (Tripura) | 98 | 84 | 78 | 78 | 76 | 76 | 76 | 80 | 82 | 80 | 82 | 84 | 90 | 92 | 90 | 86 | 98 | 112 |  | 112 | 112 | 118 | 114 | 106 | 98 | 90 | 2173440
64 | Malancha, Ctg. EPZ (United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 10 | 14 | 12 | 7 | 6 | 6 | 6 |  | 11 | 18 | 20 | 32 | 20 | 25 | 24 | 381120
65 | Feni 22MW PP (Doreen) | 22 | [6 empty] | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 334080
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 126900
67 | Jangalia 33MW PP (Summit) | [7 empty] | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 500200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 14 | 14 | 14 | 14 | 14 | 18 | 16 | 14 | 14 | 14 | 14 | 18 | 12 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 430400
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 18 | 18 | 30 | 30 | 31 | 31 | 28 | 28 | 30 | 24 | 24 | 30 | 31 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 697500
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 727000
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 17 | 17 | 33 | 33 | 33 | 25 | 25 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 744300
73 | Ghorashal 108MW PP (Regent) | 109 | 53 | 13 | 13 | 13 | 13 | 13 | 25 | 52 | 52 | 52 | 52 | 100 | 107 | 107 | 107 | 107 | 110 |  | 110 | 110 | 110 | 107 | 109 | 110 | 110 | 1693636
| Feni Lanka Power | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [16 empty] | 3 | 33 |  | 33 | [6 empty] | 74469
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [19 empty] | 14 | 16 | 16 | 0 | 0 |  |  | 34560
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.4 | 1 | 1.6 | 2.7 | 4.3 | 5.2 | 3.14 | 1 | 1.7 | 0.3 | 0 | [9 empty] | 24720
| Jodiac Power | [17 empty] | 9 |  | 17 | 17 | 17 |  |  |  |  | 46438
| Karnaphuli Power Ltd. | [17 empty] | 15 |  | 17 | 3 | [5 empty] | 45999
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 28 | 100 |  | 100 | 100 | 100 | 50 | 10 | 0 | 0 | 413640
92 | Fenchuganj 44MW (Energyprima) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 46 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 869832
93 | Ashuganj 51 MW PP (Midland) | [7 empty] | 8 | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 759368
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [16 empty] | 1 | 18 |  | 24 | 9 | 12 |  |  |  |  | 56640
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 3 | 33 |  | 82 | 52 | 52 | 50 |  |  |  | 248640
97 | Katpotti 52 MW PP (Sinha) | 6 | [16 empty] | 30 |  | 47 | 47 | 47 | 24 | 18 | 6 |  | 216288
98 | Bosila 108MW PP(CLC) | [8 empty] | 8 | 8 | 8 | 8 | 8 |  |  |  | 7 | 72 |  | 72 | 72 | 72 | 72 |  |  |  | 336000
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 15 |  | 15 | 0 | [5 empty] | 36984
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 55 | 35 | 35 |  |  |  |  | 98417
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 163 | 100 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3159572
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.5 | 1.1 | 1.5 | 1.8 | 1.8 | 1.7 | 1.4 | 0.9 | 0.3 | 0 | [9 empty] | 11300
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 10 | 17 |  | 17 | [6 empty] | 43668
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 14 | 40 | 40 | 40 | 40 | 40 | 24 | 24 | 24 | 86 | 160 |  | 200 | 200 | 200 | 200 | 140 |  |  | 1432800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 75 |  | 100 | 50 | 50 | 10 | 0 | 0 |  | 218880
116 | Chandpur 200MW (Desh energy) | [16 empty] | 10 | 80 |  | 120 | 70 | 70 | 0 | 0 |  |  | 328800
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 5 | 60 |  | 70 | 35 | 30 | 30 |  |  |  | 244218
118 | Bibiyana-III 400 MW CCPP | 363 | 382 | 365 | 370 | 364 | 366 | 396 | 363 | 365 | 334 | 398 | 406 | 362 | 362 | 344 | 342 | 340 | 396 |  | 365 | 373 | 363 | 364 | 362 | 381 | 377 | 8805000
Jamalpur 115 MW PP (United)
Anwara 300 MW PP (United)
120 | Eastern Zone Total | 4465 | 4272 | 4161 | 3969 | 3941 | 4013 | 4203.2 | 4649.2 | 4616.2 | 4524.2 | 4600.1 | 4754 | 5158.84 | 4825.1 | 4858.9 | 4819.5 | 5007 | 6135 |  | 6324 | 6073 | 6068 | 5758 | 5333 | 5051 | 4842 | 118160395
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [8 empty] | 17 | 17 | 17 | 17 | 17 | 0 | [12 empty] | 91200
130
131
132
133
| Barisal 110 MW PP (Summit ) | [7 empty] | 0 | 32 | 32 | 32 | 32 | 48 | 0 | [12 empty] | 168960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [16 empty] | 10 | 30 |  | 20 | 32 | 32 | 61 | 62 | 62 | 57 | 312951
| Bhola 225 MW CCPP | 158 | 168 | 158 | 170 | 154 | 177 | 177 | 172 | 160 | 177 | 177 | 178 | 176 | 177 | 175 | 167 | 167 | 177 |  | 153 | 176 | 154 | 177 | 170 | 177 | 153 | 4167076
140 | Bhola 33 MW PP (Venture) | 15 | 14 | 14 | 13 | 13 | 13 | 13 | 12 | 12 | 11 | 11 | 12 | 12 | 12 | 12 | 11 | 14 | 18 |  | 18 | 18 | 19 | 20 | 19 | 17 | 16 | 333900
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 40 | 40 |  | 40 | 40 | 40 | 40 |  |  |  | 182625
143 | Gopalganj 100 MW Peaking PP | [10 empty] | 1 | 2 | 2 | 3 | 4 | 0 | [10 empty] | 9344
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 297 | 297 | 297 | 298 | 297 | 298 | 299 | 298 | 299 | 445 |  | 445 | 445 | 445 | 446 | 445 | 204 | 202 | 6505455
147 | Bheramara 360 MW CCPP | 180 | 105 | 225 | 245 | 245 | 265 | 265 | 270 | 270 | 240 | 255 | 235 | 220 | 220 | 220 | 215 | 235 | 225 |  | 225 | 225 | 225 | 215 | 215 | 215 | 215 | 5646240
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4886100
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 50 | 50 | 40 | 0 | 0 | [12 empty] | 605000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 200 | 199 | 184 | 177 | 180 | 179 | 181 | 195 | 170 | 177 | 214 | 214 | 214 | 188 | 185 | 180 | 186 | 194 |  | 203 | 193 | 198 | 203 | 200 | 199 | 174 | 4881300
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 205 | 201 | 190 | 185 | 187 | 188 | 190 | 198 | 192 | 186 | 191 | 211 | 202 | 186 | 190 | 188 | 195 | 191 |  | 191 | 190 | 190 | 186 | 190 | 190 | 184 | 4901264
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 408 | 394 | 347 | 355 | 353 | 356 | 398 | 392 | 377 | 390 | 432 | 424 | 423 | 410 | 425 | 425 | 427 | 423 |  | 407 | 441 | 407 | 444 | 443 | 431 | 336 | 9741545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [7 empty] | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 |  | 317760
163 | Bogura 20 MW PP (Energyprima) | [7 empty] | 5 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 |  | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 228564
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 226278
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 12 | 50 |  | 50 | 24 | 24 | 12 | 0 | 0 |  | 143790
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 8 | 87 |  | 111 | 113 | 113 | 113 | 35 |  |  | 550656
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 3 |  | 50 | 70 | 40 | 0 | 0 |  |  | 153888
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 30 | 54 |  | 57 | 57 | 57 | 35 | 0 |  |  | 265920
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.6 | 2.3 | 3.6 | 4.2 | 4.6 | 4.2 | 3.5 | 2.8 | 0.8 | 0.1 | [9 empty] | 24840
178
178