## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-05 | Thursday
|  | Date (day): | 2019-12-05 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11714.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14273 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-04 | 2019-12-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 127 | 129 | 150 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under S/D
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 107 | 110 | 105 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 342 | 357 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 366 | 368 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 13 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 60 | 95 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 5 | 236 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 11 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 66 | 67 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 48 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 36 | 25 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 14 | 165 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1792 | 2218 | 3670 | 4214 | 598 | 1014
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 39 | 19 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 120 | 111 | 94 | 94 | 136 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 70 | 229 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 90 | 145 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 70 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 18 | 5 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 98 | 98 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.5 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 741.5 | 1065 | 1472 | 1632 | 216 | 278
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 120 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 0 | 0 |  |  | Under maint.
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 203 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 10 | 12 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 55 | 45 | 45 | 140 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 26 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 80 | 100 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 80 | 0 | 0 |  | 163 | Maintenance at S/S.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 102 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 110 | 103 | 131
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1093 | 1384 | 1604 | 2032 | 284 | 179
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 161 | 160 | 161 | 41 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 16 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.7 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 70 | 170 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 249.7 | 369 | 493.6 | 593 | 41 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 59 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 52 | 52 | 62 | 62
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 30 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 67 | 68 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 12 | 35 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 354 | 353 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1177 | 1281 | 1368 | 1368 | 0 | 492
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 300 | 444 | 450 | 747
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 2 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 200 | 300 | 300 |  | 132 | ST under S/D
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 53 | 20 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 91 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 575 | 850 | 890 | 1857 | 0 | 132
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 24 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 160 | 0 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 201 | 134 | 371 | 441 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 71 | 71
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 204 | 204 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 206 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 440 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 112 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 852 | 1094 | 1525 | 1789 | 320 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 190 | 200 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 194.8 | 313 | 321 | 347 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6876 | 8708 | 11714.6 | 14273 | 1459 | 2280
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6508.0377 | 8242 | 11087.7048 | 13509.1945
A. |  | 2019-12-04 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 8708 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5243 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8708 | MW
3 | Day peak Generation : |  |  | 6876 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8242 | MW
4 | Evening peak Generation : |  |  | 8708 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 159.3405 | MKWHr | By Solar | 0.12895 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 130.8575 | MKWHr |  | By Oil: | 14.9138 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.3898 | MKWHr |  | By Hydro: | 2.2694 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1459 | MW | Dhaka | 3154 | 3154 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2280 | MW | Chittagong | 918 | 918 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3739 | MW | Khulna | 970 | 970 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1080.28 | MMCFD |  |  | Rajshahi | 812 | 812 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 121232993.974 | ii) Oil : | Taka | 142075772.92 | Comilla | 708 | 708 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 17954282 | Total | Taka | 281263048.894 | Mymensingh | 642 | 642 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.3765 | MKWHr. | Sylhet | 325 | 325 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -290 | MW (E to W) at | 19:00 | hrs | Barisal | 210 | 210 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -333 | MW at | 19:30 | hrs | Rangpur | 503 | 503 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.3° C |  |  | Total | 8242 | 8242 |  | 0
B. |  | 2019-12-05 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14273 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7100 | MW
4 | Reserve(Generation end) |  |  |  | 5373 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 162.8538 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5196 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 6.5767 | MKWHr. | ii) HVDC Flow at Peak Time |  | 444 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 0.20429 | MKWHr. | iii) Maximum HVDC Flow : |  | 445 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.34 |  | (b) Today: | 99.17 |  | (c) Rule Curve: |  | 105.64
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 189 | 0 | 0 | 0 | 109 | 0 | 348 | 324 |  | 0 | 360 | 0 | 0 | 0 | 0 | 238 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 45 | 50 | 0 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 120 | 0 | 135 | 0 | 320 | 204 | 45 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 76 | 163 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 130 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 12 | 0 | 192 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4391 | 1463 | 5854 | 3626 | 141 | 1756 | 0 | 160 | 95 | 0 | 76 | 0 | 0 | 99.39
2:00 | 35 | 188 | 0 | 0 | 0 | 52 | 0 | 350 | 274 |  | 0 | 320 | 0 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 45 | 50 | 0 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 26 | 120 | 0 | 135 | 40 | 265 | 204 | 45 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 72 | 164 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 130 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 0 | 0 | 12 | 0 | 189 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4133 | 1443 | 5576 | 3527 | 141 | 1581 | 0 | 160 | 95 | 0 | 72 | 0 | 0 | 99.38
3:00 | 35 | 139 | 0 | 0 | 0 | 12 | 0 | 348 | 234 |  | 0 | 320 | 0 | 0 | 0 | 0 | 140 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 46 | 50 | 0 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 120 | 0 | 135 | 135 | 265 | 204 | 8 | 90 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 72 | 164 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 12 | 0 | 188 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3952 | 1440 | 5392 | 3464 | 141 | 1459 | 0 | 160 | 96 | 0 | 72 | 0 | 0 | 99.37
4:00 | 35 | 124 | 0 | 0 | 0 | 12 | 0 | 346 | 234 |  | 0 | 320 | 0 | 0 | 0 | 0 | 140 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 33 | 33 | 0 | 0 | 46 | 50 | 0 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 0 | 115 | 265 | 265 | 204 | 8 | 89 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 70 | 164 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3921 | 1394 | 5315 | 3437 | 141 | 1411 | 0 | 160 | 96 | 0 | 70 | 0 | 0 | 99.36
5:00 | 35 | 124 | 0 | 0 | 0 | 12 | 0 | 352 | 254 |  | 0 | 320 | 0 | 0 | 0 | 0 | 140 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 46 | 50 | 0 | 0 | 0 | 190 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 80 | 110 | 290 | 204 | 8 | 87 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 68 | 164 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 130 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3825 | 1418 | 5243 | 3323 | 141 | 1455 | 0 | 160 | 96 | 0 | 68 | 0 | 0 | 99.35
6:00 | 35 | 124 | 0 | 0 | 0 | 12 | 0 | 356 | 303 |  | 0 | 350 | 0 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 33 | 33 | 0 | 0 | 46 | 50 | 0 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 80 | 0 | 80 | 20 | 275 | 204 | 8 | 85 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 70 | 164 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 130 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 177 | 0 | 0 | 0 | 11 | 0 | 192 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3815 | 1594 | 5409 | 3341 | 141 | 1601 | 0 | 160 | 96 | 0 | 70 | 0 | 0 | 99.34
7:00 | 35 | 130 | 0 | 0 | 0 | 31 | 0 | 360 | 364 |  | 0 | 380 | 0 | 0 | 0 | 0 | 240 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 33 | 33 | 0 | 0 | 46 | 50 | 0 | 0 | 0 | 213 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 80 | 0 | 80 | 20 | 345 | 204 | 8 | 80 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 13 | 0 | 0 | 18 | 70 | 164 | 0 | 0 | 0.1 | 60 | 52 | 5 | 5 | 130 | 0 | 70 | 10 | 0 | 0 | 0 | 7 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  | 141 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 8 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 0 | 0 | 11 | 0 | 194 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4200 | 1608.1 | 5808.1 | 3611 | 141 | 1727 | 0 | 160 | 96 | 0 | 70 | 3.1 | 0 | 99.33
8:00 | 35 | 135 | 0 | 0 | 0 | 83 | 0 | 355 | 364 |  | 0 | 420 | 0 | 0 | 0 | 0 | 239 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 80 | 0 | 80 | 20 | 345 | 204 | 8 | 90 | 37 | 0 | 0 | 10 | 0 | 0 | 0 | 22 | 0 | 33 | 18 | 74 | 164 | 0 | 22 | 0.6 | 60 | 52 | 47 | 35 | 130 | 0 | 70 | 10 | 0 | 0 | 17 | 30 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 |  | 141 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 10 | 0 | 0 | 160 | 0 | 0 | 201 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 4169.8 | 1639.2 | 5809 | 3492 | 141 | 1924 | 7 | 160 | 0 | 0 | 74 | 11 | 0 | 99.32
9:00 | 35 | 129 | 0 | 0 | 0 | 100 | 0 | 345 | 369 |  | 0 | 400 | 0 | 0 | 0 | 0 | 42 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 0 | 0 | 0 | 19 | 25 | 23 | 33 | 33 | 4 | 0 | 40 | 40 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 90 | 0 | 14 | 18 | 7 | 120 | 0 | 135 | 20 | 320 | 204 | 8 | 80 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 78 | 163 | 0 | 22 | 1.3 | 60 | 52 | 11 | 10 | 100 | 0 | 69 | 76 | 0 | 0 | 17 | 12 | 10 | 280 | 24 | 11 | 0 | 1 | 0 | 0 | 50 | 0 | 0 | 13.6 | 100 | 0 | 0 | 354 | 0 | 0 | 22 | 1.9 | 0 | 11 | 14 | 0 |  | 299 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 160 | 0 | 0 | 195 | 0 | 0 | 0 | 11 | 0 | 193 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4437.8 | 1744.8 | 6182.6 | 3341 | 299 | 1864 | 341 | 160 | 80 | 0 | 78 | 19.6 | 0 | 99.31
10:00 | 35 | 129 | 0 | 0 | 0 | 104 | 0 | 343 | 368 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 6 | 0 | 0 | 0 | 19 | 25 | 23 | 33 | 33 | 16 | 0 | 42 | 40 | 0 | 0 | 9 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 80 | 7 | 19 | 19 | 11 | 120 | 0 | 135 | 12 | 320 | 205 | 8 | 89 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 12 | 78 | 163 | 0 | 22 | 1.8 | 60 | 52 | 11 | 10 | 100 | 0 | 66 | 74 | 0 | 0 | 17 | 12 | 10 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 0 | 70 | 0 | 0 | 354 | 0 | 0 | 105 | 3.9 | 0 | 0 | 0 | 0 |  | 300 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 10 | 0 | 0 | 160 | 0 | 0 | 167 | 0 | 0 | 0 | 11 | 0 | 202 | 0 | 418 | 3 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 4518.7 | 1784.1 | 6302.8 | 3327 | 300 | 1909 | 437 | 160 | 82 | 0 | 78 | 9.8 | 0 | 99.3
11:00 | 35 | 129 | 0 | 0 | 0 | 104 | 0 | 353 | 365 |  | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 6 | 0 | 17 | 17 | 19 | 25 | 23 | 33 | 33 | 16 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 90 | 44 | 19 | 19 | 3 | 120 | 0 | 135 | 14 | 360 | 205 | 8 | 81 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 82 | 157 | 0 | 22 | 2 | 60 | 52 | 11 | 15 | 130 | 0 | 65 | 74 | 0 | 0 | 17 | 12 | 10 | 310 | 16 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 351 | 0 | 0 | 105 | 4.3 | 0 | 0 | 0 | 0 |  | 300 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 11 | 0 | 212 | 0 | 432 | 28 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0 |  | 4742.3 | 1838.1 | 6580.4 | 3355 | 300 | 1998 | 594 | 160 | 80 | 0 | 82 | 11.4 | 0 | 99.3
12:00 | 35 | 127 | 0 | 0 | 0 | 107 | 0 | 342 | 366 |  | 0 | 430 | 0 | 0 | 0 | 13 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 11 | 0 | 17 | 35 | 19 | 25 | 23 | 33 | 33 | 36 | 0 | 80 | 40 | 0 | 0 | 0 | 70 | 0 | 90 | 0 |  | 0 | 0 | 0 | 90 | 98 | 39 | 19 | 6 | 120 | 0 | 135 | 10 | 310 | 205 | 8 | 88 | 37 | 0 | 0 | 26 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 82 | 156 | 0 | 22 | 1.7 | 60 | 52 | 11 | 30 | 163 | 0 | 67 | 76 | 0 | 0 | 17 | 12 | 10 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 354 | 0 | 0 | 105 | 4.5 | 0 | 0 | 0 | 0 |  | 300 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 190 | 0 | 0 | 204 | 0 | 0 | 0 | 11 | 0 | 208 | 0 | 397 | 35 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 5053.2 | 1822.8 | 6876 | 3436 | 300 | 1992 | 745 | 190 | 120 | 0 | 82 | 11 | 0 | 99.3
13:00 | 35 | 127 | 0 | 0 | 0 | 107 | 0 | 343 | 365 |  | 0 | 430 | 0 | 0 | 0 | 28 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 12 | 0 | 17 | 35 | 19 | 25 | 23 | 33 | 33 | 42 | 0 | 70 | 40 | 0 | 0 | 0 | 80 | 0 | 144 | 0 |  | 0 | 0 | 0 | 90 | 98 | 50 | 19 | 10 | 120 | 0 | 135 | 10 | 310 | 201 | 55 | 80 | 37 | 0 | 0 | 26 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 84 | 156 | 0 | 22 | 1.8 | 60 | 52 | 11 | 30 | 163 | 0 | 66 | 76 | 0 | 0 | 17 | 12 | 10 | 280 | 24 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 353 | 0 | 0 | 105 | 4.1 | 0 | 0 | 0 | 0 |  | 300 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 190 | 0 | 0 | 194 | 0 | 0 | 0 | 12 | 0 | 204 | 0 | 381 | 35 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 |  | 5166.9 | 1784.9 | 6951.8 | 3459 | 300 | 2019 | 779 | 190 | 110 | 0 | 84 | 10.8 | 0 | 99.29
14:00 | 35 | 129 | 0 | 0 | 0 | 110 | 0 | 345 | 307 |  | 0 | 340 | 0 | 0 | 0 | 30 | 2 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 0 | 17 | 35 | 0 | 25 | 23 | 33 | 33 | 25 | 0 | 71 | 40 | 10 | 0 | 0 | 88 | 0 | 105 | 0 |  | 0 | 0 | 0 | 90 | 98 | 50 | 19 | 6 | 120 | 0 | 135 | 10 | 310 | 170 | 55 | 91 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 88 | 152 | 0 | 22 | 1.7 | 60 | 52 | 11 | 30 | 100 | 0 | 40 | 76 | 0 | 0 | 17 | 16 | 10 | 265 | 16 | 11 | 0 | 15 | 0 | 0 | 70 | 0 | 0 | 14.05 | 50 | 0 | 0 | 372 | 0 | 0 | 105 | 3.3 | 0 | 0 | 0 | 0 |  | 300 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 198 | 0 | 0 | 173 | 0 | 0 | 0 | 12 | 0 | 185 | 0 | 430 | 17 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 |  | 4838.05 | 1750.8 | 6588.85 | 3305 | 300 | 1862 | 702 | 198 | 111 | 0 | 88 | 22.85 | 0 | 0
15:00 | 35 | 130 | 0 | 0 | 0 | 104 | 0 | 363 | 363 |  | 0 | 430 | 0 | 0 | 0 | 30 | 5 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 0 | 17 | 35 | 0 | 25 | 23 | 33 | 33 | 25 | 0 | 71 | 40 | 30 | 0 | 0 | 133 | 0 | 107 | 0 |  | 0 | 0 | 0 | 80 | 98 | 22 | 19 | 3 | 120 | 0 | 135 | 20 | 285 | 170 | 55 | 83 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 92 | 153 | 0 | 22 | 1.1 | 60 | 52 | 11 | 30 | 130 | 0 | 65 | 76 | 0 | 0 | 17 | 14 | 10 | 310 | 16 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 11.3 | 50 | 0 | 0 | 356 | 0 | 0 | 105 | 2.2 | 0 | 0 | 0 | 0 |  | 298 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 429 | 17 | 0 | 0 | 7 | 0 | 0 | 2.6 | 0 |  | 5102.6 | 1576.6 | 6679.2 | 3248 | 298 | 2059 | 654 | 200 | 111 | 0 | 92 | 17.2 | 0 | 99.28
16:00 | 35 | 128 | 0 | 0 | 0 | 104 | 0 | 347 | 306 |  | 0 | 370 | 0 | 0 | 0 | 30 | 5 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 12 | 0 | 17 | 35 | 19 | 25 | 23 | 33 | 16 | 25 | 0 | 71 | 40 | 30 | 0 | 0 | 228 | 0 | 109 | 0 |  | 0 | 0 | 0 | 80 | 98 | 19 | 19 | 6 | 120 | 0 | 135 | 10 | 305 | 170 | 55 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 84 | 153 | 0 | 22 | 0.4 | 59 | 52 | 11 | 30 | 100 | 0 | 65 | 20 | 0 | 0 | 17 | 11 | 10 | 295 | 24 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 5.61 | 20 | 0 | 0 | 376 | 0 | 0 | 105 | 1 | 0 | 0 | 0 | 0 |  | 298 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 432 | 17 | 0 | 0 | 35 | 0 | 0 | 0.9 | 0 |  | 4938.01 | 1655.9 | 6593.91 | 3357 | 298 | 1844 | 692 | 200 | 111 | 0 | 84 | 7.91 | 0 | 99.27
17:00 | 35 | 130 | 0 | 0 | 0 | 104 | 0 | 370 | 277 |  | 0 | 370 | 0 | 0 | 0 | 30 | 4 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 12 | 0 | 55 | 35 | 19 | 25 | 23 | 33 | 17 | 25 | 0 | 71 | 40 | 50 | 0 | 0 | 230 | 0 | 105 | 0 |  | 0 | 0 | 21 | 90 | 98 | 18 | 19 | 10 | 120 | 0 | 135 | 10 | 285 | 170 | 55 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 92 | 159 | 0 | 22 | 0 | 60 | 52 | 13 | 35 | 100 | 0 | 57 | 20 | 0 | 0 | 17 | 27 | 10 | 290 | 24 | 11 | 0 | 25 | 0 | 0 | 79 | 0 | 0 | 0.2 | 40 | 14 | 50 | 352 | 0 | 50 | 105 | 0 | 0 | 0 | 0 | 0 |  | 297 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 380 | 17 | 0 | 12 | 47 | 70 | 0 | 0.1 | 9 |  | 5137.2 | 1708.1 | 6845.3 | 3340 | 297 | 1788 | 996 | 200 | 111 | 21 | 92 | 0.3 | 0 | 99.27
18:00 | 35 | 128 | 0 | 0 | 0 | 110 | 0 | 355 | 362 |  | 0 | 450 | 0 | 0 | 0 | 30 | 6 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 45 | 0 | 55 | 35 | 19 | 25 | 16 | 33 | 33 | 25 | 0 | 71 | 40 | 50 | 0 | 0 | 229 | 0 | 147 | 0 |  | 0 | 0 | 34 | 90 | 98 | 18 | 19 | 7 | 120 | 0 | 135 | 20 | 345 | 202 | 55 | 90 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 157 | 16 | 22 | 0 | 58 | 52 | 53 | 50 | 130 | 0 | 67 | 76 | 0 | 0 | 17 | 34 | 10 | 305 | 24 | 11 | 0 | 140 | 0 | 0 | 120 | 0 | 0 | 0 | 70 | 65 | 50 | 381 | 0 | 105 | 105 | 0 | 0 | 14 | 0 | 0 |  | 444 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 40 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 432 | 53 | 0 | 98 | 91 | 108 | 0 | 0 | 35 |  | 6100 | 2329 | 8429 | 3608 | 444 | 2167 | 1733 | 200 | 111 | 56 | 110 | 0 | 0 | 99.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 129 | 0 | 0 | 0 | 110 | 0 | 357 | 368 |  | 0 | 450 | 0 | 0 | 0 | 30 | 5 | 0 | 95 | 0 | 0 | 7 | 0 | 0 | 67 | 0 | 47 | 0 | 55 | 35 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 71 | 40 | 100 | 0 | 0 | 229 | 0 | 145 | 0 |  | 0 | 0 | 34 | 100 | 98 | 19 | 19 | 18 | 120 | 0 | 135 | 12 | 320 | 203 | 55 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 161 | 16 | 22 | 0 | 59 | 52 | 53 | 50 | 163 | 0 | 68 | 76 | 0 | 0 | 17 | 35 | 10 | 310 | 24 | 11 | 0 | 165 | 0 | 0 | 170 | 0 | 0 | 0 | 70 | 102 | 80 | 353 | 0 | 105 | 105 | 0 | 0 | 17 | 0 | 0 |  | 444 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 440 | 53 | 0 | 112 | 91 | 113 | 0 | 0 | 35 |  | 6317 | 2391 | 8708 | 3629 | 444 | 2241 | 1917 | 200 | 111 | 56 | 110 | 0 | 0 | 99.26
19:30 | 35 | 129 | 0 | 0 | 0 | 110 | 0 | 351 | 368 |  | 0 | 450 | 0 | 0 | 0 | 15 | 5 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 35 | 35 | 19 | 25 | 23 | 33 | 33 | 16 | 0 | 71 | 40 | 100 | 0 | 0 | 230 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 98 | 19 | 19 | 22 | 120 | 0 | 135 | 40 | 330 | 204 | 55 | 85 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 162 | 0 | 22 | 0 | 59 | 52 | 53 | 50 | 163 | 0 | 67 | 76 | 0 | 0 | 17 | 35 | 10 | 315 | 24 | 11 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 50 | 108 | 80 | 352 | 0 | 52 | 105 | 0 | 0 | 0 | 0 | 0 |  | 444 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 430 | 53 | 0 | 113 | 91 | 105 | 0 | 0 | 0 |  | 6215 | 2313 | 8528 | 3652 | 444 | 2233 | 1764 | 200 | 111 | 14 | 110 | 0 | 0 | 0
20:00 | 35 | 129 | 0 | 0 | 0 | 108 | 0 | 343 | 365 |  | 0 | 450 | 0 | 0 | 0 | 15 | 5 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 0 | 35 | 19 | 25 | 23 | 33 | 33 | 16 | 0 | 71 | 40 | 100 | 0 | 0 | 230 | 0 | 145 | 0 |  | 0 | 0 | 0 | 100 | 98 | 18 | 19 | 26 | 120 | 0 | 135 | 45 | 320 | 205 | 55 | 80 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 145 | 0 | 22 | 0 | 59 | 52 | 53 | 50 | 163 | 0 | 68 | 76 | 0 | 0 | 17 | 35 | 10 | 295 | 24 | 11 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 30 | 108 | 80 | 355 | 0 | 52 | 105 | 0 | 0 | 0 | 0 | 0 |  | 444 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 427 | 53 | 0 | 113 | 91 | 72 | 0 | 0 | 0 |  | 6107 | 2286 | 8393 | 3625 | 444 | 2208 | 1675 | 200 | 111 | 22 | 108 | 0 | 0 | 99.25
21:00 | 35 | 129 | 0 | 0 | 0 | 110 | 0 | 344 | 368 |  | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 24 | 0 | 0 | 17 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 71 | 40 | 100 | 0 | 0 | 229 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 98 | 19 | 19 | 26 | 120 | 0 | 135 | 25 | 325 | 206 | 55 | 80 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 106 | 147 | 0 | 22 | 0 | 59 | 52 | 53 | 50 | 163 | 0 | 68 | 76 | 0 | 0 | 17 | 35 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 79 | 20 | 354 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 445 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 432 | 53 | 0 | 113 | 91 | 37 | 0 | 0 | 0 |  | 5892 | 2245 | 8137 | 3620 | 445 | 2224 | 1405 | 200 | 111 | 26 | 106 | 0 | 0 | 99.25
22:00 | 35 | 126 | 0 | 0 | 0 | 110 | 0 | 340 | 368 |  | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 71 | 40 | 100 | 0 | 0 | 228 | 0 | 145 | 0 |  | 0 | 0 | 0 | 50 | 12 | 0 | 19 | 29 | 120 | 0 | 135 | 75 | 320 | 205 | 55 | 80 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 96 | 147 | 0 | 22 | 0 | 60 | 52 | 53 | 50 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 35 | 10 | 300 | 24 | 11 | 0 | 110 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 445 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 385 | 17 | 0 | 50 | 91 | 0 | 0 | 0 | 0 |  | 5517 | 1991 | 7508 | 3653 | 445 | 2180 | 823 | 200 | 111 | 0 | 96 | 0 | 0 | 99.24
23:00 | 35 | 126 | 0 | 0 | 0 | 110 | 0 | 343 | 368 |  | 0 | 450 | 0 | 0 | 0 | 0 | 9 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 68 | 40 | 100 | 0 | 0 | 228 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 120 | 0 | 135 | 85 | 320 | 204 | 55 | 91 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 88 | 161 | 0 | 22 | 0 | 60 | 52 | 53 | 50 | 130 | 0 | 69 | 40 | 0 | 0 | 17 | 35 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 |  | 241 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 428 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 |  | 5076 | 1740 | 6816 | 3612 | 241 | 2144 | 423 | 200 | 108 | 0 | 88 | 0 | 0 | 99.24
24:00 | 35 | 132 | 0 | 0 | 0 | 110 | 0 | 362 | 367 |  | 0 | 450 | 0 | 0 | 0 | 0 | 22 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 68 | 40 | 100 | 0 | 0 | 229 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 120 | 0 | 130 | 40 | 330 | 205 | 55 | 50 | 37 | 0 | 0 | 42 | 0 | 0 | 0 | 22 | 0 | 8 | 21 | 80 | 161 | 0 | 22 | 0 | 60 | 52 | 5 | 50 | 130 | 0 | 68 | 5 | 0 | 0 | 17 | 35 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4773 | 1596 | 6369 | 3547 | 200 | 2054 | 180 | 200 | 108 | 0 | 80 | 0 | 0 | 99.23
KWH | 864000 | 3424400 | 0 | 0 | 0 | 1988454 | 0 | 8554490 | 7988000 |  | 0 | 9415500 | 0 | 0 | 0 | 250123 | 1925310 | 0 | 1552000 | 0 | 0 | 8640 | 0 | 0 | 865920 | 0 | 318528 | 0 | 255905 | 378165 | 239796 | 600000 | 594360 | 830200 | 749200 | 318276 | 0 | 1305393 | 964000 | 700000 | 0 | 11536 | 3648206 | 0 | 2317568 | 0 |  | 0 | 0 | 73342 | 1188720 | 1063680 | 337440 | 335040 | 666240 | 2787852 | 0 | 3005400 | 1172200 | 7573000 | 4808000 | 802909 | 2026000 | 698400 | 0 | 0 | 670460 | 0 | 0 | 0 | 382788 | 131760 | 557700 | 457040 | 204288 | 3714800 | 40320 | 384804 | 12400 | 1427000 | 1246020 | 509400 | 730008 | 3320091 | 0 | 1416768 | 1154880 | 0 | 0 | 328000 | 443600 | 176220 | 7428950 | 330720 | 158928 | 0 | 966000 | 0 | 0 | 1740000 | 0 | 0 | 57915 | 821760 | 377760 | 337890 | 8513000 | 0 | 319116 | 1517163 | 27600 | 0 | 87968 | 44327 | 0 |  | 6576727 | 0 | 5378400 | 0 | 0 | 0 | 0 | 0 | 66720 | 8720 | 183375 | 1586000 | 412574 | 917760 | 0 | 0 | 0 | 0 | 0 | 0 | 179770 | 0 | 0 | 0 | 0 | 351840 | 260136 | 222372 | 0 | 0 | 4389800 | 0 | 0 | 4895482 | 0 | 0 | 0 | 178931 | 0 | 4921882 | 0 | 9900454 | 529600 | 0 | 536544 | 654196 | 422400 | 0 | 31032 | 92160 |  | 116643637 | 42696875 | 159340512 | 84458886 | 6576727 | 46398647 | 14765042 | 4389800 | 2269393 | 148782 | 204288 | 128947 | 0
Fuel Cost | 967680 | 3698352 | 0 | 0 | 0 | 1928800.38 | 0 | 6159232.8 | 6070880 |  | 0 | 7532400 | 0 | 0 | 0 | 2566261.98 | 2387384.4 | 0 | 1940000 | 0 | 0 | 87782.4 | 0 | 0 | 7879872 | 0 | 2981422.08 | 0 | 2441333.7 | 3766523.4 | 179847 | 450000 | 0 | 0 | 0 | 3049084.08 | 0 | 339402.18 | 250640 | 1071000 | 0 | 110860.96 | 3830616.3 | 0 | 2943311.36 | 0 |  | 0 | 0 | 769357.58 | 12231928.8 | 10115596.8 | 3158438.4 | 308236.8 | 1852147.2 | 2927244.6 | 0 | 3155670 | 867428 | 6361320 | 4423360 | 786850.82 | 2694580 | 572688 | 0 | 0 | 958757.8 | 0 | 0 | 0 | 390443.76 | 98820 | 1054053 | 342780 | 1409587.2 | 3046136 | 383443.2 | 392500.08 | 203360 | 1940720 | 1694587.2 | 692784 | 912510 | 4116912.84 | 0 | 2110984.32 | 2032588.8 | 0 | 0 | 521520 | 519012 | 414117 | 5274554.5 | 248040 | 120785.28 | 0 | 10114020 | 0 | 0 | 16738800 | 0 | 0 | 668339.1 | 7658803.2 | 3543388.8 | 3166029.3 | 8002220 | 0 | 2843323.56 | 14337190.35 | 0 | 0 | 0 | 0 | 0 |  | 17757162.9 | 0 | 4195152 | 0 | 0 | 0 | 0 | 0 | 773952 | 114232 | 1813578.75 | 1268800 | 639489.7 | 9856742.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1864214.9 | 0 | 0 | 0 | 0 | 387024 | 429224.4 | 168335.604 | 0 | 0 | 17954282 | 0 | 0 | 4308024.16 | 0 | 0 | 0 | 284500.29 | 0 | 4331256.16 | 0 | 7227331.42 | 5010016 | 0 | 4925473.92 | 5828886.36 | 3945216 | 0 | 0 | 0 |  | 208808645.31 | 93082894.964 | 301891540.274 | 79173108.824 | 17757162.9 | 42059885.15 | 140418231.34 | 17954282 | 590042.18 | 1657541.58 | 1409587.2 | 871699.1 | 0
Yesterday Day Peak | 35 | 127 | 0 | 0 | 0 | 107 | 0 | 342 | 366 |  | 0 | 430 | 0 | 0 | 0 | 13 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 11 | 0 | 17 | 35 | 19 | 25 | 23 | 33 | 33 | 36 | 0 | 80 | 40 | 0 | 0 | 0 | 70 | 0 | 90 | 0 |  | 0 | 0 | 0 | 90 | 98 | 39 | 19 | 6 | 120 | 0 | 135 | 10 | 310 | 205 | 8 | 88 | 37 | 0 | 0 | 26 | 0 | 0 | 0 | 19 | 8 | 33 | 12 | 82 | 156 | 0 | 22 | 1.7 | 60 | 52 | 11 | 30 | 163 | 0 | 67 | 76 | 0 | 0 | 17 | 12 | 10 | 290 | 24 | 11 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 0 | 100 | 0 | 0 | 354 | 0 | 0 | 105 | 4.5 | 0 | 0 | 0 | 0 |  | 300 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 190 | 0 | 0 | 204 | 0 | 0 | 0 | 11 | 0 | 208 | 0 | 397 | 35 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 6876 | DayPeak
Yesterday Evening Peak | 35 | 129 | 0 | 0 | 0 | 110 | 0 | 357 | 368 | 0 | 0 | 450 | 0 | 0 | 0 | 30 | 5 | 0 | 95 | 0 | 0 | 7 | 0 | 0 | 67 | 0 | 47 | 0 | 55 | 35 | 19 | 25 | 23 | 33 | 33 | 25 | 0 | 71 | 40 | 100 | 0 | 0 | 229 | 0 | 145 | 0 | 0 | 0 | 0 | 34 | 100 | 98 | 19 | 19 | 18 | 120 | 0 | 135 | 12 | 320 | 203 | 55 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 161 | 16 | 22 | 0 | 59 | 52 | 53 | 50 | 163 | 0 | 68 | 76 | 0 | 0 | 17 | 35 | 10 | 310 | 24 | 11 | 0 | 165 | 0 | 0 | 170 | 0 | 0 | 0 | 70 | 102 | 80 | 353 | 0 | 105 | 105 | 0 | 0 | 17 | 0 | 0 |  | 444 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 40 | 0 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 440 | 53 | 0 | 112 | 91 | 113 | 0 | 0 | 35 |  | 8708 | EvPeak
Forecast for Evening | 35 | 190 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 10 | 120 | 0 | 0 | 360 | 360 | 200 | 45 | 0 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 131 | 161 | 95 | 22 | 0 | 60 | 62 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 747 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 26 | 110 | 30 | 0 | 71 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 200 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 150 | 0 | 0 | 0 | 105 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 236 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 5 | 120 | 0 | 0 | 360 | 360 | 200 | 45 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 103 | 160 | 95 | 22 | 1.6 | 60 | 62 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 0 |  | 450 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 70 | 0 | 0 | 71 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 20 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 109 | 0 | 0 | 0 | 30 | 0 | 382 | 366 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 77 | 40 | 100 | 0 | 0 | 204 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 120 | 0 | 0 | 392 | 335 | 206 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 74 | 163 | 0 | 0 | 0.7 | 30 | 40 | 5 | 7 | 100 | 0 | 52 | 5 | 0 | 0 | 0 | 6 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0
199
| Minimum Generation |  | 5243 | 5:00
| Highest Generation |  | 8708 | 19:00
| Day Peak Generation |  | 6876 | 12:00
| Evening Peak Generation |  | 8708 | 19:00
| HVDC Max Flow |  | 445 | 21:00
| HVDC EvPeak Flow |  | 444 | 19:00
| Load factor L.F |  | 76.24%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6876 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5196 | MW
Evening Peak Generation : |  | 8708 | MW Hour : | 19:00 | Available Max Generation : |  | 14273 | MW
E.P. Demand (at gen end) : |  | 8708 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8900 | MW
Maximum Generation : |  | 8708 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5373 | MW
Total Gen. (MKWH) : |  | 159.3405 | System Load Factor : | 76.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -333 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-05
Actual : | 99.17 | Ft.(MSL) , | Rule curve : | 105.64 | Ft.( MSL )
Gas Consumed : | Total = | 1080.28 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 121232993.974
: |  | Coal : | 17954282 | Oil : | 142075772.92 | Total : | 281263048.894
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3147.9419 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1064.6744 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 952.8795 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 860.6401 |  |  | 0 | 0%
) | 0 | 0:00 | 777.9503 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 627.7638 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 358.4783 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 161.8298 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 484.1269 |  |  | 0 | 0%
Total | 0 |  | 8436.2851 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,4
4) Ashuganj unit-4
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Ashuganj Precision
9) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi 230/132 kV T02 transformer was under shut down from 08:46 to 14:56 for A/M.
b) Maniknagar-Matuail 132 kV Ckt was under shut down from 08:33 to 15:45 for A/M.
c) Rampura-Ullon 132 kV Ckt-1 was under shut down from 08:30 to 15:24 for A/M.
d) Kabirpur 132/33 kV T-2 transformer & 33 kV Bus-2 were under shut down from 08:50 to 13:23 for A/M.
e) Jamalpur-Mymensing 132 kV Ckt-1 was under shut down from 09:23 to 16:32 for A/M.
f) Netrokona-Mymensing 132 kV Ckt-1 was under shut down from 09:20 to 17:27 for A/M.
g) Haripur-Sonargaon 132 kV Ckt-2 was under shut down from 09:18 to 13:45 for A/M.
h) Bhulta 400/230 kV ATR-2 transformer was shut down at 09:08 due to oil leakage maintenance.
i) Saidpur-Barapukuria 132 kV Ckt-1 was under shut down from 08:34 to 16:32 for A/M.
j) Khulna(S)-Khulna (C) 132 kV Ckt-2 was under shut down from 08:13 to 15:35 for A/M.
k) Khulna(S)132 kV Capacitor Bank was under shut down from 09:36 to 14:37 for A/M.
l) Sherpur(Mymensingh) 132/33 kV T1 transformer was under shut down from 08:40 to 14:27 for A/M.
m) Bogura-Natore 132 kV Ckt-1 was under shut down from 08:08 to 15:55 for A/M.
n) Baghabari-Ishwardi 230 kV Ckt-2 was under shut down from 08:38 to 16:40 for A/M.
o) Sherpur(Bogura) 132/33 kV T2 transformer was under shut down from 09:33 to 14:38 for A/M.
p) After maintenance Chattogram Raozan unit-1 was synchronized at 13:29.
q) Siddhirganj EGCB 335 MW GT was shut down at 09:03 for combined mode operation and
synchronized at 13:19.
r) After maintenance Bakulia 132/33 kV T3 transformer was switched on at 13:16.
s) After maintenance Kabirpur 132/33 kV T2 transformer was switched on at 13:23.
t) Barapukuria 230/132 kV T02, T06 (Master trip) & 132/33 kV T3(Busbar Protection) tripped at 10:56 |  |  |  |  | About 30 MW power interruption occurred under Barapukuria S/S area
and were switched on at 11:00(T3), 11:02(T02) & 11:04(T06). |  |  |  |  | from 10:56 to 11:02.
u) Barishal(N)-Bhola PP 230 kV Ckt-1&2 tripped at 14:27 showing dist. Protection and were
switched on at 14:53(Ckt-2) & 16:19(Ckt-1).
v) Bhola 225 MW tripped at 14:27 due to Barishal(N)-Bhola PP Ckt trip.
w) Bhola Aggreko tripped at 14:27 due to Barishal(N)-Bhola PP Ckt trip.
x) Ghorashal-Ishwardi 230 kV Ckt was charged from Ishwardi end at 22:00.
y) After maintenance Ashuganj(North) CCPP ST was synchronized at 00:11(05/12/2019).
z) Chandpur GT was shut down at 00:17(05/12/2019) for maintenance at S/S.
aa) Ashuganj unit-5 tripped at 01:31(05/12/2019) due to burner problem.
ab) Cumilla(N)-Chandpur 132 kV Ckt-2 tripped at 07:16(05/12/2019) from both ends showing dist. Z2,
B-phase at Cumilla(N) end & dist. at Chandpur end and was switched on at 07:26(05/12/2019).
ac) Gopalganj-Faridpur 132 kV Ckt-1 was shut down at 07:37(05/12/2019) for A/M.
ad) Kustia 132/33 kV T2 transformer was shut down at 07:09(05/12/2019) for A/M.
ae) Hasnabad 230/132 kV T02 transformer was shut down at 07:29(05/12/2019) for A/M.
af) Uttara 132/33 kV T3 transformer was shut down at 07:35(05/12/2019) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 864000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 129 | 3424400
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 1988454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 357 | 8554490 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 368 | 7988000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9415500
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 250123 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 239796
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 95 | 1552000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 5 | 1925310 | ST synchronizing,
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 8640 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 318528 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 255905
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 378165 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 67 | 865920 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1194360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 830200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 749200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 318276 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 165 | 966000 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 319116
| Dhaka area Total |  |  |  | 5811 | 2218 | 42406383
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 11536 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 57915
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 337440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 111 | 2269393 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 229 | 3648206 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 2317568 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1517163
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 73342 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1188720
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 821760 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 335040
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 666240
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 98 | 1063680 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27600
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 87968 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 44327 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1065 | 15167898
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2787852 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 135 | 3005400
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4808000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 12 | 1172200 | ST Synchronized
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7573000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 698400 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 802909 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 670460 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 337890 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2026000 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 102 | 377760 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 382788
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 131760
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 204288
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 557700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 457040 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1384 | 25993447
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 161 | 3714800 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 384804
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 40320 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 170 | 1740000 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 369 | 5892324
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1427000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 52 | 1246020
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3320091
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 509400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 730008
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 158928
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1416768 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1154880 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 328000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 35 | 443600 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 330720
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7428950 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 353 | 8513000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 176220
| Sylhet Area Total |  |  |  | 1949 | 1281 | 27183585
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 444 | 6576727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 66720 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 2 | 8720 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5378400 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 183375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 529600 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 91 | 654196 | Low demand
| Khulna Area Total |  |  |  | 2314 | 850 | 13397738
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 917760
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 24 | 412574 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 1586000 | Machine tripped
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 178931
| Barisal Area Total |  |  |  | 462 | 134 | 3095265
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 179770
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 204 | 4895482 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 206 | 4921882 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 440 | 9900454 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 351840
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 260136
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 222372
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 112 | 536544
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 92160 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1094 | 21360640
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4389800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 422400
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31032
| Rangpur Area Total |  |  |  | 605 | 313 | 4843232
| Total |  |  |  | 19047 | 8708 | 159340512
| Eastern Grid Total |  |  |  | 13483 | 6317 | 116643637
| Western Grid Total |  |  |  | 5564 | 2391 | 42696875
| National Grid Total |  |  |  | 19047 | 8708 | 159340512
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-04
(a) ENTIRE EASTERN GRID : |  | 5747 | MW | (b) ENTIRE WESTERN GRID : |  | 2495 | MW
i) Dhaka area |  | 3154 | MW | i) Khulna area |  | 970 | MW
ii) Chittagong area |  | 918 | MW | ii) Rajshahi area |  | 812 | MW
iii) Comilla area |  | 708 | MW | iii) Barisal area |  | 210 | MW
iv) Mymensingh area |  | 642 | MW | iv) Rangpur area |  | 503 | MW
v) Sylhet area |  | 325 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8242 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 0.83333 | Srimongal | 26 | 0.75 | Bottail | 100 | 0.75
Munsiganj | 80 | 0.83333 | Shahjibazar | 76 | 0.77083 | G.K Project | 24 | 0.75
Sonargaon | 130 | 0.041667 | Fenchuganj | 24 | 0.75 | Faridpur | 124 | 0.77083
Shyampur | 184 | 0.375 | Kulawara | 31 | 0.75 | Madaripur | 52 | 0.79167
Bhulta | 162 | 0.77083 | Sylhet | 94 | 0.75 | Sariatpur | 38 | 0.8125
Madanganj | 49 | 0.5 | Chatak | 16 | 0.83333 | Gopalganj | 62 | 0.8125
Shitalakhya | 88 | 0.77083 | Sunamganj | 29 | 0.77083 | Bagerhat | 63 | 0.75
Rahim steel | 15 | 0.041667 | Biani Bazar | 32 | 0.75 | Mongla | 34 | 0.33333
Matuail | 82 | 0.5 | Comilla (S) | 110 | 0.75 | Satkhira | 62 | 0.75
Ghorasal | 68 | 0.75 | Comilla(N) | 67 | 0.79167 | Gallamari | 36 | 0.54167
Narsingdi | 103 | 0.83333 | Chandpur | 63 | 0.79167 | Magura | 34 | 0.75
Haripur (SBU) | 86 | 0.58333 | Feni | 87 | 0.75 | Norail | 21 | 0.77083
Ullon | 53 | 0.75 | Chowmuhani | 104 | 0.77083 | Chuadanga | 57 | 0.75
Hasnabad | 143 | 0.79167 | Ashuganj | 36 | 0.8125 | Barisal(N) | 27 | 0.83333
Magbazar | 81 | 0.70833 | Daudkandi | 104 | 0.77083 | Barisal (S) | 68 | 0.875
Maniknagar | 84 | 0.54167 | B.Baria | 86 | 0.79167 | Patuakhali | 75 | 0.875
Bangabhaban | 22 | 0.5 | Ramganj | 54 | 0.83333 | Bhandaria | 36 | 0.83333
Narinda | 80 | 0.54167 | Madunaghat | 43 | 0.54167 | Borhan Uddin | 26 | 0.875
Dhanmondi | 113 | 0.54167 | Hathazari | 67 | 0.79167 | Ishurdi | 43 | 0.75
Lalbag | 58 | 0.54167 | Khulshi | 158 | 0.5 | Ruppur Paromanobik | 1 | 0.041667
Madartek | 46 | 0.83333 | Halishahar | 94 | 0.45833 | Natore | 84 | 0.75
Mirpur | 75 | 0.75 | Baraulia | 131 | 0.125 | Bogra | 130 | 0.83333
Kalyanpur | 72 | 0.75 | Sikalbaha | 27 | 0.75 | Noagaon | 76 | 0.75
Gulshan | 108 | 0.75 | Dohazari | 66 | 0.75 | Rajshahi | 88 | 0.79167
Uttara | 37 | 0.54167 | Cox'sbazar | 68 | 0.79167 | Rajshahi New | 10 | 0.75
Uttara New | 32 | 0.75 | Chandraghona | 22 | 0.75 | C.Nawabganj | 49 | 0.8125
Kamrangirchar | 66 | 0.75 | Kaptai | 3.5 | 0.75 | Amnura | 21 | 0.75
Savar | 100 | 0.5 | A. Khaer Stl. | 5 | 0.33333 | Pabna | 71 | 0.79167
Bhasantec | 116 | 0.75 | Bakulia | 76 | 0.75 | Shahjadpur | 77 | 0.79167
Agargaon | 37 | 0.54167 | Julda | 16 | 0.041667 | Serajganj | 64 | 0.77083
Satmosjid | 73 | 0.54167 | TK chemical | 1.6 | 0.75 | Niyamatpur | 41 | 0.75
Tongi | 128 | 0.75 | Modern Steel | 14 | 0.54167 | Joypurhat | 47 | 0.79167
Kabirpur | 160 | 0.70833 | Shahmirpur | 21 | 0.75 | Sherpur(Bogura) | 26 | 0.75
Basundhara | 84 | 0.45833 | Khagrachhari | 16 | 0.79167 | Mohastangor | 11 | 0.75
Manikganj | 64 | 0.77083 | Matarbari | 20.5 | 0.79167 | Rangpur | 105 | 0.77083
Joydevpur | 180 | 0.75 | Baroiar Hat | 16 | 0.75 | Lalmonirhat | 42 | 0.77083
New Tongi | 96 | 0.41667 | Rangamati | 8 | 0.33333 | Saidpur | 84 | 0.75
Korda | 182 | 0.75 | Abul Khair 230 | 85 | 0.58333 | Purbasadipur | 57 | 0.77083
Dhamrai | 48 | 0.77083 | BSRM | 109 | 0.8125 | Thakurgaon | 34 | 0.083333
Valuka | 82 | 0.75 | GPH Ispat | 5 | 0.66667 | Palashbari | 82 | 0.75
Tangail | 124 | 0.75 | Goalpara | 19 | 0.54167 | Barapukuria | 41 | 0.75
Mymensing | 151 | 0.77083 | Central s/s | 63 | 0.83333 | Panchagar | 23 | 0.29167
Kishorganj | 74 | 0.79167 | Noapara | 48 | 0.75 | Joldhaka | 20 | 0.75
Netrokona | 69 | 0.79167 | Jessore | 80 | 0.75 | Kurigram | 38 | 0.75
Jamalpur | 81 | 0.77083 | Benapol | 26 | 0.75
Sherpur | 68 | 0.75 | Jhenida | 75 | 0.75
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-04 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 389 | 0.083333 | 380 | 0.45833 | Kaliakoir | 373 | 0.16667 | 361 | 0.41667
Bheramara | 411 | 24:00 | 399 | 0.75 | Bhulta | 380 | 0.16667 | 368 | 0.5
Ashuganj(N) | 382 | 0.16667 | 370 | 0.45833
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 0.875 | 228 | 0.041667 | Hathazari | 223 | 0.375 | 213 | 0.45833
Ishurdi | 236 | 0.083333 | 226 | 0.625 | Megnaghat | 224 | 0.16667 | 216 | 0.45833
Ashuganj | 234 | 0.125 | 228 | 0.41667 | Fenchuganj | 235 | 0.16667 | 230 | 0.41667
Serajganj | 233 | 0.20833 | 229 | 0.33333 | Siddhirganj | 223 | 0.16667 | 215 | 0.41667
Baghabari | 240 | 0.125 | 231 | 0.79167 | Maniknagar | 222 | 0.125 | 213 | 0.45833
Barapukuria | 232 | 0.70833 | 226 | 0.33333 | Old Airport | 222 | 0.125 | 213 | 0.45833
Bogra | 232 | 0.16667 | 225 | 0.33333 | Barisal | 239 | 0.95833 | 218 | 0.75
Khulna South | 232 | 0.125 | 216 | 0.77083 | AKSML | 219 | 0.375 | 208 | 0.33333
Rampura | 223 | 0.20833 | 216 | 0.45833 | BSRM | 221 | 0.375 | 212 | 0.45833
Haripur | 222 | 0.20833 | 214 | 0.45833 | Bibiyana | 233 | 0.79167 | 227 | 0.41667
Hasnabad | 220 | 0.70833 | 212 | 0.041667 | Bhulta | 225 | 0.16667 | 216 | 0.45833
Aminbazar | 223 | 0.16667 | 215 | 0.45833 | Ashuganj (S) | 231 | 0.16667 | 224 | 0.625
Tongi | 218 | 0.8125 | 210 | 0.375 | Kaliakoir | 226 | 0.83333 | 214 | 0.41667
Comilla (N) | 228 | 0.041667 | 222 | 0.45833 | GPH | 220 | 0.375 | 206 | 0.45833
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 0.20833 | 130 | 0.41667 | Halishahar | 136 | 0.375 | 123 | 0.33333
Munsiganj | 133 | 0.25 | 129 | 0.5 | Baraulia | 132 | 0.375 | 123 | 0.33333
Sonargaon | 130 | 0.041667 | 129 | 0.41667 | Sikalbaha | 132 | 0.375 | 123 | 0.33333
Shyampur | 134 | 0.041667 | 129 | 0.41667 | Dohazari | 136 | 0.375 | 123 | 0.33333
Bhulta | 127 | 0.041667 | 124 | 0.41667 | Cox'sbazar | 130 | 0.375 | 124 | 0.083333
Madanganj | 136 | 0.125 | 127 | 0.45833 | Chandraghona | 134 | 0.375 | 126 | 0.33333
Shitalakhya | 137 | 0.125 | 128 | 0.41667 | Kaptai | 133 | 0.70833 | 126 | 0.33333
Rahim steal | 135 | 0.20833 | 130 | 0.45833 | A. Khaer Stl. | 130 | 0.5 | 126 | 0.16667
Matuail | 134 | 0.125 | 128 | 0.5 | Bakulia | 132 | 0.375 | 126 | 0.29167
Ghorasal | 135 | 0.041667 | 134 | 0.625 | Julda | 133 | 0.5 | 127 | 0.33333
Narsinghdi | 133 | 0.083333 | 130 | 0.75 | TK Chemical | 136 | 0.375 | 121 | 0.33333
Haripur (SBU) | 136 | 0.20833 | 131 | 0.41667 | Modern Steel | 133 | 0.375 | 121 | 0.45833
Ullon | 134 | 0.25 | 126 | 0.5 | Shahmirpur | 135 | 0.375 | 122 | 0.33333
Hasnabad | 136 | 0.25 | 128 | 0.45833 | Khagrachhari | 134 | 0.375 | 124 | 0.33333
Magbazar | 134 | 0.25 | 127 | 0.5 | Matarbari | 135 | 0.33333 | 125 | 0.45833
Maniknagar | 136 | 0.25 | 130 | 0.45833 | Baroiar Hat | 132 | 0.77083 | 126 | 0.33333
Bangabhaban | 137 | 0.29167 | 131 | 0.5 | Rangamati | 134 | 0.375 | 121 | 0.33333
Narinda | 138 | 0.33333 | 132 | 0.54167 | Goalpara | 136 | 0.083333 | 126 | 0.75
Dhanmondi | 134 | 0.25 | 126 | 0.5 | Central s/s | 134 | 0.083333 | 125 | 0.77083
Lalbag | 135 | 0.25 | 128 | 0.45833 | Noapara | 131 | 0.20833 | 120 | 0.75
Madartek | 133 | 0.25 | 126 | 0.5 | Jessore | 128 | 0.083333 | 122 | 0.75
Mirpur | 135 | 0.29167 | 130 | 0.5 | Benapol | 131 | 0.25 | 123 | 0.75
Kalyanpur | 138 | 0.20833 | 132 | 0.5 | Jhenida | 133 | 0.125 | 120 | 0.75
Gulshan | 133 | 0.20833 | 126 | 0.45833 | Bottail | 135 | 0.083333 | 126 | 0.75
Uttara | 133 | 0.20833 | 124 | 0.41667 | G.K Project | 138 | 0.125 | 131 | 0.77083
Uttara New | 135 | 0.083333 | 129 | 0.41667 | Faridpur | 135 | 0.125 | 125 | 0.77083
Kamrangirchar | 135 | 0.125 | 126 | 0.45833 | Madaripur | 134 | 0.25 | 127 | 0.77083
Savar | 135 | 0.125 | 130 | 0.41667 | Sariatpur | 135 | 0.125 | 126 | 0.77083
Bhasantec | 134 | 0.083333 | 128 | 0.5 | Gopalganj | 141 | 0.875 | 132 | 0.5
Agargaon | 135 | 0.083333 | 129 | 0.45833 | Bagerhat | 134 | 0.16667 | 121 | 0.77083
Satmosjid | 134 | 0.083333 | 129 | 0.41667 | Mongla | 131 | 0.16667 | 124 | 0.75
Tongi | 134 | 0.125 | 127 | 9.:00 | Satkhira | 134 | 0.16667 | 124 | 0.75
Kabirpur | 132 | 0.875 | 127 | 0.41667 | Gallamari | 135 | 0.125 | 127 | 0.75
Basundhara | 132 | 0.91667 | 125 | 0.58333 | Magura | 134 | 0.083333 | 121 | 0.77083
Manikganj | 137 | 0.79167 | 128 | 0.41667 | Norail | 133 | 0.16667 | 117 | 0.77083
Joydevpur | 134 | 0.125 | 130 | 0.66667 | Chuadanga | 130 | 0.083333 | 116 | 0.75
New Tongi | 133 | 0.79167 | 125 | 0.41667 | Barisal(N) | 138 | 0.125 | 129 | 0.75
Kodda | 133 | 0.54167 | 124 | 0.45833 | Barisal (S) | 137 | 0.125 | 132 | 0.70833
Dhamrai | 132 | 0.16667 | 126 | 0.45833 | Patuakhali | 135 | 0.041667 | 130 | 0.45833
Valuka | 130 | 0.91667 | 124 | 0.54167 | Bhandaria | 135 | 0.083333 | 127 | 0.75
Tangail | 132 | 0.91667 | 127 | 0.33333 | Ishurdi | 135 | 0.20833 | 129 | 0.33333
Mymensing | 132 | 0.70833 | 126 | 0.33333 | Ruppur Paromanobik | 135 | 0.041667 | 129 | 0.77083
Kishorganj | 133 | 0.125 | 128 | 0.54167 | Natore | 134 | 0.041667 | 128 | 0.625
Netrokona | 131 | 0.91667 | 125 | 0.66667 | Bogra | 136 | 0.16667 | 130 | 0.33333
Jamalpur | 137 | 0.91667 | 125 | 0.29167 | Noagaon | 134 | 0.16667 | 128 | 0.33333
Sherpur | 136 | 0.875 | 123 | 0.33333 | Rajshahi | 132 | 0.041667 | 124 | 0.5
Srimongal | 137 | 0.083333 | 135 | 0.75 | Rajshahi New | 133 | 0.20833 | 122 | 0.5
Shahjibazar | 136 | 0.375 | 134 | 0.041667 | C.Nawabganj | 130 | 0.79167 | 120 | 0.33333
Fenchuganj | 137 | 0.375 | 132 | 0.66667 | Amnura | 130 | 0.083333 | 122 | 0.45833
Khulawara | 137 | 0.375 | 133 | 0.66667 | Pabna | 136 | 0.125 | 129 | 0.5
Sylhet | 135 | 0.375 | 131 | 0.66667 | Shahjadpur | 142 | 0.041667 | 137 | 0.625
Chatak | 135 | 0.375 | 131 | 0.625 | Serajganj | 138 | 0.041667 | 131 | 0.29167
Sunamganj | 135 | 0.91667 | 131 | 0.66667 | Niyamatpur | 134 | 0.083333 | 126 | 0.33333
Biani Bazar | 135 | 0.33333 | 131 | 0.70833 | Joypurhat | 135 | 0.041667 | 125 | 0.33333
Comilla(s) | 131 | 0.041667 | 125 | 0.70833 | Sherpur(Bogura) | 137 | 0.041667 | 131 | 0.29167
Comilla(n) | 136 | 0.29167 | 134 | 0.375 | Mohastangor | 136 | 0.70833 | 129 | 0.33333
Chandpur | 135 | 0.75 | 130 | 0.58333 | Rangpur | 131 | 0.70833 | 116 | 0.45833
Feni | 131 | 0.375 | 126 | 0.41667 | Lalmonirhat | 127 | 0.70833 | 115 | 0.45833
Chowmuhani | 130 | 0.70833 | 125 | 0.875 | Saidpur | 130 | 0.70833 | 110 | 0.45833
Ashuganj | 135 | 0.041667 | 133 | 0.66667 | Purbasadipur | 125 | 0.70833 | 116 | 0.45833
Daudkandi | 132 | 0.91667 | 129 | 0.41667 | Thakurgaon | 123 | 0.16667 | 118 | 0.33333
B.Baria | 134 | 0.041667 | 131 | 0.75 | Palashbari | 134 | 0.16667 | 126 | 0.625
Ramganj | 128 | 0.95833 | 126 | 0.66667 | Barapukuria | 132 | 0.70833 | 126 | 0.33333
Madanhat | 135 | 0.375 | 129 | 0.45833 | Panchagar | 123 | 0.125 | 100 | 0.45833
Hathazari | 133 | 0.375 | 128 | 0.45833 | Joldhaka | 129 | 0.20833 | 107 | 0.45833
Khulshi | 132 | 0.375 | 124 | 0.45833 | Kurigram | 131 | 0.70833 | 123 | 0.33333
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-12-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 220 | 4773 | 1596 | 6369 |  |  |  | QF-LDC-12
0:30 | 217.5 | 4582 | 1529.5 | 6111.5 | Date: | 2019-12-04
1:00 | 215 | 4391 | 1463 | 5854
1:30 | 192.5 | 4262 | 1453 | 5715
2:00 | 170 | 4133 | 1443 | 5576
2:30 | 160 | 4042.5 | 1441.5 | 5484 | [5 empty] | Gen. at Eve. Peak | 8708 | 8708 MW (19:00 )
3:00 | 150 | 3952 | 1440 | 5392 | [6 empty] | 19:00
3:30 | 120 | 3936.5 | 1417 | 5353.5 | [5 empty] | Gen. at Day Peak | 6876 | 6876 MW (12:00 )
4:00 | 90 | 3921 | 1394 | 5315 | [6 empty] | 12:00
4:30 | 75 | 3873 | 1406 | 5279 | [5 empty] | Highest Generation | 8708
5:00 | 60 | 3825 | 1418 | 5243 | [6 empty] | 19:00
5:30 | 37.5 | 3820 | 1506 | 5326
6:00 | 15 | 3815 | 1594 | 5409
6:30 | 99.5 | 4007.5 | 1601.05 | 5608.55
7:00 | 184 | 4200 | 1608.1 | 5808.1
7:30 | 208 | 4184.9 | 1623.65 | 5808.55
8:00 | 232 | 4169.8 | 1639.2 | 5809
8:30 | 135.5 | 4303.8 | 1692 | 5995.8
9:00 | 39 | 4437.8 | 1744.8 | 6182.6
9:30 | 123.5 | 4478.25 | 1764.45 | 6242.7
10:00 | 208 | 4518.7 | 1784.1 | 6302.8
10:30 | 184.5 | 4630.5 | 1811.1 | 6441.6
11:00 | 161 | 4742.3 | 1838.1 | 6580.4
11:30 | 89 | 4897.75 | 1830.45 | 6728.2
12:00 | 17 | 5053.2 | 1822.8 | 6876
12:30 | 62 | 5110.05 | 1803.85 | 6913.9
13:00 | 107 | 5166.9 | 1784.9 | 6951.8
13:30 | 89 | 5002.475 | 1767.85 | 6770.325
14:00 | 71 | 4838.05 | 1750.8 | 6588.85
14:30 | 52 | 4970.325 | 1663.7 | 6634.025
15:00 | 33 | 5102.6 | 1576.6 | 6679.2
15:30 | 21.5 | 5020.305 | 1616.25 | 6636.555
16:00 | 10 | 4938.01 | 1655.9 | 6593.91
16:30 | 25 | 5037.605 | 1682 | 6719.605
17:00 | 40 | 5137.2 | 1708.1 | 6845.3
17:30 | 139.5 | 5618.6 | 2018.55 | 7637.15
18:00 | 239 | 6100 | 2329 | 8429
18:30 | 264.5 | 6208.5 | 2360 | 8568.5
19:00 | 290 | 6317 | 2391 | 8708
19:30 | 333 | 6215 | 2313 | 8528
20:00 | 311 | 6107 | 2286 | 8393 |  |  |  | Executive Engineer
20:30 | 268.5 | 5999.5 | 2265.5 | 8265 |  |  |  | Network Operation Division
21:00 | 226 | 5892 | 2245 | 8137
21:30 | 218.5 | 5704.5 | 2118 | 7822.5
22:00 | 211 | 5517 | 1991 | 7508 |  |  |  |  | Page 6 of 7
22:30 | 220.5 | 5296.5 | 1865.5 | 7162
23:00 | 230 | 5076 | 1740 | 6816
23:30 | 225 | 4924.5 | 1668 | 6592.5
24:00 | 220 | 4773 | 1596 | 6369
8708 MW (19:00 )
6876 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-04 |  | Energy | 159340512
[10 empty] | 2019-12-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3547 | 200 | 2054 | 423 | 200 | 108 | 0 | 0 | 80
0:30 | 3586.5 | 170.5 | 1905 | 211.5 | 180 | 101.5 | 0 | 0 | 78 | Date: | 2019-12-04
1:00 | 3626 | 141 | 1756 | 0 | 160 | 95 | 0 | 0 | 76
1:30 | 3576.5 | 141 | 1668.5 | 0 | 160 | 95 | 0 | 0 | 74 | [7 empty] | Total Energy | 159.3405 | Total Energy Gen 159.341 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.341 MKWHr
2:00 | 3527 | 141 | 1581 | 0 | 160 | 95 | 0 | 0 | 72 | [7 empty] | Energy not Served | 0
2:30 | 3495.5 | 141 | 1520 | 0 | 160 | 95.5 | 0 | 0 | 72 | [7 empty] | Energy Requirement | 159.3405
3:00 | 3464 | 141 | 1459 | 0 | 160 | 96 | 0 | 0 | 72
3:30 | 3450.5 | 141 | 1435 | 0 | 160 | 96 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3437 | 141 | 1411 | 0 | 160 | 96 | 0 | 0 | 70
4:30 | 3380 | 141 | 1433 | 0 | 160 | 96 | 0 | 0 | 69
5:00 | 3323 | 141 | 1455 | 0 | 160 | 96 | 0 | 0 | 68
5:30 | 3332 | 141 | 1528 | 0 | 160 | 96 | 0 | 0 | 69
6:00 | 3341 | 141 | 1601 | 0 | 160 | 96 | 0 | 0 | 70
6:30 | 3476 | 141 | 1664 | 0 | 160 | 96 | 0 | 0 | 70 |  |  |  |  | Coal
7:00 | 3611 | 141 | 1727 | 0 | 160 | 96 | 0 | 0 | 70
7:30 | 3551.5 | 141 | 1825.5 | 3.5 | 160 | 48 | 0 | 0 | 72 |  |  |  | Oil |  |  |  | ,
8:00 | 3492 | 141 | 1924 | 7 | 160 | 0 | 0 | 0 | 74
8:30 | 3416.5 | 220 | 1894 | 174 | 160 | 40 | 0 | 0 | 76
9:00 | 3341 | 299 | 1864 | 341 | 160 | 80 | 0 | 0 | 78
9:30 | 3334 | 299.5 | 1886.5 | 389 | 160 | 81 | 0 | 0 | 78
10:00 | 3327 | 300 | 1909 | 437 | 160 | 82 | 0 | 0 | 78
10:30 | 3341 | 300 | 1953.5 | 515.5 | 160 | 81 | 0 | 0 | 80
11:00 | 3355 | 300 | 1998 | 594 | 160 | 80 | 0 | 0 | 82
11:30 | 3395.5 | 300 | 1995 | 669.5 | 175 | 100 | 0 | 0 | 82
12:00 | 3436 | 300 | 1992 | 745 | 190 | 120 | 0 | 0 | 82
12:30 | 3447.5 | 300 | 2005.5 | 762 | 190 | 115 | 0 | 0 | 83
13:00 | 3459 | 300 | 2019 | 779 | 190 | 110 | 0 | 0 | 84
13:30 | 3459 | 300 | 2019 | 779 | 190 | 110 | 0 | 0 | 84
14:00 | 3459 | 300 | 2019 | 779 | 190 | 110 | 0 | 0 | 84
14:30 | 3353.5 | 299 | 2039 | 716.5 | 195 | 110.5 | 0 | 0 | 88
15:00 | 3248 | 298 | 2059 | 654 | 200 | 111 | 0 | 0 | 92
15:30 | 3302.5 | 298 | 1951.5 | 673 | 200 | 111 | 0 | 0 | 88
16:00 | 3357 | 298 | 1844 | 692 | 200 | 111 | 0 | 0 | 84
16:30 | 3348.5 | 297.5 | 1816 | 844 | 200 | 111 | 10.5 | 0 | 88
17:00 | 3340 | 297 | 1788 | 996 | 200 | 111 | 21 | 0 | 92
17:30 | 3474 | 370.5 | 1977.5 | 1364.5 | 200 | 111 | 38.5 | 0 | 101
18:00 | 3608 | 444 | 2167 | 1733 | 200 | 111 | 56 | 0 | 110
18:30 | 3618.5 | 444 | 2204 | 1825 | 200 | 111 | 56 | 0 | 110
19:00 | 3629 | 444 | 2241 | 1917 | 200 | 111 | 56 | 0 | 110
19:30 | 3652 | 444 | 2233 | 1764 | 200 | 111 | 14 | 0 | 110
20:00 | 3625 | 444 | 2208 | 1675 | 200 | 111 | 22 | 0 | 108
20:30 | 3622.5 | 444.5 | 2216 | 1540 | 200 | 111 | 24 | 0 | 107
21:00 | 3620 | 445 | 2224 | 1405 | 200 | 111 | 26 | 0 | 106
21:30 | 3636.5 | 445 | 2202 | 1114 | 200 | 111 | 13 | 0 | 101
22:00 | 3653 | 445 | 2180 | 823 | 200 | 111 | 0 | 0 | 96
22:30 | 3632.5 | 343 | 2162 | 623 | 200 | 109.5 | 0 | 0 | 92
23:00 | 3612 | 241 | 2144 | 423 | 200 | 108 | 0 | 0 | 88
23:30 | 3579.5 | 220.5 | 2099 | 423 | 200 | 108 | 0 | 0 | 84 | Max Temp. in Dhaka |  | 27.3° C
24:00 | 3547 | 200 | 2054 | 423 | 200 | 108 | 0 | 0 | 80
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 159.341 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.341 MKWHr
Note on W13: Author:

## Generation
2019-12-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 0 | 40 | 42 | 40 | 80 | 70 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 68 | 68 | 1305393
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | [13 empty] | 10 | 30 | 30 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 2 | 9 | [15 empty] | 0 | 11536
| Teknaf 20MW PP (Solartech) | [6 empty] | 2.7 | 8 | 13.6 | 0 |  |  |  | 14.05 | 11.3 | 5.61 | 0.2 | [9 empty] | 57915
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 182 | 190 | 202 | 213 | 0 |  |  |  | 70 | 80 | 88 | 133 | 228 | 230 | 229 |  | 229 | 230 | 230 | 229 | 228 | 228 | 229 | 3648206
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 104 | 104 | 104 | 104 | 104 | 115 | 0 |  |  |  | 90 | 144 | 105 | 107 | 109 | 105 | 147 |  | 145 | 144 | 145 | 144 | 145 | 145 | 145 | 2317568
10 | Sikalbaha 150MW GTPP(Oil) | [14 empty] | 0
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 21 | 34 |  | 34 | 0 | 0 |  |  |  |  | 73342
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 22 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 68 | 0 | 1517163
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 42 | 42 | 42 | 42 | 42 | 60 | 60 | 60 | 37 | 65 | 65 | 60 | 57 | 40 | 62 | 40 | 37 | 100 |  | 95 | 100 | 100 | 100 | 90 | 42 | 70 | 1552000
17 | Siddhirganj 335 MW CCPP | 238 | 180 | 140 | 140 | 140 | 180 | 240 | 239 | 42 | 0 | 0 |  |  | 2 | 5 | 5 | 4 | 6 |  | 5 | 5 | 5 | 5 | 5 | 9 | 22 | 1925310
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 1 | 14 | 14 | 14 | 14 | 15 | 14 | 14 | 25 | 140 |  | 165 | 200 | 200 | 200 | 110 | 0 | 0 | 966000
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 802909
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 864000
21 | Ghorasal Repowered CCPP Unit-3 | 189 | 188 | 139 | 124 | 124 | 124 | 130 | 135 | 129 | 129 | 129 | 127 | 127 | 129 | 130 | 128 | 130 | 128 |  | 129 | 129 | 129 | 129 | 126 | 126 | 132 | 3424400
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 120 | 120 | 120 | 80 | 80 | 80 | 80 | 80 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2787852
29 | Ashuganj TPP Unit- 4 | [14 empty] | 0
30 | Ashuganj TPP Unit- 5 | 135 | 135 | 135 | 115 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 130 | 3005400
32 | Ashuganj 50 MW PP | 37 | 37 | 5 | 5 | 5 | 5 | 5 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 33 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 698400
33 | Ashuganj 225 MW CCPP | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 205 | 205 | 205 | 201 | 170 | 170 | 170 | 170 | 202 |  | 203 | 204 | 205 | 206 | 205 | 204 | 205 | 4808000
34 | Ashuganj 450 MW CCPP(South) | 320 | 265 | 265 | 265 | 290 | 275 | 345 | 345 | 320 | 320 | 360 | 310 | 310 | 310 | 285 | 305 | 285 | 345 |  | 320 | 330 | 320 | 325 | 320 | 320 | 330 | 7573000
| Ashuganj 450 MW CCPP(North) |  | 40 | 135 | 265 | 110 | 20 | 20 | 20 | 20 | 12 | 14 | 10 | 10 | 10 | 20 | 10 | 10 | 20 |  | 12 | 40 | 45 | 25 | 75 | 85 | 40 | 1172200
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 89 | 87 | 85 | 80 | 90 | 80 | 89 | 81 | 88 | 80 | 91 | 83 | 90 | 80 | 90 |  | 80 | 85 | 80 | 80 | 80 | 91 | 50 | 2026000
37 | Tongi 80 MW GTPP | [14 empty] | 0
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 348 | 350 | 348 | 346 | 352 | 356 | 360 | 355 | 345 | 343 | 353 | 342 | 343 | 345 | 363 | 347 | 370 | 355 |  | 357 | 351 | 343 | 344 | 340 | 343 | 362 | 8554490
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 320 | 320 | 320 | 320 | 350 | 380 | 420 | 400 | 400 | 430 | 430 | 430 | 340 | 430 | 370 | 370 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9415500
41 | Haripur 360MW CCPP(HPL) | 324 | 274 | 234 | 234 | 254 | 303 | 364 | 364 | 369 | 368 | 365 | 366 | 365 | 307 | 363 | 306 | 277 | 362 |  | 368 | 368 | 365 | 368 | 368 | 368 | 367 | 7988000
42 | RPCL 210MW CCPP | 163 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 163 | 163 | 157 | 156 | 156 | 152 | 153 | 153 | 159 | 157 |  | 161 | 162 | 145 | 147 | 147 | 161 | 161 | 3714800
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 58 |  | 59 | 59 | 59 | 59 | 60 | 60 | 60 | 1427000
45 | Fenchugonj CCPP Phase-2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1246020
46 | Shajibazar 330 MW CCPP | [14 empty] | 0
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 70 | 70 | 69 | 66 | 65 | 67 | 66 | 40 | 65 | 65 | 57 | 67 |  | 68 | 67 | 68 | 68 | 69 | 69 | 68 | 1416768
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 76 | 74 | 74 | 76 | 76 | 76 | 76 | 20 | 20 | 76 |  | 76 | 76 | 76 | 76 | 76 | 40 | 5 | 1154880
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 328000
52 | Sylhet 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 30 | 12 | 12 | 12 | 12 | 12 | 16 | 14 | 11 | 27 | 34 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 443600
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 176220
54 | Hobiganj 11MW PP Cofidence-E | [8 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  | 0 | 158928
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 47 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 13 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 5 | 509400
56 | Shahjahanulla 25 MW PP | [8 empty] | 24 | 24 | 16 | 24 | 24 | 16 | 16 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 330720
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 280 | 295 | 295 | 300 | 315 | 300 | 280 | 290 | 310 | 290 | 280 | 265 | 310 | 295 | 290 | 305 |  | 310 | 315 | 295 | 300 | 300 | 290 | 310 | 7428950
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 |  |  | 0 | 378165
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 |  |  |  |  | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 335040
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 |  | 0 | 239796
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 384804
63 | Impoprt (Tripura) | 76 | 72 | 72 | 70 | 68 | 70 | 70 | 74 | 78 | 78 | 82 | 82 | 84 | 88 | 92 | 84 | 92 | 110 |  | 110 | 110 | 108 | 106 | 96 | 88 | 80 | 204288
64 | Malancha, Ctg. EPZ (United) | 32 | 26 | 33 | 14 | 6 | 9 | 9 | 11 | 7 | 11 | 3 | 6 | 10 | 6 | 3 | 6 | 10 | 7 |  | 18 | 22 | 26 | 26 | 29 | 31 | 15 | 666240
65 | Feni 22MW PP (Doreen) | 22 | [5 empty] | 13 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 382788
66 | Feni 11 MW PP (Doreen) | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 131760
67 | Jangalia 33MW PP (Summit) | [7 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 557700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 12 | 12 | 12 | 12 | 17 | 17 | 17 | 15 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 457040
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 29 | 29 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 16 |  | 23 | 23 | 23 | 31 | 31 | 31 | 31 | 594360
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 830200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 749200
73 | Ghorashal 108MW PP (Regent) | 109 | 52 | 12 | 12 | 12 | 12 | 31 | 83 | 100 | 104 | 104 | 107 | 107 | 110 | 104 | 104 | 104 | 110 |  | 110 | 110 | 108 | 110 | 110 | 110 | 110 | 1988454
| Feni Lanka Power | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [8 empty] | 4 | 16 | 16 | 36 | 42 | 25 | 25 | 25 | 25 | 25 |  | 25 | 16 | 16 | 8 | 0 |  | 0 | 318276
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 0 | 16 |  | 16 | 0 | 0 |  |  |  |  | 40320
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [16 empty] | 50 | 105 |  | 105 | 52 | 52 | 17 | 0 |  | 0 | 319116
| Kaptai 7 MW Solar PP | [6 empty] | 0.2 | 1.2 | 1.9 | 3.9 | 4.3 | 4.5 | 4.1 | 3.3 | 2.2 | 1 | 0 | 0 | [8 empty] | 27600
| Jodiac Power | [8 empty] | 11 | [7 empty] | 0 | 14 |  | 17 | [5 empty] | 0 | 87968
| Karnaphuli Power Ltd. | [8 empty] | 14 | [16 empty] | 0 | 44327
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL)
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 90 | 80 | 90 | 90 | 90 | 90 | 80 | 80 | 90 | 90 |  | 100 | 100 | 100 | 100 | 50 | 0 | 0 | 1188720
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 10 | 10 | 15 | 30 | 30 | 30 | 30 | 30 | 35 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 730008
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 35 | 35 | 35 | 26 | 26 | 43 | 43 | 43 | 43 | 35 |  | 43 | 35 | 35 | 35 | 35 | 35 | 42 | 670460
94 | Gagnagar 102 MW PP (Digital Power) | [14 empty] | 0 |  |  | 0 |  | 7 | 0 | 0 |  |  |  |  | 8640
95 | Patenga 50MW PP (Baraka) | [8 empty] | 14 | 19 | 19 | 39 | 50 | 50 | 22 | 19 | 18 | 18 |  | 19 | 19 | 18 | 19 |  |  | 0 | 337440
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 7 | 44 | 98 | 98 | 98 | 98 | 98 | 98 | 98 |  | 98 | 98 | 98 | 98 | 12 |  | 0 | 1063680
97 | Katpotti 52 MW PP (Sinha) | [8 empty] | 5 | 6 | 6 | 11 | 12 | 12 | 12 | 12 | 12 | 45 |  | 47 | 47 | 47 | 24 | 12 |  | 0 | 318528
98 | Bosila 108MW PP(CLC) | [8 empty] | 28 | 38 | 60 | 66 | 67 | 72 | 72 | 67 | 67 | 67 |  | 67 | 72 | 72 | 72 | 72 | 14 | 0 | 865920
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 0 | 13 | 28 | 30 | 30 | 30 | 30 | 30 |  | 30 | 15 | 15 | 0 |  |  |  | 250123
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 |  | 55 | 35 |  |  |  |  | 0 | 255905
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 100 | 100 | 130 | 130 | 130 | 130 | 100 | 100 | 130 | 163 | 163 | 100 | 130 | 100 | 100 | 130 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3320091
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.6 | 1.3 | 1.8 | 2 | 1.7 | 1.8 | 1.7 | 1.1 | 0.4 | 0 | 0 | [8 empty] | 12400
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 7 | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 79 | 120 |  | 170 | 170 | 170 | 170 | 170 | 140 | 70 | 1740000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [8 empty] | 100 | 70 | 100 | 100 | 100 | 50 | 50 | 20 | 40 | 70 |  | 70 | 50 | 30 | 0 |  |  |  | 821760
116 | Chandpur 200MW (Desh energy) | [16 empty] | 14 | 65 |  | 102 | 108 | 108 | 79 | 0 | 0 |  | 377760
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 50 | 50 |  | 80 | 80 | 80 | 20 |  |  | 0 | 337890
118 | Bibiyana-III 400 MW CCPP | 348 | 350 | 349 | 292 | 316 | 249 | 286 | 369 | 354 | 354 | 351 | 354 | 353 | 372 | 356 | 376 | 352 | 381 |  | 353 | 352 | 355 | 354 | 355 | 351 | 355 | 8513000
| Jamalpur 115 MW PP (United) | [25 empty] | 0 | 0
| Anwara 300 MW PP (United) | [19 empty] | 0 | [5 empty] | 0 | 0
120 | Eastern Zone Total | 4391 | 4133 | 3952 | 3921 | 3825 | 3815 | 4200 | 4169.8 | 4437.8 | 4518.7 | 4742.3 | 5053.2 | 5166.9 | 4838.05 | 5102.6 | 4938.01 | 5137.2 | 6100 |  | 6317 | 6215 | 6107 | 5892 | 5517 | 5076 | 4773 | 116643637
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 15 |  | 20 | 14 | 22 | 26 | 0 |  |  | 66720
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [9 empty] | 3 | 28 | 35 | 35 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 17 | 0 |  | 529600
130
131
132
133
| Barisal 110 MW PP (Summit ) | [10 empty] | 8 | 16 | 16 | 16 | 0 | 48 | 48 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 917760
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 0 | [11 empty] | 178931
| Bhola 225 MW CCPP | 172 | 153 | 157 | 154 | 177 | 177 | 177 | 177 | 154 | 177 | 177 | 160 | 154 | 177 | 0 | [11 empty] | 1586000
140 | Bhola 33 MW PP (Venture) | 20 | 20 | 19 | 19 | 13 | 14 | 13 | 12 | 11 | 10 | 11 | 14 | 16 | 16 | 16 | 16 | 18 | 22 |  | 24 | 25 | 24 | 25 | 25 | 23 | 22 | 412574
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 24 | 0 |  | 183375
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 7 |  | 2 | 0 | [5 empty] | 8720
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [14 empty] | 7 | 35 | 47 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 0 | 654196
146 | Bheramara HVDC | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 299 | 300 | 300 | 300 | 300 | 300 | 298 | 298 | 297 | 444 |  | 444 | 444 | 444 | 445 | 445 | 241 | 200 | 6576727
147 | Bheramara 360 MW CCPP | 170 | 185 | 170 | 170 | 170 | 280 | 285 | 295 | 285 | 285 | 235 | 240 | 235 | 180 | 180 | 180 | 180 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5378400
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 190 | 190 | 198 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4389800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 174 | 173 | 174 | 175 | 174 | 177 | 185 | 201 | 195 | 167 | 214 | 204 | 194 | 173 | 205 | 206 | 200 | 196 |  | 204 | 195 | 195 | 196 | 205 | 203 | 205 | 4895482
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 189 | 188 | 188 | 188 | 192 | 194 | 188 | 193 | 202 | 212 | 208 | 204 | 185 | 179 | 180 | 186 | 181 |  | 206 | 196 | 198 | 198 | 192 | 197 | 200 | 4921882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 408 | 396 | 405 | 362 | 370 | 428 | 429 | 430 | 388 | 418 | 432 | 397 | 381 | 430 | 429 | 432 | 380 | 432 |  | 440 | 430 | 427 | 432 | 385 | 428 | 431 | 9900454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 3 | 351840
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 10 | 14 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 260136
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 222372
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 32 | 0 |  |  | 179770
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 12 | 98 |  | 112 | 113 | 113 | 113 | 50 | 0 | 0 | 536544
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 9 | 35 |  | 35 | 0 | 0 | 0 |  |  |  | 92160
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 70 | 108 |  | 113 | 105 | 72 | 37 | 0 |  |  | 422400
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 1.2 | 2.8 | 4.1 | 5.1 | 4.8 | 4.9 | 3.8 | 2.6 | 0.9 | 0.1 | 0 |  | 0 | [6 empty] | 31032
178
178